## Cover
Interconnector Availability Model GHD 4.0 |  |  | To provide an open and transparent methodology to enable the availability target to be set for interconnector projects for the Ofgem Cap and Floor regime.
Model purpose:
Colour Coding / Model Key
General - Throughout Model
| Input [Project] | User Input Data
| Calculations | Figures that are a intermediate calculation rather than a final ouput
| Output | Output of worksheet
| Constant | Constant used in calculation.
| 1 | Colour scale is used to highlight the difference between a range a values. It is active "conditional formatting" rather than something the modeller has written in
2
3
4
5
Worktab Key
| Admin | Administrative pages that do not form a functional part of the model
| Input [Project] | Data specific to interconnector project currently being assessed
| Input [Component Data] | Data specific to component. Is not necessarily changed with project, but can be updated by advanced users
Cell Key
| Calcs | Figures that are a intermediate calculation rather than a final ouput
| Output | Final output of model
| Constant | Constant used in calculation.
Contents
| Spread Sheet Name | Tab Colour Key | Notes
| Cover | Admin Worksheets | Model key and content directory
| Version control |  | Version control
| Assumptions and Data sources |  | Record of sources and assumptions
| Model map |  | Model map or calculations flow
| NeuConnect | Project Worksheets | Main page of model - inputs and outputs are on this page
| Example Project |  | Example model - can be used to create another project
| Converter Availability Calcs | Component Worksheets | Input and calculations for converter availability data
| Cable Availability Calcs |  | Input and calculations for cable availability data
| Other |  | Input and calculations for others - e.g. transformers
| Converter Component Database |  | Allows user to build converter from components. See worksheet or userguide for more detail.
List of Acronyms
Appendices
| Acronym | Meaning | Notes
| GHD | Gutteridge Haskins & Davey
| SKM | Sinclair Knight Merz
| MTTR | Mean Time To Repair | Average time taken for piece of equiptment to be repaired after a failure (Days)
| MTBF | Mean Time Between Failures | Average time between each failure on the piece of equiptment (Years)
| HVDC | High Voltage Direct Current
| OFGEM | Office of Gas and Electricity Markets
| XLPE | Cross Linked Poyethylene | HVAC and HVDC cable type
| MIND | Mass Impregnated Non Draining | HVDC cable type
| IFA2 | Interconnexion France-Angleterre 2
| NSL | North Sea Link
| FPA | Final Project Assessment
| VSC | Voltage Source Converter | Type of HVDC technology
| LCC | Line Commutated Converter | Type of HVDC technology
| CIGRE | International Council on Large Electric Systems | Source of MTBF and MTTR data on Cables and other equipment
End of sheet

## Assumptions and Data sources
Assumptions and Sources
Data Sources
Data | Description | Source
Converter MTBF | Converter Mean Time Between Failures. Average time between outages caused by failures on the HVDC Converter | CIGRE B4 biannual reliability survey 2016 B4-131_2016 A Survey of the Reliability of HVDC Systems Throughout the World during 2013-2014
Converter MTTR | Mean Time To Repair for outages on converter. | CIGRE B4 biannual reliability survey 2016 B4-131_2016 A Survey of the Reliability of HVDC Systems Throughout the World during 2013-2014
Converter Availability (%) | The Availability of the component when failed. Will only be >0% if the component has redundancy. E.g. 50% if two circuits each rated at 50%. | Dependent on converter type.
Cable Average External failures | The average number of faults per year due to externally generated damage or stress of the cable e.g. third party mechanical damage. | This data is based on the failures reported in CIGRE TB 815 and TB 379.
Cable Average Internal failures | The average number of faults per year of the cable due to internal failure causes. | This data is based on the failures reported in CIGRE TB 815 and TB 379.
Cable Average MTTR | This value is based on data sourced from CIGRE, and represents a typical UK repair time (65 days). | This based on data from CIGRE TB 815 and TB 379.
Cable High MTTR | This value is sourced directly from CIGRE, increased to allow for a more restricted repair access (90 days) | This based on data from CIGRE TB 815 and TB 379.
VSC Converter Transformer Outages | Outage information for Voltage source converter. | Input data based on CIGRE A2 reliability surveys. TB642 Transformer Reliability Survey. TB617 HVDC LCC Converter Transformer Failure Survey Results from 2003 - 2012.
LCC Converter Transformer Outages | Outage information for line current commutated converter. | Input data based on CIGRE A2 reliability surveys. TB642 Transformer Reliability Survey. TB617 HVDC LCC Converter Transformer Failure Survey Results from 2003 - 2012.
HVDC Circuit breaker outages | Information avaible to model the availbilty of interconnector with HVDC Breaker | CIGRE TB150
Assumptions
Assumption | Description
Converter MTBF sensitivity | Worst case = 1.5x standard, best case = 0.5x standard. This allows the user to assess a range of converter reliability data.
Converter MTTR sensitivity | Medium case = 65 days, worst case = 90. Allows the user to asses the effect of longer repair times. 65 days represents a onsite repair where 90 days is back to workshop repair.
Cable High External Failures sensitivity | High failures – The average failure rate times by a constant to increase the risk, used to model higher risk cables, variable but set at 1.5
Cable Low External Failures sensitivity | Low failures – The average failure rate times by a low constant to increase the risk, used to model lower risk cables, variable but set at 0.75
Cable High Internal Failures sensitivity | High failures – The average failure rate times by a constant to increase the risk, used to model higher risk cables, variable but set at 1.5
Cable Low Internal Failures sensitivity | Low failures – The average failure rate times by a low constant to increase the risk, used to model lower risk cables, variable but set at 0.75
Subsea cable external risk - Low risk/very well protected | Cable protection on the basis of a CBRA. Evidence of unusual low risk or exceptional protection measures. A Multiplier of 0.8 x standard failures is used.
Subsea cable external risk - Average risk/protected | Cable protection on the basis of a CBRA on the basis of achieving lowest reasonably achievable risk. Standard failure rates assumed.
Subsea cable external risk - High risk/partial protection | Evidence of a higher than "normal" cable external risk. This may be; an annual failure rate assessed by CBRA as greater than 10E-4 per 100km; evidence of an "abnormal"; or a basic level of protection provided without supporting CBRA. Multiplier of 1.2 x standard is used.
Subsea cable external risk - Very high risk/unprotected | Un-protected without robust evidence of unusually low external risk via CBRA. Multiplier of 2.4 x standard is used.
Cable Installation risk factor Average | Standard installation of cable, standard risk.
Cable Installation risk factor Low | Low risk installation. 0.8 x standard
Cable Installation risk factor High | High risk installation. 1.2 x standard
Cable Bundling Arrangement | Allows for the modeller to select the bundling arrangement of the cable, and effect the available capacity in the event of a fault. E.g. bundled cables result in increased unavailability in event of a fault on a bipolar system.
Planned Maintenance | It is assumed that any planned unavailability would be influenced by maintenance of HVDC converters and the associated equipment, so the proposed outage period within the model is variable between 1 to 3 days per converter.

## Model map
LEGEND
[15 empty] | Input [Project] | Data specific to interconnector project currently being assessed. Most Basic Use of model will only require modification of these blocks
[15 empty] | Input [Component Data] | Data specific to component. Is not necessarily changed with project, but can be updated by advanced users
| This model map shows the calculation flows for the Availability Calculator Model. A Legend is shown, and is based on the structure that the end result is on the left and as we move across right, more and more inputs are shown. The map structure of availability is based on equipment class (Other, Converter and Cable). There is only one flow for each class, and the flow is repeated for the number of equipments in each class, allowing for any differences. For example, one interconnector will typically have 2 converter stations, one at each end, and to allow for bi-directional power flow the converter type will be the same, hence the calculation flow will simply be repeated. Although for cables, there will typically be different types of cables in one project (onshore HVDC, Offshore HVDC, onshore AC) and the whole flow must be repeated for each type. | [13 empty] | Calcs | figures that are a intermediate calculation rather than a final ouput
[15 empty] | Output | Final output of model
[15 empty] | Constant | Constant used in calculation.
Cable Unavailability | [17 empty] | Final Sum
Cable Length
Base Availability Data - External Failures (No/km/year)
Total Availability
| Cable External Risk Factor |  | * | = | External Failure Rate | [16 empty] | 1 | - | Total unavailability | =
Failure Rate Selection Factor
[7 empty] | + | = | [Cable] Failure Rate (Per Unit Length) | * | = | [Cable] Failure Rate | =
Base Availability Data - Internal Failures (No/km/year)
| Installation Risk Selection Factor |  | * | = | Internal Failure Rate
| Failure Rate Selection Factor | [10 empty] | 1/365 | =
| External MTTR from Cable Data | [12 empty] | * | = | Cable Unavailability (% Per Year) | Repeat for each type of Cable |  | + | = | Total unavailability Due to Unplanned Outages | + | = | Total unavailability
|  |  | * | = | External Failure MTTR
| MTTR Sensitivity | [5 empty] | Weighted Average |  |  |  | = | MTTR | =
|  |  | * | = | Internal Failure MTTR
External MTTR from Cable Data
| Cable Bundling Arrangement Factor | [8 empty] | 1 | - | [Cable] Available Capacity | =
|  |  | * | = | External Failure Available Capacity
Converter Arrangement Available Capacity
[7 empty] | Weighted Average | =
Cable Bundling Arrangement Factor
|  |  | * | = | Internal Failure Available Capacity
Converter Arrangement Available Capacity
Converter Unavailability
[Converter] Available Capacity
| 1 | - |  |  | [Converter] Available Capacity
| 1/365 | [5 empty] | * | = | Converter Unavailability (% Per Year) | Repeat for each Converter
[Converter] MTTR
|  |  | * | = | MTTR
MTTR (Weather) Sensitivity
MTBF Factor Choice
|  |  | * | = | [Converter] Failure Rate
1
[Converter] MTBF (years)
Other Unavailability
MTTR [Other]
| 1 | = |  |  | * | = | Other Unavailability (% Per Year) |  |  | Repeat for each "other" component
Other Equipment MTBF (years)
1/365
Planned Outages
Maintenance Frequency [calculated from converter type]
|  |  | * | = | Total unavailability Due to planned Outages (Maintenance)
Converter Outage Factor

## NeuConnect Base
|  | Design Availability Spreadsheet | [7 empty] | Weather Sensitivity |  |  |  | Asset Classes | Cable Limits
[10 empty] | Average | Typical Weather around UK - Average 65 days MTTR for cable |  |  | Converter | Max | 10000
Project: | NeuConnect | [8 empty] | Restricted access | Average 90 days MTTR for cable |  |  | Cables | Min | 0
Size: | 1400 |  | Total availability of NeuConnect |  |  |  | 94.37% | [6 empty] | Other
Timing: | 2023 | [8 empty] | Maintenance Sensitivity
Location: | GB - Germany | [8 empty] | Less frequent | Fewer Maintenance requirements equating to 36 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Input |  |  |  | Calculation |  |  |  | Output
Units | Class | Circuit Length (km) | Equipment | Failure Rate (PA) | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (%) | % Total
1 | Cables | 12.5 | NeuConnect - Germany HVDC Onshore Cable | 0.0094125 | 106.2417 | 40 | 0% | 0.1032% | 1.831% | Sensitivity | Level | Varibles effected
1 | Cables | 1.6 | NeuConnect - GB HVDC Onshore Cable | 0.0012048 | 830.0133 | 40 | 0% | 0.0132% | 0.2344% | Weather | Average | Cable MTTR
1 | Cables | 112 | NeuConnect - HVDC Subsea Cable High Mobility | 0.044195 | 22.6269 | 65 | 0% | 0.787% | 13.97% | Scheduled Maintenance | Average | Planned Maintenance Unavailbility
1 | Cables | 594 | NeuConnect - HVDC Subsea Cable Main | 0.21562 | 4.6377 | 65 | 0% | 3.84% | 68.17% | Converter Outages | Medium Case | Converter MTBF | To vary converter MTBF, change sensitivity in Example project
2 | Converter |  | Bipole no earth return (onshore) | 4 | 0.25 | 0.611 | 50% | 0.3348% | 5.944%
4 | Other |  | VSC Converter Transformer | 0.016 | 62.5 | 3 | 50% | 0.006575% | 0.1167%
|  |  |  | - | - | - | - | 0% | 0% | 1400 MW VSC Rigid Bipole - 706km offshore HVDC, 14.1 km onshore HVDC.
|  |  |  | - | - | - | - | 0% | 0% | 0.5 km of onshore cable (Germany) and 0.4 km of onshore GIL (GB) for HVAC
|  |  |  | - | - | - | - | 0% | 0% | 12,.5 km of onshore cable (Germany) and 1.6 km of onshore cable (GB) for HVDC
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | Total Unavailability Due to Scheduled unplanned outages |  |  |  | 5.085%
Availability Calculation - Scheduled Maintenance/Planned outages
Units | Class |  | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (Years) | Maintenance Duration (Days) | Available Capacity % | Unavailability (%) | % Total
1 | Other |  | Scheduled Maintenance Medium Case (1) | 1 | 1 | 2 | 0 | 0.5479% | 9.728%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | Total Unavailability Due to Scheduled Maintenance/Planned outages |  |  |  | 0.5479%
[5 empty] | Total unavailability |  |  | 5.633%
[5 empty] | Overall availability |  |  | 94.37%
NeuConnect HVDC Interconnector
GB-Germany
Onshore Converter Station VSC Rigid Bipole at ± 525 kV
400kV HVAC
Onshore Converter Station VSC Rigid Bipole at ± 525 kV
380kV HVAC
1400 MW Rated 720.1 km HVDC MIND Cable
Rated Capacity = 1400 MW
Note on E10: When Selecting a cable it is appropriate to set it up in "Cable Availability Data" Sheet. For each cable name selected a cable type and then apply sensitivities
Note on O14: This varible is changed via the same cell on the "Example Project" worksheet.

## Example Project
|  | Design Availability Spreadsheet | [7 empty] | Weather Sensitivity |  |  | Asset Classes
[10 empty] | Average | Typical Weather around UK - Average 65 days MTTR for cable |  | Converter
Project: | Example Project | [8 empty] | Restricted access | Average 90 days MTTR for cable |  | Cables
Size: | 1400 |  | Total Availability of Project: |  |  |  | 92.09% | [5 empty] | Other
Timing: | 2025 | [8 empty] | Maintenance Sensitivity
Location: | UK-EU | [8 empty] | Less frequent | Fewer Maintenance requirements equating to 36 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Input |  |  |  | Calculation
Units | Class | Circuit Length (km) | Equipment | Failure Rate (p.a.) | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (%) | % Total
1 | Converter |  | Bipole no earth return (onshore) | 2 | 0.5 | 0.611 | 50% | 0.1674% | 2.116% | Sensitivity | Level | Variables effected
1 | Cables | 714 | NSL Offshore Cable Section | 0.38877 | 2.5722 | 65 | 0% | 6.923% | 87.52% | Weather | Average | [Cable] MTTR
1 | Cables | 4 | NSL Onshore Cable Section | 0.003012 | 332.0053 | 40 | 0% | 0.03301% | 0.4172% | Scheduled Maintenance | Average | Planned Maintenance Unavailbility
1 | Converter |  | Bipole no earth return (onshore) | 2 | 0.5 | 0.611 | 50% | 0.1674% | 2.116% | Converter Outages | Medium Case | [Converter] MTBF
1 | Cables | 4.9 | NSL (High Cable MTTR) Section | 0.0020874 | 479.0649 | 120 | 0% | 0.06863% | 0.8675%
1 | Other |  | VSC Converter Transformer | 0.004 | 250 | 3 | 50% | 0.001644% | 0.02078%
1 | Other |  | VSC Converter Transformer | 0.004 | 250 | 3 | 50% | 0.001644% | 0.02078%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | Total Unavailability Due to Scheduled unplanned outages |  |  |  | 7.363%
Availability Calculation - Scheduled Maintenance/Planned outages
Units | Class |  | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Available Capacity % | Unavailability (% per year) | % Total
1 | Converter |  | Scheduled Maintenance Medium Case (1) | 1 | 1 | 2 | 0 | 0.5479% | 6.926%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | - | - | - | - | 0% | 0%
|  |  |  | Total Unavailability Due to Scheduled Maintenance/Planned outages |  |  |  | 0.5479%
[5 empty] | Total unavailability |  |  | 7.911%
[5 empty] | Overall availability |  |  | 92.09%
Note on E10: When Selecting a cable it is apprioate to set it up in "Cable Availability Data" Sheet. For each cable name selected a cable type and then apply sensitivities

## Converter Availability Calcs
Converter Outage Factors
Unplanned Outage
Range | MTTR Factor | MTBF Factor (x No of faults/year)
Worst Case | 1 | 1.5
Medium Case | 1 | 1
Best Case | 1 | 0.5
Project Converter Database - Unplanned outages
Converter Unscheduled Outages
Converter Type | MTTR | MTBF | MTBF (Years) | MTTR (Days) | Failure Rate (p.a.) | Unavailability (% per year) | Available Capacity %
Monopole (Onshore) | Medium Case | Medium Case | 0.5 | 0.611 | 2 | 0.0033479 | 0%
Monopole (Offshore) | Medium Case | Medium Case | 0.5 | 1.223 | 2 | 0.0067014 | 0%
Symmetrical Monopole (Onshore) | Medium Case | Medium Case | 0.5 | 0.611 | 2 | 0.0033479 | 0%
Symmetrical Monopole (Offshore) | Medium Case | Medium Case | 0.5 | 1.223 | 2 | 0.0067014 | 0%
Bipole with earth return (Onshore) | Medium Case | Medium Case | 0.5 | 0.611 | 2 | 0.001674 | 50%
Bipole with earth return (Offshore) | Medium Case | Medium Case | 0.5 | 1.223 | 2 | 0.0033507 | 50%
Bipole no earth return (onshore) | Medium Case | Medium Case | 0.5 | 0.611 | 2 | 0.001674 | 50%
Bipole no earth return (offshore) | Medium Case | Medium Case | 0.5 | 1.223 | 2 | 0.0033507 | 50%
User Defined 1 (Onshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
User Defined 1 (Offshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
User Defined 2 (Onshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
User Defined 2 (Offshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
User Defined 3 (Onshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
User Defined 3 (Offshore) | Medium Case | Medium Case |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
|  |  |  | 0 | 0 | 0 | 0%
Base Converter Component Availability Data - Unplanned outages
Unplanned Outage
Component | MTBF (years) | MTTR (Days) | Available Capacity (%)
Monopole (Onshore) | 0.5 | 0.611 | 0%
Monopole (Offshore) | 0.5 | 1.223 | 0%
Symmetrical Monopole (Onshore) | 0.5 | 0.611 | 0%
Symmetrical Monopole (Offshore) | 0.5 | 1.223 | 0%
Bipole with earth return (Onshore) | 0.5 | 0.611 | 50%
Bipole with earth return (Offshore) | 0.5 | 1.223 | 50%
Bipole no earth return (onshore) | 0.5 | 0.611 | 50%
Bipole no earth return (offshore) | 0.5 | 1.223 | 50%
AC Equipment | 3.2139 | 0.611 | 0%
Valves | 1.2104 | 0.611 | 0%
Control and Protection | 3.536 | 0.611 | 0%
DC Equipment | 1.96 | 0.611 | 0%
Other | 14.3467 | 0.611 | 0%
AC Filter | 0.5 | 2 | 0.5%
Energisation Resistor/Short Switch
DC Converter
DC Reactor
DC Filter
User Defined Converter Component 1
User Defined Converter Component 2
User Defined Converter Component 3
Note on C5: MTTR factor scales the MTTR depending on the factor entered below. This has been fixed and project speciifc factors can be applied on the Converter Type selection.
Note on C14: MTTR Selection factor – Select this according to converter risk, standard is Medium case based on CIGRE B4 biannual reliability surveys. Project can be adjusted by project speciifc design.
Note on D14: MTTR Selection factor – changed on Example project .
Note on E14: MTBF; sum of all the MTBF for all components of the converter as in “Converter Components Database”, otherwise equal to the input in the table below.
Note on F14: MTTR :sum of all the MTTR for all components of the converter as in “Converter Components Database”, otherwise equal to the input in the table below.
Note on G14: This is calculated on “Converter Components Database” sheet from the sum of all components of the converter, calculated from the MTBF data from CIGRE
Note on H14: This is the output of this sheet which is then called by the appropriate sheet when selected.
Note on I14: Available Capacity is the capacity that remains after a single fault in the equipment, and will depend on the converter type and arrangement. This is input in the “Converter Components Database” Worksheet.
Note on C43: MTBF – This is the input for MTBF, and is user editable. The data entered by GHD is sourced directly from CIGRE B4 biannual reliability surveys.
Note on D43: MTTR – This is the input for MTTR, and is user editable. The data entered by GHD is sourced directly from CIGREirectly from CIGRE B4 biannual reliability surveys.
Note on E43: Availability (%) - Enter the Availability of the component. Will only be >0% if the component has redundancy. E.g. 50% if two circuits each rated at 50%.
Note on B62: When entering a converter by components enter any new components here or below.

## Cable Availability Calcs
Project Cable Database - Unplanned outages
Please ensure that correct cable type (C8:C24) matches the type suggest in the cable name (B8:B24)
| Selection factors | [6 empty] | External Failures |  |  |  | Internal Failures |  |  | Total Failures
Cable Name | Cable Type | Failure Rate (H/M/L) | Installation Risk | Subsea Cable External Risk | MTTR Sensitivity | Converter arrangement | Cable Bundling Arrangement | Failure Rate (No./km/year) |  | MTTR | Available Capacity (%) | Failure Rate (No./km/year) | MTTR | Availability Capacity | Failure Rate (PA) | MTTR | Available Capacity
NEMO Offshore Cable Section | HVDC subsea MIND Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000158 |  | 65 | 0% | 0.000205 | 65 | 0% | 0.000363 | 65 | 0%
NEMO Onshore Cable Section | HVDC Onshore MIND Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000453 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.000753 | 40 | 0%
NSL Offshore Cable Section | HVDC subsea MIND Cable | High | Average | Average risk/protected | Average | Bipole no earth return | Unbundled | 0.000237 |  | 65 | 0% | 0.0003075 | 65 | 0% | 0.0005445 | 65 | 0%
NSL Onshore Cable Section | HVDC Onshore MIND Cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Unbundled | 0.000453 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.000753 | 40 | 0%
NSL (High Cable MTTR) Section | NSL HVDC High Cable MTTR | Average | Low | Average risk/protected | Average | Bipole no earth return | Unbundled | 0.00021 |  | 120 | 0% | 0.000216 | 120 | 0% | 0.000426 | 120 | 0%
NSL Onshore HVAC | AC Onshore XLPE Cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Unbundled | 0.000453 |  | 20 | 0% | 0.0003 | 20 | 0% | 0.000753 | 20 | 0%
IFA2 - Offshore HVDC Cable | IFA2 - Offshore HVDC Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.00021 |  | 90 | 0% | 0.00027 | 65 | 0% | 0.00048 | 75.9375 | 0%
IFA2 - French AC onshore Cable | AC Onshore XLPE Cable | Average | Average | Average risk/protected | Average | AC3 | Unbundled | 0.000453 |  | 20 | 49.75% | 0.0003 | 20 | 49.75% | 0.000753 | 20 | 49.75%
IFA2 - UK AC Subsea Cable | IFA2 - offshore HVDC cable | Average | Average | Average risk/protected | Average | AC3 | Unbundled | 0.00021 |  | 90 | 49.75% | 0.00027 | 65 | 49.75% | 0.00048 | 75.9375 | 49.75%
IFA2 - UK AC Onshore Cable | AC Onshore XLPE Cable | Average | Average | Average risk/protected | Average | AC3 | Unbundled | 0.000453 |  | 20 | 49.75% | 0.0003 | 20 | 49.75% | 0.000753 | 20 | 49.75%
IFA2 - UK HVDC Onshore Cable | HVDC Onshore XLPE Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000453 |  | 20 | 0% | 0.0003 | 20 | 0% | 0.000753 | 20 | 0%
IFA2 - French HVDC Onshore Cable | HVDC Onshore XLPE Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000453 |  | 20 | 0% | 0.0003 | 20 | 0% | 0.000753 | 20 | 0%
Greenlink - Ireland - HVDC Onshore Cable | HVDC Onshore XLPE Cable | Low | Average | Average risk/protected | Average | Bipole no earth return | Unbundled | 0.00033975 |  | 20 | 0% | 0.000225 | 20 | 0% | 0.00056475 | 20 | 0%
Greenlink - UK - HVDC Onshore Cable | HVDC Onshore XLPE Cable | Low | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.00033975 |  | 20 | 0% | 0.000225 | 20 | 0% | 0.00056475 | 20 | 0%
Greenlink - Offshore HVDC Cable | Greenlink - Offshore HVDC XLPE Cable | Low | Average | Average risk/protected | Average | Symetrical Monopole | Bundled | 0.0001575 |  | 65 | 0% | 0.0002025 | 65 | 0% | 0.00036 | 65 | 0%
Greenlink - UK - AC Onshore Cable | AC Onshore XLPE Cable | Low | Average | Average risk/protected | Average | AC1 | Unbundled | 0.00033975 |  | 20 | 0% | 0.000225 | 20 | 0% | 0.00056475 | 20 | 0%
Greenlink - Ireland - AC Onshore Cable | AC Onshore XLPE Cable | Low | Average | Average risk/protected | Average | AC1 | Bundled | 0.00033975 |  | 20 | 0% | 0.000225 | 20 | 0% | 0.00056475 | 20 | 0%
NeuConnect - GB HVDC Onshore Cable | HVDC Onshore MIND cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Bundled | 0.000453 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.000753 | 40 | 0%
NeuConnect - Germany HVDC Onshore Cable | HVDC Onshore MIND cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Bundled | 0.000453 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.000753 | 40 | 0%
NeuConnect - HVDC Subsea Cable Main | NeuConnect - HVDC Subsea Cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Bundled | 0.000158 |  | 65 | 0% | 0.000205 | 65 | 0% | 0.000363 | 65 | 0%
NeuConnect - HVDC Subsea Cable High Mobility | NeuConnect - HVDC Subsea Cable | Average | Average | High risk/partial protection | Average | Bipole no earth return | Bundled | 0.0001896 |  | 65 | 0% | 0.000205 | 65 | 0% | 0.0003946 | 65 | 0%
Example Project - Offshore HVDC Cable 1 | HVDC subsea XLPE Cable | Average | Average | Average risk/protected | Average | Bipole no earth return | Bundled | 0.000158 |  | 65 | 0% | 0.000205 | 65 | 0% | 0.000363 | 65 | 0%
Example Project - Offshore HVDC Cable 2 | HVDC subsea XLPE Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000158 |  | 65 | 0% | 0.000205 | 65 | 0% | 0.000363 | 65 | 0%
Example Project - Offshore HVAC Cable 1 | AC subsea XLPE Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000158 |  | 65 | 0% | 0.000463 | 65 | 0% | 0.000621 | 65 | 0%
Example Project - Offshore HVAC Cable 2 | AC subsea XLPE Cable | Average | Average | Average risk/protected | Average | Symetrical Monopole | Unbundled | 0.000158 |  | 65 | 0% | 0.000463 | 65 | 0% | 0.000621 | 65 | 0%
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | 0.00021 |  | 65 | 0 | 0.00027 | 65 | 0 | 0.00048 | 65 | 0
Base Availability Data - Unplanned outages | [12 empty] | Cable Factors
| External Failures (No/km/year) |  |  | MTTR (Days) |  | Internal Failures (No/km/year) |  |  | MTTR (Days) |  |  |  | Converter Arrangement |  |  | Cable Bundling Arrangement |  | Installation Risk Factor
Cable Type | High | Low | Average | Average | High | High | Low | Average | Average | High |  |  | Converter Arrangement | Available Capacity (%) |  | Arrangement | Factor | Risk | Factor
AC subsea XLPE cable | 0.000237 | 0.0001185 | 0.000158 | 65 | 90 | 0.0006945 | 0.00034725 | 0.000463 | 65 | 90 |  |  | Monopole | 0% |  | Bundled | 0 | High | 1.2
AC onshore XLPE cable | 0.0006795 | 0.00033975 | 0.000453 | 20 | 30 | 0.00045 | 0.000225 | 0.0003 | 20 | 30 |  |  | Symetrical Monopole | 0% |  | Unbundled | 1 | Low | 0.8
HVDC subsea XLPE cable | 0.000237 | 0.0001185 | 0.000158 | 65 | 90 | 0.0003075 | 0.00015375 | 0.000205 | 65 | 90 |  |  | Bipole no earth return | 0% |  |  |  | Average | 1
HVDC onshore XLPE cable | 0.0006795 | 0.00033975 | 0.000453 | 20 | 30 | 0.00045 | 0.000225 | 0.0003 | 20 | 30 |  |  | Bipole with earth rerun | 50%
HVDC subsea MIND cable | 0.000237 | 0.0001185 | 0.000158 | 65 | 90 | 0.0003075 | 0.00015375 | 0.000205 | 65 | 90 |  |  | User Defined 2 | 50% |  | Subsea Cable External Risk
HVDC Onshore MIND cable | 0.0006795 | 0.00033975 | 0.000453 | 40 | 65 | 0.00045 | 0.000225 | 0.0003 | 40 | 65 |  |  | User Defined 3 | 75% |  | Cable External Risk | Factor
NSL HVDC high cable MTTR | 0.000315 | 0.0001575 | 0.00021 | 120 | 145 | 0.000405 | 0.0002025 | 0.00027 | 120 | 145 |  |  | AC1 | 0% |  | Low risk/very well protected | 0.8
IFA2 - offshore HVDC cable | 0.000315 | 0.0001575 | 0.00021 | 90 | 115 | 0.000405 | 0.0002025 | 0.00027 | 65 | 90 |  |  | AC2 | 86.4% |  | Average risk/protected | 1
Greenlink - Offshore HVDC XLPE Cable | 0.000315 | 0.0001575 | 0.00021 | 65 | 90 | 0.000405 | 0.0002025 | 0.00027 | 65 | 90 |  |  | AC3 | 49.75% |  | High risk/partial protection | 1.2
NeuConnect - HVDC Subsea Cable | 0.000158 | 0.000158 | 0.000158 | 65 | 90 | 0.0003075 | 0.00015375 | 0.000205 | 65 | 90 | [5 empty] | Very high risk/unprotected | 2.4
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
"Project" "onshore/offshore" "cable type" cable
Note on C7: The “Cable Type” selection factor is used to select the apprioate type of cable from the base availbity table below. Please ensure that correct "cable type" is selected for each cable name, as this is where the basis of the data is linked
Note on D7: “Failure rate” selection factor Is used to selection a factor of “High”, “Medium” or “low”. This will apply a scaling factor that will model a riskier or safer cable, depending on project specific circumstances. This Effects both External and Internal Failures and can be adjusted based on speciifc project cable risks.
Note on E7: “Installtion risk factor” will apply a scaling factor depending on the selection. For example where a cable is installed in a high risk area potentially causing cable defects, the model can allow for this. This only effects internal failures
Note on F7: Burial Factor allows the user to model the effect of the burial depth of the cable on the overall availability. A deep buried cable is less likely to fail, and a unburied is more exposed and hence more likely to fail due to external damage.
Note on G7: Subsea Cable MTTR is affected by the weather sensitivity (in Project Sheets), and hence MTTR for each of these is non variable. Otherwise the MTTR sensitivity is used to model a cable installation in hard to access areas, such as tubing or tunnels, where the MTTR would be increase.
Note on H7: “Converter Arrangment” is used to select the converter set up that goes with the cable, and is project specific. This will also determine the capacity that remains after a single cable failure.
Note on I7: “Cable Bundling Arrangement” allows for the modeller to select the bundling arrangement of the cable, and effect the available capacity in the event of a fault. E.g. bundled cables result in increased unavailability in event of a fault on a bipole system.
Note on G27: NON-VARIBLE. This value is determined by the weather sensitivity on the Greenlink Project Sheet.
Note on G28: NON-VARIBLE. This value is determined by the weather sensitivity on the Greenlink Project Sheet.
Note on G29: NON-VARIBLE. This value is determined by the weather sensitivity on the Example Project Sheet.
Note on G30: NON-VARIBLE. This value is determined by the weather sensitivity on the Example Project Sheet.
Note on G31: NON-VARIBLE. This value is determined by the weather sensitivity on the Example Project Sheet.
Note on G32: NON-VARIBLE. This value is determined by the weather sensitivity on the Example Project Sheet.
Note on B33: Add additonal onshore cables by inserting line at this row
Note on C40: High failures – The average failure rate times by a constant to increase the risk, used to model higher risk sites.
Note on D40: Low failures – The average failure rate times by a low constant to increase the risk, used to model lower risk sites.
Note on E40: Average External failures – The average number of fails per year due to damage to the exterior of the cable. This data is sourced directly from CIGRE TB 379.
Note on F40: Average MTBR.- This value is sourced directly from CIGRE TB 379, and represents repair time. It can be edited by the model user to reflect future updates in reliability data.
Note on G40: High MTBR.- This value is sourced directly from CIGRE TB 379, but with a factor applied to indicate a longer than the average, e.g. for a very long or inaccessible cable. It can be edited by the model user to reflect updates in reliability data.
Note on H40: High failures – The average failure rate times by a constant to increase the risk, used to model higher risk sites.
Note on I40: Low failures – The average failure rate times by a low constant to increase the risk, used to model lower risk sites.
Note on J40: Average Internal failures – The average number of fails per year due to damage to the exterior of the cable. This data is sourced directly from CIGRE TB 379.
Note on K40: Average MTBR.- This value is sourced directly from CIGRE, and represents a on-site repair. It can be edited by the model user to reflect updates in reliability data.
Note on L40: High MTBR.- This value is sourced directly from CIGRE, it is greater than the average, as this represents a “back to workshop” type repair where it is unable to be fixed on site. It can be edited by the model user to reflect updates in reliability data.

## Other Component Database
Other Equipment Database
| Unplanned Outage |  | Scheduled Maintenance |  | Available Capacity (%) | Source Comment
Component | Failure Rate (PA) | MTTR (Days) | Maintainence Rate (PA) | MTTR (Days)
Scheduled Maintenance Less frequent Case (1) | 0 | 0 | 1 | 1.5 | 0% | All data in this selection is user editable input data. The separate columns for “unplanned outage” or “scheduled maintenance” will be filled in according to the component type, any Scheduled maintenance data will be in the scheduled maintenance columns, everything else, including transformer or circuit breakers are in the unplanned column.
Scheduled Maintenance Medium Case (1) | 0 | 0 | 1 | 2 | 0%
Scheduled Maintenance more frequent Case (1) | 0 | 0 | 1 | 3 | 0%
HVDC Circuit Breaker (3-1) | 0.045 | 8 | 0 | 0 | 0%
Scheduled Maintenance less frequent Case (3-2) | 0 | 0 | 1 | 1.5 | 50%
Scheduled Maintenance Medium Case (3-2) | 0 | 0 | 1 | 2 | 50%
Scheduled Maintenance more frequent Case (3-2) | 0 | 0 | 1 | 3 | 50%
HVDC Circuit Breaker (3-2) | 0.045 | 8 | 0 | 0 | 50%
Scheduled Maintenance less frequent Case (2) | 0 | 0 | 1 | 1.5 | 50%
Scheduled Maintenance Medium Case (2) | 0 | 0 | 1 | 2 | 50%
Scheduled Maintenance more frequent Case (2) | 0 | 0 | 1 | 3 | 50%
Scheduled Maintenance less frequent Case (3-1) | 0 | 0 | 1 | 1.5 | 0%
Scheduled Maintenance Medium Case (3-1) | 0 | 0 | 1 | 2 | 0%
Scheduled Maintenance more frequent Case (3-1) | 0 | 0 | 1 | 3 | 0%
VSC Converter Transformer | 0.004 | 3 | 0 | 0 | 50%
LCC Converter Transformer | 0.015 | 32.25 | 0 | 0 | 0%
Transformer Failure Rate Detail
Name | Outage Type | Failure Rate (p.a.) | MTTR (Days)
Transformers - Unplanned Outages
VSC Converter Transformer | In-Situ Repair | 0.0028 | 3
| Back to Workshop Repair | 0.0012 | 3
| Overall | 0.004 | 3
Name | Outage Type | Failure Rate (p.a.) | MTTR (Days)
Transformers - Unplanned Outages
LCC Converter Transformer | In-Situ Repair | 0.0105 | 7.5
| Back to Workshop Repair | 0.0045 | 90
| Overall | 0.015 | 32.25
Note on E27: Failure rate - Input data based on CIGRE A2 reliability surveys that is user editable
Note on F27: MTTR – input data that is user editable
Note on E33: Failure rate - Input data based on CIGRE A2 reliability surveys that is user editable
Note on F33: MTTR – input data that is user editable

## Converter Components Database
Converter Component Database
The purpose of this page is for advanced users and/or future use. It allows the user to build a converter from components, rather than enter as a whole unit. The first editable table is "User defined 1 (Offshore)", in which the user can see that the first two columns, "units" and "components" are user editable. This is where the number of, and component will be selected when constructing a converter by components
Monopole (Onshore) | Total Unavailability | 0.0033479 | [5 empty] | Total Unscheduled | 0.0033479
| Availability | 99.67%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate (p.a.) | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Monopole (Onshore) | 2 | 0.5 | 0.611 | 0% | 0.0033479 | 100% | 1.222 | 0 | 2 | 0.611 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Monopole (Offshore) | Total Unavailability | 0.0067014 | [5 empty] | Total Unscheduled | 0.0067014
| Availability | 99.33%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Monopole (Offshore) | 2 | 0.5 | 1.223 | 0% | 0.0067014 | 100% | 2.446 | 0 | 2 | 1.223 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Symmetrical Monopole (Onshore) | Total Unavailability | 0.0033479 | [5 empty] | Total Unscheduled | 0.0033479
| Availability | 99.67%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.611 | 0% | 0.0033479 | 100% | 1.222 | 0 | 2 | 0.611 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Symmetrical Monopole (Offshore) | Total Unavailability | 0.0067014 | [5 empty] | Total Unscheduled | 0.0067014
| Availability | 99.33%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Symmetrical Monopole (Offshore) | 2 | 0.5 | 1.223 | 0% | 0.0067014 | 100% | 2.446 | 0 | 2 | 1.223 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Bipole with earth return (Onshore) | Total Unavailability | 0.001674 | [5 empty] | Total Unscheduled | 0.001674
| Availability | 99.83%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Bipole with earth return (Onshore) | 2 | 0.5 | 0.611 | 50% | 0.001674 | 100% | 1.222 | 0.611 | 2 | 0.611 | 50%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Bipole with earth return (Offshore) | Total Unavailability | 0.0033507 | [5 empty] | Total Unscheduled | 0.0033507
| Availability | 99.66%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Bipole with earth return (Offshore) | 2 | 0.5 | 1.223 | 50% | 0.0033507 | 100% | 2.446 | 1.223 | 2 | 1.223 | 50%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Bipole no earth return (onshore) | Total Unavailability | 0.001674 | [5 empty] | Total Unscheduled | 0.001674
| Availability | 99.83%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF Years | MTTR Days | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Bipole no earth return (onshore) | 2 | 0.5 | 0.611 | 50% | 0.001674 | 100% | 1.222 | 0.611 | 2 | 0.611 | 50%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
Bipole no earth return (offshore) | Total Unavailability | 0.0033507 | [5 empty] | Total Unscheduled | 0.0033507
| Availability | 99.66%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
1 | Bipole no earth return (offshore) | 2 | 0.5 | 1.223 | 50% | 0.0033507 | 100% | 2.446 | 1.223 | 2 | 1.223 | 50%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 1 (Onshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 1 (Offshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 2 (Onshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 2 (Offshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 3 (Onshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
User Defined 3 (Offshore) | Total Unavailability | 0 | [5 empty] | Total Unscheduled | 0
| Availability | 100%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations |  | Converter Availbility Summary
Units | Component | Failure Rate | MTBF (Years) | MTTR (Days) | Available Capacity % | Unavailability (per Unit) | % Tot | Unscheduled Overall MTTR | Unscheduled Overall Capacity Availability | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0 | 0 | 0 | 0%
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0
|  | 0 | 0 | 0 | 0% | 0 | 0% | 0 | 0