## Index
Index for data in newdistper#12000.xls
References the worksheets in this file to the graphs in the 'Report on distribution and transmission performance 1999/2000'
Sheet | data for:
A to N | Dist Companies individual performance (data in figures 3, 6, 7, 8, 11, 12, 13, 14, 15)
O | Pie chart data - part of data for figures 9 & 10
P | Fig 9
Q | Fig 10
Subsequent sheets are identified by Fig number
In Section 3 the figures are given for 18 hoursin 2000/2001 instead of 24 hours for previous years.

## A
Eastern | [12 empty] | Year as |  |  |  |  | better than avg |  | Ten year performance
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception" |  |  |  | better than last 9 yrs
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.12 | 0.12 | 0.17 | 0.42 | 0.63 | 0.6 | 0.38 | 0.22 | 0.33 | 0.55 | 0.354
LV Faults (All) | 4.21 | 3.88 | 4.03 | 3.86 | 3.13 | 5.36 | 4.58 | 4.07 | 3.54 | 4.79 | 4.145 | [8 empty] | 138344.7221
HV faults:U/G, no dam | 0.65 | 0.52 | 0.6 | 0.79 | 0.29 | 0.36 | 0.14 | 0.24 | 0.68 | 1.31 | 0.558
HV faults:U/G, damage | 19.04 | 18.77 | 16.33 | 15.09 | 23.24 | 22.68 | 21.09 | 21.1 | 20.33 | 26.01 | 20.368
HV faults:O/H, no dam | 4.38 | 8.62 | 4.49 | 8.25 | 0.76 | 0.68 | 0.02 | 0.19 | 1.43 | 1.08 | 2.99 |  |  |  |  | CUSTOMER INTERRUPTIONS
HV faults:O/H, damage | 10.18 | 13.17 | 9.66 | 8.98 | 14.48 | 14.64 | 13.54 | 11.87 | 6.47 | 7.81 | 11.08 |  |  |  |  | 2056930.875
HV faults: All other | 11.92 | 14.98 | 12.82 | 10.29 | 27.24 | 28.19 | 13.12 | 13.29 | 15.45 | 16.27 | 16.357 |  |  |  |  | 2978205.1664
HV faults: Total | 46.16 | 56.06 | 43.9 | 43.41 | 66.01 | 66.55 | 47.91 | 46.68 | 44.34 | 52.48 | 51.35 | 2.201% |  |  |  | 1846017.6735 |  |  |  | 1713872.4915
EHV faults | 8.03 | 14.29 | 6.15 | 6.41 | 8.56 | 9.76 | 11.69 | 6.77 | 8.18 | 9.37 | 8.921 | 5.033% |  |  |  | 2044336.8054 |  |  |  | 297749.8831
132kV faults | 4.58 | 18.29 | 2.77 | 8.48 | 4.21 | 6.5 | 8.43 | 1.78 | 8.91 | 1.4 | 6.535 | -78.58% |  |  |  | 2685336.16 |  |  |  | 218114.0552
Total of (a) | 62.98 | 92.53 | 56.85 | 62.16 | 81.92 | 88.19 | 72.59 | 59.31 | 65 | 68.04 | 70.957 | -4.111% |  |  |  | 2876067.8301
(b) Planned Outages | 4.52 | 3.89 | 2.3 | 2.61 | 2.87 | 1.06 | 1.12 | 1.09 | 1.61 | 0.78 | 2.185 | -64.3% |  |  |  | 2401129.0485 |  |  |  | 72927.1937
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.02 | 0.03 | 0 | 0 | 0 | 0.01 | 0.006 |  |  |  |  | 2006602.76
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2223194.6769 |  |  |  | 200.2577
Total of (a+b+c+d) | 67.5 | 96.41 | 59.15 | 64.77 | 84.8 | 89.27 | 73.71 | 60.4 | 66.61 | 68.83 | 73.145 | -5.899% | 96.41 | 59.15 |  | 2306097.5275 | 84.163 | 1 | 0 | 2441308.7321
[9 empty] | 65 | ¢ - combined with LV mains figure | [5 empty] | 2169458.85
2 AVAILABILITY: Minutes Lost per Connected Customer | [19 empty] | 2302863.8811
(a) Distribution
LV service faults | ¢ | ¢ | ¢ | ¢ | [5 empty] | ¢ | 0
LV Faults (All) | 6.47 | 6.21 | 7.84 | 35.5 | 11.77 | 7.88 | 6.69 | 6.35 | 6.4 | 11.34 | 10.645 | [8 empty] | 35529060.705
HV faults:U/G, no dam | 0.5 | 0.37 | 0.43 | 0.63 | 0.18 | 0.39 | 0.14 | 0.18 | 0.45 | 0.9 | 0.417
HV faults:U/G, damage | 17.05 | 18.51 | 15.72 | 15.79 | 23.65 | 22.16 | 23.88 | 19.46 | 15.67 | 22.4 | 19.429
HV faults:O/H, no dam | 3.59 | 7.67 | 4.53 | 8.41 | 0.72 | 0.63 | 0.01 | 0.21 | 0.07 | 0.53 | 2.637 |  |  |  |  | CUSTOMER MINUTES
HV faults:O/H, damage | 9.98 | 14.85 | 11.23 | 12.89 | 15.29 | 14.53 | 14.55 | 10.3 | 6.83 | 12.13 | 12.258 |  |  |  |  | 199354693.1
HV faults:All other | 8.51 | 12.92 | 9.58 | 8.51 | 22.03 | 21.53 | 11.03 | 9.24 | 11.55 | 12.63 | 12.753 |  |  |  |  | 279749258.24
HV faults:Total | 39.63 | 54.33 | 41.49 | 46.24 | 61.87 | 59.24 | 49.62 | 39.4 | 34.57 | 48.6 | 47.499 | 2.318% |  |  |  | 197678376.06 |  |  |  | 158534039.871
EHV faults | 2.98 | 7.32 | 4.87 | 2.71 | 6.52 | 4.9 | 6.38 | 3.25 | 3.31 | 3.6 | 4.584 | -21.47% |  |  |  | 297449900.48 |  |  |  | 15299691.336
132kV faults | 0.39 | 9.06 | 0.87 | 2.36 | 0.99 | 2.19 | 3.29 | 0.66 | 4.08 | 0.28 | 2.417 | -88.42% |  |  |  | 268976949.8 |  |  |  | 8067049.293
Total of (a) | 49.48 | 76.92 | 55.07 | 86.81 | 81.15 | 74.2 | 65.97 | 49.66 | 48.36 | 63.82 | 65.144 | -2.032% |  |  |  | 249589979.61
(b) Planned Outages | 15.94 | 13.64 | 8.27 | 7.43 | 3.58 | 3.27 | 4.11 | 3.19 | 4.64 | 2.42 | 6.649 | -63.6% |  |  |  | 228320628.15 |  |  |  | 22191895.221
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.2 | 0 | 0 | 0.03 | 0 | 0.01 | 0.024 | -58.33% |  |  |  | 175677407.2
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 176894337 |  |  |  | 80103.096
Total of (a+b+c+d) | 65.42 | 90.56 | 63.34 | 94.24 | 84.94 | 77.47 | 70.09 | 52.88 | 53 | 66.24 | 71.818 | -7.767% | 94.24 | 52.88 |  | 221932152 | 85.7596 | 1 | 0 | 239701839.522
[9 empty] | 48.36 | [6 empty] | 161407738.44
3(i) QUALITY OF SERVICE: Percentage of Interruptions due to Distribution Faults (Total of (a)) Restored within time specified
LV Faults: 3 hours | 77.08% | 75.62% | 71.74% | 82.16% | 68.88% | 75.13% | 73.98% | 71.2% | 68.61% | 65.48% | 72.99% | -10.29%
18 hours | 99.76% | 99.62% | 98.58% | 99.85% | 99.71% | 99.99% | 100% | 100% | 99.96% | 98.68% | 99.61% | -0.9386%
HV faults:U/G n/dmg 3hrs | 99.98% | 99.98% | 99.97% | 99.88% | 99.99% | 99.97% | 99.99% | 99.99% | 99.94% | 99.88% | 99.96% | -0.07703%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV faults:U/G dmg 3hrs | 97.89% | 98.15% | 97.94% | 97.1% | 98.4% | 98.18% | 97.71% | 97.98% | 98.52% | 97.35% | 97.92% | -0.5841%
18 hours | 99.98% | 99.96% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 99.98% | 99.99% | -0.008001%
HV faults:O/H n/dmg 3hrs | 99.43% | 98.87% | 99.18% | 98.15% | 99.93% | 99.93% | 100% | 99.98% | 99.94% | 99.95% | 99.54% | 0.4159%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV faults:O/H dmg 3hrs | 97.7% | 97.4% | 96.72% | 96.44% | 98.01% | 98.29% | 98.16% | 98.63% | 98.76% | 97.5% | 97.76% | -0.267%
18 hours | 100% | 99.99% | 99.97% | 100% | 99.97% | 100% | 100% | 100% | 100% | 99.93% | 99.99% | -0.05601%
HV faults:Other 3hr | 98.72% | 98.21% | 98.32% | 98.41% | 98.1% | 98.07% | 98.89% | 99.18% | 98.18% | 98.17% | 98.42% | -0.2591%
18 hours | 99.98% | 99.96% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 99.97% | 99.99% | -0.02%
HV Faults:Total 3 hours | 93.73% | 92.61% | 92.12% | 89.98% | 94.43% | 94.44% | 94.74% | 95.76% | 95.35% | 92.85% | 93.6% | -0.8023%
18 hours | 99.96% | 99.91% | 99.93% | 99.98% | 99.97% | 100% | 100% | 100% | 100% | 99.89% | 99.96% | -0.07403%
EHV Faults: 3 hours | 99.99% | 98.99% | 98.64% | 99.93% | 99.67% | 99.75% | 99.79% | 99.93% | 99.99% | 99.97% | 99.67% | 0.306%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 98.22% | 100% | 100% | 100% | 100% | 99.67% | 99.96% | 100% | 100% | 99.78% | 0.2155%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 92.6% | 89.22% | 89.41% | 89.43% | 93.13% | 93.05% | 93.13% | 94.18% | 93.83% | 90.98% | 91.9% | -0.9968% | 94.18% | 89.22% |  | 2022662.517
18 hours | 99.95% | 99.9% | 99.84% | 99.97% | 99.96% | 100% | 100% | 100% | 100% | 99.81% | 99.94% | -0.1331% | 100% | 99.81% |  | 2218970.607
TOTAL not rest in 3 hrs | 7.4% | 10.78% | 10.59% | 10.57% | 6.87% | 6.95% | 6.87% | 5.82% | 6.17% | 9.02% | 8.104% | 11.3% | 10.78% | 5.82% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.05% | 0.1% | 0.16% | 0.03% | 0.04% | 0% | 0% | 0% | 0% | 0.19% | 0.057% | 233.3% | 0.19% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | NIL * | N\A |  | N\A
- Load Disconnection | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | NIL * | N\A |  | N\A
Total | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A
(b) Eastern Elec.
- Voltage Reductions | NIL | NIL | NIL | NIL | NIL | NIL | NIL | NIL | NIL | NIL | N\A |  | N\A
- Load Disconnection | NIL * | NIL * | NIL | NIL | NIL | NIL | NIL | NIL | nil | NIL * | N\A |  | N\A
Total | N/A | 0.028 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.62 | 1.35 | 1.05 | 1.46 | 0.88 | 0.99 | 1.29 | 1.92 | 1.37 | 0.2 | 1.213 | 10 | 1.92 | 0.2 |  |  |  | 0 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 11.75 | 13.01 | 10.32 | 11.2 | 10.91 | 11.2 | 10.68 | 10.85 | 11.15 | 12.35 | 11.342 |  | 13.01 | 10.32 |  |  |  | 1 | 0
RELEVANT DATA: | N\A: av'ge |  | 10yr av
Number of Customers | 3047305 | 3089104 | 3120909 | 3156302 | 3166670 | 3221763 | 3257535 | 3322190 | 3337629 | 3350425 |  |  | 106%
Embedded Gen.Stations | N/A | 1 | 4 | 4 | 4 | 4 | 4 | 52 | 53 | 96 | N\A
Emb.Gen.Capacity MWSO | N/A | 140 | 570 | 570 | 570 | 570 | 570 | 509 | 537 | 596 | N\A
Mains in commission (circuit kilometres)
Overhead Line | [11 empty] | SUM ALL PESs
132kV | 2316 | 2322 | 2330 | 2330 | 2340 | 2341 | 2341 | 2365 | 2365 | 2357 | 2340.7 | 15370.2 | 100.7% |  | 15370.2
183618.9
33kV | 3777 | 3818 | 3838 | 3838 | 3875 | 3884 | 3884 | 3883 | 3883 | 3877 | 3855.7 | 28687.5 | 100.6% |  | 69106.4
25kV | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0.4 | 1833 | 250% |  | 0
11kV | 19542 | 19559 | 19688 | 19832 | 19696 | 19747 | 19547 | 19377 | 19352 | 19308 | 19564.8 | 139757.4 | 98.69%
6.6kV | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.4 | 1024 | 0%
3.3kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12317
3kV | 0 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0%
LV | 9658 | 9649 | 9640 | 9636 | 9627 | 9619 | 9610 | 9533 | 9515 | 9499 | 9598.6 | 69106.4 | 98.96%
TOTAL | 35294 | 35355 | 35505 | 35643 | 35538 | 35591 | 35382 | 35158 | 35116 | 35042 | 35362.4 |  | 99.09%
0
Underground Cable | N\A: 0
132kV | 216 | 216 | 218 | 219 | 219 | 220 | 220 | 220 | 221 | 228 | 219.7 | 2788.2 | 103.8% |  | 5499.4 | 20869.6
[12 empty] | 2711.2 |  |  | 141753.8 | 325372.7
33kV | 2361 | 2363 | 2368 | 2371 | 2390 | 2405 | 2436 | 2450 | 2486 | 2522 | 2415.2 | 14637.3 | 104.4% |  | 309515.4 | 378621.8
25kV | 19 | 19 | 21 | 22 | 22 | 23 | 23 | 23 | 27 | 27 | 22.6 | 42 | 119.5% |  | 0 | 0
724864.1
11kV | 15017 | 15177 | 15345 | 15470 | 15650 | 15878 | 16317 | 16625 | 16783 | 17017 | 15927.9 | 117404.5 | 106.8%
6.6kV | 83 | 82 | 82 | 71 | 75 | 29 | 29 | 29 | 29 | 29 | 53.8 | 9558 | 53.9%
3.3kV | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 112
3kV | 18 | 33 | 33 | 30 | 25 | 21 | 21 | 21 | 21 | 0 | 22.3 | 0 | 0%
LV | 32761 | 33233 | 33640 | 33822 | 34120 | 34519 | 34875 | 35221 | 35601 | 35926 | 34371.8 | 309515.4 | 104.5%
TOTAL | 50475 | 51123 | 51707 | 52005 | 52501 | 53095 | 53921 | 54589 | 55168 | 55749 | 53033.3 | 487582.6
Total System length | 85769 | 86478 | 87212 | 87648 | 88039 | 88686 | 89303 | 89747 | 90284 | 90791 | 88395.7 | 503475.9 | 102.7%
Transformers
Primary Voltage
132kV | 219 | 225 | 229 | 228 | 228 | 229 | 229 | 230 | 233 | 233
33kV | 871 | 853 | 858 | 857 | 850 | 848 | 871 | 869 | 872 | 872
Distribution pole-mounted | 34051 | 33942 | 34232 | 34256 | 34517 | 34571 | 34579 | 34502 | 34479 | 34572
Distribution Other | 26845 | 25828 | 25871 | 25905 | 26254 | 26416 | 26661 | 26904 | 27230 | 27353
Capacity | 61986 | 60848 | 61190 | 61246 | 61849 | 62064 | 62340 | 62505 | 62814 | 63030
132kV | 12683 | 12683 | 12872 | 12975 | 13228 | 13288 | 13288 | 13306 | 13392 | 13392
33kV | 10316 | 10242 | 10467 | 10535 | 10104 | 10164 | 10392 | 10360 | 10383 | 10383
Distribution | 14956 | 15206 | 14110 | 14149 | 14421 | 14504 | 14615 | 14719 | 14868 | 14923
| 37955 | 38131 | 37449 | 37659 | 37753 | 37956 | 38295 | 38385 | 38643 | 38698
Network ratios
km 11kV O/H/PMT | NIL: 0.57896; NIL: 0.57062; NIL: 0.5712; NIL: 0.56529; NIL: 0.56162; nil: 0.56127
km 11kV U/G/GMT | NIL: 0.59992; NIL: 0.59896; NIL: 0.60217; NIL: 0.61311; NIL: 0.61902; nil: 0.61741
cust/(PMT+GMT) | NIL: 52.4643; NIL: 52.1082; NIL: 52.827; NIL: 53.1929; NIL: 54.102; nil: 54.0866
HV O/H length (km) | 19543 | 19566 | 19695 | 19839 | 19696 | 19747 | 19547 | 19377 | 19352 | 19308
HV U/G length (km) | 15118 | 15292 | 15460 | 15571 | 15750 | 15928 | 16367 | 16675 | 16833 | 17046
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 1.3102 | 1.0504 | 1.2112 | 1.6014 | 0.58307 | 0.72817 | 0.27864 | 0.47816 | 1.3483 | 2.5748 | 0.95439 |  | 2.5748 | 0.27864
HV faults: U/G damage | 38.3785 | 37.9169 | 32.9654 | 30.588 | 46.726 | 45.8749 | 41.9756 | 42.0379 | 40.3101 | 51.1232 | 39.6415 |  | 51.1232 | 30.588
HV faults: O/H no damage | 8.8287 | 17.4131 | 9.064 | 16.7231 | 1.528 | 1.3754 | 0.039806 | 0.32576 | 2.4663 | 2.1228 | 6.4182 |  | 17.4131 | 0.039806
HV faults: O/H damage | 20.5196 | 26.6044 | 19.5006 | 18.2028 | 29.1133 | 29.6124 | 26.9488 | 20.3511 | 11.1588 | 15.3507 | 22.4458 |  | 29.6124 | 11.1588
Security - HV underground networks | 39.6887 | 38.9673 | 34.1766 | 32.1894 | 47.309 | 46.6031 | 42.2542 | 42.5161 | 41.6584 | 53.698 | 41.9061 |  | 53.698 | 32.1894 |  |  |  | 1 | 0
Security - HV overhead networks | 29.3483 | 44.0175 | 28.5646 | 34.9259 | 30.6413 | 30.9878 | 26.9886 | 20.6769 | 13.6251 | 17.4735 | 27.7249 |  | 44.0175 | 13.6251 |  |  |  | 1 | 1
customer supply interruptions per circuit km
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 100.784 | 74.7429 | 86.8041 | 127.7034 | 36.1905 | 78.8855 | 27.8643 | 35.8617 | 89.2255 | 176.8968 | 83.4959 |  | 176.8968 | 27.8643
HV faults: U/G damage | 3436.7344 | 3739.1653 | 3173.3952 | 3200.6941 | 4755.0315 | 4482.3122 | 4752.8524 | 3877.0505 | 3107.0306 | 4402.7643 | 3892.703 |  | 4755.0315 | 3107.0306
HV faults: O/H no damage | 559.7823 | 1210.949 | 717.8328 | 1337.9959 | 115.7597 | 102.7858 | 1.6665 | 36.0045 | 12.0729 | 91.9684 | 418.6818 |  | 1337.9959 | 1.6665
HV faults: O/H damage | 1556.1635 | 2344.5362 | 1779.5282 | 2050.7451 | 2458.2851 | 2370.5989 | 2424.7779 | 1765.9368 | 1177.9664 | 2104.861 | 2003.3399 |  | 2458.2851 | 1177.9664
Availability - HV underground networks | 3537.5184 | 3813.9082 | 3260.1992 | 3328.3976 | 4791.222 | 4561.1976 | 4780.7167 | 3912.9122 | 3196.2561 | 4579.6611 | 3976.1989 |  | 4791.222 | 3196.2561 |  |  |  | 1 | 1
Availability - HV overhead networks | 2115.9458 | 3555.4851 | 2497.361 | 3388.741 | 2574.0448 | 2473.3847 | 2426.4444 | 1801.9413 | 1190.0393 | 2196.8293 | 2422.0217 |  | 3555.4851 | 1190.0393 |  |  |  | 1 | 1
thousands of customer minutes lost per circuit km
| 99/2000: 10066.666 | #mains faults
| 99/2000: 9445.5527 | #faults restd within 3 hrs
0
0
| 99/2000: #DIV/0! | %age of all faults restored within 3 hrs
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01
| 2056930.875 | 2978205.1664 | 1846017.6735 | 2044336.8054 | 2685336.16 | 2876067.8301 | 2401129.0485 | 2006602.76 | 2223194.6769 | 2306097.5275
| 199354693.1 | 279749258.24 | 197678376.06 | 297449900.48 | 268976949.8 | 249589979.61 | 228320628.15 | 175677407.2 | 176894337 | 221932152

## B
East Midlands
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.27 | 1.7 | 1.77 | 2.14 | 2.26 | 2.14 | 1.56 | 1.36 | 0.87 | 0.72 | 1.579
LV faults | 5.92 | 6.56 | 8.3 | 9.25 | 7.95 | 6.98 | 6.44 | 6.32 | 6.44 | 7.52 | 7.168 | [8 empty] | 239241.2467
HV faults: U/G no damage | 0.65 | 0.96 | 1.51 | 1.26 | 1.2 | 3.34 | 3.81 | 4.81 | 5.47 | 1.59 | 2.46
HV faults: U/G damage | 24.08 | 23.3 | 25.4 | 27.8 | 26.15 | 22.59 | 28.12 | 26.86 | 22.72 | 26.57 | 25.359
HV faults: O/H no damage | 5.47 | 7.69 | 7.86 | 10.9 | 9.5 | 11.09 | 10.7 | 6.67 | 8.55 | 9.04 | 8.747
HV faults: O/H damage | 11.15 | 10.93 | 13.79 | 14.64 | 14.13 | 12.07 | 11.37 | 9.08 | 8.92 | 12.34 | 11.842 |  |  |  |  | 1719270
HV faults: All other | 10.65 | 10.86 | 13.65 | 12.47 | 10.55 | 13.48 | 10.41 | 10.35 | 11.75 | 19.65 | 12.382 |  |  |  |  | 1639880
HV faults: Total | 52 | 53.74 | 62.21 | 67.07 | 61.53 | 62.57 | 64.41 | 57.76 | 57.42 | 69.2 | 60.791 | 13.83% |  |  |  | 2018500 |  |  |  | 1458984
EHV faults | 5.71 | 4.56 | 8.5 | 11.22 | 7.32 | 9.86 | 12.42 | 6.18 | 8.39 | 7.21 | 8.137 | -11.39% |  |  |  | 2113980 |  |  |  | 195288
132kV faults | 5.47 | 1.13 | 5.36 | 1.59 | 12.32 | 7.39 | 3.69 | 0.87 | 1.88 | 3.51 | 4.321 | -18.77% |  |  |  | 2234680 |  |  |  | 103704
Total of (a) | 70.36 | 67.69 | 86.14 | 91.28 | 91.39 | 88.95 | 88.53 | 72.5 | 75 | 88.15 | 81.999 | 7.501% |  |  |  | 2186610
(b) Planned Outages | 9.21 | 6.85 | 5.62 | 4.82 | 5.75 | 4.58 | 4.58 | 3.97 | 2.8 | 3.23 | 5.141 | -37.17% |  |  |  | 2141300 |  |  |  | 123384
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.02 | 0 | 0 | 0 | 0 | 0 | 0.002 |  |  |  |  | 1758810
(d) Other Systems | 2.3 | 0 | 0 | 0 | 0 | 1.55 | 0 | 0 | 0 | 7.8 | 1.165 |  |  |  |  | 1867200 |  |  |  | 28008
Total of (a+b+c+d) | 81.87 | 74.54 | 91.75 | 96.09 | 97.16 | 95.07 | 93.1 | 76.47 | 77.8 | 91.38 | 87.523 | 4.407% | 97.16 | 74.54 |  | 2193120 | 84.163 | 1 | 0 | 2100552
[9 empty] | 75 | [6 empty] | 1800000
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 1.34 | 2.41 | 3.11 | 4.35 | 3.65 | 2.69 | 2.21 | 1.96 | 1.48 | 2.19 | 2.539
LV faults | 8.52 | 11.52 | 15.02 | 18.26 | 14.8 | 11.21 | 12.27 | 12 | 12.17 | 16.03 | 13.18 | [8 empty] | 43989950.22
HV faults: U/G no damage | 0.47 | 0.63 | 1.2 | 0.82 | 0.62 | 2.47 | 2.35 | 2.89 | 3.73 | 1.25 | 1.643
HV faults: U/G damage | 19.79 | 20.75 | 23.89 | 25.86 | 23.18 | 19.21 | 22.39 | 21.17 | 19.73 | 28.23 | 22.42
HV faults: O/H no damage | 5.02 | 5.38 | 5.2 | 8.73 | 7.52 | 7.04 | 7.34 | 3.78 | 5.98 | 11.84 | 6.783
HV faults: O/H damage | 11.63 | 13.16 | 14.94 | 16.65 | 16.28 | 12.11 | 12.09 | 9.03 | 10.92 | 24.09 | 14.09 |  |  |  |  | 183414000
HV faults: All other | 6.9 | 9.48 | 9.3 | 11.19 | 7.18 | 7.43 | 6.38 | 6.73 | 7.71 | 14.91 | 8.721 |  |  |  |  | 191114000
HV faults: Total | 43.81 | 49.4 | 54.52 | 63.26 | 54.79 | 48.26 | 50.55 | 43.59 | 48.08 | 80.31 | 53.657 | 49.67% |  |  |  | 214280000 |  |  |  | 179087159.253
EHV faults | 1.86 | 2.4 | 3.65 | 4.39 | 2.81 | 2.96 | 3.86 | 1.48 | 2.45 | 2.79 | 2.865 | -2.618% |  |  |  | 230846000 |  |  |  | 9562307.085
132kV faults | 0.48 | 0.01 | 4.11 | 0.66 | 2.59 | 0.98 | 0.84 | 0.11 | 0.12 | 0.96 | 1.086 | -11.6% |  |  |  | 217557000 |  |  |  | 3624665.094
Total of (a) | 56.02 | 65.73 | 80.4 | 90.92 | 78.64 | 66.09 | 69.73 | 59.13 | 64.3 | 101.58 | 73.254 | 38.67% |  |  |  | 181631000
(b) Planned Outages | 30.49 | 21.14 | 17 | 14.01 | 15.92 | 12.7 | 12.51 | 11.19 | 7.59 | 10.04 | 15.259 | -34.2% |  |  |  | 189152000 |  |  |  | 50928880.911
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.03 | 0 | 0 | 0 | 0 | 0 | 0.003 |  |  |  |  | 161736000
(d) Other Systems | 0.83 | 0 | 0 | 0 | 0 | 0.19 | 0 | 0 | 0 | 0 | 0.102 |  |  |  |  | 172536000 |  |  |  | 350451.045
Total of (a+b+c+d) | 87.34 | 86.87 | 97.4 | 104.93 | 94.59 | 78.97 | 82.24 | 70.32 | 71.89 | 111.62 | 88.617 | 25.96% | 111.62 | 70.32 |  | 267888000 | 85.7596 | 1 | 0 | 295770669.093
[9 empty] | 64.3 | [6 empty] | 154320000
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 77.09% | 69.04% | 66.04% | 63.55% | 66.55% | 73.33% | 65.51% | 65.37% | 64.85% | 64.98% | 67.63% | -3.92%
24 hours | 99.9% | 99.72% | 99.98% | 99.89% | 99.89% | 99.99% | 99.95% | 99.94% | 99.96% | 98.67% | 99.79% | -1.121%
HV Faults:U/G no damage 3 hours | 98.55% | 94.69% | 89.31% | 97.79% | 98.49% | 94.38% | 98.36% | 98.76% | 95.67% | 86.88% | 95.29% | -8.824%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.85% | 99.98% | -0.135%
HV Faults: U/G damage 3 hours | 94.97% | 92.67% | 91.85% | 94.09% | 93.75% | 94.6% | 95.04% | 94.54% | 92.58% | 88.4% | 93.25% | -5.2%
24 hours | 99.97% | 99.98% | 99.98% | 99.99% | 99.99% | 99.99% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
HV Faults: O/H no damage 3 hours | 88.26% | 92.19% | 94.01% | 90.15% | 91.99% | 95.06% | 93.55% | 97.31% | 92.85% | 80.02% | 91.54% | -12.58%
24 hours | 99.96% | 99.98% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.52% | 99.94% | -0.4242%
HV Faults: O/H damage 3 hours | 85.36% | 78.71% | 85.25% | 83.55% | 83.52% | 87.6% | 85.68% | 87.37% | 82.25% | 70.95% | 83.02% | -14.54%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.74% | 99.87% | -1.135%
HV Faults: Other 3 hours | 89.93% | 85.45% | 86.79% | 80.88% | 95.15% | 96.56% | 94.92% | 94.53% | 92.73% | 90.64% | 90.76%
24 hours | 99.95% | 100% | 99.96% | 99.86% | 100% | 100% | 100% | 100% | 100% | 99.87% | 99.96%
HV Faults: Total 3 hours | 91.86% | 89.2% | 90.83% | 90.04% | 91.46% | 93.74% | 93.31% | 94.08% | 91.33% | 84.92% | 91.08% | -6.76%
24 hours | 99.98% | 99.99% | 99.99% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.67% | 99.96% | -0.2911%
EHV Faults: 3 hours | 99.99% | 94.54% | 98.28% | 98.7% | 98.73% | 100% | 99.92% | 100% | 100% | 99.97% | 99.01% | 0.9665%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 93.61% | 100% | 100% | 100% | 100% | 99.99% | 100% | 98.64% | 99.22% | -0.5886%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 91.64% | 87.28% | 88.84% | 87.97% | 90.41% | 92.86% | 92.01% | 91.61% | 89.94% | 84.83% | 89.74% | -5.47% | 92.86% | 84.83% |  | 1583945.76
24 hours | 99.97% | 99.96% | 99.99% | 99.97% | 99.98% | 100% | 99.99% | 99.99% | 99.99% | 99.62% | 99.95% | -0.3262% | 100% | 99.62% |  | 1793160
TOTAL not rest in 3 hrs | 8.36% | 12.72% | 11.16% | 12.03% | 9.59% | 7.14% | 7.99% | 8.39% | 10.06% | 15.17% | 10.26% | 47.84% | 15.17% | 7.14% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.03% | 0.04% | 0.01% | 0.03% | 0.02% | 0% | 0.01% | 0.01% | 0.01% | 0.38% | 0.054% | 603.7% | 0.38% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers | [5 empty] | 0
| 2.072 | 2.215 | 1.557 | 1.101 | 1.087 | 0.865 | 0.987 | 1.107 | 0.736 | 0.513 | 1.224 | 10 | 2.215 | 0.513 |  |  |  | 1 | 1
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
EME total distribution system | 15.69 | 15.09 | 15.66 | 17.3 | 16.23 | 16.31 | 16.42 | 15.93 | 17.02 | 19.49 | 16.514 | -30.65% | 19.49 | 15.09 |  |  |  | 0 | 0
5 RELEVANT DATA:
Number of Customers | 2100000 | 2200000 | 2200000 | 2200000 | 2300000 | 2300000 | 2300000 | 2300000 | 2400000 | 2400000
Embedded Gen.Stations | 2 | 2 | 3 | 2 | 2 | 2 | 2 | 2 | 2 | 2
Emb.Gen.Capacity MWSO | 449 | 449 | 799 | 570 | 570 | 570 | 570 | 570 | 570 | 570
[8 empty] | %age overhead all voltages | 35.31%
Mains in commission (circuit kilometres) as at 30 September 1995
Overhead Line
132kV |  | 2243 | 2190 | 2183 | 2183 | 2183 | 2183 | 2183 | 2183 | 2183
66kV |  |  |  | 1272 | 0 | 0
33kV |  | 3691 | 3709 | 3615 | 3405 | 3251 | 3054 | 3030 | 3021 | 3011
25kV |  | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11 | 11
22kV |  |  |  | 5752 | 0 | 0
11kV |  | 13841 | 13792 | 13945 | 13636 | 13228 | 13225 | 13241 | 13249 | 13233
6.6kV |  | 41 | 41 | 41 | 41 | 41 | 41 | 40 | 36 | 36
3.3kV |  |  |  |  | 0 | 0 | 0
3kV |  |  |  |  | 0 | 0 | 0
2.2kV |  |  |  |  | 0 | 0 | 0
LV |  | 6410 | 6341 | 6143 | 6109 | 5904 | 5725 | 5613 | 5549 | 5498
TOTAL |  |  | 26237 | 32962 | 25943 | 24618 | 24239 | 24118 | 24049 | 23972
Underground cable
132kV |  | 164 | 164 | 193 | 163 | 163 | 163 | 164 | 164 | 164
66kV |  |  |  | 1138 | 0 | 0
33kV |  | 1530 | 1373 | 1360 | 1452 | 1454 | 1473 | 1473 | 1485 | 1482
25kV |  | 5 | 5 | 6 | 6 | 6 | 6 | 6 | 6 | 6
22kV |  |  |  | 10069.91 | 0 | 0
11kV |  | 10912 | 11027 | 11189 | 11896 | 12127 | 12300 | 12425 | 12526 | 12570
6.6kV |  | 942 | 890 | 880 | 902 | 898 | 899 | 897 | 897 | 897
3.3kV |  |  |  |  | 0 | 0
3kV |  |  |  |  | 0 | 0
LV |  | 26980 | 27044 | 27809 | 27995 | 28412 | 28477 | 28668 | 28975 | 29105
TOTAL |  |  |  | 52644.91 | 42414 | 40417 | 43318 | 43633 | 44053 | 44224
[8 empty] | 67751 | 68102
Transformers
Primary Voltage
132kV | [5 empty] | 185 | 181 | 180 | 180 | 181
33kV | [5 empty] | 685 | 688 | 694 | 701 | 706
Distribution pole-mounted | [5 empty] | 22026 | 22535 | 22443 | 22432 | 22738
Distribution Other | [5 empty] | 15536 | 15987 | 16359 | 18656 | 17050
Capacity | [8 empty] | 41969
132kV | [5 empty] | 11090 | 11141 | 11185 | 11185 | 11275
33kV | [5 empty] | 10985 | 11112 | 10998 | 11190 | 11266
Distribution | [5 empty] | 9349 | 9669 | 9886 | 11283 | 10288
[6 empty] | 31424 | 31922 | 32069 | 33658 | 32829
HV O/H length (km) | 13455.3333 | 13526.4444 | 13597.5556 | 13668.6667 | 13739.7778 | 13810.8889 | 13882 | 13281 | 13285 | 13384.2222
HV U/G length (km) | 10843.3333 | 11011.7778 | 11180.2222 | 11348.6667 | 11517.1111 | 11685.5556 | 11854 | 13322 | 13423 | 13467
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 1.2588 | 1.9179 | 2.9713 | 2.4426 | 2.3964 | 6.5739 | 7.3924 | 8.3043 | 9.7802 | 2.8336 | 4.5872 |  | 9.7802 | 1.2588
HV faults: U/G damage | 46.6351 | 46.5502 | 49.9811 | 53.8918 | 52.2223 | 44.4626 | 54.5605 | 46.3729 | 40.6228 | 47.3513 | 48.2651 |  | 54.5605 | 40.6228
HV faults: O/H no damage | 8.5371 | 12.5074 | 12.717 | 17.5438 | 15.9027 | 18.4688 | 17.728 | 11.5511 | 15.446 | 16.2101 | 14.6612 |  | 18.4688 | 8.5371
HV faults: O/H damage | 17.402 | 17.777 | 22.3114 | 23.5634 | 23.6532 | 20.1008 | 18.8381 | 15.7247 | 16.1144 | 22.1275 | 19.7613 |  | 23.6532 | 15.7247
HV underground networks | 47.8939 | 48.4681 | 52.9524 | 56.3344 | 54.6187 | 51.0365 | 61.9529 | 54.6772 | 50.403 | 50.1849 | 52.8522 |  | 61.9529 | 47.8939 |  |  |  | 1 | 0
HV overhead networks | 25.9392 | 30.2844 | 35.0284 | 41.1072 | 39.556 | 38.5696 | 36.5661 | 27.2758 | 31.5604 | 38.3377 | 34.4225 |  | 41.1072 | 25.9392 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 91.0237 | 125.8652 | 236.1313 | 158.9614 | 123.8158 | 486.1557 | 455.9642 | 498.9491 | 666.915 | 222.7668 | 306.6548 |  | 666.915 | 91.0237
HV faults: U/G damage | 3832.6775 | 4145.5613 | 4700.9799 | 5013.0999 | 4629.1122 | 3780.9927 | 4344.272 | 3654.9317 | 3527.6764 | 5030.9646 | 4266.0268 |  | 5030.9646 | 3527.6764
HV faults: O/H no damage | 783.4811 | 875.0267 | 841.3277 | 1405.1114 | 1258.8268 | 1172.4082 | 1216.1072 | 654.6194 | 1080.3161 | 2123.0968 | 1141.0322 |  | 2123.0968 | 654.6194
HV faults: O/H damage | 1815.1167 | 2140.3999 | 2417.1992 | 2679.8517 | 2725.226 | 2016.742 | 2003.0975 | 1563.813 | 1972.7512 | 4319.7131 | 2365.391 |  | 4319.7131 | 1563.813
HV underground networks | 3923.7012 | 4271.4266 | 4937.1112 | 5172.0613 | 4752.928 | 4267.1484 | 4800.2362 | 4153.8808 | 4194.5914 | 5253.7313 | 4572.6816 |  | 5253.7313 | 3923.7012 |  |  |  | 1 | 0
HV overhead networks | 2598.5978 | 3015.4266 | 3258.5269 | 4084.9632 | 3984.0528 | 3189.1503 | 3219.2047 | 2218.4323 | 3053.0674 | 6442.8099 | 3506.4232 |  | 6442.8099 | 2218.4323 |  |  |  | 1 | 0
11590.9604
10424.9098
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1719270 | 1639880 | 2018500 | 2113980 | 2234680 | 2186610 | 2141300 | 1758810 | 1867200 | 2193120
| 183414000 | 191114000 | 214280000 | 230846000 | 217557000 | 181631000 | 189152000 | 161736000 | 172536000 | 267888000

## C
London
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 2.44 | 2.11 | 2.21 | 2.31 | 1.71 | 1.59 | 2.33 | 1.95 | 1.79 | 1.26 | 1.97
LV faults | 5.88 | 5.28 | 4.96 | 4.89 | 4.05 | 4.77 | 4.67 | 5.33 | 4.39 | 4.87 | 4.909 | [8 empty] | 163844.2076
HV faults: U/G no damage | 0.05 | 1.6 | 0 | 0.23 | 0.85 | 0 | 0.27 | 0.04 | 0 | 0.14 | 0.318
HV faults: U/G damage | 17.04 | 18.03 | 25.29 | 26.26 | 20.41 | 24.83 | 23.35 | 19.43 | 21.3 | 24.78 | 22.072
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 913331.9
HV faults: All other | 4.77 | 3.44 | 2.09 | 2.19 | 1.42 | 2.13 | 2.64 | 5.74 | 4.9 | 1.93 | 3.125 |  |  |  |  | 738765.6
HV faults: Total | 21.85 | 23.06 | 27.37 | 28.68 | 22.68 | 26.96 | 26.27 | 25.21 | 26.2 | 26.85 | 25.513 | 5.24% |  |  |  | 689838.4 |  |  |  | 528119.1
EHV faults | 4.61 | 4.36 | 0 | 1.03 | 0.67 | 1.57 | 1.8 | 1.4 | 0.3 | 5.74 | 2.148 | 167.2% |  |  |  | 767594.3 |  |  |  | 44463.6
132kV faults | 9.56 | 2.66 | 0 | 1.03 | 0.35 | 1.7 | 2.8 | 1.42 | 1.87 | 0 | 2.139 | -100% |  |  |  | 645992.4 |  |  |  | 44277.3
Total of (a) | 44.35 | 37.47 | 34.55 | 37.95 | 29.46 | 36.6 | 37.87 | 35.33 | 34.55 | 38.72 | 36.685 | 5.547% |  |  |  | 758458.8
(b) Planned Outages | 2.33 | 0.65 | 1.24 | 1.76 | 3.59 | 1.92 | 1.31 | 1.56 | 1.64 | 1.03 | 1.703 | -39.52% |  |  |  | 776547.6 |  |  |  | 35252.1
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 741857.9
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 745514 |  |  |  | 0
Total of (a+b+c+d) | 46.67 | 38.12 | 35.78 | 39.71 | 33.06 | 38.52 | 39.18 | 36.89 | 36.19 | 39.75 | 38.387 | 3.551% | 46.67 | 33.06 |  | 822825 | 84.163 | 0 | 0 | 794610.9
[9 empty] | 34.55 | [6 empty] | 711730
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | ¢ | ¢ | 5.54 | 5.36 | [5 empty] | ¢ | 2.18
LV faults | 18.38 | 17.1 | 16.69 | 18.71 | 16.44 | 16.96 | 16.27 | 18.92 | 16.43 | 18.05 | 17.395 | [8 empty] | 58058056.455
HV faults: U/G no damage | 0.11 | 2.32 | 0 | 0.36 | 1.08 | 0 | 0.4 | 0.01 | 0 | 0.1 | 0.438
HV faults: U/G damage | 23.29 | 25.85 | 30.06 | 31.96 | 25.65 | 30.7 | 25.94 | 18.73 | 13.83 | 15.7 | 24.171
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 131725670
HV faults: All other | 5.66 | 4.03 | 2.27 | 2.14 | 1.77 | 2.17 | 2.68 | 3.67 | 3.53 | 1.23 | 2.915 |  |  |  |  | 102287640
HV faults: Total | 29.06 | 32.2 | 32.34 | 34.46 | 28.5 | 32.87 | 29.02 | 22.42 | 17.36 | 17.04 | 27.527 | -38.1% |  |  |  | 99870400 |  |  |  | 91874913.483
EHV faults | 8.26 | 1.54 | 0 | 0.8 | 0.31 | 1.71 | 1.16 | 0.9 | 0.45 | 5.55 | 2.068 | 168.4% |  |  |  | 112229980 |  |  |  | 6902216.772
132kV faults | 5.43 | 0.05 | 0 | 0.07 | 0.03 | 0.17 | 1.05 | 0.04 | 1.28 | 0 | 0.812 | -100% |  |  |  | 105398760 |  |  |  | 2710154.748
Total of (a) | 61.12 | 50.89 | 49.03 | 54.03 | 45.27 | 51.71 | 47.5 | 42.27 | 35.52 | 40.64 | 47.798 | -14.98% |  |  |  | 110106480
(b) Planned Outages | 6.19 | 1.89 | 2.77 | 4.04 | 8.67 | 4.21 | 2.55 | 2.94 | 3.23 | 2.85 | 3.934 | -27.55% |  |  |  | 99199100 |  |  |  | 13130232.486
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 90917310
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 79845600 |  |  |  | 0
Total of (a+b+c+d) | 67.31 | 52.78 | 51.8 | 58.06 | 53.94 | 55.92 | 50.05 | 45.21 | 38.76 | 43.49 | 51.732 | -15.93% | 67.31 | 38.76 |  | 90024300 | 85.7596 | 1 | 1 | 172662223.428
[9 empty] | 35.53 | [6 empty] | 73191800
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 80.2% | 54.07% | 53.07% | 44.8% | 40.31% | 39.53% | 46.57% | 39.83% | 43.01% | 36.13% | 47.75% | -9.93%
18 hours | 99.56% | 99.59% | 99.88% | 99.96% | 99.61% | 99.84% | 99.93% | 99.85% | 99.83% | 99.17% | 99.72% | 0.1083%
HV Faults:U/G no damage 3 hours | 30% | 73.56% | # | 97.53% | 93.5% | # | 69.66% | 100% | # | 94.41% | 55.87% | #VALUE!
18 hours | 100% | 100% | # | 100% | 100% | # | 100% | 100% | 100% | 100% | 80% | 25%
HV Faults: U/G damage 3 hours | 78.68% | 81.54% | 92.63% | 88.29% | 88.77% | 88.15% | 89.09% | 92.74% | 95.27% | 93.19% | 88.83% | 7.244%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: O/H no damage 3 hours | # | # | # | # | # | # | # | # | # | # | 0%
18 hours | # | # | # | # |  | # | # | # | # | # | 0%
HV Faults: O/H damage 3 hours | # | # | # | # | # | # | # | # | # | # | 0%
18 hours | # | # | # | # | # | # | # | # | # | # | 0%
HV Faults: Other 3 hours | 87.72% | 84.48% | 83.28% | 93.97% | 95.97% | 86.02% | 63.32% | 85.98% | 83.02% | 75.6% | 83.94%
18 hours | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
HV Faults: Total 3 hours | 78.07% | 81.54% | 92.35% | 88.9% | 89.32% | 87.98% | 89.29% | 92.2% | 94.21% | 93.16% | 88.7% | 6.21%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
EHV Faults: 3 hours | 67.38% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 87.92% | 95.53% | 4.679%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | # | 100% | 100% | 100% | 100% | 100% | 83.41% | 100% | 88.34% | -5.582%
18 hours | 100% | 100% | # | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 90% | 11.11%
Total Faults:3 hours | 77.67% | 79.59% | 84.2% | 81.14% | 80.1% | 80.63% | 82.69% | 82.02% | 84.5% | 83.36% | 81.59% | 3.567% | 84.5% | 77.67% |  | 629959.33
18 hours | 99.92% | 99.92% | 99.97% | 99.99% | 99.92% | 99.97% | 99.99% | 99.98% | 99.97% | 99.95% | 99.96% | 0.01201% | 99.99% | 99.92% |  | 745290.3458
TOTAL not rest in 3 hrs | 22.33% | 20.41% | 15.8% | 18.86% | 19.9% | 19.37% | 17.31% | 17.98% | 15.5% | 16.64% | 18.41% | -15.81% | 22.33% | 15.5% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.08% | 0.08% | 0.03% | 0.01% | 0.08% | 0.03% | 0.01% | 0.02% | 0.03% | 0.05% | 0.042% | -28.57% | 0.08% | 0.01% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC | 0 | 2 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | N/A
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action |  | 0 | 0 | 0 | [5 empty] | 0 |  | N/A
- Voltage Reductions | 0.026 | 0.003 | 0 | 0.003 | 0.001 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0.008 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0.033 | 0.003 | 0 | 0.003 | 0.001 | 0 | 0 | 0 | 0 | 0 |  | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 0.302 | 0.614 | 0.581 | 0.269 | 0.169 | 0.168 | 0.121 | 0.204 | 0.369 | 0.111 | 0.2908 | 9 | 0.614 | 0.111 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 14.44 | 14.73 | 16.17 | 17.11 | 15.73 | 14.58 | 14.31 | 14.61 | 14.98 | 16.49 | 15.315 | -25.34% | 17.11 | 14.31 |  |  |  | 0 | 0
5 RELEVANT DATA:
Number of Customers | 1957000 | 1938000 | 1928000 | 1933000 | 1954000 | 1969000 | 1982000 | 2011000 | 2060000 | 2070000 |  | N/A
Embedded Gen.Stations | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 |  | N/A
Emb.Gen.Capacity MWSO | 140 | 140 | 140 | 132 | 132 | 132 | 132 | 132 | 132 | 132 |  | N/A
[8 empty] | %age overhead all voltages | 0.1353%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 38 | 38 | 38 | 38 | 38 | 26 | 26 | 28 | 28
66kV |  | 13 | 13 | 13 | 13 | 13 | 12 | 12 | 12 | 12
33kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25kV
22kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11kV |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
6.6kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3.3kV |  | 11 | 11 | 11
3kV
2.2kV
LV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL |  | 63 | 52 | 52 | 52 | 52 | 39 | 39 | 41 | 42
Underground cable
132kV |  | 465 | 467 | 480 | 480 | 485 | 413 | 493 | 492 | 470
66kV |  | 535 | 540 | 540 | 546 | 570 | 406 | 430 | 424 | 445
33kV |  | 597 | 622 | 623 | 623 | 623 | 621 | 649 | 650 | 638
25kV
22kV |  | 276 | 270 | 270 | 278 | 278 | 268 | 256 | 256 | 215
11kV |  | 6564 | 6603 | 6610 | 6621 | 6651 | 8013 | 8045 | 8126 | 8217
6.6kV |  | 1706 | 1706 | 1706 | 1706 | 1708 | 642 | 639 | 640 | 640
3.3kV |  | 388 | 383 | 376
3kV
LV |  | 19486 | 19514 | 19543 | 19559 | 19590 | 19593 | 19608 | 19673 | 19717
TOTAL |  |  | 30105 | 29629 | 29722 | 29772 | 29813 | 30120 | 30261 | 30342
30302
Transformers
Primary Voltage
132kV | [5 empty] | 137 | 143 | 146 | 146 | 146
33kV | [5 empty] | 267 | 261 | 255 | 255 | 252
Distribution pole-mounted | [5 empty] | 0 | 0 | 0 | 0 | 0
Distribution Other | [6 empty] | 12869 | 13033 | 13191 | 13870
Capacity | [8 empty] | 13592 | 14268
132kV | [5 empty] | 6578 | 6861 | 7041 | 7041 | 7041
33kV | [5 empty] | 4334 | 4244 | 4154 | 4154 | 4080
Distribution | [5 empty] | 8939 | 8961 | 9174 | 8274 | 9802
[6 empty] | 19851 | 20066 | 20369 | 19469 | 20923
HV O/H length (km) | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
HV U/G length (km) | 8016.8267 | 8059.0222 | 8101.2178 | 8143.4133 | 8185.6089 | 8227.8044 | 8270 | 8684 | 8766 | 8857
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 0.12206 | 3.8476 | 0 | 0.54595 | 2.029 | 0 | 0.64709 | 0.09263 | 0 | 0.3272 | 0.76116 |  | 3.8476 | 0
HV faults: U/G damage | 41.5966 | 43.3578 | 60.1874 | 62.3333 | 48.721 | 59.4208 | 55.9609 | 44.9951 | 50.0548 | 57.9142 | 52.4542 |  | 62.3333 | 41.5966
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV underground networks | 41.7187 | 47.2054 | 60.1874 | 62.8792 | 50.7501 | 59.4208 | 56.608 | 45.0877 | 50.0548 | 58.2414 | 53.2153 |  | 62.8792 | 41.7187 |  |  |  | 1 | 0
HV overhead networks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0
customer supply interruptions per circuit km
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 26.8523 | 557.9039 | 0 | 85.4531 | 257.8086 | 0 | 95.8646 | 2.3158 | 0 | 23.3713 | 104.957 |  | 557.9039 | 0
HV faults: U/G damage | 5685.358 | 6216.3 | 7153.9467 | 7586.3373 | 6122.9532 | 7346.8324 | 6216.8174 | 4337.4056 | 3250.0342 | 3669.3011 | 5758.5286 |  | 7586.3373 | 3250.0342
HV faults: O/H no damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV faults: O/H damage | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
HV underground networks | 5712.2103 | 6774.2039 | 7153.9467 | 7671.7904 | 6380.7617 | 7346.8324 | 6312.682 | 4339.7213 | 3250.0342 | 3692.6725 | 5863.4855 |  | 7671.7904 | 3250.0342 |  |  |  | 1 | 1
HV overhead networks | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  |  |  | 0 | 0
thousands of customer minutes lost per circuit km
4539.2396
3835.6575
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 913331.9 | 738765.6 | 689838.4 | 767594.3 | 645992.4 | 758458.8 | 776547.6 | 741857.9 | 745514 | 822825
| 131725670 | 102287640 | 99870400 | 112229980 | 105398760 | 110106480 | 99199100 | 90917310 | 79845600 | 90024300

## D
Manweb
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.43 | 1.279 | 1.6 | 1.39 | 1.11 | 1.16 | 1.29 | 1.11 | 1.29 | 1.45 | 1.3109
LV faults | 4.76 | 4.28 | 4.75 | 4.72 | 5.19 | 4.32 | 4.62 | 4.29 | 4.39 | 4.54 | 4.586 | [8 empty] | 153063.6659
HV faults: U/G no damage | 2.9 | 3.39 | 3.56 | 2.27 | 1.13 | 2.71 | 1.06 | 2.33 | 0.73 | 0.59 | 2.067
HV faults: U/G damage | 8.09 | 8.96 | 7.68 | 7.82 | 10.78 | 9.86 | 8.4 | 8.58 | 13.56 | 12.96 | 9.669
HV faults: O/H no damage | 11.17 | 19.75 | 12.2 | 10.77 | 11.52 | 11.06 | 8.36 | 10.35 | 7.47 | 7.06 | 10.971
HV faults: O/H damage | 11.67 | 10.11 | 13.18 | 9.94 | 8.05 | 11.54 | 15.81 | 7.85 | 8.81 | 9.41 | 10.637 |  |  |  |  | 967600
HV faults: All other | 3.76 | 3.85 | 3.28 | 3.14 | 4.13 | 3.41 | 3.89 | 3.08 | 5.44 | 7.21 | 4.119 |  |  |  |  | 1135055.98
HV faults: Total | 37.59 | 46.06 | 39.9 | 33.94 | 35.6 | 38.58 | 37.52 | 32.19 | 36.01 | 37.23 | 37.462 | -0.6193% |  |  |  | 1181571.2 |  |  |  | 539421.7065
EHV faults | 12.62 | 19.53 | 10.27 | 14.46 | 10.01 | 5.63 | 8.1 | 2.5 | 6.36 | 6.77 | 9.625 | -29.66% |  |  |  | 942738.4 |  |  |  | 138592.0113
132kV faults | 1.91 | 0 | 0 | 2.45 | 0.96 | 1.51 | 0.46 | 0 | 1.58 | 0 | 0.887 | -100% |  |  |  | 834555 |  |  |  | 12772.0638
Total of (a) | 58.31 | 71.149 | 56.52 | 56.97 | 52.87 | 51.19 | 51.99 | 40.08 | 49.63 | 49.99 | 53.8699 | -7.202% |  |  |  | 784074.9
(b) Planned Outages | 15.44 | 14.71 | 14.68 | 12.94 | 8.62 | 6 | 5.34 | 4.05 | 3.37 | 3 | 8.815 | -65.97% |  |  |  | 792300.6 |  |  |  | 126928.6836
(c) Embedded Gen. | 0 | 0 | 0.19 | 0.02 | 0 | 0 | 0 | 0 | 0.08 | 0.02 | 0.031 |  |  |  |  | 614730.9
(d) Other Systems | 0 | 0 | 17.25 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0 | 1.736 |  |  |  |  | 743650.8 |  |  |  | 25443.3334
Total of (a+b+c+d) | 73.75 | 85.859 | 88.64 | 70.04 | 61.5 | 57.19 | 57.33 | 44.13 | 53.08 | 53.01 | 64.4529 | -17.75% | 88.64 | 44.13 |  | 763300.0017 | 84.163 | 1 | 0 | 928068.2641
[9 empty] | 49.71 | 50.01 | [5 empty] | 696437.1
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 2.25 | 1.81 | 2.5 | 1.78 | 1.51 | 1.37 | 1.48 | 1.27 | 1.81 | 2.09 | 1.787
LV faults | 7.8 | 7.02 | 7.37 | 6.52 | 7.24 | 5.85 | 9.9 | 5.43 | 5.76 | 6.67 | 6.956 | [8 empty] | 23305556.3
HV faults: U/G no damage | 3.12 | 3.41 | 4.13 | 2.16 | 1.22 | 2.93 | 1.06 | 1.92 | 0.89 | 0.51 | 2.135
HV faults: U/G damage | 10.79 | 9.7 | 9.58 | 10.85 | 13.64 | 12.17 | 9.95 | 9.6 | 14.66 | 13.65 | 11.459
HV faults: O/H no damage | 10.47 | 26.63 | 14.31 | 11.68 | 17.1 | 9.9 | 6.64 | 9.53 | 6.52 | 6.78 | 11.956
HV faults: O/H damage | 14.91 | 17.02 | 20.79 | 12.99 | 10.99 | 22.26 | 46.71 | 13.33 | 9.98 | 10.38 | 17.936 |  |  |  |  | 142299520
HV faults: All other | 4.41 | 4.48 | 3.41 | 3.4 | 5.26 | 3.68 | 3.69 | 3.29 | 5.02 | 6.53 | 4.317 |  |  |  |  | 170921380
HV faults: Total | 43.7 | 61.24 | 52.22 | 41.09 | 48.21 | 50.94 | 68.05 | 37.68 | 37.07 | 37.85 | 47.805 | -20.82% |  |  |  | 161013070 |  |  |  | 160167067.125
EHV faults | 8.62 | 13.43 | 8.73 | 16.21 | 7.56 | 3.03 | 4.58 | 1.24 | 3.28 | 2.53 | 6.921 | -63.44% |  |  |  | 137022800 |  |  |  | 23188291.425
132kV faults | 0.1 | 0 | 0 | 0.53 | 0.04 | 0.21 | 0.06 | 0 | 0.46 | 0 | 0.14 | -100% |  |  |  | 119918090 |  |  |  | 469059.5
Total of (a) | 62.47 | 83.5 | 70.82 | 66.14 | 64.56 | 61.41 | 84.07 | 45.61 | 48.38 | 49.14 | 63.61 | -22.75% |  |  |  | 106266210
(b) Planned Outages | 45.99 | 45.79 | 43.2 | 35.61 | 23.81 | 16.1 | 12.63 | 9.08 | 7.24 | 5.94 | 24.539 | -75.79% |  |  |  | 133639400 |  |  |  | 82216079.075
(c) Embedded Gen. | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.04 | 0.01 | 0.015 |  |  |  |  | 76183170
(d) Other Systems | 0 | 0 | 6.67 | 0.06 | 0 | 0 | 0 | 0 | 0 | 0 | 0.673 |  |  |  |  | 77979660 |  |  |  | 2305092.4
Total of (a+b+c+d) | 108.46 | 129.29 | 120.79 | 101.8 | 88.37 | 77.51 | 96.7 | 54.69 | 55.66 | 55.09 | 88.836 | -37.99% | 129.29 | 54.69 | 63.46 | 79325027.53 | 85.7596 | 1 | 0 | 297638355.3
[9 empty] | 48.42 | 49.15 | [5 empty] | 67836420
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 72.57% | 74.91% | 76.85% | 80.62% | 80.24% | 81.9% | 79.89% | 82.42% | 77.62% | 73.87% | 78.09% | -0.6006%
18 hours | 99.7% | 99.79% | 99.68% | 99.95% | 99.96% | 99.7% | 97.98% | 99.99% | 100% | 99.94% | 99.67% | 0.3321%
HV Faults:U/G no damage 3 hours | 85.44% | 91.56% | 88.92% | 97.63% | 92.83% | 87.46% | 95.78% | 89.03% | 82.14% | 98.52% | 90.93% | -9.668%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 82.8% | 91.72% | 85.7% | 82.84% | 85.75% | 86.59% | 87.42% | 89.17% | 88.28% | 90.81% | 87.11% | 1.345%
18 hours | 99.9% | 99.91% | 99.98% | 100% | 99.92% | 100% | 100% | 100% | 100% | 100% | 99.97% | 0.02901%
HV Faults: O/H no damage 3 hours | 90.76% | 84.25% | 85.42% | 91.49% | 80.18% | 92.99% | 94.01% | 88.83% | 89.9% | 89.02% | 88.69% | 1.37%
18 hours | 100% | 99.84% | 99.65% | 99.3% | 99% | 99.67% | 99.97% | 100% | 100% | 99.99% | 99.74% | 0.2587%
HV Faults: O/H damage 3 hours | 78.19% | 70.31% | 77.41% | 83.36% | 81.63% | 76.07% | 67.44% | 74.26% | 80.5% | 84.15% | 77.33% | 4.097%
18 hours | 99.98% | 99.97% | 100% | 100% | 99.72% | 97.25% | 95.51% | 100% | 100% | 99.72% | 99.22% | 0.7912%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
24 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 84.03% | 83.62% | 83.33% | 86.82% | 82.88% | 85.08% | 80.75% | 85.24% | 86.81% | 88.16% | 84.67% | 4.119%
18 hours | 99.98% | 99.9% | 99.89% | 99.75% | 99.51% | 99.08% | 98.1% | 100% | 100% | 99.93% | 99.61% | 0.3172%
EHV Faults: 3 hours | 97.04% | 98.29% | 97.62% | 88.59% | 97.55% | 98.19% | 99.15% | 94.08% | 100% | 99.96% | 97.05% | 3.002%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | n/a | 100% | 100% | 100% | 100% | 100% | 100% | 100% | n/a | 80% | #VALUE!
18 hours | 100% | n/a | 100% | 100% | 100% | 100% | 100% | 100% | 100% | n/a | 80% | #VALUE!
Total Faults:3 hours | 86.15% | 86.96% | 85.2% | 87.17% | 85.65% | 86.62% | 83.69% | 85.41% | 87.87% | 88.05% | 86.28% | 2.055% | 88.05% | 83.69% |  | 654784.5294
18 hours | 99.96% | 99.92% | 99.88% | 99.85% | 99.67% | 99.27% | 98.4% | 100% | 100% | 99.94% | 99.69% | 0.2518% | 100% | 98.4% |  | 743204.6095
TOTAL not rest in 3 hrs | 13.85% | 13.04% | 14.8% | 12.83% | 14.35% | 13.38% | 16.31% | 14.59% | 12.13% | 11.95% | 13.72% | -12.92% | 16.31% | 11.95% | 11.14% |  |  | 1 | 1
TOTAL not rest in 18 hrs | 0.04% | 0.08% | 0.12% | 0.15% | 0.33% | 0.73% | 1.6% | 0% | 0% | 0.06% | 0.311% | -80.71% | 1.6% | 0% | 0% |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0
(b) due to plc action
- Voltage Reductions | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
-Total | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.84 | 1.63 | 2.85 | 2.56 | 2.01 | 1.61 | 2.54 | 1.66 | 2 | 1.53 | 2.023 | -24.37% | 2.85 | 1.53 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Total distribution system | 18.37 | 21.646 | 18.12 | 17.96 | 18.01 | 16.54 | 17.11 | 15 | 15.24 | 16.55 | 17.4546 | -13.51% | 21.646 | 15 | 15.97 |  |  | 1 | 0
5 RELEVANT DATA:
Number of Customers | 1312000 | 1322000 | 1333000 | 1346000 | 1357000 | 1371000 | 1382000 | 1393000 | 1401000 | 1439917
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
* Data Unavailable | [7 empty] | %age overhead all voltages | 47.25% | 47.24%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 1253.95 | 1235 | 1235 | 1275 | 1300 | 1299 | 1299 | 1299 | 1299
66kV
33kV |  | 1922.433 | 1944 | 1959 | 1963 | 1984 | 2021 | 2006 | 2006 | 2006
25kV
22kV
11kV |  | 12851.33 | 12903 | 12964 | 13018 | 13061 | 13069 | 13052 | 13052 | 13052
6.6kV |  | 45.401 | 45 | 45 | 45 | 2 | 2 | 2 | 2 | 2
3.3kV
3kV
2.2kV
LV |  | 5105.507 | 5092 | 5081 | 5093 | 5093 | 5141 | 5112 | 5088 | 5208
TOTAL |  | 21178.621 | 21219 | 21284 | 21394 | 21440 | 21532 | 21471 | 21477 | 21567
Underground cable
132kV |  | 213.074 | 211 | 211 | 212 | 213 | 213 | 213 | 213 | 213
66kV
33kV |  | 1387.178 | 1404 | 1413 | 1418 | 1427 | 1455 | 1491 | 1501 | 1521
25kV
22kV
11kV |  | 4706.065 | 4769 | 4895 | 4974 | 4984 | 5044 | 5143 | 5172 | 5218
6.6kV |  | 1136.547 | 1159 | 1172 | 1184 | 1174 | 1174 | 1149 | 1149 | 1149
3.3kV
3kV
LV |  | 15186.726 | 15290 | 15473 | 15640 | 15663 | 15705 | 15846 | 15939 | 15985
TOTAL |  |  |  | 22629.59 | 22833 | 23164 | 23428 | 23842 | 23974 | 24086
[9 empty] | 45451 | 45653
Transformers
Primary Voltage
132kV | [5 empty] | 78 | 78 | 78 | 79 | 79
33kV | [5 empty] | 602 | 597 | 611 | 611 | 632
Distribution pole-mounted | [5 empty] | 30836 | 31186 | 31280 | 31455 | 31923
Distribution Other | [5 empty] | 9536 | 9627 | 9663 | 9712 | 9823
Capacity | [6 empty] | 41488 | 41632 | 41857 | 42457
132kV | [5 empty] | 6559 | 6685 | 6685 | 6775 | 6775
33kV | [5 empty] | 4710 | 4893 | 5003 | 5003 | 5258
Distribution | [5 empty] | 5389 | 5427 | 5420 | 5449 | 5909
[6 empty] | 16657 | 17005 | 17108 | 17227 | 17942
HV O/H length (km) | 12849.577 | 12857.436 | 12865.295 | 12873.154 | 12881.013 | 12888.872 | 12896.731 | 13054 | 13054 | 13054
HV U/G length (km) | 5774.204 | 5785.6053 | 5797.0067 | 5808.408 | 5819.8093 | 5831.2107 | 5842.612 | 6292 | 6321 | 6367
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 6.5893 | 7.7461 | 8.1861 | 5.2603 | 2.6348 | 6.3716 | 2.5073 | 5.1584 | 1.618 | 1.3343 | 4.7406 |  | 8.1861 | 1.3343
HV faults: U/G damage | 18.3819 | 20.4734 | 17.6599 | 18.1215 | 25.1356 | 23.1823 | 19.8692 | 18.9955 | 30.0547 | 29.3094 | 22.1183 |  | 30.0547 | 17.6599
HV faults: O/H no damage | 11.4051 | 20.3069 | 12.6407 | 11.261 | 12.1362 | 11.7646 | 8.9585 | 11.0445 | 8.0171 | 7.7875 | 11.5322 |  | 20.3069 | 7.7875
HV faults: O/H damage | 11.9156 | 10.3951 | 13.6561 | 10.3931 | 8.4806 | 12.2752 | 16.9418 | 8.3768 | 9.4552 | 10.3797 | 11.2269 |  | 16.9418 | 8.3768
HV underground networks | 24.9712 | 28.2195 | 25.846 | 23.3819 | 27.7704 | 29.5538 | 22.3765 | 24.1539 | 31.6727 | 30.6437 | 26.859 |  | 31.6727 | 22.3765 |  |  |  | 0 | 0
HV overhead networks | 23.3207 | 30.702 | 26.2967 | 21.6541 | 20.6168 | 24.0398 | 25.9003 | 19.4213 | 17.4723 | 18.1672 | 22.7591 |  | 30.702 | 17.4723 |  |  |  | 1 | 1
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 708.9185 | 779.1786 | 949.6781 | 500.5434 | 284.4664 | 688.8844 | 250.7303 | 425.0731 | 197.2615 | 115.3381 | 490.0072 |  | 949.6781 | 115.3381
HV faults: U/G damage | 2451.6765 | 2216.4319 | 2202.8852 | 2514.3034 | 3180.4272 | 2861.3389 | 2353.5535 | 2125.3655 | 3249.2738 | 3086.9903 | 2624.2246 |  | 3249.2738 | 2125.3655
HV faults: O/H no damage | 1069.0344 | 2738.0933 | 1482.6889 | 1221.2454 | 1801.4655 | 1053.0712 | 711.5353 | 1016.9519 | 699.7487 | 747.8656 | 1254.17 |  | 2738.0933 | 699.7487
HV faults: O/H damage | 1522.3785 | 1749.9943 | 2154.0952 | 1358.2173 | 1157.7839 | 2367.8147 | 5005.394 | 1422.4521 | 1071.0878 | 1144.9623 | 1895.418 |  | 5005.394 | 1071.0878
HV underground networks | 3160.5949 | 2995.6105 | 3152.5632 | 3014.8468 | 3464.8936 | 3550.2233 | 2604.2838 | 2550.4387 | 3446.5354 | 3202.3284 | 3114.2319 |  | 3550.2233 | 2550.4387 |  |  |  | 0 | 0
HV overhead networks | 2591.4129 | 4488.0877 | 3636.7841 | 2579.4627 | 2959.2494 | 3420.8859 | 5716.9294 | 2439.404 | 1770.8365 | 1892.8279 | 3149.588 |  | 5716.9294 | 1770.8365 |  |  |  | 1 | 1
6926.7324
6086.5198
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 967600 | 1135055.98 | 1181571.2 | 942738.4 | 834555 | 784074.9 | 792300.6 | 614730.9 | 743650.8 | 763300.0017
| 142299520 | 170921380 | 161013070 | 137022800 | 119918090 | 106266210 | 133639400 | 76183170 | 77979660 | 79325027.53

## E
Midlands
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.16 | 0.16 | 0.19 | 0.21 | 0.31 | 0.3 | 0.26 | 0.25 | 0.29 | 0.29 | 0.242
LV faults | 5.71 | 5.34 | 7.9 | 10.92 | 13.33 | 12.19 | 10.03 | 10.07 | 8.32 | 13.59 | 9.74 | [8 empty] | 325085.0646
HV faults: U/G no damage | 0.82 | 0.86 | 0.5 | 2.83 | 1.38 | 3.72 | 4.28 | 5.02 | 2.17 | 2.37 | 2.395
HV faults: U/G damage | 27.8 | 21.27 | 28.69 | 26.34 | 30.27 | 28.48 | 28.21 | 30.5 | 35.52 | 36.64 | 29.372
HV faults: O/H no damage | 8.42 | 14.06 | 14.13 | 8.95 | 13.69 | 19.02 | 14.18 | 9.27 | 13.98 | 10.75 | 12.645
HV faults: O/H damage | 16.85 | 17.79 | 21.89 | 19.29 | 19.02 | 21.89 | 21.64 | 17.34 | 17.37 | 21.06 | 19.414 |  |  |  |  | 2359992
HV faults: All other | 18.4 | 20.92 | 21.33 | 20.68 | 23.66 | 21.59 | 22.54 | 21.58 | 27.61 | 24.86 | 22.317 |  |  |  |  | 2795904
HV faults: Total | 72.29 | 74.9 | 86.56 | 78.08 | 88.04 | 94.7 | 90.85 | 83.7 | 96.64 | 95.68 | 86.144 | 11.07% |  |  |  | 2732412 |  |  |  | 1946854.4
EHV faults | 13.92 | 23.68 | 13.47 | 11.2 | 24.77 | 17.52 | 17.7 | 15.64 | 19.33 | 18.68 | 17.591 | 6.191% |  |  |  | 2669040 |  |  |  | 397556.6
132kV faults | 3.51 | 10.14 | 5.4 | 9.16 | 0.7 | 10.88 | 3.14 | 1.64 | 8.14 | 11.98 | 6.469 | 85.19% |  |  |  | 3048540 |  |  |  | 146199.4
Total of (a) | 95.42 | 114.06 | 113.33 | 109.36 | 126.84 | 135.29 | 121.72 | 111.05 | 132.43 | 139.93 | 119.943 | 16.66% |  |  |  | 3246100
(b) Planned Outages | 14.86 | 10.98 | 12.01 | 11.96 | 11.73 | 12.26 | 10.26 | 9.77 | 7.26 | 7.84 | 10.893 | -28.03% |  |  |  | 2969550 |  |  |  | 246181.8
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2730532
(d) Other Systems | 0 | 4.41 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.441 |  |  |  |  | 3156994 |  |  |  | 9966.6
Total of (a+b+c+d) | 110.28 | 129.44 | 125.34 | 121.32 | 138.57 | 147.55 | 131.98 | 120.82 | 139.69 | 147.77 | 131.276 | 12.56% | 147.77 | 110.28 |  | 3339602 | 84.163 | 0 | 0 | 2966837.6
[9 empty] | 132.43 | 139.93 | [5 empty] | 3162418
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  |  |  | 0.91838 | [6 empty] | 0.91838
LV faults | 9.81 | 9.67 | 13.51 | 15.92 | 17.72 | 16.24 | 17.66 | 16.37 | 12.73 | 23.59 | 15.322 | [8 empty] | 51139151.538
HV faults: U/G no damage | 0.33 | 0.43 | 0.18 | 2.12 | 1.07 | 2.95 | 2.84 | 3.26 | 1.98 | 2.27 | 1.743
HV faults: U/G damage | 22.19 | 18.6 | 24.41 | 24.32 | 24.77 | 21.9 | 21.42 | 24.08 | 32.67 | 32.49 | 24.685
HV faults: O/H no damage | 6.79 | 11.21 | 13.62 | 8.22 | 16.26 | 9.01 | 7.84 | 4.68 | 9.06 | 11.17 | 9.786
HV faults: O/H damage | 16.81 | 21.55 | 34.61 | 21.46 | 24.36 | 26 | 21.96 | 15.34 | 17.52 | 28.48 | 22.809 |  |  |  |  | 252819600
HV faults: All other | 11.94 | 17.65 | 15.51 | 16.59 | 21.18 | 13.94 | 12.74 | 10.14 | 21.11 | 15.76 | 15.656 |  |  |  |  | 263995200
HV faults: Total | 58.05 | 69.45 | 88.33 | 72.7 | 87.64 | 73.8 | 66.8 | 57.49 | 82.34 | 90.17 | 74.677 | 20.75% |  |  |  | 314181600 |  |  |  | 249244120.833
EHV faults | 4.43 | 6.55 | 3.45 | 1.78 | 13.4 | 1.75 | 4.7 | 2.19 | 4.79 | 2.85 | 4.589 | -37.89% |  |  |  | 281512000 |  |  |  | 15316379.481
132kV faults | 0.53 | 2.64 | 3.11 | 2.73 | 0.03 | 2.02 | 1.25 | 0.13 | 0.9 | 5.03 | 1.837 | 173.8% |  |  |  | 332860000 |  |  |  | 6131224.473
Total of (a) | 72.8 | 88.31 | 108.4 | 93.12 | 118.79 | 93.81 | 90.4 | 76.18 | 100.76 | 121.64 | 96.421 | 26.16% |  |  |  | 277134000
(b) Planned Outages | 45.34 | 33.78 | 35.72 | 34.82 | 32.51 | 32.16 | 25.81 | 23.51 | 16.19 | 21.58 | 30.142 | -28.41% |  |  |  | 261472500 |  |  |  | 100602813.318
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 225299400
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 264307000 |  |  |  | 0
Total of (a+b+c+d) | 118.14 | 122.22 | 144.12 | 127.96 | 151.3 | 125.97 | 116.21 | 99.69 | 116.95 | 143.22 | 126.578 | 13.15% | 151.3 | 99.69 |  | 323677200 | 85.7596 | 0 | 0 | 424090095.65
[9 empty] | 100.76 | 121.64 | [5 empty] | 274906400
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 71.32% | 70.42% | 72.13% | 77.26% | 80.32% | 80.08% | 73.74% | 72.65% | 60.04% | 70.48% | 72.84% | -3.245%
18 hours | 99.81% | 99.73% | 99.79% | 99.99% | 100% | 99.99% | 99.25% | 100% | 99.94% | 99.21% | 99.77% | -0.5623%
HV Faults:U/G no damage 3 hours | 97.13% | 99.57% | 99.8% | 94.48% | 93.98% | 94.6% | 96.7% | 97.77% | 86.94% | 87.14% | 94.81% | -8.091%
18 hours | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
HV Faults: U/G damage 3 hours | 94.94% | 92.85% | 93.95% | 91.22% | 94.79% | 96.06% | 95.09% | 94.66% | 92.78% | 92.81% | 93.92% | -1.177%
18 hours | 99.98% | 100% | 99.9% | 99.98% | 100% | 100% | 100% | 100% | 100% | 99.99% | 99.98% | 0.005001%
HV Faults: O/H no damage 3 hours | 90.79% | 88.51% | 87.23% | 86.51% | 86.02% | 96.14% | 93.44% | 94.88% | 89.68% | 84.47% | 89.77% | -5.901%
18 hours | 100% | 100% | 99.66% | 100% | 99.8% | 99.98% | 100% | 100% | 100% | 99.32% | 99.88% | -0.5567%
HV Faults: O/H damage 3 hours | 85.78% | 81.35% | 76.79% | 82.47% | 81.45% | 82.65% | 84.64% | 86.76% | 83.45% | 79.72% | 82.51% | -3.377%
18 hours | 100% | 99.99% | 99.31% | 99.99% | 99.98% | 99.55% | 99.97% | 100% | 99.99% | 98.85% | 99.76% | -0.9152%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
18 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 91.95% | 88.02% | 88.04% | 88.36% | 88.98% | 92.17% | 91.94% | 93.49% | 89.13% | 88.64% | 90.07% | -1.59%
18 hours | 99.99% | 99.99% | 99.73% | 99.98% | 99.94% | 99.89% | 99.98% | 100% | 99.99% | 99.64% | 99.91% | -0.2732%
EHV Faults: 3 hours | 99.44% | 97.49% | 94.93% | 98.2% | 89.14% | 100% | 98.45% | 100% | 97.99% | 98.94% | 97.46% | 1.521%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 100% | 100% | 100% | 100% | 90.21% | 100% | 100% | 93.6% | 98.38% | -4.86%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 92.11% | 90.23% | 88.32% | 89.23% | 88.16% | 92.72% | 91.34% | 92.61% | 89.26% | 82.1% | 89.61% | -8.384% | 92.72% | 82.1% |  | 2591735.3149
18 hours | 99.98% | 99.93% | 99.78% | 99.99% | 99.96% | 99.92% | 99.92% | 100% | 99.99% | 99.68% | 99.91% | -0.2352% | 100% | 99.68% |  | 3146891.6192
TOTAL not rest in 3 hrs | 7.89% | 9.77% | 11.68% | 10.77% | 11.84% | 7.28% | 8.66% | 7.39% | 10.74% | 17.9% | 10.39% | 72.29% | 17.9% | 7.28% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.02% | 0.07% | 0.22% | 0.01% | 0.04% | 0.08% | 0.08% | 0% | 0.01% | 0.32% | 0.085% | 276.5% | 0.32% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | N/A
(b) due to plc action
- Voltage Reductions | 119 | 89.88 | 43.81 | 6.32 | 93.5 | 10.2 | 3.4 | 5.9 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 97 | 0 | 0 | 0 | 107.6 | 0
Total | 119 | 89.88 | 43.81 | 6.32 | 190.5 | 10.2 | 3.4 | 5.9 | 107.6 |  |  | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.04 | 1.69 | 2.25 | 0.51 | 0.72 | 0.37 | 0.23 | 0.15 | 0.12 | 0.8 | 0.888 | 10 | 2.25 | 0.12 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Excluding service faults# | 9.72 | 10.07 | 11.26 | 12 | 13.88 | 13.59 | 13.03 | 12.78 | 13.24 | 16.12 | 12.569 | -6.626% | 16.12 | 9.72 |  |  |  | 0 | 0
MEB plc total distribution system | 15.01 | 15.6 | 17.62 | 19.26 | 24.43 | 24.06 | 22.32 | 21.72 | 24.2 | 27.1
Number of Customers | 2140000 | 2160000 | 2180000 | 2200000 | 2200000 | 2200000 | 2250000 | 2260000 | 2260000 | 2260000
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 0
NOTES N/A - Information not applicable |  |  | # - Nine year average |  |  |  |  | %age overhead all voltages | 40.24% | * - Information not available
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 1369.7 | 1406 | 1406 | 1406 | 1349 | 1348.9 | 1347.1 | 1347.1 | 1338.2
66kV |  | 786.7 | 788.2 | 793.8 | 793.8 | 764.8 | 767.7 | 767.5 | 775.1 | 774.8
33kV |  | 1231.7 | 1204.8 | 1176.7 | 1176.7 | 1093.2 | 1050.3 | 1047.4 | 1027.8 | 1017.5
25kV |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22kV
11kV |  | 16153.3 | 16159 | 16163 | 16163 | 14886.4 | 14691.7 | 14618.2 | 14586.3 | 14760.4
7kV |  | 0 | 0
6.6kV & 7kV |  | 63.6 | 63.6 | 45.3 | 45.3 | 14.2 | 13.1 | 9.9 | 5.6 | 0
3.3kV
2.2kV
LV |  | 7697.2 | 7684.1 | 7680.1 | 7680.1 | 7680.7 | 7680.7 | 7680.7 | 6335.6 | 6314.4
TOTAL |  |  | 27305.7 | 27305.7 | 27264.9 | 27264.9 | 25552.4 | 25470.8 | 24077.5 | 24205.3
Underground cable
132kV |  | 256.6 | 257 | 257 | 257 | 294 | 294.2 | 302.3 | 303 | 303.4
66kV |  | 15.6 | 15.6 | 17 | 17 | 16.9 | 17.4 | 17.6 | 17.7 | 18.2
33kV |  | 718 | 726.8 | 710.2 | 710.2 | 436.7 | 418.9 | 408.4 | 389.5 | 385.9
25kV |  | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0
22kV
11kV |  | 10536.9 | 10686.6 | 10882.8 | 10882.8 | 10655.7 | 10476.8 | 10745.2 | 11061.8 | 11459.5
7kV |  | 78 | 78 | 24
6.6kV & 7kV |  | 878.6 | 854.5 | 768.3 | 768.3 | 635.5 | 520.7 | 479.9 | 446.7 | 0
3.3kV
LV |  | 24076.8 | 24396.1 | 24852.6 | 24852.6 | 25603.7 | 25987.8 | 26377.6 | 23539.3 | 23756.4
TOTAL |  | 36565.5 | 37019.6 | 37516.9 | 37492.9 | 37642.5 | 37715.8 | 38331 | 35758 | 35923.4
[9 empty] | 59835.5 | 60128.7
Transformers
Primary Voltage
132kV | [5 empty] | 223 | 219 | 220 | 227 | 226
33kV | [5 empty] | 361 | 334 | 329 | 332 | 323
Distribution pole-mounted | [5 empty] | 33207 | 33675 | 33980 | 34412 | 34669
Distribution Other | [5 empty] | 14062 | 14206 | 14271 | 14369 | 14385
Capacity | [6 empty] | 48434 | 48800 | 49340 | 49603
33kV | [5 empty] | 5600 | 9928 | 9928 | 10378 | 10393
Distribution | [5 empty] | 9304 | 5141 | 5101 | 5191 | 4975
[6 empty] | 25042 | 9409 | 9466 | 9542 | 9573
[7 empty] | 24478 | 24495 | 25111 | 24941
HV O/H length (km) | 16112.3 | 16129.7333 | 16147.1667 | 16217 | 16217 | 16208 | 16208 | 14628.1 | 14591.9 | 14760.4
HV U/G length (km) | 10811.1667 | 10924.8889 | 11038.6111 | 11494 | 11494 | 11651 | 11651 | 11225.1 | 11508.5 | 11459.5
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 1.6231 | 1.7003 | 0.98744 | 5.4167 | 2.6414 | 7.0243 | 8.2654 | 10.107 | 4.2614 | 4.674 | 4.6697 |  | 10.107 | 0.98744
HV faults: U/G damage | 55.0283 | 42.0537 | 56.6595 | 50.4159 | 57.9381 | 53.7774 | 54.4782 | 61.407 | 69.753 | 72.26 | 55.7234 |  | 72.26 | 42.0537
HV faults: O/H no damage | 11.1833 | 18.8283 | 19.0767 | 12.1416 | 18.5719 | 25.8169 | 19.6847 | 14.3219 | 21.6523 | 16.4596 | 17.9197 |  | 25.8169 | 11.1833
HV faults: O/H damage | 22.3798 | 23.8233 | 29.5533 | 26.1688 | 25.8026 | 29.7125 | 30.0407 | 26.7898 | 26.9027 | 32.2455 | 26.7971 |  | 32.2455 | 22.3798
HV underground networks | 56.6514 | 43.754 | 57.6469 | 55.8326 | 60.5794 | 60.8016 | 62.7435 | 71.514 | 74.0143 | 76.9341 | 60.3931 |  | 76.9341 | 43.754 |  |  |  | 0 | 0
HV overhead networks | 33.5631 | 42.6517 | 48.63 | 38.3104 | 44.3744 | 55.5294 | 49.7254 | 41.1117 | 48.555 | 48.705 | 44.7168 |  | 55.5294 | 33.5631 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 65.3213 | 85.0169 | 35.548 | 405.7769 | 204.8025 | 557.0337 | 548.4508 | 656.3505 | 388.8257 | 447.681 | 339.4807 |  | 656.3505 | 35.548
HV faults: U/G damage | 4392.3659 | 3677.4745 | 4820.697 | 4654.9504 | 4741.0823 | 4135.2674 | 4136.5548 | 4848.135 | 6415.6232 | 6407.557 | 4822.9708 |  | 6415.6232 | 3677.4745
HV faults: O/H no damage | 901.8328 | 1501.1779 | 1838.8118 | 1115.1261 | 2205.8334 | 1222.9763 | 1088.3514 | 723.0467 | 1403.2169 | 1710.2653 | 1371.0639 |  | 2205.8334 | 723.0467
HV faults: O/H damage | 2232.667 | 2885.8506 | 4672.634 | 2911.266 | 3304.6803 | 3529.1214 | 3048.4946 | 2369.9865 | 2713.5054 | 4360.6406 | 3202.8846 |  | 4672.634 | 2232.667
HV underground networks | 4457.6873 | 3762.4914 | 4856.245 | 5060.7273 | 4945.8848 | 4692.3011 | 4685.0056 | 5504.4855 | 6804.4489 | 6855.238 | 5162.4515 |  | 6855.238 | 3762.4914 |  |  |  | 0 | 0
HV overhead networks | 3134.4997 | 4387.0285 | 6511.4458 | 4026.3921 | 5510.5137 | 4752.0977 | 4136.846 | 3093.0333 | 4116.7223 | 6070.9059 | 4573.9485 |  | 6511.4458 | 3093.0333 |  |  |  | 1 | 0
792222.02
7922.2202
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 2359992 | 2795904 | 2732412 | 2669040 | 3048540 | 3246100 | 2969550 | 2730532 | 3156994 | 3339602
| 252819600 | 263995200 | 314181600 | 281512000 | 332860000 | 277134000 | 261472500 | 225299400 | 264307000 | 323677200

## F
Northern
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.8852 | 1.48 | 1.44 | 1.61 | 1.83 | 2.05 | 1.42 | 2.04 | 1.21 | 1.44 | 1.6405
LV faults | 6.5404 | 5.9 | 6.36 | 6.19 | 5.93 | 6.69 | 6.39 | 6.42 | 8.59 | 10.16 | 6.917 | [8 empty] | 230865.2676
HV faults: U/G no damage | 0.62 | 0.61 | 0.18 | 0.92 | 0.56 | 0.6 | 0.88 | 1.38 | 1.4 | 0.5 | 0.765
HV faults: U/G damage | 25.53 | 24.11 | 28.45 | 24.66 | 21.12 | 22.7 | 27.15 | 23.68 | 26.5 | 24.02 | 24.792
HV faults: O/H no damage | 5.37 | 5.45 | 5.78 | 7.72 | 8.1 | 6.3 | 8.01 | 7.48 | 8.71 | 2.5 | 6.542
HV faults: O/H damage | 10.07 | 12.63 | 10.71 | 8.97 | 11.66 | 9.89 | 13.05 | 12.76 | 11 | 24.7 | 12.544 |  |  |  |  | 1276037
HV faults: All other | 13.6936 | 15.2 | 10.75 | 13.76 | 12.12 | 13.52 | 13.68 | 15.41 | 11.51 | 13.85 | 13.3494 |  |  |  |  | 1235022.1498
HV faults: Total | 55.2836 | 58 | 55.87 | 57.46 | 53.58 | 53.02 | 62.77 | 60.71 | 59.12 | 70.49 | 58.6304 | 20.23% |  |  |  | 1142137.5 |  |  |  | 877263.7798
EHV faults | 6.6666 | 4.88 | 3.47 | 8.21 | 5.19 | 9.19 | 5.02 | 9.98 | 7.83 | 8.92 | 6.9357 | 28.61% |  |  |  | 1258224.4947 |  |  |  | 103775.5966
132kV faults | 3.6961 | 0.77 | 0 | 3.36 | 0 | 8.12 | 4.41 | 0 | 4.15 | 0.9 | 2.5406 | -64.58% |  |  |  | 1308751.574 |  |  |  | 38014.1868
Total of (a) | 74.0719 | 71.03 | 67.14 | 76.85 | 66.53 | 79.06 | 80.01 | 79.15 | 80.88 | 91.91 | 76.6632 | 19.89% |  |  |  | 1283776.9392
(b) Planned Outages | 16.1935 | 15.67 | 12.66 | 11.87 | 9.56 | 9.96 | 10.06 | 11.83 | 9.02 | 6.18 | 11.3003 | -45.31% |  |  |  | 1298627.4586 |  |  |  | 169082.7821
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0.00014231 | 0.0020142 |  |  |  |  | 1343278.1279
(d) Other Systems | 0 | 0 | 0 | 0 | 13.86 | 0 | 0 | 1.61 | 0 | 0 | 1.547 |  |  |  |  | 1313247.0384 |  |  |  | 23177.3113
Total of (a+b+c+d) | 90.2653 | 86.69 | 79.8 | 88.71 | 89.96 | 89.04 | 90.07 | 92.59 | 89.91 | 98.09 | 89.5125 | 9.582% | 98.09 | 79.8 |  | 1467683.3958 | 84.163 | 0 | 0 | 1339342.044
* inc service | [8 empty] | 80.89 | 91.91 | [5 empty] | 1181498.7536
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 1.88 | 1.55 | 1.54 | 1.93 | 2.16 | 2.08 | 1.59 | 3.48 | 1.46 | 1.67 | 1.934
LV faults | 13.154 | 12.74 | 12.83 | 11.72 | 12.54 | 12.04 | 9.06 | 11.41 | 12.74 | 15.44 | 12.3674 | [8 empty] | 41277780.6991
HV faults: U/G no damage | 0.23 | 0.14 | 0.07 | 0.36 | 0.18 | 0.22 | 0.3 | 0.74 | 0.35 | 0.33 | 0.292
HV faults: U/G damage | 18.62 | 19.21 | 25.71 | 20.64 | 16.82 | 17.98 | 19.65 | 19.41 | 22.88 | 19.72 | 20.064
HV faults: O/H no damage | 4.98 | 5.07 | 4.97 | 6.78 | 6.13 | 3.33 | 6.06 | 7.01 | 5.19 | 1.34 | 5.086
HV faults: O/H damage | 12.18 | 16.7 | 17.94 | 11.4 | 15.67 | 9.93 | 20.31 | 23 | 13.34 | 39.05 | 17.952 |  |  |  |  | 137172826.8
HV faults: All other | 7.2329 | 10.25 | 7.64 | 9.88 | 8.01 | 8.56 | 8.65 | 9.99 | 7.48 | 14.4 | 9.2093 |  |  |  |  | 145242251.9
HV faults: Total | 43.2429 | 51.37 | 56.33 | 49.07 | 46.8 | 40.01 | 54.97 | 60.15 | 49.23 | 74.84 | 52.6013 | 42.28% |  |  |  | 146373937.5 |  |  |  | 175563587.96
EHV faults | 1.9314 | 0.34 | 0.97 | 6.52 | 1.82 | 3.03 | 1.07 | 3.4 | 2.7 | 1.87 | 2.3651 | -20.93% |  |  |  | 134261673.62 |  |  |  | 7893954.2477
132kV faults | 1.7279 | 0.12 | 0 | 0.28 | 0 | 7.95 | 0.38 | 0 | 2.36 | 1.01 | 1.3828 | -26.96% |  |  |  | 125492341.9 |  |  |  | 4615255.1241
Total of (a) | 60.0562 | 64.54 | 70.13 | 67.59 | 61.16 | 63.03 | 67.07 | 78.44 | 68.49 | 94.83 | 69.5336 | 36.38% |  |  |  | 117939076.4
(b) Planned Outages | 36.9783 | 37.37 | 32.14 | 27.07 | 18.85 | 18.76 | 19.57 | 19.13 | 16.74 | 14.93 | 24.1538 | -38.19% |  |  |  | 124917378.72 |  |  |  | 80616507.6095
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0.01 | 0.01 | 0 | 0 | 0 | 0.00051231 | 0.0020512 |  |  |  |  | 141828350.56
(d) Other Systems | 0 | 0 | 0 | 0 | 6.24 | 0 | 0 | 0.19 | 0 | 0 | 0.643 |  |  |  |  | 124503589.76 |  |  |  | 2152941.6935
Total of (a+b+c+d) | 97.0344 | 101.95 | 102.27 | 94.66 | 86.26 | 81.8 | 86.64 | 97.76 | 85.24 | 109.76 | 94.3374 | 16.35% | 109.76 | 81.8 |  | 164229717.12 | 85.7596 | 0 | 0 | 314863387.3833
[9 empty] | 68.5 | 94.83 | [5 empty] | 100052744
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 72.06% | 72.89% | 71.05% | 72.75% | 73.69% | 77.9% | 80.31% | 76.16% | 77.21% | 77.24% | 75.13% | 2.774%
18 hours | 99.89% | 99.85% | 100% | 99.95% | 99.99% | 99.97% | 99.36% | 99.22% | 100% | 99.84% | 99.81% | 0.1936%
HV Faults:U/G no damage 3 hours | 100% | 100% | 100% | 92.62% | 100% | 92.72% | 98.55% | 94.96% | 98.62% | 78.21% | 95.57% | 3.194%
18 hours | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 0.002%
HV Faults: U/G damage 3 hours | 94.72% | 92.95% | 91.66% | 92.77% | 92.89% | 95.35% | 95.68% | 94.65% | 93.09% | 94.2% | 93.8% | -0.7527%
18 hours | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.8% | 99.98% | 0.021%
HV Faults: O/H no damage 3 hours | 85.26% | 91.64% | 86.15% | 89.28% | 92.09% | 95.57% | 92.88% | 90.22% | 96.64% | 95.23% | 91.5% | 5.622%
18 hours | 99.99% | 99.99% | 99.99% | 99.98% | 100% | 100% | 100% | 99.21% | 100% | 100% | 99.92% | 0.08407%
HV Faults: O/H damage 3 hours | 80.94% | 78.49% | 66.93% | 81.5% | 73.73% | 83.94% | 79.76% | 75.89% | 81.47% | 79.53% | 78.22% | 4.158%
18 hours | 100% | 99.98% | 100% | 100% | 100% | 100% | 99.51% | 98.3% | 100% | 97.86% | 99.56% | 0.4369%
HV Faults: Other 3 hours | [10 empty] | #DIV/0!
18 hours | [10 empty] | #DIV/0!
HV Faults: Total 3 hours | 91.61% | 89.92% | 85.95% | 90.52% | 88.54% | 92.28% | 91.62% | 89.99% | 91.59% | 88.17% | 90.02% | -2.054%
18 hours | 99.99% | 100% | 99.99% | 99.98% | 99.99% | 100% | 99.81% | 99.49% | 100% | 99.07% | 99.83% | -0.7637%
EHV Faults: 3 hours | 98.41% | 100% | 100% | 87.85% | 100% | 100% | 100% | 100% | 99.99% | 95.77% | 98.2% | -2.476%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | -0.0008566%
132kV F'lts: 3 hours | 100% | 100% | 0% | 100% | 100% | 63% | 100% | 100% | 100% | 85.71% | 84.87% | 0.9886%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 90.41% | 88.95% | 84.94% | 88.85% | 88.91% | 88.58% | 91.5% | 89.77% | 91.09% | 87.51% | 89.05% | -1.731% | 91.5% | 84.94% |  | 1149222.4833
18 hours | 99.98% | 99.98% | 100% | 99.98% | 99.99% | 100% | 99.79% | 99.51% | 100% | 99.27% | 99.85% | -0.5811% | 100% | 99.27% |  | 1303660.335
TOTAL not rest in 3 hrs | 9.585% | 11.05% | 15.06% | 11.15% | 11.09% | 11.42% | 8.5% | 10.23% | 8.91% | 12.49% | 10.95% | 14.08% | 15.06% | 8.5% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.01729% | 0.02% | 0% | 0.02% | 0.01% | 0% | 0.21% | 0.49% | 0% | 0.73% | 0.1497% | 387.5% | 0.73% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | *
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 0.34662 | 0.39 | 0.43 | 0.36 | 0.49 | 0.52 | 0.04 | 0.17 | 0.25 | 0.27 | 0.32666 | 10 | 0.52 | 0.04 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Total distribution system | 13.7308 | 12.92 | 13.5 | 13.45 | 12.55 | 12.78 | 11.97 | 13.66 | 14.21 | 15.81 | 13.4581 | -6.485% | 15.81 | 11.97 |  |  |  | 0 | 0
5 RELEVANT DATA:
Number of Customers | 1413651 | 1424642 | 1431250 | 1418357 | 1454815 | 1441798 | 1441798 | 1450781 | 1460624 | 1496262
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 90 | 75 | 112 | 102 | 120 | 123
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 72.154 | 62.94 | 602090 | 548590 | 682700 | 687700
* Data Unavailable | [7 empty] | %age overhead all voltages | 39.13%
Mains in commission (circuit kilometres)
Overhead Line
132kV | 664 | 664 | 711.4 | 682.777 | 682.777 | 683.977 | 683.977 | 683.977 | 711 | 711
66kV | 1163 | 1163 | 1160 | 975.203 | 975.203 | 975.203 | 975.203 | 975.203 | 980 | 980
33kV | 341 | 340 | 340.5 | 340.451 | 317.257 | 317.257 | 317.257 | 317.257 | 317 | 317
25kV
22kV | 6013 | 6019 | 6027.6 | 6033.098 | 6034.842 | 6037.357 | 6045.136 | 6045.14 | 6049 | 6061
11kV | 4997 | 5006 | 5016.5 | 5025.661 | 5036.533 | 5050.035 | 5078.596 | 5078.6 | 5079 | 5097
6.6kV | 38 | 38 | 38 | 37.968 | 37.968 | 37.968 | 37.968 | 37.968 | 38 | 35
3.3kV
3kV |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
2.2kV |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
LV | 4090 | 4086 | 4099 | 4093.338 | 4091.742 | 4091.241 | 4091.961 | 4091.96 | 4091 | 4092
TOTAL |  | 17306 | 17316 | 17393 | 17188.496 | 17193.038 | 17230.098 | 17230.105 | 17265 | 17293
Underground cable
132kV | 69 | 69 | 69 | 74.626 | 74.626 | 74.626 | 74.626 | 74.626 | 69 | 69
66kV | 398 | 398 | 400.1 | 400.361 | 400.361 | 400.361 | 400.361 | 400.361 | 401 | 402
33kV | 310 | 311 | 310.5 | 310.921 | 310.921 | 310.921 | 310.921 | 310.921 | 312 | 326
25kV
22kV | 1951 | 1958 | 1978.8 | 2005.069 | 2029.216 | 2054.56 | 2067.643 | 2067.64 | 2077 | 2098
11kV | 5403 | 5523 | 5693.9 | 5800.417 | 5931.856 | 6054.037 | 6173.183 | 6173.18 | 6223 | 6375
6.6kV | 438 | 433 | 432.8 | 432.76 | 432.76 | 432.76 | 432.76 | 432.76 | 432 | 432
3.3kV
3kV |  |  |  | 0 | 0 | 0 | 0 |  |  | 0
LV | 14464 | 14692 | 14940.1 | 15134.966 | 16855.607 | 17039.665 | 17247.5 | 17247.5 | 17347 | 17572
TOTAL |  |  | 23033 | 23384 | 23825.2 | 24159.12 | 26706.994 | 26706.988 | 26861 | 27274
[9 empty] | 44126 | 44567
Transformers in commission
Primary voltage | [9 empty] | Aggregate Capacity
| OH | GM | [7 empty] | (KVA)
over 650 Volts | 0 | 425 | [7 empty] | 7737300
650 Volts & under | 14713 | 8765 | [7 empty] | 5539508
total | 14713 | 9190 | [7 empty] | 13291212
23903
HV O/H length (km) | 6981.3333 | 7659.1111 | 8336.8889 | 9014.6667 | 9692.4444 | 10370.2222 | 11048 | 11161.708 | 11166 | 11193
HV U/G length (km) | 6071.3333 | 6358.1111 | 6644.8889 | 6931.6667 | 7218.4444 | 7505.2222 | 7792 | 8673.58 | 8732 | 8905
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 1.4436 | 1.3668 | 0.3877 | 1.8825 | 1.1286 | 1.1526 | 1.6283 | 2.3082 | 2.3418 | 0.84012 | 1.448 |  | 2.3418 | 0.3877
HV faults: U/G damage | 59.4441 | 54.0225 | 61.2788 | 50.4593 | 42.5655 | 43.6081 | 50.2372 | 39.6082 | 44.3272 | 40.3596 | 48.591 |  | 61.2788 | 39.6082
HV faults: O/H no damage | 10.8737 | 10.1373 | 9.9229 | 12.1466 | 12.1579 | 8.759 | 10.4533 | 9.7224 | 11.3935 | 3.342 | 9.8909 |  | 12.1579 | 3.342
HV faults: O/H damage | 20.3908 | 23.4926 | 18.3866 | 14.1133 | 17.5014 | 13.7503 | 17.0307 | 16.5852 | 14.3891 | 33.0186 | 18.8658 |  | 33.0186 | 13.7503
HV underground networks | 60.8877 | 55.3893 | 61.6665 | 52.3418 | 43.6942 | 44.7607 | 51.8655 | 41.9165 | 46.669 | 41.1997 | 50.0391 |  | 61.6665 | 41.1997 |  |  |  | 1 | 0
HV overhead networks | 31.2645 | 33.6299 | 28.3095 | 26.2598 | 29.6593 | 22.5094 | 27.4839 | 26.3076 | 25.7826 | 36.3605 | 28.7567 |  | 36.3605 | 22.5094 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 53.5533 | 31.3694 | 15.0774 | 73.6632 | 36.2774 | 42.2633 | 55.5107 | 123.7756 | 58.5454 | 55.4482 | 54.5484 |  | 123.7756 | 15.0774
HV faults: U/G damage | 4335.4862 | 4304.3244 | 5537.7055 | 4223.3549 | 3389.9254 | 3454.0654 | 3635.9511 | 3246.6017 | 3827.1962 | 3313.4516 | 3926.8062 |  | 5537.7055 | 3246.6017
HV faults: O/H no damage | 1008.4008 | 943.0513 | 853.2335 | 1066.7572 | 920.0998 | 462.9783 | 790.8486 | 911.1486 | 678.9037 | 179.129 | 781.4551 |  | 1066.7572 | 179.129
HV faults: O/H damage | 2466.3296 | 3106.3032 | 3079.8809 | 1793.6625 | 2352.0332 | 1380.5928 | 2650.5175 | 2989.5033 | 1745.0049 | 5220.1404 | 2678.3968 |  | 5220.1404 | 1380.5928
HV underground networks | 4389.0394 | 4335.6938 | 5552.7828 | 4297.0181 | 3426.2029 | 3496.3287 | 3691.4618 | 3370.3773 | 3885.7416 | 3368.8998 | 3981.3546 |  | 5552.7828 | 3368.8998 |  |  |  | 1 | 0
HV overhead networks | 3474.7304 | 4049.3545 | 3933.1144 | 2860.4197 | 3272.133 | 1843.5711 | 3441.3662 | 3900.6519 | 2423.9085 | 5399.2694 | 3459.8519 |  | 5399.2694 | 1843.5711 |  |  |  | 1 | 0
6270.3046
5711.6205
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1276037 | 1235022.1498 | 1142137.5 | 1258224.4947 | 1308751.574 | 1283776.9392 | 1298627.4586 | 1343278.1279 | 1313247.0384 | 1467683.3958
| 137172826.8 | 145242251.9 | 146373937.5 | 134261673.62 | 125492341.9 | 117939076.4 | 124917378.72 | 141828350.56 | 124503589.76 | 164229717.12

## G
NORWEB
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 3.6 | 3.95 | 3.87 | 4.8 | 5 | 3.9 | 3.3 | 2.1 | 1.6 | 1.5 | 3.362
LV faults | 8 | 8.27 | 8.07 | 8.8 | 8.2 | 6.8 | 8 | 7.4 | 6.5 | 5.9 | 7.594 | [8 empty] | 253459.5463
HV faults: U/G no damage | 0.93 | 1.93 | 1.61 | 1 | 1 | 0.8 | 1.7 | 1.7 | 3.6 | 1.5 | 1.577
HV faults: U/G damage | 18.5 | 16.37 | 15.7 | 18.7 | 18.2 | 22.4 | 22 | 19.4 | 17.7 | 19.5 | 18.847
HV faults: O/H no damage | 2.69 | 4 | 2.62 | 4.3 | 4.5 | 3.8 | 4.8 | 3.4 | 4.3 | 3.15 | 3.756
HV faults: O/H damage | 5.9 | 5.83 | 5.83 | 7.2 | 5.8 | 5.4 | 8 | 7.7 | 7.5 | 6.3 | 6.546 |  |  |  |  | 1301955
HV faults: All other | 4.4 | 4.44 | 3.75 | 4.3 | 6.9 | 4.8 | 4.7 | 5.9 | 5.9 | 5.1 | 5.019 |  |  |  |  | 1205796.3
HV faults: Total | 32.4 | 32.6 | 29.48 | 35.4 | 36.4 | 37.2 | 41.2 | 38.1 | 39 | 37.5 | 35.928 | 4.375% |  |  |  | 1195190 |  |  |  | 811972.8
EHV faults | 5.1 | 4.21 | 4.36 | 5.3 | 4.4 | 4.7 | 5.8 | 6.7 | 4.7 | 4.5 | 4.977 | -9.584% |  |  |  | 1505520 |  |  |  | 112480.2
132kV faults | 7.7 | 1.27 | 1.98 | 9.4 | 1.8 | 3.9 | 9.3 | 0 | 0 | 1.2 | 3.655 | -67.17% |  |  |  | 1316480 |  |  |  | 82603
Total of (a) | 56.8 | 50.3 | 47.76 | 63.6 | 55.7 | 56.5 | 67.6 | 54.3 | 51.9 | 50.6 | 55.506 | -8.839% |  |  |  | 1303050
(b) Planned Outages | 4.7 | 6.39 | 6.69 | 6.1 | 4.8 | 3 | 3.2 | 3.3 | 2.9 | 3.5 | 4.458 | -21.49% |  |  |  | 1845276 |  |  |  | 100750.8
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1232640
(d) Other Systems | 0 | 0 | 1.4 | 0 | 0 | 0 | 13 | 0 | 0 | 0 | 1.44 |  |  |  |  | 1205041 |  |  |  | 32544
Total of (a+b+c+d) | 61.5 | 56.69 | 55.85 | 69.7 | 60.5 | 59.5 | 83.8 | 57.6 | 54.7 | 54.1 | 61.394 | -11.88% | 83.8 | 54.1 |  | 1222660 | 84.163 | 1 | 1 | 1387504.4
[9 empty] | 51.8 | 50.6 | [5 empty] | 1143560
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 3.1 | 3.58 | 2.9 | 3.1 | 3.9 | 3.7 | 3 | 2.1 | 1.5 | 1.5 | 2.838
LV faults | 14.8 | 15.13 | 13.2 | 13.4 | 12.2 | 11.8 | 14.1 | 11.7 | 9.4 | 9.8 | 12.553 | [8 empty] | 41897256.837
HV faults: U/G no damage | 1 | 1.3 | 1.5 | 0.4 | 1 | 0.8 | 1.5 | 1.5 | 2.9 | 1.3 | 1.32
HV faults: U/G damage | 18.77 | 17.14 | 13.63 | 14.9 | 15.6 | 21 | 22.5 | 18.3 | 16.7 | 17 | 17.554
HV faults: O/H no damage | 3.2 | 3.71 | 2.33 | 4.1 | 3.9 | 3.5 | 5.5 | 6.6 | 4.2 | 4.4 | 4.144
HV faults: O/H damage | 10.9 | 8.88 | 7.44 | 10.2 | 7.5 | 7.4 | 20.2 | 17.8 | 8.8 | 8.3 | 10.742 |  |  |  |  | 158139900
HV faults: All other | 4.11 | 5.05 | 3.4 | 3.5 | 6.2 | 4.5 | 6.8 | 5.4 | 5.9 | 4.6 | 4.946 |  |  |  |  | 162715500
HV faults: Total | 38 | 36.1 | 28.28 | 33.1 | 34.2 | 37.2 | 56.5 | 49.6 | 38.4 | 35.6 | 38.698 | -8.006% |  |  |  | 147018000 |  |  |  | 129654746.65
EHV faults | 3 | 0.98 | 1.6 | 1.2 | 1.9 | 1.2 | 4.2 | 6.5 | 4.2 | 1.6 | 2.638 | -39.35% |  |  |  | 151200000 |  |  |  | 8838421.15
132kV faults | 0.7 | 0.36 | 0.59 | 0.7 | 1.5 | 2.9 | 4.9 | 0 | 0 | 0.1 | 1.175 | -91.49% |  |  |  | 145792000 |  |  |  | 3936749.375
Total of (a) | 59.6 | 56.15 | 46.57 | 51.6 | 53.6 | 56.8 | 82.7 | 69.9 | 53.5 | 48.6 | 57.902 | -16.07% |  |  |  | 144321000
(b) Planned Outages | 15.1 | 20.33 | 21.64 | 18.4 | 13.3 | 9.1 | 9.2 | 9.9 | 9.2 | 11.1 | 13.727 | -19.14% |  |  |  | 212272800 |  |  |  | 45991283.975
(c) Embedded Gen. | 0.002 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0002 |  |  |  |  | 170986000
(d) Other Systems | 0 | 0 | 0.49 | 0 | 0 | 0 | 4.5 | 0 | 0 | 0 | 0.499 |  |  |  |  | 138128100 |  |  |  | 1672532.16
Total of (a+b+c+d) | 74.7 | 76.5 | 68.7 | 70 | 67 | 65.9 | 96.4 | 79.9 | 62.7 | 59.7 | 72.15 | -17.26% | 96.4 | 59.7 |  | 134922000 | 85.7596 | 1 | 1 | 241733163.75
Note: * indicates information either not available or inapplicable | [8 empty] | 53.5 | 48.6 | [5 empty] | 107065800
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 78.2% | 78.5% | 81.82% | 84.2% | 83.36% | 78.86% | 76.78% | 81.02% | 84.12% | 78.97% | 80.58% | -2.002%
24 hours | 100% | 99.7% | 99.93% | 99.99% | 99.99% | 99.86% | 99.87% | 99.83% | 100% | 99.98% | 99.91% | 0.06506%
HV Faults:U/G no damage 3 hours | 94.4% | 97.61% | 98.07% | 99.9% | 94.28% | 94.25% | 94.41% | 94.65% | 94.61% | 95.58% | 95.78% | -0.2046%
24 hours | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
HV Faults: U/G damage 3 hours | 91.57% | 91.82% | 95.18% | 96.8% | 94.71% | 93.69% | 92.61% | 94.47% | 94.77% | 94.57% | 94.02% | 0.5861%
24 hours | 100% | 99.91% | 99.99% | 99.99% | 100% | 99.97% | 99.95% | 100% | 99.99% | 99.99% | 99.98% | 0.011%
HV Faults: O/H no damage 3 hours | 83.93% | 91.4% | 90.98% | 91.1% | 94.51% | 93.64% | 90.42% | 82.36% | 92.96% | 94.12% | 90.54% | 3.952%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 99.5% | 98.52% | 100% | 100% | 99.8% | 0.1984%
HV Faults: O/H damage 3 hours | 66.59% | 75.29% | 83.36% | 80.7% | 83.97% | 81.19% | 71.5% | 77.93% | 83.85% | 78.93% | 78.33% | 0.7647%
24 hours | 99.9% | 99.92% | 100% | 99.99% | 99.99% | 99.97% | 97.28% | 97.16% | 100% | 99.87% | 99.41% | 0.4648%
HV Faults: Other 3 hours | 87.85% | 82.55% | 90.13% | 93.7% | 93.11% | 89.98% | 82.84% | 91.92% | 89.67% | 91.21% | 89.3%
24 hours | 99.9% | 100% | 100% | 99.99% | 100% | 100% | 99.42% | 99.82% | 100% | 100% | 99.91%
HV Faults: Total 3 hours | 86.1% | 87.89% | 92% | 92.5% | 92.66% | 91.39% | 87.24% | 89.66% | 91.68% | 91.47% | 90.26% | 1.342%
24 hours | 99.9% | 99.94% | 99.99% | 99.99% | 100% | 99.98% | 99.32% | 99.27% | 100% | 99.97% | 99.84% | 0.1342%
EHV Faults: 3 hours | 94.2% | 100% | 95.22% | 100% | 93.4% | 98.88% | 92.69% | 89.11% | 89.92% | 100% | 95.34% | 4.886%
24 hours | 99.8% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02%
132kV F'lts: 3 hours | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 33.33% | 50% | 100% | 88.32% | 13.22%
24 hours | 99.9% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
Total Faults:3 hours | 87% | 87.3% | 90.36% | 92.5% | 90.77% | 90.24% | 87.73% | 88.08% | 90.34% | 90.59% | 89.49% | 1.228% | 92.5% | 87% |  | 1091646.6419
24 hours | 99.9% | 99.9% | 99.98% | 99.99% | 100% | 99.96% | 99.57% | 99.45% | 100% | 99.98% | 99.87% | 0.1071% | 100% | 99.45% |  | 1204799.9918
TOTAL not rest in 3 hrs | 13% | 12.7% | 9.64% | 7.5% | 9.23% | 9.76% | 12.27% | 11.92% | 9.66% | 9.41% | 10.51% | -10.46% | 13% | 7.5% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.1% | 0.1% | 0.02% | 0.01% | 0% | 0.04% | 0.43% | 0.55% | 0% | 0.02% | 0.127% | -84.25% | 0.55% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N\A
- Load Disconnection | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0 | 0 | N\A
TOTAL | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0.00047467 | 0.0002 | 0.0002 | 0.0001 | 0.001 | 0.0006 | 0.0063 | 0.0009 | 0 | 0 | N\A
- Load Disconnection | nil | nil | nil | nil | 0 | 0 | 0 | 0 | 0 | 0 | N\A
- Total | 0.00047467 | 0.0002 | 0.0002 | 0.0001 | 0.001 | 0.0006 | 0.0063 | 0.0009 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.9 | 2.01 | 2.09 | 1.9 | 1.82 | 0.89 | 0.89 | 0.76 | 0.64 | 0.82 | 1.372 | 10 | 2.09 | 0.64 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
total distribution system (excluding service faults) | 17.4 | 17.2 | 16.05 | 16.2 | 15.1 | 14.2 | 17.5 | 17.6 | 17.1 | 16.9 | 16.4833 | -18.89% | 17.6 | 14.2 |  |  |  | 0 | 0
5 RELEVANT DATA:
(i) Total Connected Customers (000's) | 2117000 | 2127000 | 2140000 | 2160000 | 2176000 | 2190000 | 2202000 | 2140000 | 2203000 | 2260000 | 2846786.6 | 7.044%
Embedded Gen.Stations | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | N\A
Emb.Gen.Capacity MWSO | 621 | 621 | 589 | 589 | 589 | 589 | 589 | 575 | 575 | 575 | N\A
Note: * indicates information either not available or inapplicable | [7 empty] | %age overhead all voltages | 23.7% | 23.97%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 1572 | 1572 | 1572 | 1572 | 1572 | 1331 | 1331 | 1331 | 1331
66kV
33kV |  | 1357 | 1356 | 1356 | 1346 | 1346 | 1411 | 1412 | 1412 | 1361
25kV |  | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 1 | 1
22kV
11kV |  | 7446 | 7474 | 7494 | 7550 | 7550 | 7115 | 7136 | 7114 | 7186
6.6kV |  | 882 | 886 | 883 | 889 | 889 | 894 | 896 | 885 | 892
3.3kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3kV
2.2kV |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV |  | 3389 | 3381 | 3343 | 3278 | 3278 | 3186 | 3180 | 3180 | 3086
TOTAL |  |  | 14653 | 14649 | 14649 | 14636 | 13937 | 13955 | 13923 | 13857
Underground cable
132kV |  | 236 | 233 | 233 | 234 | 234 | 234 | 233 | 233 | 233
66kV
33kV |  | 1716 | 1719 | 1719 | 1780 | 1780 | 1780 | 1781 | 1790 | 1613
25kV |  | 10 | 10 | 10 | 10 | 10 | 10 | 10 | 9 | 9
22kV
11kV |  | 5981 | 6031 | 6090 | 6198 | 6198 | 6218 | 6218 | 6218 | 5428
6.6kV |  | 6440 | 6485 | 6515 | 6568 | 6568 | 6588 | 6588 | 6588 | 5733
3.3kV |  | 28 | 28 | 24 | 24 | 24 | 24 | 1.4 | 1.4 | 0
2.2kV |  | 31 | 31 | 31 | 36 | 36 | 36 | 0 | 0 | 0
LV |  | 29150 | 29369 | 29622 | 29859 | 29859 | 29986 | 29986 | 29986 | 30946
TOTAL |  |  |  | 43592 | 44709 | 44247 | 44709 | 44817.4 | 44825.4 | 43962
[9 empty] | 58748.4 | 57819
Transformers
Primary Voltage
132kV | [5 empty] | 143 | 143 | 141 | 144 | 146
33kV | [5 empty] | 707 | 671 | 666 | 681 | 676
Distribution pole-mounted | [5 empty] | 16104 | 16352 | 16357 | 16390 | 16413
Distribution Other | [5 empty] | 14364 | 14630 | 14866 | 14970 | 15068
Capacity | [5 empty] | 31318 | 31796 | 32030 | 32185 | 32303
132kV | [5 empty] | 9937 | 9658 | 9528 | 9698 | 9779
33kV | [5 empty] | 12294 | 12434 | 12485 | 12787 | 12879
Distribution | [5 empty] | 8302 | 8506 | 8666 | 8674 | 8858
[6 empty] | 30533 | 30598 | 30679 | 31159 | 31516
HV O/H length (km) | 8194 | 8217.3333 | 8240.6667 | 8264 | 8287.3333 | 8310.6667 | 8334 | 8032 | 7999 | 8078
HV U/G length (km) | 11990.6667 | 12072.2222 | 12153.7778 | 12235.3333 | 12316.8889 | 12398.4444 | 12480 | 12807.4 | 12807.4 | 11161
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 1.642 | 3.4005 | 2.8348 | 1.7654 | 1.7667 | 1.4131 | 2.9995 | 2.8405 | 6.1924 | 3.0374 | 2.7892 |  | 6.1924 | 1.4131
HV faults: U/G damage | 32.6625 | 28.8422 | 27.6441 | 33.0126 | 32.1536 | 39.5663 | 38.8173 | 32.4156 | 30.4458 | 39.4857 | 33.5046 |  | 39.5663 | 27.6441
HV faults: O/H no damage | 6.9499 | 10.3537 | 6.8038 | 11.2391 | 11.8156 | 10.0136 | 12.6825 | 9.0588 | 11.8426 | 8.8128 | 9.9572 |  | 12.6825 | 6.8038
HV faults: O/H damage | 15.2432 | 15.0906 | 15.1398 | 18.819 | 15.229 | 14.2299 | 21.1375 | 20.5154 | 20.6557 | 17.6256 | 17.3686 |  | 21.1375 | 14.2299
HV underground networks | 34.3044 | 32.2427 | 30.4789 | 34.778 | 33.9203 | 40.9793 | 41.8168 | 35.2562 | 36.6381 | 42.5231 | 36.2938 |  | 42.5231 | 30.4789 |  |  |  | 0 | 0
HV overhead networks | 22.1931 | 25.4443 | 21.9436 | 30.0581 | 27.0446 | 24.2435 | 33.82 | 29.5742 | 32.4983 | 26.4385 | 27.3258 |  | 33.82 | 21.9436 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 176.554 | 229.0465 | 264.1154 | 70.6152 | 176.668 | 141.308 | 264.6635 | 250.6364 | 498.8288 | 263.2381 | 233.5674 |  | 498.8288 | 70.6152
HV faults: U/G damage | 3313.9183 | 3019.8897 | 2399.9287 | 2630.4146 | 2756.0206 | 3709.3363 | 3969.9519 | 3057.7635 | 2872.5659 | 3442.3439 | 3117.2133 |  | 3969.9519 | 2399.9287
HV faults: O/H no damage | 826.7513 | 960.3079 | 605.0724 | 1071.636 | 1024.0206 | 922.3087 | 1453.2037 | 1758.4661 | 1156.7196 | 1230.9978 | 1100.9484 |  | 1758.4661 | 605.0724
HV faults: O/H damage | 2816.1216 | 2298.5267 | 1932.0767 | 2666.0213 | 1969.2704 | 1950.0241 | 5337.221 | 4742.5299 | 2423.603 | 2322.1094 | 2845.7504 |  | 5337.221 | 1932.0767
HV underground networks | 3490.4723 | 3248.9362 | 2664.0441 | 2701.0298 | 2932.6886 | 3850.6443 | 4234.6154 | 3308.3998 | 3371.3947 | 3705.5819 | 3350.7807 |  | 4234.6154 | 2664.0441 |  |  |  | 0 | 0
HV overhead networks | 3642.8728 | 3258.8346 | 2537.1491 | 3737.6573 | 2993.291 | 2872.3327 | 6790.4248 | 6500.996 | 3580.3225 | 3553.1072 | 3946.6988 |  | 6790.4248 | 2537.1491 |  |  |  | 1 | 0
10045.9764
9075.5351
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1301955 | 1205796.3 | 1195190 | 1505520 | 1316480 | 1303050 | 1845276 | 1232640 | 1205041 | 1222660
| 158139900 | 162715500 | 147018000 | 151200000 | 145792000 | 144321000 | 212272800 | 170986000 | 138128100 | 134922000

## H
SEEBOARD
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.36 | 1.43 | 1.2 | 1.1 | 1 | 1.4 | 1.2 | 1 | 1.2 | 1.3 | 1.219
LV faults | 4.63 | 4.37 | 4 | 4.3 | 4.1 | 5.7 | 4.7 | 4 | 4.2 | 4.2 | 4.42 | [8 empty] | 148088.785
HV faults: U/G no damage | 1.6 | 2 | 1.6 | 3.2 | 3.7 | 4.8 | 2.3 | 3.1 | 1.9 | 1 | 2.52
HV faults: U/G damage | 40.2 | 43.7 | 38.8 | 45.6 | 37.4 | 32.7 | 37.2 | 44.6 | 36.4 | 39.5 | 39.61
HV faults: O/H no damage | 6.9 | 9.4 | 5 | 8.9 | 7.9 | 6.4 | 6.6 | 5.5 | 4.8 | 4.1 | 6.55
HV faults: O/H damage | 8.7 | 10.1 | 8.2 | 10.3 | 8.8 | 9.5 | 9.3 | 10.6 | 9.9 | 7.4 | 9.28 |  |  |  |  | 1994395.8
HV faults: All other | 16.7 | 15.9 | 15 | 15.2 | 17 | 19.7 | 17.6 | 16.2 | 17.4 | 15.9 | 16.66 |  |  |  |  | 3121248
HV faults: Total | 74 | 81.1 | 68.6 | 83.3 | 74.8 | 73.1 | 73 | 79.9 | 70.5 | 67.3 | 74.56 | -9.737% |  |  |  | 1960885.956 |  |  |  | 1604531.2
EHV faults | 7.4 | 9.5 | 6.4 | 7.9 | 8.4 | 5 | 6.4 | 7.2 | 6 | 3.6 | 6.78 | -46.9% |  |  |  | 2056080 |  |  |  | 145905.6
132kV faults | 10.3 | 7.8 | 16.5 | 5.2 | 5.3 | 4.2 | 4.7 | 2.6 | 7.5 | 11.9 | 7.6 | 56.58% |  |  |  | 1889720 |  |  |  | 163552
Total of (a) | 96.4 | 102.8 | 95.4 | 100.7 | 92.7 | 88 | 88.8 | 93.7 | 88.3 | 87.2 | 93.4 | -6.638% |  |  |  | 1847332
(b) Planned Outages | 6.51 | 6.24 | 4.2 | 3.3 | 2.3 | 1.2 | 2.2 | 1.8 | 1.6 | 1.3 | 3.065 | -57.59% |  |  |  | 1918280 |  |  |  | 65958.8
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 2030330
(d) Other Systems | 0 | 50.9 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 5.12 |  |  |  |  | 1922961 |  |  |  | 110182.4
Total of (a+b+c+d) | 102.91 | 159.9 | 99.6 | 104 | 95.2 | 89.2 | 91 | 95.5 | 89.9 | 88.5 | 101.571 | -12.87% | 159.9 | 88.5 |  | 1904520 | 84.163 | 1 | 1 | 2185807.92
* inc service | [8 empty] | 88.3 | 87.2 | [5 empty] | 1876544
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | * | 4.9 | 0.99 | 2.41 |  |  | 1.6 | 1.4 | 1 | 2.3 | 1.825
LV faults | 6.56 | 6.6 | 7 | 7.9 | 7.01 | 13.27 | 8.4 | 6.9 | 7.7 | 8.9 | 8.024 | [8 empty] | 26781135.096
HV faults: U/G no damage | 0.8 | 1.5 | 1.1 | 2.1 | 2.6 | 3.4 | 2 | 1.9 | 1.4 | 0.3 | 1.71
HV faults: U/G damage | 28.2 | 36.2 | 30 | 34.6 | 27.2 | 29.9 | 32.4 | 32.4 | 30.1 | 32.4 | 31.34
HV faults: O/H no damage | 6.3 | 11.9 | 4.8 | 10.9 | 7.2 | 6.9 | 8.6 | 5 | 4.9 | 3.7 | 7.02
HV faults: O/H damage | 10.1 | 11.2 | 9.4 | 13 | 8.8 | 13.4 | 12.6 | 10.8 | 10.9 | 8.5 | 10.87 |  |  |  |  | 186435600
HV faults: All other | 12 | 11.9 | 10.9 | 10.3 | 12.4 | 16.4 | 15.5 | 9.8 | 11.6 | 11.7 | 12.25 |  |  |  |  | 230921600
HV faults: Total | 57.3 | 72.8 | 56.3 | 70.9 | 58.3 | 70 | 71.1 | 60 | 58.9 | 56.6 | 63.22 | -10.47% |  |  |  | 165572800.1 |  |  |  | 211813868.5
EHV faults | 7.1 | 5.7 | 3.4 | 4.5 | 5.7 | 2.3 | 2.7 | 3.5 | 2 | 2.1 | 3.9 | -46.15% |  |  |  | 184454100 |  |  |  | 13066657.5
132kV faults | 3.7 | 0 | 5.6 | 1 | 0.9 | 0.2 | 4.4 | 1.5 | 1.3 | 4.4 | 2.3 | 91.3% |  |  |  | 154631500 |  |  |  | 7705977.5
Total of (a) | 74.7 | 85.1 | 72.4 | 84.3 | 71.9 | 85.8 | 86.6 | 71.9 | 69.9 | 72 | 77.46 | -7.049% |  |  |  | 184940300
(b) Planned Outages | 21.52 | 19.3 | 11.7 | 9 | 6.01 | 3.58 | 5.7 | 3.9 | 3.3 | 2.5 | 8.651 | -71.1% |  |  |  | 193936000 |  |  |  | 28984526.675
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 161150800
(d) Other Systems | 0 | 13.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.39 |  |  |  |  | 156574800 |  |  |  | 4657090.75
Total of (a+b+c+d) | 96.2 | 118.3 | 84.1 | 93.3 | 77.9 | 89.3 | 92 | 75.8 | 73.2 | 74.5 | 87.46 | -14.82% | 118.3 | 73.2 |  | 160324000 | 85.7596 | 1 | 1 | 293028170.5
[10 empty] | 72 | [5 empty] | 154944000
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 76.1% | 74% | 69% | 68.4% | 70.3% | 57% | 66.7% | 70.3% | 69.7% | 62.7% | 68.42% | -8.36%
18 hours | 100% | 100% | 99.7% | 99.7% | 99.9% | 100% | 100% | 100% | 99.8% | 98.8% | 99.79% | -0.9921%
HV Faults:U/G no damage 3 hours | 97.9% | 94.8% | 93.6% | 95.9% | 92.4% | 95.3% | 89.7% | 93.4% | 94.2% | 99% | 94.62% | 4.629%
18 hours | 100% | 100% | 100% | 99.8% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.02%
HV Faults: U/G damage 3 hours | 95.6% | 94.8% | 94.3% | 95% | 94.8% | 92.8% | 94% | 95.6% | 93.9% | 93.7% | 94.45% | -0.7941%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: O/H no damage 3 hours | 87.9% | 78.2% | 88.5% | 83.4% | 90.9% | 84.7% | 85.9% | 92% | 85.8% | 86.4% | 86.37% | 0.03473%
18 hours | 100% | 100% | 100% | 99.7% | 100% | 100% | 100% | 100% | 100% | 99.7% | 99.94% | -0.2401%
HV Faults: O/H damage 3 hours | 81.5% | 83.5% | 81.3% | 79.5% | 88.2% | 78.5% | 76.2% | 84.5% | 86.2% | 83% | 82.24% | 0.9241%
18 hours | 100% | 100% | 99.8% | 99.9% | 99.9% | 100% | 100% | 100% | 99.9% | 100% | 99.95% | 0.05003%
HV Faults: Other 3 hours | 93.5% | 91.8% | 91% | 93.9% | 93.2% | 91.5% | 91.2% | 93% | 93.5% | 93.3% | 92.59%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.9% | 99.99%
HV Faults: Total 3 hours | 92.8% | 90.9% | 91.6% | 91.7% | 93.1% | 90% | 90.2% | 93.3% | 92.1% | 92.1% | 91.78% | 0.3487%
18 hours | 100% | 100% | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 99.9% | 99.98% | -0.08002%
EHV Faults: 3 hours | 67.8% | 94.3% | 98.9% | 97.7% | 90.6% | 99.3% | 99.1% | 97.7% | 99.1% | 95.2% | 93.97% | 1.309%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 100% | 98.7% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.87% | 0.1302%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 90.7% | 91.1% | 92.2% | 91.5% | 92.1% | 88.7% | 90.1% | 92.8% | 92.2% | 92.1% | 91.35% | 0.821% | 92.8% | 88.7% |  | 1771047.081
18 hours | 100% | 100% | 100% | 99.9% | 100% | 100% | 100% | 100% | 100% | 99.9% | 99.98% | -0.08002% | 100% | 99.9% |  | 1921038.039
TOTAL not rest in 3 hrs | 9.3% | 8.9% | 7.8% | 8.5% | 7.9% | 11.3% | 9.9% | 7.2% | 7.8% | 7.9% | 8.65% | -8.671% | 11.3% | 7.2% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0% | 0% | 0% | 0.1% | 0% | 0% | 0% | 0% | 0% | 0.1% | 0.02% | 400% | 0.1% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.1 | 1 | 0.6 | 0.78 | 0.61 | 2.58 | 1.02 | 1.47 | 1.06 | 0.75 | 1.097 | 10 | 2.58 | 0.6 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
EME total distribution system | 13.6 | 13.8 | 12.96 | 16.9 | 14.63 | 20 | 16.95 | 13.4 | 12.5 | 12 | 14.9711 | -5.1% | 20 | 12 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1938000 | 1952000 | 1968761 | 1977000 | 1985000 | 2071000 | 2108000 | 2126000 | 2139000 | 2152000
Embedded Gen.Stations | 1 | 1 | 1 | 1 | 37 | 50 | 61 | 73 | 76 | 100
Emb.Gen.Capacity MWSO | 342 | 342 | 342 | 342 | 248 | 257 | 260.93 | 326 | 330 | 790
[8 empty] | %age overhead all voltages | 27.26% | 27.13%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 0 | 1179 | 1178 | 1178 | 1178 | 1178 | 1179 | 1179
EHV |  |  | 0 | 1323 | 1322 | 1322 | 1321 | 1322 | 1321 | 1317
25kV |  |  | 0
11kV |  |  | 0
6.6kV |  |  | 0
HV |  |  | 0 | 5657 | 5882 | 5882 | 5646 | 5624 | 5610 | 5605
3kV |  |  | 0
0
0
0
LV |  |  | 0 | 4180 | 4283 | 4283 | 4165 | 4161 | 4156 | 4155
TOTAL |  |  |  |  | 12339 | 12665 | 12310 | 12285 | 12266 | 12256
Underground cable
132kV |  |  | 0 | 333 | 333 | 333 | 333 | 333 | 333 | 333
EHV |  |  | 0 | 1239 | 1237 | 1237 | 1250 | 1250 | 1250 | 1261
25kV |  |  | 0
11kV |  |  | 0
6.6kV |  |  | 0
HV |  |  | 0 | 10127 | 10323 | 10323 | 10659 | 10750 | 10870 | 10950
3kV |  |  | 0
0
0
LV |  |  | 0 | 19761 | 20354 | 20354 | 20019 | 20155 | 20283 | 20381
TOTAL | [5 empty] | 31460 | 32247 | 32488 | 32736 | 32925
[9 empty] | 45002 | 45181
Transformers
Primary Voltage
132kV | [5 empty] | 157 | 154 | 154 | 154 | 154
33kV | [5 empty] | 450 | 570 | 452 | 448 | 448
Distribution pole-mounted | [5 empty] | 12806 | 13490 | 13497 | 13519 | 13525
Distribution Other | [5 empty] | 17752 | 17768 | 18169 | 18464 | 18606
Capacity | [6 empty] | 31982 | 32272 | 32585 | 32733
132kV | [5 empty] | 8369 | 8249 | 8262 | 8684 | 8262
33kV | [5 empty] | 6844 | 6606 | 6663 | 6882 | 6842
Distribution | [5 empty] | 8669 | 8886 | 8930 | 8930 | 9346
[6 empty] | 23883 | 23741 | 23855 | 24496 | 24450
HV O/H length (km) | 5950 | 5917 | 5884 | 5851 | 5818 | 5785 | 5752 | 5752 | 5610 | 5605
HV U/G length (km) | 10095.3033 | 10091.0711 | 10086.8389 | 10082.6067 | 10078.3744 | 10074.1422 | 10069.91 | 10750 | 10870 | 10950
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 3.0715 | 3.8688 | 3.1229 | 6.2746 | 7.2874 | 9.8676 | 4.8147 | 6.1308 | 3.7388 | 1.9653 | 5.0142 |  | 9.8676 | 1.9653
HV faults: U/G damage | 77.1721 | 84.5326 | 75.7303 | 89.4126 | 73.6617 | 67.2233 | 77.8732 | 88.2043 | 71.628 | 77.6292 | 78.3067 |  | 89.4126 | 67.2233
HV faults: O/H no damage | 22.4743 | 31.0103 | 16.7298 | 30.0723 | 26.9534 | 22.9117 | 24.1878 | 20.3286 | 18.3016 | 15.7417 | 22.8711 |  | 31.0103 | 15.7417
HV faults: O/H damage | 28.3371 | 33.3196 | 27.4368 | 34.8028 | 30.0241 | 34.0095 | 34.0828 | 39.1787 | 37.7471 | 28.4118 | 32.735 |  | 39.1787 | 27.4368
HV underground networks | 80.2437 | 88.4013 | 78.8532 | 95.6872 | 80.9491 | 77.0909 | 82.6879 | 94.3351 | 75.3668 | 79.5945 | 83.321 |  | 95.6872 | 75.3668 |  |  |  | 1 | 1
HV overhead networks | 50.8114 | 64.3299 | 44.1666 | 64.8751 | 56.9775 | 56.9212 | 58.2705 | 59.5073 | 56.0487 | 44.1534 | 55.6062 |  | 64.8751 | 44.1534 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 153.5764 | 290.1575 | 214.6993 | 411.7685 | 512.0866 | 698.9578 | 418.6731 | 375.7581 | 275.4922 | 58.9589 | 341.0128 |  | 698.9578 | 58.9589
HV faults: U/G damage | 5413.5669 | 7002.4677 | 5855.4351 | 6784.3765 | 5357.2131 | 6146.7169 | 6782.5035 | 6407.6651 | 5923.0819 | 6367.5616 | 6204.0588 |  | 7002.4677 | 5357.2131
HV faults: O/H no damage | 2052 | 3925.7732 | 1606.0593 | 3683.0115 | 2456.5143 | 2470.1642 | 3151.7385 | 1848.0529 | 1868.2888 | 1420.5888 | 2448.2191 |  | 3925.7732 | 1420.5888
HV faults: O/H damage | 3289.7143 | 3694.8454 | 3145.1994 | 4392.5825 | 3002.4063 | 4797.1305 | 4617.6634 | 3991.7942 | 4155.9893 | 3263.5147 | 3835.084 |  | 4797.1305 | 3002.4063
HV underground networks | 5567.1433 | 7292.6253 | 6070.1343 | 7196.145 | 5869.2997 | 6845.6746 | 7201.1766 | 6783.4233 | 6198.5741 | 6426.5205 | 6545.0717 |  | 7292.6253 | 5567.1433 |  |  |  | 1 | 0
HV overhead networks | 5341.7143 | 7620.6186 | 4751.2587 | 8075.5939 | 5458.9206 | 7267.2947 | 7769.4019 | 5839.847 | 6024.2781 | 4684.1035 | 6283.3031 |  | 8075.5939 | 4684.1035 |  |  |  | 1 | 0
5625.25
5186.4805
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1994395.8 | 3121248 | 1960885.956 | 2056080 | 1889720 | 1847332 | 1918280 | 2030330 | 1922961 | 1904520
| 186435600 | 230921600 | 165572800.1 | 184454100 | 154631500 | 184940300 | 193936000 | 161150800 | 156574800 | 160324000

## I
Southern
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 3.7 | 4.11 | 4.1 | 3.71 | 2.99 | 2.56 | 2.26 | 2.11 | 2.61 | 1.22 | 2.937
LV faults | 4.74 | 5.34 | 4.96 | 4.45 | 5.09 | 3.96 | 3.63 | 3.37 | 4.42 | 5.86 | 4.582 | [8 empty] | 152930.1608
HV faults: U/G no damage | 0.49 | 0.42 | 0.13 | 0.25 | 0.66 | 0.33 | 0.55 | 0.23 | 0.66 | 0.56 | 0.428
HV faults: U/G damage | 20.64 | 22.74 | 20.29 | 21.05 | 22.98 | 22.27 | 20.61 | 22.08 | 23.46 | 23.97 | 22.009
HV faults: O/H no damage | 6.28 | 7.07 | 5.15 | 5.62 | 6.73 | 6.98 | 4.55 | 3.98 | 7.54 | 7.49 | 6.139
HV faults: O/H damage | 10.62 | 10.82 | 12.01 | 10.7 | 12.71 | 11.55 | 10.28 | 6.81 | 7.72 | 8.48 | 10.17 |  |  |  |  | 2029718.25
HV faults: All other | 11.98 | 11.05 | 11.98 | 13.48 | 16.34 | 16.84 | 13.8 | 13.72 | 13.65 | * | 12.284 |  |  |  |  | 2085361.2233
HV faults: Total | 50.01 | 52.1 | 49.56 | 51.1 | 59.42 | 57.97 | 49.79 | 46.82 | 53.03 | 55.09 | 52.489 | 4.955% |  |  |  | 1994223.6072 |  |  |  | 1414527.6357
EHV faults | 7.49 | 9.87 | 8.93 | 8.09 | 5.7 | 6.62 | 7.63 | 5.98 | 9.7 | 9.97 | 7.998 | 24.66% |  |  |  | 1938143.5174 |  |  |  | 215538.3419
132kV faults | 0.76 | 0.79 | 2.79 | 1.24 | 2.77 | 2.33 | 6.34 | 2.71 | 2.96 | 0 | 2.269 | -100% |  |  |  | 2061414.4166 |  |  |  | 61147.3491
Total of (a) | 66.7 | 72.21 | 70.34 | 68.62 | 75.97 | 73.44 | 69.65 | 60.99 | 72.72 | 72.15 | 70.279 | 2.662% |  |  |  | 2072131.9776
(b) Planned Outages | 10.67 | 8.81 | 7.87 | 6.69 | 3.33 | 2.91 | 1.93 | 1.83 | 1.65 | 1.63 | 4.732 | -65.55% |  |  |  | 1925294.7413 |  |  |  | 127522.81
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1696745.3976
(d) Other Systems | 3.9 | 1.47 | 0 | 0 | 0 | 2.67 | 1.15 | 1.15 | 0 | 0 | 1.034 |  |  |  |  | 1993902.0909 |  |  |  | 27865.297
Total of (a+b+c+d) | 81.27 | 82.49 | 78.21 | 75.31 | 79.31 | 79.02 | 72.73 | 63.97 | 74.37 | 73.78 | 76.046 | -2.98% | 82.49 | 63.97 |  | 1988299.4334 | 84.163 | 1 | 0 | 2049365.9354
[9 empty] | 72.72 | 72.15 | [5 empty] | 1944372.5145
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 5.54 | 5.36 | 4.97 | 6.81 | 4.31 | 3.35 | 2.71 | 2.49 | 3.4 | 2.65 | 4.159
LV faults | 10.95 | 11.46 | 10.73 | 11.4 | 12.34 | 9.37 | 8.43 | 8.35 | 11.38 | 15.55 | 10.996 | [8 empty] | 36700568.484
HV faults: U/G no damage | 0.36 | 0.22 | 0.11 | 0.14 | 0.41 | 0.2 | 0.21 | 0.11 | 0.41 | 0.32 | 0.249
HV faults: U/G damage | 20.56 | 19.88 | 17.14 | 18.62 | 19.35 | 17.3 | 14.46 | 15.62 | 15.56 | 16.61 | 17.51
HV faults: O/H no damage | 4.74 | 4.17 | 3.31 | 4.52 | 4.99 | 4.51 | 2.7 | 2.27 | 3.28 | 3.36 | 3.785
HV faults: O/H damage | 12.3 | 11.57 | 12.27 | 11.87 | 16.77 | 12.79 | 9.39 | 6.46 | 6.95 | 11.93 | 11.23 |  |  |  |  | 272677050
HV faults: All other | 10.38 | 7.45 | 7.92 | 10.28 | 10.92 | 10.51 | 6.99 | 7.16 | 6.94 | * | 7.855 |  |  |  |  | 230807952.1
HV faults: Total | 48.34 | 43.29 | 40.75 | 45.43 | 52.44 | 45.31 | 33.75 | 31.62 | 33.14 | 40.8 | 41.487 | -20.12% |  |  |  | 189707500.8 |  |  |  | 138999081.975
EHV faults | 3.1 | 5.71 | 3.44 | 2.98 | 2.38 | 2.85 | 2.61 | 3.97 | 4.13 | 5.85 | 3.702 | 11.56% |  |  |  | 199733525.94 |  |  |  | 12403273.35
132kV faults | 0.61 | 0.02 | 0.11 | 0.01 | 0.22 | 0.14 | 3.43 | 0.11 | 1.2 | 0 | 0.585 | 105.1% |  |  |  | 202684524.28 |  |  |  | 1959998.625
Total of (a) | 68.54 | 65.84 | 60 | 66.68 | 71.69 | 61.02 | 50.93 | 46.54 | 53.25 | 64.85 | 60.934 | -12.61% |  |  |  | 176296422.24
(b) Planned Outages | 39.37 | 24.3 | 14.4 | 10.92 | 6.29 | 6.05 | 4.77 | 4.74 | 4.29 | 3.89 | 11.902 | -63.96% |  |  |  | 148321551.43 |  |  |  | 39876758.35
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 136943825.04
(d) Other Systems | 1.27 | 1.16 | 0 | 0 | 0 | 0.16 | 0.33 | 0.35 | 0 | 0 | 0.327 |  |  |  |  | 154268019.78 |  |  |  | 1095588.975
Total of (a+b+c+d) | 109.18 | 91.3 | 74.4 | 77.61 | 77.98 | 67.23 | 56.03 | 51.63 | 57.54 | 68.74 | 73.164 | -6.047% | 109.18 | 51.63 |  | 185247632.22 | 85.7596 | 1 | 0 | 244194288.156
[9 empty] | 53.25 | 64.85 | [5 empty] | 173866546.45
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 57.17% | 70.13% | 71.24% | 60.91% | 63.16% | 63.46% | 66.89% | 65.35% | 62.79% | 59.93% | 64.1% | -6.51%
24 hours | 99.65% | 99.79% | 99.82% | 99.78% | 99.97% | 100% | 99.99% | 100% | 99.98% | 97.03% | 99.6% | -2.581%
HV Faults:U/G no damage 3 hours | 94.23% | 99.13% | 89.51% | 98.88% | 97.28% | 99.67% | 100% | 100% | 91.49% | 98.41% | 96.86% | 1.6%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 91.94% | 94.42% | 94.81% | 94.76% | 94.54% | 95.31% | 96.17% | 95.9% | 96.1% | 95.16% | 94.91% | 0.2624%
24 hours | 99.96% | 99.97% | 99.94% | 99.96% | 100% | 100% | 100% | 100% | 100% | 100% | 99.98% | 0.017%
HV Faults: O/H no damage 3 hours | 92.85% | 96.84% | 95.88% | 93.5% | 93.75% | 93.42% | 96.5% | 94.84% | 97.35% | 95.32% | 95.03% | 0.3104%
24 hours | 100% | 100% | 100% | 100% | 99.93% | 100% | 100% | 100% | 100% | 99.99% | 99.99% | -0.002%
HV Faults: O/H damage 3 hours | 84.99% | 84.35% | 86.07% | 84.04% | 82.55% | 84.74% | 89.93% | 87.5% | 89.23% | 76.94% | 85.03% | -9.519%
24 hours | 99.96% | 99.99% | 100% | 99.95% | 99.75% | 100% | 99.97% | 100% | 100% | 99.85% | 99.95% | -0.09705%
HV Faults: Other 3 hours
24 hours
HV Faults: Total 3 hours | 90.46% | 92.67% | 92.85% | 92.26% | 92.07% | 92.99% | 94.94% | 94.59% | 94.99% | 91.85% | 92.97% | -1.202%
24 hours | 99.96% | 99.98% | 99.97% | 99.97% | 99.94% | 100% | 99.99% | 100% | 100% | 99.97% | 99.98% | -0.008002%
EHV Faults: 3 hours | 98.31% | 92.39% | 99.37% | 97.53% | 96.88% | 98.43% | 99.77% | 94.3% | 95.43% | 93.75% | 96.62% | -2.966%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 85.68% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.57% | 1.453%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 88.83% | 90% | 91.22% | 89.37% | 89.8% | 91.64% | 93.7% | 92.35% | 92.17% | 89.01% | 90.81% | -1.981% | 93.7% | 88.83% |  | 1837779.5572
24 hours | 99.94% | 99.96% | 99.97% | 99.95% | 99.95% | 100% | 99.99% | 100% | 100% | 99.69% | 99.94% | -0.2551% | 100% | 99.69% |  | 1993902.0909
TOTAL not rest in 3 hrs | 11.17% | 10% | 8.78% | 10.63% | 10.2% | 8.36% | 6.3% | 7.65% | 7.83% | 10.99% | 9.191% | 19.57% | 11.17% | 6.3% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.06% | 0.04% | 0.03% | 0.05% | 0.05% | 0% | 0.01% | 0% | 0% | 0.31% | 0.055% | 463.6% | 0.31% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At NGC request* | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0
*No. of occasions upto and including1990/91. | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
Demand in MWh lost per 100 customers thereafter | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A
TOTAL | N/A | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
(b) due to plc action | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
*No. of occasions upto and including1990/91. | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A
Demand in MWh lost per 100 customers thereafter | N/A | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A | N/A
Total* | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.36 | 1.74 | 2.73 | 2.31 | 2.32 | 1.51 | 1.19 | 1.05 | 1.53 | 1.74 | 1.848 | 10 | 2.73 | 1.05 |  |  |  | 1 | 0
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
Excluding service faults# | 12.01 | 14.85 | 13.64 | 13.74 | 13.16 | 11.74 | 12.38 | 12.12 | 13.57 | 23.92 | 14.113 | -3.848% | 23.92 | 11.74 |  |  |  | 1 | 0
5 RELEVANT DATA: | [11 empty] | 7.865%
Number of Customers | 2497500 | 2528017 | 2549832 | 2573554 | 2599186 | 2622288 | 2647181 | 2652408 | 2681057 | 2694903 |  | 4.339%
Embedded Gen.Stations | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 4 | 4 | N/A | N/A
Emb.Gen.Capacity MWSO | 588 | 588 | 588 | 308 | 308 | 308 | 308 | 308 | 474 | 474 | N/A | N/A
NOTES N/A - Information not applicable |  | * - Information not available |  |  | # - Nine year average |  |  | %age overhead all voltages | 38.26% | 37.94%
Mains in commission (circuit kilometres)
Overhead Line
132kV | 1981 | 1981 | 1981 | 1981 | 1981 | 1981 | 1894 | 1900 | 1920 | 1920
66kV |  |  |  |  | 6 | 6 | 6 | 6 | 6 | 6
33kV | 3392 | 3605 | 3604 | 3604 | 3612 | 3610 | 3503 | 3552 | 3465 | 3458
25kV
22kV | 13 | 13 | 13 | 13 | 13 | 13 | 7 | 7 | 7 | 7
11kV | 14344 | 14360 | 14380 | 14388 | 14381 | 14331 | 13597 | 13347 | 13400 | 13372
6.6kV | 98 | 95 | 93 | 93 | 93 | 91 | 63 | 60 | 60 | 59
2kV to 3.3kV | 11 | 11 | 11 | 11 | 11 | 10 | 5 | 3 | 2 | 2
LV | 8860 | 8852 | 8836 | 8836 | 8836 | 8828 | 9038 | 9038 | 8968 | 8960
TOTAL | 28699 | 28917 | 28918 | 28926 | 28933 | 28870 | 28113 | 27913 | 27828 | 27784
Underground cable
132kV | 313 | 321 | 321 | 321 | 321 | 322 | 366 | 392 | 387 | 406
66kV | 198 | 200 | 201 | 201 | 179 | 184 | 141 | 165 | 148 | 153
33kV | 1093 | 1098 | 1101 | 1103 | 1103 | 1107 | 1228 | 1234 | 1332 | 1360
25kV |  |  |  | 5
22kV | 484 | 485 | 484 | 480 | 480 | 469 | 366 | 354 | 358 | 359
11kV | 11453 | 11622 | 11779 | 11807 | 11898 | 12244 | 12479 | 12731 | 13121 | 13321
6.6kV | 1488 | 1492 | 1482 | 1478 | 1478 | 1482 | 632 | 629 | 647 | 654
2kV to 3.3kV | 383 | 376 | 368 | 368 | 368 | 343 | 146 | 124 | 121 | 112
LV | 26147 | 26437 | 26644 | 26736 | 26890 | 27224 | 27984 | 28392 | 28798 | 29080
TOTAL | 41559 | 42031 | 42380 | 42499 | 42717 | 43375 | 43342 | 44021 | 44912 | 45445
72740
Transformers
Primary Voltage
132kV | [6 empty] | 231 | 231 | 234 | 232
33kV | [6 empty] | 859 | 862 | 864 | 876
Distribution pole-mounted | [6 empty] | 25483 | 25477 | 25629 | 25683
Distribution Other | [6 empty] | 25966 | 24889 | 26486 | 27911
Capacity | [6 empty] | 52539 | 51429 | 53213 | 54702
132kV | [6 empty] | 14538 | 14515 | 14359 | 14236
33kV | [6 empty] | 14669 | 14552 | 14853 | 15059
Distribution | [6 empty] | 13537.1 | 13106.6 | 13521.5 | 13690.3
[7 empty] | 42744.1 | 42173.6 | 42733.5 | 42985.3
HV O/H length (km) | 14453 | 14466 | 14484 | 14492 | 14485 | 14432 | 13665 | 13410 | 13462 | 13433
HV U/G length (km) | 13324 | 13490 | 13629 | 13653 | 13744 | 14069 | 13257 | 13484 | 13889 | 14087
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 0.91847 | 0.78708 | 0.24322 | 0.47124 | 1.2482 | 0.61508 | 1.0982 | 0.45243 | 1.274 | 1.0713 | 0.81793 |  | 1.274 | 0.24322
HV faults: U/G damage | 38.6884 | 42.6146 | 37.9603 | 39.6787 | 43.4585 | 41.5085 | 41.1544 | 43.4331 | 45.2859 | 45.8556 | 41.9638 |  | 45.8556 | 37.9603
HV faults: O/H no damage | 10.8519 | 12.3552 | 9.0663 | 9.9802 | 12.0763 | 12.6826 | 8.8143 | 7.8722 | 15.0165 | 15.0263 | 11.3742 |  | 15.0263 | 7.8722
HV faults: O/H damage | 18.3515 | 18.9086 | 21.143 | 19.0015 | 22.8068 | 20.9863 | 19.9144 | 13.4697 | 15.375 | 17.0124 | 18.6969 |  | 22.8068 | 13.4697
HV underground networks | 39.6069 | 43.4017 | 38.2035 | 40.1499 | 44.7066 | 42.1236 | 42.2527 | 43.8855 | 46.5599 | 46.9269 | 42.7817 |  | 46.9269 | 38.2035 |  |  |  | 0 | 0
HV overhead networks | 29.2035 | 31.2638 | 30.2093 | 28.9818 | 34.8831 | 33.6689 | 28.7286 | 21.3419 | 30.3914 | 32.0387 | 30.0711 |  | 34.8831 | 21.3419 |  |  |  | 0 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 67.4797 | 41.2279 | 20.5798 | 26.3896 | 77.5368 | 37.2775 | 41.9332 | 21.6379 | 79.1442 | 61.2174 | 47.4424 |  | 79.1442 | 20.5798
HV faults: U/G damage | 3853.8427 | 3725.4987 | 3206.7005 | 3509.8202 | 3659.3604 | 3224.5065 | 2887.3981 | 3072.5759 | 3003.6177 | 3177.5636 | 3332.0884 |  | 3853.8427 | 2887.3981
HV faults: O/H no damage | 819.0791 | 728.7316 | 582.7081 | 802.6818 | 895.4048 | 819.465 | 523.0434 | 448.9908 | 653.2363 | 674.0768 | 694.7418 |  | 895.4048 | 448.9908
HV faults: O/H damage | 2125.4584 | 2021.9243 | 2160.0689 | 2107.9275 | 3009.206 | 2323.9373 | 1819.0289 | 1277.7446 | 1384.144 | 2393.374 | 2062.2814 |  | 3009.206 | 1277.7446
HV underground networks | 3921.3224 | 3766.7266 | 3227.2802 | 3536.2098 | 3736.8972 | 3261.7841 | 2929.3313 | 3094.2137 | 3082.7619 | 3238.781 | 3379.5308 |  | 3921.3224 | 2929.3313 |  |  |  | 1 | 0
HV overhead networks | 2944.5375 | 2750.6559 | 2742.777 | 2910.6093 | 3904.6108 | 3143.4023 | 2342.0723 | 1726.7354 | 2037.3803 | 3067.4508 | 2757.0232 |  | 3904.6108 | 1726.7354 |  |  |  | 1 | 0
9870.818
9097.933
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 2029718.25 | 2085361.2233 | 1994223.6072 | 1938143.5174 | 2061414.4166 | 2072131.9776 | 1925294.7413 | 1696745.3976 | 1993902.0909 | 1988299.4334
| 272677050 | 230807952.1 | 189707500.8 | 199733525.94 | 202684524.28 | 176296422.24 | 148321551.43 | 136943825.04 | 154268019.78 | 185247632.22
* figures not supplied

## J
SWALEC
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.2689 | 0.51214 | 0.6 | 0.5 | 0.3 | 0.4 | 0.5 | 0.7 | 0.5 | 0.6 | 0.5881
LV faults | 7.881 | 4.1 | 4.1 | 3.5 | 2.4 | 3.3 | 3.1 | 3.5 | 3.6 | 3.2 | 3.8681 | [8 empty] | 129102.9523
HV faults: U/G no damage | 1.0828 | 1.6689 | 1.3 | 1.6 | 2.8 | 4.2 | 0.9 | 2.4 | 1.5 | 1.3 | 1.8752
HV faults: U/G damage | 47.8439 | 59.2444 | 59.9 | 62.3 | 46.7 | 47 | 44.3 | 36.8 | 36.6 | 35.9 | 47.6588
HV faults: O/H no damage | 10.0233 | 10.7154 | 12.9 | 17.6 | 15.7 | 14.3 | 18.5 | 20.8 | 23.2 | 30 | 17.3739
HV faults: O/H damage | 29.16 | 26.0832 | 35.3 | 27.5 | 38 | 28 | 26.6 | 23.4 | 21.1 | 28.4 | 28.3543 |  |  |  |  | 2104469.64
HV faults: All other | 41.4945 | 32.2513 | 35.1 | 31.4 | 31.5 | 29.2 | 30.6 | 16.5 | 16 | 22 | 28.6046 |  |  |  |  | 1825729.543
HV faults: Total | 129.6045 | 129.9633 | 144.6 | 140.4 | 134.7 | 122.8 | 120.9 | 99.9 | 98.4 | 117.5 | 123.8768 | -5.148% |  |  |  | 2024396.325 |  |  |  | 1237157.3615
EHV faults | 13.8443 | 11.4253 | 15.8 | 17.7 | 27.5 | 17.1 | 17.9 | 11.2 | 9.8 | 11.9 | 15.417 | -22.81% |  |  |  | 2101430.5 |  |  |  | 153969.2207
132kV faults | 0.92631 | 14.9093 | 7 | 19.1 | 17.2 | 5.1 | 1.4 | 2.2 | 16.4 | 7.8 | 9.2036 | -15.25% |  |  |  | 2152165.4 |  |  |  | 91915.9583
Total of (a) | 152.3 | 160.3846 | 171.5 | 180.6 | 181.9 | 148.3 | 143.3 | 116.8 | 128.3 | 140.4 | 152.3785 | -7.861% |  |  |  | 1858723.2
(b) Planned Outages | 75.7 | 34.9 | 42 | 38.9 | 41.2 | 43.4 | 42.4 | 33.4 | 17.1 | 17.8 | 38.68 | -53.98% |  |  |  | 1813546.2 |  |  |  | 386297.16
(c) Embedded Gen. | 0 | 0 | 0 | 0.2 | 0.2 | 0 | 0 | 0 | 0 | 0 | 0.04 |  |  |  |  | 1473762.4
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.3 | 5.6 | 1.29 |  |  |  |  | 1509744.9 |  |  |  | 13282.71
Total of (a+b+c+d) | 228 | 195.2846 | 213.5 | 219.7 | 223.3 | 191.7 | 185.7 | 150.2 | 152.7 | 158.2 | 191.8285 | -17.53% | 228 | 150.2 |  | 1579943.4 | 84.163 | 1 | 0 | 1915790.8458
[9 empty] | 135.6 | 140.4 | [5 empty] | 1402174.8
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | * | 0.91838 | 1.1 | 0.8 | 0.6 | 0.8 | 0.8 | 0.9 | 1.2 | 0.9 | 0.80184
LV faults | 17.2 | 8.9 | 7.9 | 6.9 | 5.2 | 6.6 | 8.2 | 4.7 | 6.8 | 6.1 | 7.85 | [8 empty] | 26300836.25
HV faults: U/G no damage | 0.7 | 1.1 | 0.8 | 0.9 | 1.3 | 3.8 | 0.5 | 1.6 | 1.3 | 1.2 | 1.32
HV faults: U/G damage | 44.5 | 52.1 | 52.3 | 58 | 46.5 | 45.1 | 41.2 | 33.6 | 33.3 | 29.4 | 43.6
HV faults: O/H no damage | 6.9 | 9.2 | 10.7 | 16.6 | 17.8 | 12.4 | 14.2 | 17.3 | 16.2 | 22.7 | 14.4
HV faults: O/H damage | 32.8 | 28.2 | 46.8 | 38.8 | 72.2 | 35.3 | 34.2 | 25.1 | 22 | 30.8 | 36.62 |  |  |  |  | 300329362.17
HV faults: All other | 27 | 24.7 | 28.4 | 25.6 | 26.2 | 23.7 | 22.8 | 14.1 | 11.4 | 12.2 | 21.61 |  |  |  |  | 198512099.2
HV faults: Total | 112.0313 | 115.2781 | 139 | 140 | 164.2 | 120.3 | 112.9 | 91.7 | 84.2 | 96.2 | 117.5809 | -18.18% |  |  |  | 189164902.5 |  |  |  | 393946112.4386
EHV faults | 3.7811 | 3.5554 | 6.3 | 8.2 | 10.5 | 9.6 | 10.1 | 6.8 | 3.2 | 5.1 | 6.7136 | -24.04% |  |  |  | 202778000 |  |  |  | 22493554.2964
132kV faults | 0.10189 | 6.9655 | 2.4 | 4.6 | 8.9 | 0.5 | 1 | 0.6 | 12.3 | 0.4 | 3.7767 | -89.41% |  |  |  | 224276260 |  |  |  | 12653696.2281
Total of (a) | 133.0893 | 134.7335 | 155.6 | 159.6 | 188.7 | 137 | 132.2 | 103.8 | 106.6 | 107.8 | 135.9123 | -20.68% |  |  |  | 183545280
(b) Planned Outages | 192.29 | 77.6 | 43.9 | 52.3 | 43.8 | 52.3 | 50.7 | 41.4 | 18 | 15.5 | 58.779 | -73.63% |  |  |  | 178620140 |  |  |  | 196934631.075
(c) Embedded Gen. | 0 | 0 | 0 | 0.1 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0.02 |  |  |  |  | 142470240
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.2 | 0 | 1.22 |  |  |  |  | 135254160 |  |  |  | 4154527
Total of (a+b+c+d) | 325.3793 | 212.3335 | 199.5 | 212 | 232.7 | 189.3 | 182.9 | 145.2 | 136.8 | 123.3 | 195.9413 | -37.07% | 325.3793 | 123.3 |  | 123139710 | 85.7596 | 1 | 1 | 656486585.4595
Note: * indicates information either not available or inapplicable | [8 empty] | 118.8 | 107.8 | [5 empty] | 106581860
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 47.6% | 50.01% | 56.38% | 55.67% | 50.49% | 56.84% | 53.9% | 55.7% | 62.4% | 72.7% | 56.17% | 29.43%
18 hours | 99.76% | 99.97% | 99.78% | 99.84% | 99.76% | 99.92% | 94.7% | 99.8% | 100% | 97.9% | 99.14% | -1.255%
HV Faults:U/G no damage 3 hours | 96.35% | 98.37% | 98.14% | 98.61% | 98.29% | 84.91% | 100% | 98.7% | 84.4% | 99.1% | 95.69% | 3.568%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 91.25% | 93.07% | 92.63% | 91.2% | 89.67% | 91.31% | 92.6% | 90.5% | 92.7% | 92.7% | 91.76% | 1.022%
18 hours | 100% | 100% | 100% | 99.97% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.003295%
HV Faults: O/H no damage 3 hours | 92.87% | 90.3% | 89.9% | 90.84% | 87.32% | 89.5% | 90.9% | 91.8% | 93.9% | 91% | 90.83% | 0.1829%
18 hours | 100% | 100% | 100% | 99.72% | 99.38% | 99.99% | 100% | 100% | 100% | 100% | 99.91% | 0.09138%
HV Faults: O/H damage 3 hours | 84.18% | 86.92% | 79.77% | 81.11% | 75.32% | 78.6% | 76.5% | 84.8% | 84.8% | 84.1% | 81.61% | 3.052%
18 hours | 100% | 100% | 99.89% | 99.94% | 98.34% | 99.98% | 99.9% | 100% | 100% | 100% | 99.8% | 0.1959%
HV Faults: Other 3 hours | 93.42% | 91.52% | 91.99% | 90.06% | 89.82% | 92.17% | 92.7% | 89.4% | 91.2% | 95.4% | 91.77%
18 hours | 100% | 99.98% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 100% | 100%
HV Faults: Total 3 hours | 90.52% | 91.29% | 89.14% | 89.01% | 85.56% | 88.18% | 88.9% | 89.5% | 90.9% | 90.8% | 89.38% | 1.589%
18 hours | 100% | 100% | 99.97% | 99.93% | 99.46% | 100% | 100% | 100% | 100% | 100% | 99.94% | 0.06415%
EHV Faults: 3 hours | 99.62% | 100% | 97.22% | 93.56% | 99.65% | 93.07% | 87.8% | 95.3% | 98.8% | 100% | 96.5% | 3.625%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
132kV F'lts: 3 hours | 100% | 93.13% | 100% | 100% | 86.09% | 100% | 100% | 100% | 100% | 100% | 97.92% | 2.123%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
Total Faults:3 hours | 89.18% | 91.02% | 89.55% | 89.97% | 87.28% | 88.47% | 88.1% | 89.2% | 91.6% | 91.4% | 89.58% | 2.035% | 91.6% | 87.28% |  | 1379906.8386
18 hours | 99.99% | 100% | 99.97% | 99.94% | 99.59% | 99.99% | 99.9% | 100% | 100% | 100% | 99.94% | 0.06222% | 100% | 99.59% |  | 1402174.8
TOTAL not rest in 3 hrs | 10.82% | 8.984% | 10.45% | 10.03% | 12.72% | 11.53% | 11.9% | 10.8% | 8.4% | 8.6% | 10.42% | -17.49% | 12.72% | 8.4% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.0143% | 0.004467% | 0.028% | 0.055% | 0.41% | 0.01% | 0.1% | 0% | 0% | 0% | 0.06218% | -100% | 0.41% | 0% |  |  |  | 1 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
- Load Disconnection | * | nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
(b) due to plc action
- Voltage Reductions | * | 0.006 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
- Load Disconnection | * | nil | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N/A | N/A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 3.7 | 2.0537 | 1.2 | 1.9 | 2.2 | 1 | 1 | 0.9 | 0.7 | 0.6 | 1.5254 | 10 | 3.7 | 0.6 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
SWaE total system | 21.6036 | 21.3981 | 18.5 | 17.53 | 15.95 | 16.51 | 16.12 | 15.07 | 14.15 | 15.51 | 17.2342 | 0.375% | 21.6036 | 14.15 |  |  |  | 1 | 1
5 RELEVANT DATA: | [6 empty] | Restated to exclude services | Restated to exclude services
Number of Customers | 923013 | 934907 | 948195 | 956500 | 963800 | 969600 | 976600 | 981200 | 988700 | 998700
Embedded Gen.Stations | * | * | * | 3 | * | * | * | * | 1 | 1
Emb.Gen.Capacity MWSO | * | * | * | 621 | * | * | * | * | 240 | 240
Note: * indicates information either not available or inapplicable | [7 empty] | %age overhead all voltages | 56.51% | 55.92%
Mains in commission (circuit kilometres)
Overhead Line
132kV | 1123 | 1124 | 1136 | 1144 | 1149 | 1149 | 1157 | 1165 | 1165 | 1165
66 & 33kV | 1856 | 1800 | 1805 | 1814 | 1809 | 1812 | 1800 | 1800 | 1799 | 1820
33kV |  |  |  | 1357
25kV |  |  |  | 1
22kV
11kV | 12654 | 12475 | 12147 | 12297 | 12282 | 12282 | 12316 | 12316 | 12316 | 12315
6.6kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV | 3397 | 3389 | 3393 | 3375 | 3373 | 3378 | 3378 | 3378 | 3378 | 3165
TOTAL | 19030 | 18788 | 18481 | 18630 | 18613 | 18621 | 18651 | 18659 | 18658 | 18465
Underground cable
132kV | 67 | 67 | 60 | 60 | 68 | 68 | 69 | 69 | 71 | 71
66 & 33kV | 364 | 357 | 358 | 359 | 361 | 363 | 379 | 391 | 392 | 380
33kV
25kV |  |  |  | 236
22kV
11kV | 4513 | 4160 | 4171 | 4265 | 4432 | 4432 | 4619 | 4803 | 4863 | 4970
6.6kV | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 16
3.3kV
3kV
LV | 8205 | 8275 | 8363 | 8441 | 8504 | 8627 | 8787 | 8927 | 9007 | 9120
TOTAL | 13173 | 12883 | 12976 | 13149 | 13389 | 13514 | 13878 | 14214 | 14357 | 14557
|  | 31671 | 31457 | 31779 | 32002 | 32135 | 32529 | 32873 | 33015 | 33022
Transformers in commission |  |  | 29150
Not pole mounted |  |  |  |  | 58351
132kV | 86 | 90 | 91 | 95 | 105 | 109 | 112 | 114 | 118 | 118
66kV or 33kV | 296 | 304 | 302 | 300 | 292 | 290 | 286 | 279 | 277 | 277
11kV and 6.6kV | 6940 | 7011 | 7052 | 7138 | 7180 | 7238 | 7287 | 7337 | 7425 | 7425
TOTAL | 7322 | 7405 | 7445 | 7533 | 7577 | 7637 | 7685 | 7730 | 7820 | 7820
33kV
Pole mounted
11kV and 6.6kV | 30733 | 30944 | 31073 | 31164 | 31158 | 31139 | 31046 | 30888 | 30935 | 30715
TOTAL | 30733 | 30944 | 31073 | 31164 | 31158 | 31139 | 31046 | 30888 | 30935 | 30715
[9 empty] | 38755 | 38535
Aggregate Capacity (MVA)
132kV | 4700 | 4740 | 4820 | 4860 | 5000 | 5090 | 5100 | 5065 | 5170 | 5170
66kV or 33kV | 2658 | 2676 | 2719 | 2736 | 2817 | 2866 | 2877 | 2835 | 2827 | 2827
11kV and 6.6kV | 3699 | 3819 | 3898 | 3938 | 3994 | 4057 | 4105 | 4362 | 4390 | 4390
TOTAL | 11057 | 11235 | 11437 | 11534 | 11811 | 12013 | 12082 | 12262 | 12387 | 12387
HV O/H length (km) | 12654 | 12475 | 12147 | 12297 | 12282 | 12282 | 12316 | 12282 | 12316 | 12315
HV U/G length (km) | 4537 | 4184 | 4195 | 4289 | 4456 | 4456 | 4643 | 4827 | 4887 | 4986
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 20.3914 | 3.7292 | 2.9384 | 3.5682 | 6.0562 | 9.139 | 1.893 | 4.8786 | 3.0347 | 2.6039 | 5.8233 |  | 20.3914 | 1.893
HV faults: U/G damage | 97.3341 | 132.3805 | 135.3918 | 138.9367 | 101.0087 | 102.2693 | 93.1798 | 74.8046 | 74.0463 | 71.908 | 102.126 |  | 138.9367 | 71.908
HV faults: O/H no damage | 7.3112 | 8.0304 | 10.0697 | 13.6898 | 12.3202 | 11.2891 | 14.6696 | 16.617 | 18.6244 | 24.3289 | 13.695 |  | 24.3289 | 7.3112 |  |  |  | 0 | 0
HV faults: O/H damage | 21.27 | 19.5474 | 27.5552 | 21.3904 | 29.8196 | 22.1045 | 21.0925 | 18.6941 | 16.9386 | 23.0313 | 22.1444 |  | 29.8196 | 16.9386 |  |  |  | 1 | 1
Security - HV underground networks | 117.7256 | 136.1097 | 138.3302 | 142.5049 | 107.0649 | 111.4083 | 95.0728 | 79.6831 | 77.081 | 74.5119 | 107.9492 |  | 142.5049 | 74.5119
Security - HV overhead networks | 28.5812 | 27.5778 | 37.6249 | 35.0802 | 42.1398 | 33.3936 | 35.7621 | 35.3111 | 35.563 | 47.3602 | 35.8394 |  | 47.3602 | 27.5778
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 142.4089 | 245.7929 | 180.8238 | 200.7111 | 281.1804 | 826.8582 | 105.1691 | 325.2372 | 263.0059 | 240.361 | 281.1549 |  | 826.8582 | 105.1691
HV faults: U/G damage | 9053.1361 | 11641.6479 | 11821.3584 | 12934.7167 | 10057.6077 | 9813.5009 | 8665.9315 | 6829.9814 | 6736.9982 | 5888.8448 | 9344.3724 |  | 12934.7167 | 5888.8448
HV faults: O/H no damage | 503.3025 | 689.4705 | 835.2422 | 1291.2011 | 1396.8116 | 978.9155 | 1125.9922 | 1382.0844 | 1300.4985 | 1840.8843 | 1134.4403 |  | 1840.8843 | 503.3025 |  |  |  | 0 | 0
HV faults: O/H damage | 2392.5104 | 2113.3769 | 3653.2087 | 3017.9881 | 5665.7189 | 2786.7513 | 2711.8967 | 2005.2206 | 1766.1091 | 2497.7637 | 2861.0545 |  | 5665.7189 | 1766.1091 |  |  |  | 1 | 1
Availability - HV underground networks | 9195.545 | 11887.4408 | 12002.1822 | 13135.4278 | 10338.7882 | 10640.3591 | 8771.1006 | 7155.2186 | 7000.0041 | 6129.2058 | 9625.5272 |  | 13135.4278 | 6129.2058
Availability - HV overhead networks | 2895.8129 | 2802.8474 | 4488.4509 | 4309.1892 | 7062.5305 | 3765.6668 | 3837.8889 | 3387.305 | 3066.6077 | 4338.648 | 3995.4947 |  | 7062.5305 | 2802.8474
16.697
15.2945
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 2104469.64 | 1825729.543 | 2024396.325 | 2101430.5 | 2152165.4 | 1858723.2 | 1813546.2 | 1473762.4 | 1509744.9 | 1579943.4
| 300329362.17 | 198512099.2 | 189164902.5 | 202778000 | 224276260 | 183545280 | 178620140 | 142470240 | 135254160 | 123139710

## K
South Western
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 2.1 | 2.6 | 1.6 | 1.3 | 1.4 | 1.1 | 1.1 | 1 | 1 | 0.7 | 1.39
LV faults | 7.1 | 5.3 | 5.5 | 5.3 | 5.3 | 4.8 | 4.4 | 4 | 3.7 | 4.1 | 4.95 | [8 empty] | 165212.6355
HV faults: U/G no damage | 1.3 | 1.2 | 1.3 | 0.6 | 1.4 | 1.3 | 1 | 1.1 | 2.3 | 2.8 | 1.43
HV faults: U/G damage | 25.5 | 26.4 | 22.2 | 24.5 | 22.9 | 22.7 | 18.1 | 16.9 | 15.5 | 17.8 | 21.25
HV faults: O/H no damage | 6.7 | 5.4 | 10.3 | 7.6 | 7.1 | 7 | 7.4 | 7.6 | 9.3 | 9 | 7.74
HV faults: O/H damage | 22.3 | 18.9 | 25.3 | 20 | 18.3 | 18.1 | 32.8 | 15.4 | 16.2 | 18.9 | 20.62 |  |  |  |  | 1613859.77
HV faults: All other | 19 | 22.6 | 20.1 | 19.7 | 22.9 | 16.2 | 14.7 | 12 | 13 | 16.7 | 17.69 |  |  |  |  | 1499123.626
HV faults: Total | 74.8 | 74.5 | 79.2 | 72.4 | 72.6 | 65.3 | 74 | 53 | 56.3 | 65.2 | 68.73 | -5.136% |  |  |  | 1525041.276 |  |  |  | 935585.0631
EHV faults | 15.8 | 17.3 | 16 | 12.2 | 16.1 | 18 | 17 | 13.1 | 23.8 | 11.7 | 16.1 | -27.33% |  |  |  | 1597071 |  |  |  | 219160.767
132kV faults | 1.3 | 0 | 0.6 | 14 | 8 | 0 | 1 | 2.7 | 0 | 0 | 2.76 | -100% |  |  |  | 1507114 |  |  |  | 37570.4172
Total of (a) | 101.1 | 99.7 | 102.9 | 105.2 | 103.4 | 89.2 | 97.5 | 73.8 | 84.9 | 81.7 | 93.94 | -13.03% |  |  |  | 1379940
(b) Planned Outages | 27.4 | 18.6 | 16.5 | 18.7 | 12.8 | 16.3 | 8 | 6.3 | 5.5 | 4.8 | 13.49 | -64.42% |  |  |  | 1395765 |  |  |  | 183632.2203
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1076544
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1214976 |  |  |  | 0
Total of (a+b+c+d) | 128.5 | 118.3 | 119.4 | 123.9 | 116.2 | 105.5 | 105.5 | 80.1 | 90.4 | 86.5 | 107.43 | -19.48% | 128.5 | 80.1 | 99.9 | 1177478.655 | 84.163 | 1 | 0 | 1462387.6521
[9 empty] | 84.9 | 81.7 | [5 empty] | 1112138.799
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV faults | 15.8 | 14.6 | 14.8 | 12.7 | 13.1 | 12.9 | 12.3 | 9.4 | 9.2 | 10.4 | 12.52 | [8 empty] | 41787115.08
HV faults: U/G no damage | 0.8 | 1.3 | 1.2 | 0.5 | 1 | 1 | 0.7 | 0.6 | 1.4 | 1.3 | 0.98
HV faults: U/G damage | 29 | 28.4 | 22.7 | 21.9 | 18.3 | 18.2 | 13.3 | 9.8 | 9.8 | 11.4 | 18.28
HV faults: O/H no damage | 4.9 | 5 | 12.1 | 6.8 | 6.7 | 6.7 | 4.2 | 3.5 | 4.7 | 4.2 | 5.88
HV faults: O/H damage | 27 | 26 | 38 | 24.5 | 19.8 | 19.6 | 49 | 12.8 | 14 | 20.7 | 25.14 |  |  |  |  | 221042272
HV faults: All other | 16.2 | 20.3 | 17.7 | 11.6 | 16.7 | 10.2 | 8.4 | 6 | 7.3 | * | 11.44 |  |  |  |  | 232661959.2
HV faults: Total | 77.9 | 81 | 91.7 | 65.3 | 62.5 | 55.7 | 75.6 | 32.7 | 37.2 | 47.6 | 62.72 | -24.11% |  |  |  | 213429143.4 |  |  |  | 210138656
EHV faults | 6.8 | 24.4 | 6.7 | 3.8 | 8.3 | 6.9 | 4.7 | 3.3 | 6 | 1.8 | 7.27 | -75.24% |  |  |  | 171565900 |  |  |  | 24357589.75
132kV faults | 0.3 | 0 | 0.1 | 12.2 | 1 | 0 | 0.5 | 0.2 | 0 | 0 | 1.43 | -100% |  |  |  | 143707600 |  |  |  | 4791107.75
Total of (a) | 100.8 | 120 | 113.3 | 94 | 84.9 | 75.5 | 93.1 | 45.6 | 52.4 | 59.8 | 83.94 | -28.76% |  |  |  | 134854800
(b) Planned Outages | 75.2 | 63.6 | 53.8 | 39.1 | 25.9 | 27.6 | 15.3 | 12.1 | 12 | 10.2 | 33.48 | -69.53% |  |  |  | 143413200 |  |  |  | 112172229
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 77548800
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 86553600 |  |  |  | 0
Total of (a+b+c+d) | 176 | 183.6 | 167.1 | 133.1 | 110.8 | 103.1 | 108.4 | 57.7 | 64.4 | 70 | 117.42 | -40.38% | 183.6 | 57.7 | 93.1 | 95287290 | 85.7596 | 1 | 0 | 393406903.5
[9 empty] | 52.4 | 59.8 | [5 empty] | 70425600
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 70.85% | 66.71% | 63.85% | 66.26% | 64.45% | 60.32% | 59.04% | 67.3% | 66.61% | 74.2% | 65.96% | 12.49%
18 hours | 99.76% | 99.95% | 99.85% | 99.91% | 99.98% | 99.97% | 99.97% | 99.98% | 99.83% | 99.7% | 99.89% | -0.1902%
HV Faults:U/G no damage 3 hours | 95.04% | 89.74% | 97.79% | 89.51% | 93.94% | 93.94% | 92.47% | 95.66% | 95.74% | 95.6% | 93.94% | 1.764%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 89.33% | 91.89% | 90.98% | 92.56% | 93.27% | 93.27% | 94.13% | 95.64% | 95.38% | 95.1% | 93.16% | 2.088%
18 hours | 99.86% | 99.99% | 100% | 99.99% | 99.99% | 99.99% | 100% | 100% | 99.96% | 99.9% | 99.97% | -0.06802%
HV Faults: O/H no damage 3 hours | 96.41% | 91.56% | 85.8% | 92.97% | 87.6% | 87.6% | 96.49% | 97.21% | 95.41% | 97.3% | 92.84% | 4.81%
18 hours | 99.98% | 100% | 100% | 100% | 99.98% | 99.98% | 100% | 100% | 100% | 100% | 99.99% | 0.006%
HV Faults: O/H damage 3 hours | 80.09% | 77.46% | 75.29% | 82.24% | 84.73% | 84.73% | 77.98% | 89.76% | 88.16% | 83.9% | 82.43% | 1.778%
18 hours | 100% | 99.95% | 100% | 99.99% | 100% | 100% | 99.02% | 100% | 100% | 99.9% | 99.89% | 0.01402%
HV Faults: Other 3 hours
24 hours
HV Faults: Total 3 hours | 87.29% | 87.53% | 84.49% | 89.98% | 89.61% | 91.74% | 87.29% | 93.99% | 93.2% | 91.9% | 89.7% | 2.45%
18 hours | 99.95% | 99.98% | 100% | 99.99% | 99.99% | 99.98% | 99.57% | 100% | 99.98% | 99.9% | 99.93% | -0.03402%
EHV Faults: 3 hours | 99.73% | 75.6% | 97.39% | 100% | 97.55% | 99.17% | 100% | 99.89% | 99.75% | 100% | 96.91% | 3.191%
18 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.91% | 100% | 99.99% | 0.009001%
132kV F'lts: 3 hours | 100% | * | 100% | 78.5% | 100% | 100% | 100% | 100% | * | * | 67.85% | #VALUE!
18 hours | 100% | * | 100% | 100% | 100% | 100% | 100% | 100% | * | * | 70% | #VALUE!
Total Faults:3 hours | 87.9% | 83.81% | 85.16% | 88.11% | 90.01% | 91.45% | 88.03% | 93.44% | 93.7% | 91.3% | 89.29% | 2.25% | 93.7% | 83.81% |  | 1109273.088
18 hours | 99.94% | 99.98% | 99.99% | 99.99% | 99.99% | 99.98% | 99.67% | 100% | 99.96% | 99.9% | 99.94% | -0.04002% | 100% | 99.67% |  | 1111026.6602
TOTAL not rest in 3 hrs | 12.1% | 16.19% | 14.84% | 11.89% | 9.99% | 8.55% | 11.97% | 6.56% | 6.3% | 8.7% | 10.71% | -18.76% | 16.19% | 6.3% |  |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.06% | 0.02% | 0.01% | 0.01% | 0.01% | 0.02% | 0.33% | 0% | 0.04% | 0.1% | 0.06% | 66.67% | 0.33% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
TOTAL |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
Total |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0%
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 3.2 | 3.6 | 3.2 | 3.8 | 2 | 1.5 | 1 | 0.7 | 0.8 | 2 | 2.18 | 10 | 3.8 | 0.7 |  |  |  | 1 | 0
NOTES - * Information not available/applicable | [9 empty] | .
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 19.2 | 17.6 | 19.7 | 17.5 | 18.6 | 18.8 | 15.9 | 15.9 | 15.6 | 15.8 | 17.6444 | -4.361% | 19.7 | 15.6 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1255922 | 1267222 | 1277254 | 1289000 | 1297000 | 1308000 | 1323000 | 1344000 | 1344000 | 1361247
Embedded Gen.Stations | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Emb.Gen.Capacity MWSO | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | %age overhead all voltages | 61.02% | 60.62%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  | 1461 | 1461 | 1461 | 1461 | 1464 | 1464 | 1464 | 1464 | 1802
66kV
33kV |  | 2785 | 2784 | 2795 | 2796 | 2800 | 2812 | 2817 | 2835 | 2842
25kV
22kV
11kV |  | 17040 | 17060 | 17107 | 17189 | 17271 | 19031 | 17111 | 17120 | 17430
6.6kV |  | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 24 | 0
3.3kV
3kV
2.2kV
LV |  | 7708 | 7699 | 7682 | 7664 | 7646 | 8911 | 7888 | 7834 | 7793
TOTAL |  |  | 29018 | 29028 | 29069 | 29134 | 32242 | 29304 | 29277 | 29867
Underground cable
132kV |  | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 105.8
66kV
33kV |  | 969 | 971 | 977 | 978 | 981 | 982 | 929 | 929 | 1030.4
25kV
22kV
11kV |  | 5939 | 6021 | 6114 | 6181 | 6248 | 6350 | 6408 | 6218 | 6444
6.6kV |  | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 124 | 0
3.3kV
3kV
LV |  | 10799 | 10896 | 11006 | 11103 | 11200 | 11309 | 11185 | 11369 | 11826
TOTAL |  |  |  | 17890 | 18071 | 18280 | 18445 | 18705 | 18699 | 19406.2
[9 empty] | 47976 | 49273.2
Transformers in commission
Primary voltage
| ground mounted | agg. capacity (MVA) | [7 empty] | pole
132kV | 89 | 5595 | [7 empty] | 0
66kV or 33kV | 538 | 7685 | [7 empty] | 0
11kV and 6.6kV | 11646 | 6946
TOTAL | 12273 | 20226 | [7 empty] | 0
12273
HV O/H length (km) | 16797.3333 | 16841.7778 | 16886.2222 | 16930.6667 | 16975.1111 | 17019.5556 | 17064 | 17135 | 17144 | 17430
HV U/G length (km) | 5697 | 5758 | 5819 | 5880 | 5941 | 6002 | 6063 | 6532 | 6342 | 6444
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 2.8659 | 2.641 | 2.8535 | 1.3153 | 3.0564 | 2.8331 | 2.1821 | 2.2633 | 4.8742 | 5.9148 | 3.0799 |  | 5.9148 | 1.3153
HV faults: U/G damage | 56.2156 | 58.1012 | 48.7284 | 53.7083 | 49.9938 | 49.4695 | 39.4958 | 34.7728 | 32.8477 | 37.6012 | 46.0934 |  | 58.1012 | 32.8477
HV faults: O/H no damage | 5.0095 | 4.0631 | 7.7908 | 5.7862 | 5.4248 | 5.3797 | 5.7373 | 5.9611 | 7.2907 | 7.0288 | 5.9472 |  | 7.7908 | 4.0631
HV faults: O/H damage | 16.6735 | 14.2209 | 19.1366 | 15.2268 | 13.9823 | 13.9104 | 25.4304 | 12.0791 | 12.7 | 14.7605 | 15.812 |  | 25.4304 | 12.0791
HV underground networks | 59.0815 | 60.7421 | 51.5818 | 55.0236 | 53.0502 | 52.3026 | 41.6779 | 37.0361 | 37.7219 | 43.516 | 49.1734 |  | 60.7421 | 37.0361 |  |  |  | 1 | 0
HV overhead networks | 21.683 | 18.284 | 26.9274 | 21.013 | 19.4071 | 19.29 | 31.1677 | 18.0403 | 19.9907 | 21.7893 | 21.7593 |  | 31.1677 | 18.0403 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 176.3626 | 286.1043 | 263.3966 | 109.6088 | 218.3134 | 217.9274 | 152.7462 | 123.4538 | 296.6887 | 274.6153 | 211.9217 |  | 296.6887 | 109.6088
HV faults: U/G damage | 6393.1434 | 6250.2787 | 4982.5856 | 4800.8673 | 3995.1355 | 3966.2779 | 2902.1771 | 2016.4115 | 2076.8212 | 2408.1651 | 3979.1863 |  | 6393.1434 | 2016.4115
HV faults: O/H no damage | 366.3687 | 376.2138 | 915.2298 | 517.7115 | 511.9201 | 514.9136 | 325.6329 | 274.5258 | 368.4554 | 328.0113 | 449.8983 |  | 915.2298 | 274.5258
HV faults: O/H damage | 2018.7665 | 1956.312 | 2874.2753 | 1865.2839 | 1512.8384 | 1506.3143 | 3799.0506 | 1003.9802 | 1097.5268 | 1616.6272 | 1925.0975 |  | 3799.0506 | 1003.9802
HV underground networks | 6569.506 | 6536.383 | 5245.9822 | 4910.4762 | 4213.4489 | 4184.2053 | 3054.9233 | 2139.8653 | 2373.5099 | 2682.7804 | 4191.1081 |  | 6569.506 | 2139.8653 |  |  |  | 1 | 0
HV overhead networks | 2385.1352 | 2332.5258 | 3789.5051 | 2382.9954 | 2024.7585 | 2021.2279 | 4124.6835 | 1278.506 | 1465.9823 | 1944.6386 | 2374.9958 |  | 4124.6835 | 1278.506 |  |  |  | 1 | 0
7484.256
7012.7479
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1613859.77 | 1499123.626 | 1525041.276 | 1597071 | 1507114 | 1379940 | 1395765 | 1076544 | 1214976 | 1177478.655
| 221042272 | 232661959.2 | 213429143.4 | 171565900 | 143707600 | 134854800 | 143413200 | 77548800 | 86553600 | 95287290
* figure not given in report

## L
Yorkshire
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 3.7628 | 3.82 | 3.37 | 3.73 | 2.41 | 2.36 | 2.52 | 2.3 | 1.69 | 1.63 | 2.7593
LV faults | 7.0294 | 6.55 | 7.05 | 6.5 | 5.06 | 4.79 | 4.91 | 4.12 | 6.04 | 4.55 | 5.6599 | [8 empty] | 188907.955
HV faults: U/G no damage | 2.14 | 1.9 | 0.74 | 2.19 | 2.79 | 2.27 | 3.8 | 2.34 | 5.79 | 8.21 | 3.217
HV faults: U/G damage | 21.9 | 23.08 | 25.17 | 28.69 | 26.83 | 27.83 | 23.15 | 24.01 | 23.81 | 19.1 | 24.357
HV faults: O/H no damage | 4.35 | 5.08 | 2.92 | 7.39 | 3.34 | 6.82 | 5.12 | 3.96 | 3.53 | 4.61 | 4.712
HV faults: O/H damage | 5.87 | 5.58 | 7.96 | 7.28 | 7.38 | 7.09 | 6.57 | 4.57 | 5.37 | 4.85 | 6.252 |  |  |  |  | 1374546
HV faults: All other | 7.9511 | 10.01 | 11.62 | 13.14 | 14.58 | 15.52 | 14.73 | 20.38 | 14.29 | 13.39 | 13.5611 |  |  |  |  | 1439094.6864
HV faults: Total | 42.2111 | 45.65 | 48.41 | 58.69 | 54.92 | 59.53 | 53.37 | 55.26 | 52.78 | 50.16 | 52.0981 | -3.72% |  |  |  | 1432705.4875 |  |  |  | 1076840.3143
EHV faults | 6.2417 | 8.65 | 7.14 | 6.45 | 7.92 | 6.63 | 13.7 | 3.6 | 6.13 | 10.6 | 7.7062 | 37.55% |  |  |  | 1718358.3432 |  |  |  | 159282.4575
132kV faults | 2.4395 | 0.91 | 0 | 2.14 | 11.53 | 13.17 | 2 | 3.75 | 5.75 | 1.09 | 4.278 | -74.52% |  |  |  | 1771544.3985 |  |  |  | 88423.0551
Total of (a) | 61.6846 | 65.58 | 65.97 | 77.51 | 81.84 | 86.48 | 76.5 | 69.03 | 70.68 | 68.03 | 72.3305 | -5.946% |  |  |  | 1918431.2352
(b) Planned Outages | 7.3753 | 6.29 | 5.08 | 5.05 | 4.65 | 4.44 | 3.5 | 2.76 | 2.35 | 1.79 | 4.3285 | -58.65% |  |  |  | 1658397.6 |  |  |  | 89468.3422
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 1498918.4859
(d) Other Systems | 0 | 0 | 0 | 2.22 | 0 | 2.2 | 0 | 0 | 0 | 0 | 0.442 |  |  |  |  | 1457116.469 |  |  |  | 9135.9057
Total of (a+b+c+d) | 69.0598 | 71.82 | 71.05 | 84.78 | 86.49 | 93.12 | 80 | 71.79 | 73.03 | 69.82 | 77.096 | -9.438% | 93.12 | 69.0598 |  | 1443142.3954 | 84.163 | 1 | 0 | 1593533.0934
* inc service | [8 empty] | 70.68 | 68.03
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults | 3.7628 | 3.82 | 3.37 | [6 empty] | * | 2.7382
LV faults | 13.0389 | 13.14 | 13.42 | 13.52 | 11.37 | 10.71 | 11.01 | 9.81 | 9.54 | 10.44 | 11.5999 | [8 empty] | 38864568.962
HV faults: U/G no damage | 1.07 | 1.05 | 0.37 | 1.62 | 1.62 | 1.36 | 2.47 | 1.65 | 3.75 | 5.32 | 2.028
HV faults: U/G damage | 14.49 | 15.69 | 17.74 | 19.59 | 18.66 | 18.33 | 15.32 | 17.35 | 16.31 | 13.45 | 16.693
HV faults: O/H no damage | 1.8 | 2.13 | 1.6 | 4.68 | 1.64 | 2.61 | 3.16 | 2.57 | 3.27 | 3.54 | 2.7
HV faults: O/H damage | 4.49 | 4.99 | 6.9 | 7.43 | 6.13 | 4.58 | 5.45 | 3.91 | 5.32 | 5.72 | 5.492 |  |  |  |  | 118829340
HV faults: All other | 4.26 | 4.67 | 6.88 | 7.58 | 7.84 | 7.62 | 8.82 | 10.95 | 8.11 | 8.02 | 7.475 |  |  |  |  | 118822493.6
HV faults: Total | 26.1581 | 28.53 | 33.47 | 40.9 | 35.89 | 34.5 | 35.22 | 36.43 | 36.8 | 36.05 | 34.3948 | 4.812% |  |  |  | 122299208.75 |  |  |  | 115237228.3489
EHV faults | 0.88443 | 1.92 | 1.28 | 0.57 | 1.06 | 1.19 | 3.65 | 0.77 | 2.54 | 1.5 | 1.5364 | -2.372% |  |  |  | 139021229.96 |  |  |  | 5147736.5435
132kV faults | 0.14638 | 0.01 | 0 | 0.38 | 2.5 | 1.89 | 0.77 | 0.78 | 0.06 | 4.05 | 1.0586 | 282.6% |  |  |  | 127586426.85 |  |  |  | 3546888.8438
Total of (a) | 40.2278 | 43.57 | 48.17 | 55.38 | 50.83 | 48.29 | 50.65 | 47.79 | 48.93 | 52.04 | 48.5878 | 7.105% |  |  |  | 122992208.7
(b) Planned Outages | 19.4743 | 15.73 | 12.48 | 12.84 | 11.46 | 10.88 | 8.45 | 5.91 | 4.73 | 4.17 | 10.6124 | -60.71% |  |  |  | 122514122.7 |  |  |  | 35420357.0645
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 112121357.7
(d) Other Systems | 0 | 0 | 0 | 0.38 | 0 | 0.53 | 0 | 0 | 0 | 0 | 0.091 |  |  |  |  | 107064041.8 |  |  |  | 304888.675
Total of (a+b+c+d) | 59.7021 | 59.3 | 60.65 | 68.59 | 62.29 | 59.7 | 59.1 | 53.7 | 53.66 | 56.21 | 59.2902 | -5.195% | 68.59 | 53.66 |  | 116183090.87 | 85.7596 | 1 | 1 | 198647413.8283
[9 empty] | 48.93 | 52.04 | [5 empty] | 107563921.88
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 81.4% | 80.44% | 80.07% | 79.63% | 75.42% | 75.08% | 75.15% | 74.73% | 74.98% | 74.22% | 77.11% | -3.75%
24 hours | 99.92% | 99.86% | 99.94% | 100% | 100% | 100% | 100% | 100% | 100% | 99.73% | 99.95% | -0.2152%
HV Faults:U/G no damage 3 hours | 98.57% | 96.63% | 98.22% | 98.01% | 96.67% | 98.05% | 98.15% | 96.28% | 97.6% | 97.83% | 97.6% | 0.2346%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 97.59% | 95.9% | 96.23% | 96.94% | 96.65% | 96.94% | 96.64% | 96.17% | 97.17% | 96.21% | 96.64% | -0.4491%
24 hours | 99.94% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.99% | 0.01%
HV Faults: O/H no damage 3 hours | 96.64% | 96.99% | 96.11% | 90.56% | 95.62% | 97.08% | 94.13% | 93.55% | 86.93% | 90.81% | 93.84% | -3.231%
24 hours | 100% | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
HV Faults: O/H damage 3 hours | 92.49% | 90.25% | 88.77% | 85.09% | 90.76% | 94.78% | 91.49% | 90.29% | 86.43% | 78.11% | 88.85% | -12.08%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.82% | 99.98% | -0.162%
HV Faults: Other 3 hours
24 hours
HV Faults: Total 3 hours | 96.67% | 95.65% | 95.18% | 94.14% | 95.76% | 96.55% | 95.51% | 95.67% | 94.83% | 93.8% | 95.38% | -1.652%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 99.97% | 100% | -0.027%
EHV Faults: 3 hours | 100% | 96.86% | 100% | 100% | 100% | 95.11% | 97.55% | 100% | 92.66% | 100% | 98.22% | 1.814%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | -0.0009998%
132kV F'lts: 3 hours | 100% | 100% | 100% | 100% | 100% | 100% | 98.15% | 100% | 100% | 66.07% | 96.42% | -31.48%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 95.32% | 99.53% | -4.232%
Total Faults:3 hours | 94.47% | 93.24% | 93.31% | 92.87% | 94.91% | 95.35% | 93.96% | 94.26% | 93.37% | 92.54% | 93.83% | -1.373% | 95.35% | 92.54% |  | 1348415.5804
24 hours | 99.98% | 99.97% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 99.88% | 99.98% | -0.102% | 100% | 99.88% |  | #VALUE!
TOTAL not rest in 3 hrs | 5.53% | 6.76% | 6.69% | 7.13% | 5.09% | 4.65% | 6.04% | 5.74% | 6.63% | 7.46% | 6.172% | 20.87% | 7.46% | 4.65% |  |  |  | 0 | 0
TOTAL not rest in 24 hrs | 0.02% | 0.03% | 0.01% | 0% | 0% | 0% | 0% | 0% | 0% | 0.12% | 0.018% | 566.7% | 0.12% | 0% |  |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0%
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.095 | 0.898 | 1.562 | 1.219 | 0.947 | 0.67 | 0.844 | 0.91 | 0.687 | 0.561 | 0.9393 | 10 | 1.562 | 0.561 |  |  |  | 1 | 0
* Overall reliability for 1991/2 affected by change in measured length of system
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 14.788 | 14.9 | 15.48 | 17.04 | 15.07 | 14.93 | 14.27 | 12.71 | 12.17 | 12.86 | 14.4218 | 4.068% | 17.04 | 12.17 |  |  |  | 1 | 1
5 RELEVANT DATA:
Number of Customers | 1990370 | 2003752 | 2016475 | 2026844 | 2048265 | 2060171 | 2072997 | 2087921 | 1995230 | 2066947
Embedded Gen.Stations | 1 | 0 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1
Emb.Gen.Capacity MWSO | 234 | 0 | 240 | 240 | 240 | 240 | 240 | 240 | 240 | 240
[8 empty] | %age overhead all voltages | 28.47% | 28.26%
Mains in commission (circuit kilometres)
Overhead Line
132kV |  |  | 0 | 1235 | 1235 | 1235 | 1235 | 1235 | 1222 | 1222
66kV |  |  | 946 | 986 | 958 | 948 | 944 | 940 | 942 | 941
33kV |  |  | 1290 | 1325 | 1292 | 1316 | 1316 | 1291 | 1298 | 1296
25kV |  |  | 0
22kV |  |  | 0
11kV |  |  | 9684 | 9724 | 9852 | 9836 | 9841 | 9851 | 9818 | 9810
6.6kV |  |  | 0
3.3kV |  |  | 0
3kV |  |  | 0
2.2kV |  |  | 0
LV |  |  | 2678 | 2540 | 2574 | 2560 | 2554 | 2575 | 2537 | 2529
TOTAL |  |  |  |  | 15810 | 15911 | 15890 | 15892 | 15817 | 15798
Underground cable
132kV |  |  | 174 | 174 | 174 | 179 | 179 | 174 | 179 | 192
66kV |  |  | 42 | 42 | 42 | 38 | 35 | 43 | 37 | 52
33kV |  |  | 1217 | 1218 | 1241 | 1180 | 1205 | 1241 | 1258 | 1326
25kV |  |  | 0
22kV |  |  | 0
11kV |  |  | 10163 | 10181 | 10316 | 10202 | 10316 | 10444 | 10583 | 10699
6.6kV |  |  | 18 | 18 | 18 | 18 | 18 | 18 | 8 | 8
3.3kV |  |  | 0
3kV |  |  | 0
LV |  |  | 26089 | 26112 | 26456 | 27132 | 27300 | 26456 | 27674 | 27827
TOTAL | [5 empty] | 37745 | 38247 | 38376 | 39739 | 40104
55556
Transformers in commission 1996/97
Primary voltage
Secondary >650 V | [6 empty] | 642 | 766 | 762 | 760
Secondary 650 V and under:
Pole Mounted | [6 empty] | 16616 | 16671 | 16665 | 16702
Ground Mounted | [6 empty] | 14190 | 14338 | 14328 | 14321
TOTAL | [6 empty] | 31448 | 31775 | 30993 | 31023
Aggregate transforming Capacity (MVA)
Secondary >650 V | [6 empty] | 20777 | 20595 | 20668 | 20632
Secondary 650 V and under: | [6 empty] | 9396 | 9455 | 9509 | 9513
TOTAL | [6 empty] | 30173 | 30050 | 30177 | 30145
HV O/H length (km) | 9395.3333 | 9394.4444 | 9393.5556 | 9392.6667 | 9391.7778 | 9390.8889 | 9390 | 9851 | 9818 | 9810
HV U/G length (km) | 9797.3333 | 9853.1111 | 9908.8889 | 9964.6667 | 10020.4444 | 10076.2222 | 10132 | 10462 | 10591 | 10707
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 4.3475 | 3.8639 | 1.5059 | 4.4545 | 5.703 | 4.6412 | 7.7748 | 4.67 | 10.9077 | 15.8491 | 6.3718 |  | 15.8491 | 1.5059
HV faults: U/G damage | 44.4908 | 46.936 | 51.2214 | 58.3563 | 54.8428 | 56.9008 | 47.3647 | 47.9172 | 44.8555 | 36.8718 | 48.9757 |  | 58.3563 | 36.8718
HV faults: O/H no damage | 9.2153 | 10.8352 | 6.2682 | 15.9469 | 7.2842 | 14.9617 | 11.3032 | 8.3932 | 7.1737 | 9.7132 | 10.1095 |  | 15.9469 | 6.2682
HV faults: O/H damage | 12.4354 | 11.9016 | 17.0874 | 15.7095 | 16.0951 | 15.554 | 14.5044 | 9.6861 | 10.913 | 10.2189 | 13.4105 |  | 17.0874 | 9.6861
HV underground networks | 48.8383 | 50.7999 | 52.7273 | 62.8109 | 60.5458 | 61.5421 | 55.1394 | 52.5872 | 55.7632 | 52.721 | 55.3475 |  | 62.8109 | 48.8383 |  |  |  | 0 | 0
HV overhead networks | 21.6507 | 22.7368 | 23.3556 | 31.6564 | 23.3794 | 30.5157 | 25.8076 | 18.0793 | 18.0867 | 19.932 | 23.52 |  | 31.6564 | 18.0793 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 217.3751 | 213.5305 | 75.2956 | 329.513 | 331.1419 | 278.0638 | 505.3595 | 329.2936 | 706.4595 | 1027.0064 | 401.3039 |  | 1027.0064 | 75.2956
HV faults: U/G damage | 2943.7052 | 3190.7555 | 3610.1188 | 3984.6666 | 3814.2644 | 3747.7274 | 3134.4566 | 3462.5721 | 3072.6278 | 2596.4731 | 3355.7368 |  | 3984.6666 | 2596.4731
HV faults: O/H no damage | 381.324 | 454.3102 | 343.4653 | 1009.8974 | 357.6697 | 572.5812 | 697.622 | 544.7119 | 664.5347 | 745.8708 | 577.1987 |  | 1009.8974 | 343.4653
HV faults: O/H damage | 951.1915 | 1064.3229 | 1481.1939 | 1603.3201 | 1336.8997 | 1004.7593 | 1203.1772 | 828.7251 | 1081.1391 | 1205.1923 | 1175.9921 |  | 1603.3201 | 828.7251
HV underground networks | 3161.0803 | 3404.286 | 3685.4144 | 4314.1796 | 4145.4064 | 4025.7912 | 3639.8161 | 3791.8657 | 3779.0873 | 3623.4795 | 3757.0407 |  | 4314.1796 | 3161.0803 |  |  |  | 0 | 0
HV overhead networks | 1332.5155 | 1518.6331 | 1824.6592 | 2613.2175 | 1694.5694 | 1577.3405 | 1900.7992 | 1373.437 | 1745.6738 | 1951.0631 | 1753.1908 |  | 2613.2175 | 1332.5155 |  |  |  | 1 | 0
customer minutes lost per circuit km
6761.1652
6312.8999
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1374546 | 1439094.6864 | 1432705.4875 | 1718358.3432 | 1771544.3985 | 1918431.2352 | 1658397.6 | 1498918.4859 | 1457116.469 | 1443142.3954
| 118829340 | 118822493.6 | 122299208.75 | 139021229.96 | 127586426.85 | 122992208.7 | 122514122.7 | 112121357.7 | 107064041.8 | 116183090.87

## M
Hydro-Electric
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 0.2768 | 0.255 | 0.23 | 0.9 | 1.2 | 0.5 | 1 | 1.4 | 1.5 | 1.81 | 0.90718
LV faults | 4.4 | 5.3 | 4.3 | 2 | 3 | 5 | 4 | 4 | 4 | 4.28 | 4.028 | [8 empty] | 134955.119
HV faults: U/G no damage | 0.9 | 0.68 | 0.39 | 0.6 | 0.5 | 0.5 | 0.5 | 0.8 | 0 | 0.2 | 0.507
HV faults: U/G damage | 13.93 | 17.18 | 16.24 | 17 | 16 | 13 | 15.5 | 16.4 | 19.7 | 22.3 | 16.725
HV faults: O/H no damage | 15.66 | 20.32 | 19.25 | 20 | 17 | 16 | 15.4 | 15.2 | 14.3 | 9.5 | 16.263
HV faults: O/H damage | 34.32 | 49.94 | 38.74 | 29 | 39 | 26 | 29.3 | 30.2 | 28.6 | 26.1 | 33.12 |  |  |  |  | 1214632.3323
HV faults: All other | 40.75 | 46.98 | 32.58 | 27.4 | 36.5 | 24.5 | 25.4 | 25.4 | 23.1 | 27 | 30.961 |  |  |  |  | 1395920.8644
HV faults: Total | 105.56 | 135.1 | 107.2 | 94 | 109 | 80 | 86.1 | 88 | 85.7 | 85.1 | 97.576 | -12.79% |  |  |  | 1067520 |  |  |  | 644001.6
EHV faults | 48.4 | 55.4 | 34.2 | 46 | 53 | 33 | 38 | 39 | 37 | 28.22 | 41.222 | -31.54% |  |  |  | 1119360 |  |  |  | 272065.2
132kV faults | [15 empty] | 1217160 |  |  |  | 0
Total of (a) | 158.6368 | 196.055 | 145.93 | 142.9 | 166.2 | 118.5 | 129.1 | 132.4 | 128.2 | 118.7 | 143.6622 | -17.38% |  |  |  | 944000
(b) Planned Outages | 26.7 | 24.4 | 26.8 | 27 | 27 | 29 | 24 | 22 | 13 | 9.35 | 22.925 | -59.21% |  |  |  | 979840 |  |  |  | 151305
(c) Embedded Gen. | 18.8 | 14.15 | 5.19 | 5 | 0 | 0 | 0 | 0 | 0 | 3.56 | 4.67 |  |  |  |  | 988160
(d) Other Systems | * | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 903680 |  |  |  | 30822
Total of (a+b+c+d) | 204.1368 | 234.605 | 177.92 | 174.9 | 193.2 | 147.5 | 153.1 | 154.4 | 141.2 | 131.61 | 171.2572 | -23.15% | 234.605 | 131.61 |  | 868626 | 84.163 | 1 | 1 | 1130297.388
[9 empty] | 128.2 | [6 empty] | 0
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  | 1.89 | 1.65 | 1 | 1 | 1 | 1.3 | 2 | 1.7 | 2.1 | 1.5156
LV faults | 7.6 | 10 | 7.9 | 5 | 8 | 8 | 7 | 8 | 5 | 6.26 | 7.276 | [8 empty] | 24284588.604
HV faults: U/G no damage | 0.63 | 0.34 | 0.23 | 0.6 | 0.3 | 0.5 | 0.6 | 0.6 | 0 | 0.2 | 0.4
HV faults: U/G damage | 15.26 | 18.52 | 18.68 | 21 | 22 | 17.1 | 16.8 | 20.2 | 12.3 | 15.1 | 17.696
HV faults: O/H no damage | 16.87 | 18.46 | 17.53 | 16 | 18 | 11.3 | 11.7 | 14.5 | 12.5 | 8.2 | 14.506
HV faults: O/H damage | 75.69 | 124.6 | 71.9 | 49 | 142 | 40.9 | 63 | 52.5 | 32.1 | 31.1 | 68.279 |  |  |  |  | 160807132.34
HV faults: All other | 31.76 | 49.58 | 25.76 | 25.4 | 34.7 | 18.9 | 22.1 | 24.2 | 14.7 | 16.1 | 26.32 |  |  |  |  | 211716102.38
HV faults: Total | 140.21 | 211.5 | 134.1 | 112 | 217 | 88.7 | 114.2 | 112 | 71.6 | 70.8 | 127.211 | -44.34% |  |  |  | 152472000 |  |  |  | 426210914.675
EHV faults | 49.4 | 60 | 36.6 | 42 | 66 | 26 | 30 | 43 | 21 | 15.67 | 38.967 | -59.79% |  |  |  | 149120000 |  |  |  | 130556010.975
132kV faults | [15 empty] | 229950000 |  |  |  | 0
Total of (a) | 197.21 | 283.39 | 180.25 | 160 | 293 | 123.7 | 152.5 | 165 | 99.3 | 94.59 | 174.894 | -45.92% |  |  |  | 131648000
(b) Planned Outages | 70 | 68.4 | 73.2 | 72 | 72 | 82 | 67 | 55 | 24 | 16.34 | 59.994 | -72.76% |  |  |  | 140480000 |  |  |  | 201005397.45
(c) Embedded Gen. | 3.05 | 4.03 | 0.67 | 1 | 0 | 0 | 0 | 0 | 0 | 0.53 | 0.928 |  |  |  |  | 140800000
(d) Other Systems | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  |  |  | 78912000 |  |  |  | 3109194.4
Total of (a+b+c+d) | 270.26 | 355.82 | 254.12 | 233 | 365 | 205.7 | 219.5 | 220 | 123.3 | 111.46 | 235.816 | -52.73% | 365 | 111.46 |  | 73563600 | 85.7596 | 1 | 1 | 790083821.8
[9 empty] | 99.3 | [6 empty] | 0
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 77.34% | 71.68% | 70.3% | 72% | 66% | 74.05% | 74.72% | 74% | 81% | 77.19% | 73.83% | 4.554%
24 hours | 99.25% | 98.27% | 99.73% | 100% | 99% | 99.93% | 99.48% | 99.71% | 100% | 99.99% | 99.54% | 0.4561%
HV Faults:U/G no damage 3 hours | 90.96% | 97.47% | 100% | 92.45% | 85.34% | 86.57% | 91.7% | 100% | 100% | 100% | 94.45% | 5.877%
24 hours | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0%
HV Faults: U/G damage 3 hours | 90% | 91.11% | 89.25% | 84.72% | 84.37% | 84.84% | 90.4% | 61.1% | 95.6% | 93.62% | 86.5% | 8.23%
24 hours | 99.62% | 99.94% | 100% | 99.99% | 99.81% | 99.99% | 100% | 99.9% | 100% | 99.99% | 99.92% | 0.06605%
HV Faults: O/H no damage 3 hours | 86.39% | 90.31% | 88.04% | 89.88% | 84.36% | 91.44% | 91.2% | 95.1% | 82.2% | 88.78% | 88.77% | 0.01127%
24 hours | 99.98% | 99.87% | 100% | 100% | 99.74% | 100% | 100% | 99.7% | 100% | 100% | 99.93% | 0.07105%
HV Faults: O/H damage 3 hours | 69.94% | 60.8% | 69.68% | 67.07% | 53.99% | 70.7% | 67.5% | 86.8% | 81.9% | 79.48% | 70.79% | 12.28%
24 hours | 98.15% | 98.22% | 99.17% | 99.88% | 93.68% | 99.92% | 99.6% | 99% | 99.6% | 99.99% | 98.72% | 1.285%
HV Faults: Other 3 hours |  |  | 90.62% | [6 empty] | 94.99% | 92.81%
24 hours |  |  | 99.14% | [6 empty] | 100% | 99.57%
HV Faults: Total 3 hours | 83.25% | 78.17% | 82.83% | 80.46% | 73.58% | 83.13% | 82.45% | 82% | 89.8% | 89.2% | 82.49% | 8.138%
24 hours | 99.19% | 99.22% | 99.66% | 99.94% | 97.63% | 99.66% | 99.83% | 97.18% | 99.9% | 99.99% | 99.22% | 0.7761%
EHV Faults: 3 hours | 84.93% | 87.63% | 82.5% | 87% | 84% | 87.8% | 90.55% | 86% | 95% | 95.57% | 88.1% | 8.481%
24 hours | 99.58% | 99.59% | 99.98% | 100% | 100% | 99.97% | 99.83% | 96.71% | 100% | 100% | 99.57% | 0.4359%
132kV F'lts: 3 hours
18 hours
Total Faults:3 hours | 83.25% | 78.17% | 82.83% | 80.46% | 73.58% | 83.15% | 84.58% | 83% | 91% | 90.22% | 83.02% | 8.667% | 91% | 73.58% |  | 815300.096
24 hours | 99.19% | 99.22% | 99.66% | 99.94% | 97.63% | 99.66% | 99.82% | 97.15% | 100% | 99.99% | 99.23% | 0.77% | 100% | 97.15% |  | 903589.632
TOTAL not rest in 3 hrs | 16.75% | 21.83% | 17.17% | 19.54% | 26.42% | 16.85% | 15.42% | 17% | 9% | 9.78% | 16.98% | -42.39% | 26.42% | 9% |  |  |  | 1 | 1
TOTAL not rest in 24 hrs | 0.81% | 0.78% | 0.34% | 0.06% | 2.37% | 0.34% | 0.18% | 2.85% | 0% | 0.01% | 0.774% | -98.71% | 2.85% | 0% |  |  |  | 1 | 1
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
(a) At request of NGC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | * | *
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 1.9832 | 3.479 | 5.9 | 6.1 | 4 | 4 | 4.41 | 2.6 | 1.5 | 1.5 | 3.7747 | 10 | 6.1 | 1.5 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 12.4 | 15.49 | 12.49 | 11 | 13 | 15.14 | 15.86 | 16.07 | 15.5 | 16.22 | 14.317 | -2.28% | 16.22 | 11 |  |  |  | 0 | 0
5 RELEVANT DATA:
Total Connected Customers (millions) | 595009 | 595009 | 600000 | 640000 | 630000 | 640000 | 640000 | 640000 | 640000 | 660000
Embedded Gen.Stations | 153 | 152 | 159 | 172 | 164 | 164 | 164 | 164 | 167 | 175
Emb.Gen.Capacity MWSO | 391 | 369 | 420 | 422 | 365 | 365 | 365 | 365 | 406 | 416
[8 empty] | %age overhead all voltages | 68.28% | 68.19%
Mains in commission (circuit kilometres)
Overhead Line
33kV |  | 5242 | 5242 | 5119 | 4949 | 5131 | 5315 | 5422 | 5325 | 5325
22kV |  | 248 | 248 | 143 | 151.6 | 152 | 0 | 0 | 0 | 0
11kV |  | 20635 | 20635 | 23371 | 22264 | 21314 | 20793 | 20905 | 20823 | 20903
6.6kV |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
LV |  | 6683 | 6683 | 5648 | 5339 | 4363 | 4299 | 4035 | 4299 | 4259
TOTAL |  | 32808 | 32808 | 34281 | 32703.6 | 30960 | 30407 | 30362 | 30447 | 30487
L.V. Services | [5 empty] | 2030
Underground cable
33kV |  | 469 | 469 | 592 | 592 | 601 | 640 | 566 | 640 | 640
22kV |  | 0 | 0 | 15 | 15 | 15 | 0 | 0 | 0 | 0
11kV |  | 3979 | 3979 | 4433 | 4440 | 4570 | 4606 | 4435 | 4702 | 4736
6.6kV |  | 146 | 146 | 9.4 | 9.4 | 9 | 0 | 0 | 0 | 0
LV |  | 7329 | 7329 | 8057 | 8111 | 8514 | 8709 | 8750 | 8800 | 8847
TOTAL |  | 11923 | 11923 | 13106.4 | 13167.4 | 13709 | 13955 | 13751 | 14142 | 14223
[9 empty] | 44589 | 44710
Transformers
Transformers in commission
TYPES OF TRANSFORMER | [9 empty] | AGGREGATE TRANSFORMING
CAPACITY (MVA)
| ground mounted | aggregate capacity (MVA) | [7 empty] | pole mounted
33 kV / 11 or 6.6 kV | 491 | 4815 | [7 empty] | 40
22 kV / 11 or 6.6 kV | 0 | 0 | [7 empty] | 0
33 kV / LV | 6 | 65 | [7 empty] | 1535
22 kV / LV | 0 | 0 | [7 empty] | 0
11 kV / LV | 6440 | 5010 | [7 empty] | 39957
6.6 kV / LV | 0 | 0 | [7 empty] | 0
Total | 6937 | 9890 | [7 empty] | 41532
48469
HV O/H length (km) | 19964.2506 | 20635 | 20635 | 23371 | 22264 | 21314 | 20793 | 20905 | 20823 | 20903
HV U/G length (km) | 3990.9151 | 4125 | 4125 | 4442.4 | 4449.4 | 4579 | 4606 | 4435 | 4702 | 4736
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 1.3418 | 0.98086 | 0.56727 | 0.8644 | 0.70796 | 0.69884 | 0.69475 | 1.1545 | 0 | 0.27872 | 0.72891 |  | 1.3418 | 0
HV faults: U/G damage | 20.7684 | 24.7812 | 23.6218 | 24.4913 | 22.6547 | 18.1699 | 21.5371 | 23.6663 | 26.8141 | 31.0769 | 23.7582 |  | 31.0769 | 18.1699
HV faults: O/H no damage | 4.6673 | 5.8593 | 5.5973 | 5.4769 | 4.8105 | 4.8044 | 4.7401 | 4.6534 | 4.3951 | 2.9996 | 4.8004 |  | 5.8593 | 2.9996
HV faults: O/H damage | 10.2286 | 14.4002 | 11.2644 | 7.9415 | 11.0358 | 7.8071 | 9.0184 | 9.2456 | 8.7903 | 8.2409 | 9.7973 |  | 14.4002 | 7.8071
HV underground networks | 22.1102 | 25.7621 | 24.1891 | 25.3557 | 23.3627 | 18.8687 | 22.2319 | 24.8207 | 26.8141 | 31.3556 | 24.4871 |  | 31.3556 | 18.8687 |  |  |  | 0 | 0
HV overhead networks | 14.8959 | 20.2594 | 16.8616 | 13.4183 | 15.8462 | 12.6114 | 13.7585 | 13.8991 | 13.1854 | 11.2405 | 14.5976 |  | 20.2594 | 11.2405 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 90/91 | 10 Yr Avg
HV faults: U/G no damage | 93.9272 | 49.0432 | 33.4545 | 86.4398 | 42.4776 | 69.8843 | 83.3695 | 86.584 | 0 | 27.8716 | 57.3052 |  | 93.9272 | 0
HV faults: U/G damage | 2275.1266 | 2671.4101 | 2717.0909 | 3025.3917 | 3115.0267 | 2390.0415 | 2334.3465 | 2914.9944 | 1674.1812 | 2104.3074 | 2522.1917 |  | 3115.0267 | 1674.1812
HV faults: O/H no damage | 502.7888 | 532.293 | 509.7165 | 438.1498 | 509.3424 | 339.3075 | 360.1212 | 443.9129 | 384.1906 | 258.9102 | 427.8733 |  | 532.293 | 258.9102
HV faults: O/H damage | 2255.8438 | 3592.8336 | 2090.6227 | 1341.8339 | 4018.1459 | 1228.113 | 1939.1141 | 1607.271 | 986.6014 | 981.9643 | 2004.2344 |  | 4018.1459 | 981.9643
HV underground networks | 2369.0539 | 2720.4533 | 2750.5455 | 3111.8314 | 3157.5044 | 2459.9257 | 2417.716 | 3001.5784 | 1674.1812 | 2132.1791 | 2579.4969 |  | 3157.5044 | 1674.1812 |  |  |  | 1 | 1
HV overhead networks | 2758.6326 | 4125.1266 | 2600.3392 | 1779.9837 | 4527.4883 | 1567.4205 | 2299.2353 | 2051.1839 | 1370.7919 | 1240.8745 | 2432.1077 |  | 4527.4883 | 1240.8745 |  |  |  | 1 | 1
6911.295
6289.2784
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1214632.3323 | 1395920.8644 | 1067520 | 1119360 | 1217160 | 944000 | 979840 | 988160 | 903680 | 868626
| 160807132.34 | 211716102.38 | 152472000 | 149120000 | 229950000 | 131648000 | 140480000 | 140800000 | 78912000 | 73563600

## N
ScottishPower
Year: | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg | % Diff | Max | Min | "Exception"
1 SECURITY : Supply Interruptions per 100 Connected Customers
(a) Distribution
LV service faults | 1.8 | 1.7 | 1.49 | 1.67 | 1.38 | 1.34 | 2.17 | 2.12 | 2.14 | 2.01 | 1.782
LV faults | 7.44 | 7.1 | 6.97 | 5.84 | 5.69 | 5.38 | 7.86 | 6.81 | 6.28 | 6.62 | 6.599 | [8 empty] | 221094.5457
HV faults: U/G no damage | 2.65 | 1.42 | 1.15 | 2.48 | 0.33 | 0.25 | 0.87 | 0.55 | 1.04 | 0.69 | 1.143
HV faults: U/G damage | 17.22 | 14.73 | 14.8 | 14.35 | 16.11 | 17 | 21.78 | 22.37 | 21.87 | 22.74 | 18.297
HV faults: O/H no damage | 4.57 | 8.64 | 5.69 | 4.19 | 5.49 | 4.83 | 7.64 | 8.5 | 5.89 | 7.65 | 6.309
HV faults: O/H damage | 5.87 | 10.31 | 8.14 | 6.39 | 8.1 | 7.84 | 8.1 | 15.26 | 9.66 | 11.15 | 9.082 |  |  |  |  | 1228116.6881
HV faults: All other | 9.31 | 10.67 | 8.34 | 7.61 | 12.45 | 10.36 | 11.98 | 13.27 | 13.89 | 13.04 | 11.092 |  |  |  |  | 1454977.956
HV faults: Total | 39.56 | 45.8 | 38.12 | 35.02 | 42.48 | 40.28 | 50.37 | 59.95 | 52.35 | 55.27 | 45.92 | 20.36% |  |  |  | 1023636.374 |  |  |  | 877072
EHV faults | 14.3 | 10.6 | 6.23 | 9.51 | 8.79 | 5.88 | 10.2 | 9.08 | 9.46 | 16.2 | 10.025 | 61.6% |  |  |  | 1081116 |  |  |  | 191477.5
132kV faults | [15 empty] | 1178280 |  |  |  | 0
Total of (a) | 61.3 | 63.5 | 51.32 | 50.37 | 56.96 | 51.54 | 68.43 | 75.84 | 68.09 | 78.09 | 62.544 | 24.86% |  |  |  | 1026180
(b) Planned Outages | 6.32 | 5.6 | 4.77 | 4.48 | 3.76 | 2.36 | 2.04 | 1.8 | 1.88 | 1.75 | 3.476 | -49.65% |  |  |  | 1356870 |  |  |  | 66391.6
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 1.04 | 0 | 0 | 0 | 0.104 | -100% |  |  |  | 1603525
(d) Other Systems | 3.35 | 14 | 2.09 | 6.23 | 4.74 | 3.11 | 1.44 | 8.11 | 12.27 | 11.68 | 6.702 | 74.28% |  |  |  | 1546112 |  |  |  | 129994.6
Total of (a+b+c+d) | 70.97 | 83.1 | 58.18 | 61.08 | 65.46 | 57.01 | 72.95 | 85.75 | 82.24 | 91.52 | 72.826 | 25.67% | 91.52 | 57.01 | 51.03 | 1748032 | 84.163 | 0 | 0 | 1390976.6
[9 empty] | 80.36 | 89.77 | [5 empty] | 1714607
2 AVAILABILITY: Minutes Lost per Connected Customer
(a) Distribution
LV service faults |  |  |  | 1.89 |  |  |  |  | 2.9 | 3.06 | 2.6167
LV faults | 11.77 | 11.8 | 11.33 | 9.37 | 9.5 | 9.66 | 9.69 | 11.35 | 8.61 | 11.06 | 10.414 | [8 empty] | 34758068.406
HV faults: U/G no damage | 2.31 | 1.45 | 1.34 | 2.31 | 0.39 | 0.37 | 0.87 | 0.61 | 0.67 | 0.54 | 1.086
HV faults: U/G damage | 16.81 | 15.3 | 15.92 | 15.96 | 17.92 | 21.06 | 23.17 | 23.74 | 23.24 | 23.1 | 19.622
HV faults: O/H no damage | 4.12 | 11.78 | 5.49 | 4.14 | 6.67 | 6.22 | 6.74 | 21.81 | 5.71 | 9.32 | 8.2
HV faults: O/H damage | 8.25 | 22.36 | 13.53 | 8.65 | 13.07 | 26.21 | 11.44 | 74.88 | 12.95 | 60.18 | 25.152 |  |  |  |  | 130789149.34
HV faults: All other | 7.56 | 10.71 | 6.97 | 6.88 | 13.88 | 10.45 | 11.1 | 16.79 | 11.62 | 13.36 | 10.932 |  |  |  |  | 170710410
HV faults: Total | 39.05 | 61.6 | 43.25 | 37.94 | 51.93 | 64.31 | 53.32 | 137.83 | 54.19 | 106.5 | 64.992 | 63.87% |  |  |  | 135388138.5 |  |  |  | 217750821.6
EHV faults | 7.06 | 7.6 | 4.46 | 8.72 | 8.5 | 7.81 | 6.77 | 16.34 | 6.67 | 14.64 | 8.857 | 65.29% |  |  |  | 123758400 |  |  |  | 29674714.225
132kV faults | [15 empty] | 145854000 |  |  |  | 0
Total of (a) | 57.88 | 81 | 59.04 | 56.03 | 69.93 | 81.78 | 69.78 | 165.52 | 69.47 | 132.2 | 84.263 | 56.89% |  |  |  | 159426000
(b) Planned Outages | 16.76 | 14 | 12.82 | 11.63 | 9.9 | 6.07 | 4.94 | 4.69 | 4.22 | 4.42 | 8.945 | -50.59% |  |  |  | 143889600 |  |  |  | 29969551.625
(c) Embedded Gen. | 0 | 0 | 0 | 0 | 0 | 0 | 2.4 | 0 | 0 | 0 | 0.24 |  |  |  |  | 331569700
(d) Other Systems | 0.94 | 2.5 | 5.09 | 2.26 | 1.2 | 0.72 | 0.24 | 7.1 | 2.89 | 15.26 | 3.82 |  |  |  |  | 143970400 |  |  |  | 13602725.5
Total of (a+b+c+d) | 75.58 | 97.5 | 76.95 | 69.92 | 81.03 | 88.57 | 77.36 | 177.31 | 76.58 | 151.88 | 97.268 | 56.15% | 177.31 | 69.92 | 61.9 | 290090800 | 85.7596 | 0 | 0 | 325889138.9
[9 empty] | 72.36 | 147.46 | [5 empty] | 281648600
3(i) QUALITY OF SERVICE: Percentage of Interruptions Restored within time specified
LV Faults: 3 hours | 72.22% | 71.8% | 71.84% | 73.28% | 70.6% | 67.5% | 80.5% | 82.1% | 79.1% | 76.9% | 74.58% | 3.105%
18 hours | 99.6% | 99.4% | 99.79% | 99.84% | 99.6% | 99.2% | 99.9% | 98.4% | 100% | 98.7% | 99.44% | -0.7472%
HV Faults:U/G no damage 3 hours | 93.7% | 90.6% | 80.98% | 89.23% | 77.9% | 53% | 89.3% | 80.2% | 93% | 92.5% | 84.04% | 10.07%
18 hours | 100% | 100% | 99.99% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.001%
HV Faults: U/G damage 3 hours | 92.5% | 91.3% | 90.68% | 88.17% | 87.9% | 85.8% | 88.9% | 89.5% | 89.7% | 91.3% | 89.58% | 1.926%
18 hours | 100% | 100% | 99.98% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 0.002%
HV Faults: O/H no damage 3 hours | 91.7% | 80.2% | 91.89% | 88.51% | 85.2% | 84.7% | 90% | 71% | 88.4% | 87% | 85.86% | 1.328%
18 hours | 100% | 100% | 100% | 100% | 99.4% | 99.8% | 100% | 97.6% | 100% | 99.3% | 99.61% | -0.3112%
HV Faults: O/H damage 3 hours | 76.3% | 61.9% | 70.45% | 77.06% | 73.1% | 64.5% | 76.2% | 59.7% | 72.5% | 62.3% | 69.4% | -10.23%
18 hours | 100% | 99.9% | 99.99% | 100% | 99.3% | 95% | 100% | 91.2% | 100% | 88.9% | 97.43% | -8.754%
HV Faults: Other 3 hours
24 hours
HV Faults: Total 3 hours | 90.22% | 81.8% | 86.37% | 87.06% | 84.3% | 82.3% | 87.3% | 78.7% | 86% | 84.3% | 84.84% | -0.6306%
18 hours | 99.98% | 100% | 99.99% | 99.93% | 99.8% | 99% | 100% | 97.2% | 100% | 97.6% | 99.35% | -1.761%
EHV Faults: 3 hours | 97.01% | 91% | 95.14% | 90.3% | 92% | 81.5% | 97.6% | 74.3% | 96.4% | 94.1% | 90.94% | 3.481%
18 hours | 99.88% | 99.8% | 99.99% | 99.91% | 99.4% | 99.9% | 100% | 96.3% | 100% | 98.5% | 99.37% | -0.8735%
132kV F'lts: 3 hours
24 hours
Total Faults:3 hours | 89.66% | 82.3% | 85.46% | 86.15% | 85.6% | 80.6% | 88% | 78.4% | 86.8% | 85.7% | 84.87% | 0.9815% | 89.66% | 78.4% |  | 1325017.984
18 hours | 99.91% | 99.8% | 99.96% | 99.97% | 99.7% | 99.1% | 100% | 97.2% | 100% | 97.8% | 99.34% | -1.554% | 100% | 97.2% |  | 1676885.646
TOTAL not rest in 3 hrs | 10.34% | 17.7% | 14.54% | 13.85% | 14.4% | 19.4% | 12% | 21.6% | 13.2% | 14.3% | 15.13% | -5.505% | 21.6% | 10.34% | 16.2% |  |  | 1 | 0
TOTAL not rest in 24 hrs | 0.09% | 0.2% | 0.04% | 0.03% | 0.3% | 0.9% | 0% | 2.8% | 0% | 2.2% | 0.656% | 235.4% | 2.8% | 0% | 0.1% |  |  | 0 | 0
3(ii) Total Demand lost: MWhrs per 100 Connected Customers
At GCC
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
TOTAL | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
(b) due to plc action
- Voltage Reductions | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
- Load Disconnection | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
Totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | N / A | N / A
3(iii) Verified Voltage Complaints per 10,000 Connected Customers
| 2.26 | 2.3 | 3.24 | 2.38 | 1.91 | 2.89 | 2.42 | 2.2 | 1.45 | 0.99 | 2.204 | 10 | 3.24 | 0.99 |  |  |  | 1 | 1
4 OVERALL RELIABILITY: Number of Faults per 100km of Distribution System (Mains only)
| 17.16 | 19.4 | 17.81 | 15.33 | 17.5 | 15.7 | 14.93 | 17.06 | 14.38 | 15.55 | 16.482 |  | 19.4 | 14.38 | 14.71 |  |  | 1 | 1
RELEVANT DATA:
Number of Customers | 1730473 | 1750876 | 1759430 | 1770000 | 1800000 | 1800000 | 1860000 | 1870000 | 1880000 | 1910000
Embedded Gen.Stations | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 0
Emb.Gen.Capacity MWSO | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 59 | 0
[8 empty] | %age overhead all voltages | 37.74% | 37.42%
Mains in commission (circuit kilometres)
Overhead Line
EHV |  | 2905 | 2901 | 3000 | 3000 | 3015 | 3018 | 3012 | 3012 | 3012
HV |  | 14975 | 15149 | 15774 | 15827 | 16618 | 16654 | 16773 | 16864 | 16896
3.3kV
3kV
L.V. Main |  | 4525 | 4439 | 4646 | 4640 | 4633 | 4628 | 4607 | 4572 | 4548
TOTAL |  |  | 22405 | 22489 | 25144 | 25191 | 24300 | 24392 | 24448 | 24456
L.V. Services |  |  |  | 2030 | 2030
Underground cable
EHV |  | 1623 | 1637 | 1658 | 1662 | 1672 | 1697 | 1727 | 1737 | 1793
HV |  | 13888 | 14001 | 14250 | 14403 | 14532 | 14674 | 14794 | 14910 | 15114
3.3kV
3kV
L.V. Main |  | 21663 | 21998 | 22392 | 22637 | 22927 | 23273 | 23483 | 23690 | 23990
TOTAL |  |  |  | 37174 | 38702 | 38458 | 38860 | 40004 | 40337 | 40897
[7 empty] | 22042 | 22584 | 64785 | 65353
TYPES OF TRANSFORMER |  | GROUND MOUNTED |  | AGGREGATE TRANSFORMING | [5 empty] | POLE MOUNTED
CAPACITY (MVA)
33 kV / 11 or 6.6 kV |  | 752 |  | 12948 | [5 empty] | 0
11 or 6.6 kV / LV |  | 15986 |  | 10528 | [5 empty] | 23510
Total |  | 16738 |  | 23476 | [5 empty] | 23510
40248
HV O/H length (km) | 14833.6667 | 14857.2222 | 14880.7778 | 14904.3333 | 14927.8889 | 14951.4444 | 14975 | 16773 | 16864 | 16896
HV U/G length (km) | 13084 | 13218 | 13352 | 13486 | 13620 | 13754 | 13888 | 14794 | 14910 | 15114
SECURITY : customer supply interruptions per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 3.5049 | 1.881 | 1.5154 | 3.2549 | 0.43612 | 0.32718 | 1.1652 | 0.69521 | 1.3113 | 0.87197 | 1.4963 |  | 3.5049 | 0.32718
HV faults: U/G damage | 22.775 | 19.5116 | 19.5024 | 18.834 | 21.2907 | 22.2481 | 29.1696 | 28.2763 | 27.5759 | 28.7372 | 23.7921 |  | 29.1696 | 18.834
HV faults: O/H no damage | 5.3313 | 10.182 | 6.7276 | 4.9759 | 6.6198 | 5.8148 | 9.4894 | 9.4765 | 6.5662 | 8.6479 | 7.3831 |  | 10.182 | 4.9759
HV faults: O/H damage | 6.8479 | 12.15 | 9.6243 | 7.5886 | 9.767 | 9.4386 | 10.0608 | 17.0132 | 10.769 | 12.6045 | 10.5864 |  | 17.0132 | 6.8479
HV underground networks | 26.2798 | 21.3925 | 21.0178 | 22.0889 | 21.7269 | 22.5753 | 30.3348 | 28.9715 | 28.8872 | 29.6092 | 25.2884 |  | 30.3348 | 21.0178 |  |  |  | 0 | 0
HV overhead networks | 12.1791 | 22.332 | 16.3519 | 12.5645 | 16.3868 | 15.2534 | 19.5502 | 26.4897 | 17.3352 | 21.2524 | 17.9695 |  | 26.4897 | 12.1791 |  |  |  | 1 | 0
Availability : customer minutes lost per circuit km | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01 | 10 Yr Avg
HV faults: U/G no damage | 305.5176 | 192.0692 | 176.5755 | 303.1811 | 51.5419 | 48.4223 | 116.5179 | 77.1056 | 84.4802 | 68.2414 | 142.3653 |  | 305.5176 | 48.4223
HV faults: U/G damage | 2223.269 | 2026.6608 | 2097.8225 | 2094.7056 | 2368.2819 | 2756.1437 | 3103.125 | 3000.7976 | 2930.3286 | 2919.214 | 2552.0349 |  | 3103.125 | 2026.6608
HV faults: O/H no damage | 480.6329 | 1388.2352 | 649.1106 | 491.6557 | 804.2664 | 748.824 | 837.1553 | 2431.5686 | 636.5512 | 1053.5748 | 952.1575 |  | 2431.5686 | 480.6329
HV faults: O/H damage | 962.4325 | 2635.0543 | 1599.7207 | 1027.2516 | 1575.9764 | 3155.4142 | 1420.9282 | 8348.274 | 1443.667 | 6803.0185 | 2897.1737 |  | 8348.274 | 962.4325
HV underground networks | 2528.7866 | 2218.73 | 2274.398 | 2397.8867 | 2419.8238 | 2804.5659 | 3219.6429 | 3077.9032 | 3014.8089 | 2987.4553 | 2694.4001 |  | 3219.6429 | 2218.73 |  |  |  | 0 | 0
HV overhead networks | 1443.0654 | 4023.2895 | 2248.8313 | 1518.9073 | 2380.2428 | 3904.2382 | 2258.0835 | 10779.8426 | 2080.2182 | 7856.5933 | 3849.3312 |  | 10779.8426 | 1443.0654 |  |  |  | 1 | 0
9316.083
8086.36
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/2000 | 00/01
| 1228116.6881 | 1454977.956 | 1023636.374 | 1081116 | 1178280 | 1026180 | 1356870 | 1603525 | 1546112 | 1748032
| 130789149.34 | 170710410 | 135388138.5 | 123758400 | 145854000 | 159426000 | 143889600 | 331569700 | 143970400 | 290090800

## O
USED IN GRAPHS ON THIS SHEET
Vertical line indicates range over 10 years
Vertical line indicates range since recording started
SECURITY - Supply Interruptions per 100 connected Customers
NUMBER OF INTERRUPTIONS/100 CUSTOMERS
AVAILABILITY - Minutes Lost per connected Customer
NUMBER OF MINUTES LOST/CUSTOMER
RESTORATION OF SUPPLY - Percentage of Interruptions Not Restored within 3 hours
PERCENTAGE NOT RESTORED
RESTORATION OF SUPPLY - Percentage of Interruptions Not Restored within 24 hours
OVERALL RELIABILITY - Number of Faults per 100km of Distribution System (Mains only)
NUMBER OF FAULTS/100KM
Verified Voltage Complaints per 10,000 Connected Customers
COMPLAINTS/10,000 CUSTOMERS
99/00 average
ints/100 custs GB
99/00 average 84 interruptions/100 customers
Mins lost GB
99/00 average 86 mins/cust
Average of faults restored within 24 hours (all companies)
Last year | This year | 99/00 | 88.55% | 90/91 | 83.6%
99.99% | 99.67% | 98/99 | 90.55% | 91/92 | 88.7%
|  | 97/98 | 89.08% | 92/93 | 87.3%
|  | 96/97 | 89.18% | 93/94 | 87.9%
|  | 95/96 | 88.86% | 94/95 | 88.3%
|  | 90/91 | 83.8% | 95/96 | 88.1%
|  |  |  | 96/97 | 88.8%
Supply Interruptions per 100 Connected Customers | GB 10 year average of averages
LV Faults (All) | 5.6547 | 0% | LV
HV faults:U/G, no dam | 1.5186 | 10% | HV u/g ND
HV faults:U/G, damage | 24.3133 | 10% | HV u/g D
HV faults:O/H, no dam | 7.9098 | 10% | HV o/h ND
HV faults:O/H, damage | 13.4958 | 10% | HV o/h D
HV faults: All other | 14.8229 | 10% | HV other
EHV faults | 11.6845 | 0% | EHV
132kV faults | 4.3881 | 0% | 132kV
(b) Planned Outages | 9.6566 | 0% | Planned
(c) Embedded Gen. | 0.34679 | 0% | Emb. Gen
(d) Other Systems | 1.4941 | 0% | Other
Total of (a+b+c+d) | 95.9818
Sum of averages | 95.2852
DATA FOR TWO PIE CHARTS
Note: "Other" includes generation and transmission
Security 1990/2000 | Number and sources of supply interruptions per 100 customers
LV 10 | 9.7498 |  |  | 6
Planned 7 | 7.172 |  |  | 10
HV 58 | 57.7654 |  |  | 62
EHV 10 | 9.7613 |  |  | 12
132kV 4 | 4.0128 |  |  | 4
Other 2 | 1.6247 |  |  | 1
Total of (a+b+c+d) | 87.3379 | Average of 90 interruptions per 100 customers |  | 95.9818
Sum of averages | 90.0861 |  |  | 95
Availability 1990/2000 | Number and sources of minutes lost per customer
LV 19 | 19.3461 |  |  | 11
Planned 38 | 38.349 |  |  | 22
HV 105 | 105.3901 |  |  | 61
EHV 12 | 11.9726 |  |  | 7
132kV 2 | 2.2202 |  |  | 2
Other 1 | 1.2347 |  |  | 1
Total of (a+b+c+d) | 180.2406 | Average of 179 minutes per connected customer
Sum of averages | 178.5127
GB circuit lengths (km)
132kV O/H | 15370.2
132kV U/G | 2788.2
EHV O/H | 28687.5
EHV U/G | 14637.3
HV O/H | 13341
HV U/G | 18790
LV O/H | 364197.7
LV U/G | 309515.4
km 132kV | 18158.4
km EHV | 43324.8
km HV | 32131
km LV | 673713.1
| 00/01 | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00
inst/100 custs GB | 1089.7063 | 1129.7778 | 1309.4012 | 1176.5944 | 1363.8238 | 1136.5454 | 1065.592 | 915.6473 | 1056.1807 | 1265.3313
Mins per cust GB | 93.6561 | 96.7156 | 83.851 | 87.0854 | 85.2942 | 76.575 | 77.853 | 72.2363 | 60.9358 | 73.8248
Cust ints GB | 272614463.2554 | 285749381.0954 | 333283263.7992 | 301755953.3607 | 353663193.3491 | 297372776.8821 | 281775674.2484 | 243365304.9714 | 282953339.9752 | 343162927.8088
Cust GB | 25017243 | 25292529 | 25453106 | 25646557 | 25931736 | 26164620 | 26443111 | 26578500 | 26790240 | 27120401
Mins lost GB | 2343016515.75 | 2446182646.62 | 2134267477.61 | 2233441510 | 2211825452.83 | 2003556756.95 | 2058675921 | 1919932960.5 | 1632484308.34 | 2002157319.74

## P
SECURITY TRENDS : Supply Interruptions per 100 Customers
| 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01
SECURITY - ALL PES AVERAGES SINCE VESTING | 101.1916 | 108.0892 | 96.7264 | 99.5721 | 101.765 | 95.6564 | 95.0107 | 85.0436 | 87.2729 | 89.49 | average of averages
SECURITY - ALL PES AVERAGES SINCE VESTING | 88.5583 | 97.0646 | 85.7816 | 89.3414 | 91.9789 | 89.7581 | 88.0105 | 78.2453 | 81.3854 | 84.163 | weighted average
91/92 | 91/92: 22154855.2554; 92/93: 25017243; 93/94: 88.5583
92/93 | 91/92: 24550085.0954; 92/93: 25292529; 93/94: 97.0646
93/94 | 91/92: 21834075.7992; 92/93: 25453106; 93/94: 85.7816
94/95 | 91/92: 22912993.3607; 92/93: 25646557; 93/94: 89.3414
95/96 | 91/92: 23851733.3491; 92/93: 25931736; 93/94: 91.9789
96/97 | 91/92: 23484876.8821; 92/93: 26164620; 93/94: 89.7581
97/98 | 91/92: 23272724.2484; 92/93: 26443111; 93/94: 88.0105
98/99 | 91/92: 20796436.9714; 92/93: 26578500; 93/94: 78.2453
99/00 | 91/92: 21803333.9752; 92/93: 26790240; 93/94: 81.3854
00/01 | 91/92: 22825329.8088; 92/93: 27120401; 93/94: 84.163

## Q
Minutes lost per connected customer
AVAILABILITY TRENDS : Minutes lost per Connected Customers |  | 91/92 | 92/93 | 93/94 | 94/95 | 95/96 | 96/97 | 97/98 | 98/99 | 99/00 | 00/01
|  | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10
AVAILABILITY - ALL PES AVERAGES SINCE VESTING |  | 123.6219 | 127.0231 | 111.8029 | 109.9407 | 116.7214 | 97.6029 | 99.5443 | 91.5564 | 76.4057 | 88.9436 | average of averages
AVAILABILITY - ALL PES AVERAGES SINCE VESTING |  | 103.7619 | 107.1533 | 96.1945 | 98.062 | 98.1302 | 87.167 | 87.7411 | 80.7131 | 70.8016 | 85.7596 | weighted average
year 1 | 2595836115.75 | 91/92 1: 25017243; 92/93 2: 103.7619
2 | 2710177846.62 | 91/92 1: 25292529; 92/93 2: 107.1533
3 | 2448449077.61 | 91/92 1: 25453106; 92/93 2: 96.1945
4 | 2514953510 | 91/92 1: 25646557; 92/93 2: 98.062
5 | 2544685452.83 | 91/92 1: 25931736; 92/93 2: 98.1302
6 | 2280690756.95 | 91/92 1: 26164620; 92/93 2: 87.167
7 | 2320148421 | 91/92 1: 26443111; 92/93 2: 87.7411
8 | 2145232360.5 | 91/92 1: 26578500; 92/93 2: 80.7131
9 | 1896791308.34 | 91/92 1: 26790240; 92/93 2: 70.8016
10 | 2325834519.74 | 91/92 1: 27120401; 92/93 2: 85.7596
SUMMARY OF PERFORMANCE
Better than 10 yr average:
Security | 10 | 91/92 1: Sec U/G; 92/93 2: 6
Availability | 11 | 91/92 1: Sec O/H; 92/93 2: 8
3hr restn | 8 | 91/92 1: Av U/G; 92/93 2: 8
24hr restn | 5 | 91/92 1: Av O/H; 92/93 2: 12
Voltage | 13
Overall rel | 8
Better than last 9 years
Security | 3 | 91/92 1: Sec U/G; 92/93 2: 1
Availability | 6 | 91/92 1: Sec O/H; 92/93 2: 2
3hr restn | 4 | 91/92 1: Av U/G; 92/93 2: 3
24hr restn | 1 | 91/92 1: Av O/H; 92/93 2: 3
Voltage | 6
Overall rel | 5
3hr and 24 GB summary
Total interruptions in last year
22825329.8088
Total rest in 3 hours
19310696.8018 | 84.6%
Total rest in 24 hours
#VALUE! | #VALUE!

## Fig1
Security
| 00/01 | 10yr Max | 10yr Min | 10 yr Av.
Eastern | 68.83 | 96.41 | 59.15 | 73.145
East Midlands | 91.38 | 97.16 | 74.54 | 87.523
London | 39.75 | 46.67 | 33.06 | 38.387
Manweb | 53.01 | 88.64 | 44.13 | 64.4529
GPU(Midland) | 147.77 | 147.77 | 110.28 | 131.276
Northern | 98.09 | 98.09 | 79.8 | 89.5125
Norweb | 54.1 | 83.8 | 54.1 | 61.394
Seeboard | 88.5 | 159.9 | 88.5 | 101.571
Southern | 73.78 | 82.49 | 63.97 | 76.046
WPD(SWales) | 158.2 | 228 | 150.2 | 191.8285
WPD(SWest) | 86.5 | 128.5 | 80.1 | 107.43
Yorkshire | 69.82 | 93.12 | 69.0598 | 77.096
Hydro Electric | 131.61 | 234.605 | 131.61 | 171.2572
Scottish Power | 91.52 | 91.52 | 57.01 | 72.826
GB average - 84int/100 cons.

## Fig 4
Availability
| 00/01 | Max | Min | 10 yr Av.
Eastern | 66.24 | 94.24 | 52.88 | 71.818
East Midlands | 111.62 | 111.62 | 70.32 | 88.617
London | 43.49 | 67.31 | 38.76 | 51.732
Manweb | 55.09 | 129.29 | 54.69 | 88.836
GPU(Midland) | 143.22 | 151.3 | 99.69 | 126.578
Northern | 109.76 | 109.76 | 81.8 | 94.3374
Norweb | 59.7 | 96.4 | 59.7 | 72.15
Seeboard | 74.5 | 118.3 | 73.2 | 87.46
Southern | 68.74 | 109.18 | 51.63 | 73.164
WPD(SWales) | 123.3 | 325.3793 | 123.3 | 195.9413
WPD(SWest) | 70 | 183.6 | 57.7 | 117.42
Yorkshire | 56.21 | 68.59 | 53.66 | 59.2902
Hydro Electric | 111.46 | 365 | 111.46 | 235.816
Scottish Power | 151.88 | 177.31 | 69.92 | 97.268
GB 00/01 average - 86min

## Fig 7
3 hr Restoration
| 00/01 | Max | Min | 10 yr Av.
Eastern | 0.0902 | 0.1078 | 0.0582 | 0.08104
East Midlands | 0.1517 | 0.1517 | 0.0714 | 0.10261
London | 0.1664 | 0.2233 | 0.155 | 0.1841
Manweb | 0.1195 | 0.1631 | 0.1195 | 0.13723
GPU(Midland) | 0.17905 | 0.17905 | 0.0728 | 0.10392
Northern | 0.1249 | 0.1506 | 0.085 | 0.10949
Norweb | 0.0941 | 0.13 | 0.075 | 0.10509
Seeboard | 0.079 | 0.113 | 0.072 | 0.0865
Southern | 0.1099 | 0.1117 | 0.063 | 0.09191
WPD(SWales) | 0.086 | 0.1272 | 0.084 | 0.10423
WPD(SWest) | 0.087 | 0.1619 | 0.063 | 0.10709
Yorkshire | 0.0746 | 0.0746 | 0.0465 | 0.06172
Hydro Electric | 0.0978 | 0.2642 | 0.09 | 0.16976
Scottish Power | 0.143 | 0.216 | 0.1034 | 0.15133

## Fig 8
24 hr Restoration
| 00/01 | Max | Min | 10 yr Av.
*Eastern | 0.0019 | 0.0019 | 0 | 0.00057
East Midlands | 0.0038 | 0.0038 | 0 | 0.00054
*London | 0.0005 | 0.0008 | 0.0001 | 0.00042
*Manweb | 0.0006 | 0.016 | 0 | 0.00311
GPU(Midland) | 0.0032 | 0.0032 | 0 | 0.00085
*Northern | 0.0073 | 0.0073 | 0 | 0.0014973
Norweb | 0.0002 | 0.0055 | 0 | 0.00127
*Seeboard | 0.001 | 0.001 | 0 | 0.0002
Southern | 0.0031 | 0.0031 | 0 | 0.00055
WPD(SWales) | 0 | 0.0041 | 0 | 0.00062177
WPD(SWest) | 0.001 | 0.0033 | 0 | 0.0006
Yorkshire | 0.0012 | 0.0012 | 0 | 0.00018
Hydro Electric | 0.0001 | 0.0285 | 0 | 0.00774
*Scottish Power | 0.022 | 0.028 | 0 | 0.00656

## Fig 11
Overall Reliability
| 00/01 | Max | Min | 10 yr Av.
Eastern | 12.35 | 13.01 | 10.32 | 11.342
East Midlands | 19.49 | 19.49 | 15.09 | 16.514
London | 16.49 | 17.11 | 14.31 | 15.315
Manweb | 16.55 | 21.646 | 15 | 17.4546
GPU(Midland) | 16.12 | 16.12 | 9.72 | 12.569
Northern | 15.81 | 15.81 | 11.97 | 13.4581
Norweb | 16.9 | 17.6 | 14.2 | 16.4833
Seeboard | 12 | 20 | 12 | 14.9711
Southern | 23.92 | 23.92 | 11.74 | 14.113
WPD(SWales) | 15.51 | 21.6036 | 14.15 | 17.2342
WPD(SWest) | 15.8 | 19.7 | 15.6 | 17.6444
Yorkshire | 12.86 | 17.04 | 12.17 | 14.4218
Hydro Electric | 16.22 | 16.22 | 11 | 14.317
Scottish Power | 15.55 | 19.4 | 14.38 | 16.482

## FIG 12
Security - HV UG
| 00/01 | Max | Min | 10 yr Av.
Eastern | 53.698 | 53.698 | 32.1894 | 41.9061
East Midlands | 50.1849 | 61.9529 | 47.8939 | 52.8522
London | 58.2414 | 62.8792 | 41.7187 | 53.2153
Manweb | 30.6437 | 31.6727 | 22.3765 | 26.859
GPU(Midland) | 76.9341 | 76.9341 | 43.754 | 60.3931
Northern | 41.1997 | 61.6665 | 41.1997 | 50.0391
Norweb | 42.5231 | 42.5231 | 30.4789 | 36.2938
Seeboard | 79.5945 | 95.6872 | 75.3668 | 83.321
Southern | 46.9269 | 46.9269 | 38.2035 | 42.7817
WPD(SWales) | 74.5119 | 142.5049 | 74.5119 | 107.9492
WPD(SWest) | 43.516 | 60.7421 | 37.0361 | 49.1734
Yorkshire | 52.721 | 62.8109 | 48.8383 | 55.3475
Hydro Electric | 31.3556 | 31.3556 | 18.8687 | 24.4871
Scottish Power | 29.6092 | 30.3348 | 21.0178 | 25.2884

## Fig 13
Security - HV OH
| 00/01 | Max | Min | 10 yr Av.
Eastern | 17.4735 | 44.0175 | 13.6251 | 27.7249
East Midlands | 38.3377 | 41.1072 | 25.9392 | 34.4225
London | 0 | 0 | 0 | 0
Manweb | 18.1672 | 30.702 | 17.4723 | 22.7591
GPU(Midland) | 48.705 | 55.5294 | 33.5631 | 44.7168
Northern | 36.3605 | 36.3605 | 22.5094 | 28.7567
Norweb | 26.4385 | 33.82 | 21.9436 | 27.3258
Seeboard | 44.1534 | 64.8751 | 44.1534 | 55.6062
Southern | 32.0387 | 34.8831 | 21.3419 | 30.0711
WPD(SWales) | 47.3602 | 47.3602 | 27.5778 | 35.8394
WPD(SWest) | 21.7893 | 31.1677 | 18.0403 | 21.7593
Yorkshire | 19.932 | 31.6564 | 18.0793 | 23.52
Hydro Electric | 11.2405 | 20.2594 | 11.2405 | 14.5976
Scottish Power | 21.2524 | 26.4897 | 12.1791 | 17.9695

## Fig 14
Availability - HV UG
| 00/01 | Max | Min | 10 yr Av.
Eastern | 4579.6611 | 4791.222 | 3196.2561 | 3976.1989
East Midlands | 5253.7313 | 5253.7313 | 3923.7012 | 4572.6816
London | 3692.6725 | 7671.7904 | 3250.0342 | 5863.4855
Manweb | 3202.3284 | 3550.2233 | 2550.4387 | 3114.2319
GPU(Midland) | 6855.238 | 6855.238 | 3762.4914 | 5162.4515
Northern | 3368.8998 | 5552.7828 | 3368.8998 | 3981.3546
Norweb | 3705.5819 | 4234.6154 | 2664.0441 | 3350.7807
Seeboard | 6426.5205 | 7292.6253 | 5567.1433 | 6545.0717
Southern | 3238.781 | 3921.3224 | 2929.3313 | 3379.5308
WPD(SWales) | 6129.2058 | 13135.4278 | 6129.2058 | 9625.5272
WPD(SWest) | 2682.7804 | 6569.506 | 2139.8653 | 4191.1081
Yorkshire | 3623.4795 | 4314.1796 | 3161.0803 | 3757.0407
Hydro Electric | 2132.1791 | 3157.5044 | 1674.1812 | 2579.4969
Scottish Power | 2987.4553 | 3219.6429 | 2218.73 | 2694.4001

## Fig 15
Availability - HV OH
| 00/01 | Max | Min | 10 yr Av.
Eastern | 2196.8293 | 3555.4851 | 1190.0393 | 2422.0217
East Midlands | 6442.8099 | 6442.8099 | 2218.4323 | 3506.4232
London | 0 | 0 | 0 | 0
Manweb | 1892.8279 | 5716.9294 | 1770.8365 | 3149.588
GPU(Midland) | 6070.9059 | 6511.4458 | 3093.0333 | 4573.9485
Northern | 5399.2694 | 5399.2694 | 1843.5711 | 3459.8519
Norweb | 3553.1072 | 6790.4248 | 2537.1491 | 3946.6988
Seeboard | 4684.1035 | 8075.5939 | 4684.1035 | 6283.3031
Southern | 3067.4508 | 3904.6108 | 1726.7354 | 2757.0232
WPD(SWales) | 4338.648 | 7062.5305 | 2802.8474 | 3995.4947
WPD(SWest) | 1944.6386 | 4124.6835 | 1278.506 | 2374.9958
Yorkshire | 1951.0631 | 2613.2175 | 1332.5155 | 1753.1908
Hydro Electric | 1240.8745 | 4527.4883 | 1240.8745 | 2432.1077
Scottish Power | 7856.5933 | 10779.8426 | 1443.0654 | 3849.3312

## Fig 25
Voltage Complaints
| 00/01 | Max | Min | 10 yr Av.
Eastern | 0.2 | 1.92 | 0.2 | 1.213
East Midlands | 0.513 | 2.215 | 0.513 | 1.224
London | 0.111 | 0.614 | 0.111 | 0.2908
Manweb | 1.53 | 2.85 | 1.53 | 2.023
GPU(Midland) | 0.8 | 2.25 | 0.12 | 0.888
Northern | 0.27 | 0.52 | 0.04 | 0.32666
Norweb | 0.82 | 2.09 | 0.64 | 1.372
Seeboard | 0.75 | 2.58 | 0.6 | 1.097
Southern | 1.74 | 2.73 | 1.05 | 1.848
WPD(SWales) | 0.6 | 3.7 | 0.6 | 1.5254
WPD(SWest) | 2 | 3.8 | 0.7 | 2.18
Yorkshire | 0.561 | 1.562 | 0.561 | 0.9393
Hydro Electric | 1.5 | 6.1 | 1.5 | 3.7747
Scottish Power | 0.99 | 3.24 | 0.99 | 2.204

## Fig 26
Company | Area (sq km) | customers (,000) | Overhead km | Underground km | No of Transformers | Aggregate transformer capacity (MVA)
Eastern
East Midlands
London
Manweb
Midlands
Northern
NORWEB