## 4.3.1 Risk Matrix
Asset Health and Criticality
Definitions
Asset health index |  | Criticality index |  | Risk index
HI1 | New or as new | C1 | Very High | RI1 | Very high risk
HI2 | Good or serviceable condition | C2 | High | RI2 | High risk
HI3 | Deterioration, requires assessment or monitoring | C3 | Medium | RI3 | Medium risk
HI4 | Material deterioration, intervention requires consideration | C4 | Low | RI4 | Low risk
HI5 | End of serviceable life, intervention required |  |  | RI5 | Very low risk
Risk matrix (to be completed by GDNs)
[7 empty] | HI1 | HI2 | HI3 | HI4 | HI5
[6 empty] | C1 | RI4 | RI3 | RI2 | RI1 | RI1
[6 empty] | C2 | RI5 | RI4 | RI3 | RI2 | RI1
[6 empty] | C3 | RI5 | RI4 | RI3 | RI2 | RI2
[6 empty] | C4 | RI5 | RI5 | RI4 | RI3 | RI2

## 4.3.3 Input Sheet
Asset categories |  | Component | Units | Criticality Index | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register
[5 empty] | Starting Position | [5 empty] | With Proposed Investment (50/50 Estimate) | [5 empty] | Without Investment (50/50 Estimate) | [5 empty] | With Proposed Investment (50/50 Estimate) | [5 empty] | Without Investment (50/50 Estimate)
[5 empty] | Asset health index |  |  |  |  | 2013-03-31 | Asset health index |  |  |  |  | 2017-03-31 | Asset health index |  |  |  |  | 2017-03-31 | Asset health index |  |  |  |  | 2021-03-31 | Asset health index |  |  |  |  | 2021-03-31
[5 empty] | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5
1 | Storage Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 0 | 5 | 0 | 5 | 1 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 1 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 5 | 5
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Above7 bar Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 21 | 35 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56
|  |  |  | Very High | 0 | 0 | 2 | 83 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85
3 | Below7 bar Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1
|  |  |  | Medium | 0 | 0 | 6 | 0 | 3 | 9 | 0 | 0 | 3 | 3 | 3 | 9 | 0 | 0 | 3 | 3 | 3 | 9 | 0 | 0 | 0 | 6 | 3 | 9 | 0 | 0 | 0 | 6 | 3 | 9
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Block Valves | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 4 | 3 | 0 | 1 | 8 | 0 | 1 | 4 | 2 | 1 | 8 | 0 | 1 | 4 | 2 | 1 | 8 | 0 | 1 | 3 | 3 | 1 | 8 | 0 | 1 | 3 | 3 | 1 | 8
|  |  |  | High | 0 | 0 | 7 | 1 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Valves | Asset Level | Number of | Low | 8 | 28 | 28 | 14 | 8 | 86 | 8 | 36 | 28 | 14 | 0 | 86 | 8 | 28 | 28 | 14 | 8 | 86 | 8 | 8 | 28 | 42 | 0 | 86 | 8 | 0 | 28 | 42 | 8 | 86
|  |  |  | Medium | 5 | 99 | 86 | 10 | 4 | 204 | 5 | 113 | 86 | 0 | 0 | 204 | 5 | 99 | 86 | 10 | 4 | 204 | 5 | 4 | 99 | 96 | 0 | 204 | 5 | 0 | 99 | 96 | 4 | 204
|  |  |  | High | 6 | 56 | 74 | 35 | 3 | 174 | 6 | 94 | 74 | 0 | 0 | 174 | 6 | 56 | 74 | 35 | 3 | 174 | 6 | 108 | 56 | 4 | 0 | 174 | 6 | 0 | 56 | 109 | 3 | 174
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Pig Traps | Asset Level | Number of | Low | 0 | 7 | 1 | 0 | 0 | 8 | 6 | 7 | 1 | 0 | 0 | 14 | 0 | 7 | 1 | 0 | 0 | 8 | 10 | 0 | 7 | 1 | 0 | 18 | 0 | 0 | 7 | 1 | 0 | 8
|  |  |  | Medium | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 0 | 3 | 1 | 0 | 5 | 1 | 0 | 3 | 1 | 0 | 5
|  |  |  | High |  | 6 | 3 | 0 | 0 | 9 | 0 | 6 | 3 | 0 | 0 | 9 | 0 | 6 | 3 | 0 | 0 | 9 | 0 | 0 | 6 | 3 | 0 | 9 | 0 | 0 | 6 | 3 | 0 | 9
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Sleeves (Nitrogen & other) | Asset Level | Number of | Low | 11 | 23 | 28 |  | 0 | 62 | 11 | 23 | 28 | 0 | 0 | 62 | 11 | 23 | 28 | 0 | 0 | 62 | 11 | 0 | 23 | 28 | 0 | 62 | 11 | 0 | 23 | 28 |  | 62
|  |  |  | Medium |  | 268 | 58 | 8 | 0 | 334 | 0 | 290 | 44 | 0 | 0 | 334 |  | 268 | 58 | 0 | 8 | 334 | 0 | 51 | 268 | 15 | 0 | 334 | 0 | 0 | 268 | 58 | 8 | 334
|  |  |  | High |  | 481 |  | 7 | 0 | 488 | 0 | 488 | 0 | 0 | 0 | 488 |  | 481 |  |  | 7 | 488 | 0 | 7 | 481 | 0 | 0 | 488 | 0 | 0 | 481 |  | 7 | 488
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | LTS Pipelines - Piggable | Asset Level | Km | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 9.48 | 331.82 | 144.1 | 0 | 0 | 485.4 | 34.08 | 316.82 | 154.1 | 5 | 0 | 510 | 9.48 | 316.82 | 154.1 | 5 | 0 | 485.4 | 34.08 | 312 | 154.1 | 9.82 | 0 | 510 | 9.48 | 312 | 154.1 | 9.82 | 0 | 485.4
|  |  |  | High | 0 | 478.09 | 0 | 10.38 | 0 | 488.47 | 0 | 462.59 | 15.5 | 10.38 | 0 | 488.47 | 0 | 462.59 | 15.5 | 10.38 | 0 | 488.47 | 0 | 459.59 | 18.5 | 10.38 | 0 | 488.47 | 0 | 459.59 | 18.5 | 10.38 | 0 | 488.47
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | LTS Pipelines – Non Piggable | Asset Level | Km | Low | 114.98 | 66.19 | 33.39 | 37.67 | 0 | 252.23 | 114.98 | 66.19 | 23.39 | 47.67 | 0 | 252.23 | 114.98 | 66.19 | 23.39 | 47.67 | 0 | 252.23 | 114.98 | 60.19 | 23.39 | 53.67 | 0 | 252.23 | 114.98 | 60.19 | 23.39 | 53.67 | 0 | 252.23
|  |  |  | Medium | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 41.73 | 24 | 5.01 | 0 | 82.81 | 12.07 | 41.73 | 24 | 5.01 | 0 | 82.81
|  |  |  | High | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12
|  |  |  | Very High | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8
10 | Cathodic Protection | Asset Level | Number of Schemes | Low | 75 | 258 | 284 | 93 | 0 | 710 | 85 | 273 | 305 | 83 | 0 | 746 | 70 | 241 | 284 | 105 | 46 | 746 | 100 | 253 | 314 | 72 | 12 | 751 | 48 | 235 | 284 | 120 | 64 | 751
|  |  |  | Medium | 31 | 136 | 109 | 45 | 0 | 321 | 47 | 150 | 124 | 32 | 0 | 353 | 26 | 120 | 109 | 75 | 23 | 353 | 52 | 150 | 121 | 32 | 10 | 365 | 23 | 110 | 109 | 92 | 31 | 365
|  |  |  | High | 6 | 163 | 58 | 18 | 0 | 245 | 19 | 162 | 50 | 8 | 0 | 239 | 5 | 142 | 58 | 25 | 9 | 239 | 10 | 161 | 60 | 10 | 3 | 244 | 3 | 134 | 58 | 37 | 12 | 244
|  |  |  | Very High | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1
11 | Above7 bar Special Crossings | Asset Level | Number of | Low | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10
|  |  |  | Medium | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 0 | 42 | 3 | 0 | 46 | 1 | 0 | 42 | 3 | 0 | 46
|  |  |  | High | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 0 | 32 | 7 | 0 | 39 | 0 | 0 | 32 | 7 | 0 | 39
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Below7 bar Special Crossings | Asset Level | Number of | Low | 46 | 0 | 49 | 77 | 0 | 172 | 46 | 0 | 49 | 77 | 0 | 172 | 23 | 23 | 25 | 63 | 38 | 172 | 46 | 0 | 49 | 77 | 0 | 172 | 0 | 46 | 0 | 49 | 77 | 172
|  |  |  | Medium | 147 | 0 | 145 | 85 | 0 | 377 | 147 | 0 | 145 | 85 | 0 | 377 | 74 | 73 | 73 | 115 | 42 | 377 | 147 | 0 | 145 | 85 | 0 | 377 | 0 | 147 | 0 | 145 | 85 | 377
|  |  |  | High | 24 | 0 | 183 | 0 | 0 | 207 | 24 | 0 | 183 | 0 | 0 | 207 | 12 | 12 | 92 | 91 | 0 | 207 | 24 | 0 | 183 | 0 | 0 | 207 | 0 | 24 | 0 | 183 | 0 | 207
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Distribution Mains (Iron) | Asset Level | Km | Low | 0 | 0 | 0.65895 | 3645.4722 | 1444.7625 | 5090.8936 | 0 | 0 | 0.54852 | 3034.2743 | 1202.6483 | 4237.4711 | 0 | 0 | 0.65895 | 3646.3302 | 1443.9044 | 5090.8936 | 0 | 0 | 0.4381 | 2423.0763 | 960.5342 | 3384.0486 | 0 | 0 | 0.65895 | 3647.1883 | 1443.0464 | 5090.8936
|  |  |  | Medium | 0 | 0 | 0.051 | 387.7529 | 97.4847 | 485.2886 | 0 | 0 | 0.042453 | 322.2415 | 81.1481 | 403.4321 | 0 | 0 | 0.051 | 389.3389 | 95.8987 | 485.2886 | 0 | 0 | 0.033907 | 256.7301 | 64.8116 | 321.5756 | 0 | 0 | 0.051 | 390.9249 | 94.3127 | 485.2886
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Distribution Mains (PE) | Asset Level | Km | Low | 12822.6282 | 5.0716 | 0 | 0 | 0 | 12827.6998 | 14065.2372 | 5.0716 | 0 | 0 | 0 | 14070.3088 | 12822.7977 | 4.9021 | 0 | 0 | 0 | 12827.6998 | 15307.8462 | 5.0716 | 0 | 0 | 0 | 15312.9178 | 12822.9672 | 4.7326 | 0 | 0 | 0 | 12827.6998
|  |  |  | Medium | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2896.4846 | 1.7815 | 0 | 0 | 0 | 2898.2661 | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2897.2593 | 1.0068 | 0 | 0 | 0 | 2898.2661
|  |  |  | High | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 227.0409 | -0.12 | 0 | 0 | 0 | 226.9209 | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 227.1609 | -0.24 | 0 | 0 | 0 | 226.9209
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Distribution Mains (Steel) | Asset Level | Km | Low | 0 | 0 | 352.7423 | 192.431 | 54.5418 | 599.7151 | 0 | 0 | 312.6551 | 170.6344 | 48.3639 | 531.6534 | 0 | 0 | 353.3261 | 191.8472 | 54.5418 | 599.7151 | 0 | 0 | 272.5678 | 148.8378 | 42.186 | 463.5916 | 0 | 0 | 353.9099 | 191.2634 | 54.5418 | 599.7151
|  |  |  | Medium | 0 | 0 | 10.1724 | 179.1802 | 14.032 | 203.3845 | 0 | 0 | 8.1473 | 158.8846 | 12.4426 | 179.4744 | 0 | 0 | 14.0253 | 175.3273 | 14.032 | 203.3845 | 0 | 0 | 6.1222 | 138.5889 | 10.8532 | 155.5643 | 0 | 0 | 17.8783 | 171.4743 | 14.032 | 203.3845
|  |  |  | High | 0 | 0 | 44.7987 | 839.0303 | 13.8193 | 897.6483 | 0 | 0 | 38.4685 | 743.9937 | 12.254 | 794.7162 | 0 | 0 | 50.3423 | 833.4867 | 13.8193 | 897.6483 | 0 | 0 | 32.1383 | 648.957 | 10.6887 | 691.7841 | 0 | 0 | 55.8859 | 827.9431 | 13.8193 | 897.6483
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Distribution Mains (other) | Asset Level | Km | Low | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Services | Asset Level | Number of | Low | 0 | 760241 | 0 | 1313660 | 0 | 2073901 | 113827 | 760241 | 0 | 1232403 | 0 | 2106471 | 0 | 760241 | 0 | 1313660 | 0 | 2073901 | 225168 | 760241 | 0 | 1153631 | 0 | 2139040 | 0 | 760241 | 0 | 1313660 | 0 | 2073901
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | MOB Risers | Asset Level | Number of | Low | 1300 | 325 | 0 | 2809 | 2809 | 7243 | 0 | 2941 | 0 | 2060 | 2242 | 7243 | 0 | 1625 | 0 | 2060 | 3558 | 7243 | 0 | 4257 | 0 | 1311 | 1675 | 7243 | 0 | 1625 | 0 | 1311 | 4307 | 7243
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Operational Holders | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | 0 | 0 | 22 | 22
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | High Pressure Vessels | Asset Level | Number of | Low | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | NTS Offtakes | Asset Level | no | Low | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | Medium | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | High | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5
|  | Regulators System | System |  | 1 | 2 | 0 | 1 | 1 |  | 0 | 1 | 2 | 1 | 1 |  | 0 | 1 | 2 | 1 | 1 |  | 1 | 1 | 1 | 2 | 0 |  | 0 | 1 | 1 | 2 | 1
|  | Slam Shut System | System |  | 0 | 3 | 2 | 0 | 0 |  | 0 | 1 | 3 | 1 | 0 |  | 0 | 1 | 3 | 1 | 0 |  | 1 | 1 | 2 | 1 | 0 |  | 0 | 1 | 2 | 2 | 0
|  | Filter System | System |  | 1 | 2 | 2 | 0 | 0 |  | 0 | 2 | 2 | 1 | 0 |  | 0 | 2 | 2 | 1 | 0 |  | 1 | 1 | 2 | 1 | 0 |  | 0 | 1 | 2 | 2 | 0
|  | Pre-heating System | System |  | 2 | 1 | 0 | 0 | 2 |  | 0 | 3 | 0 | 0 | 2 |  | 0 | 3 | 0 | 0 | 2 |  | 2 | 1 | 2 | 0 | 0 |  | 0 | 1 | 2 | 0 | 2
|  | Odorisation System | System |  | 4 | 0 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 0 | 4 | 0 | 0 | 0
|  | Metering System | System |  | 3 | 2 | 0 | 0 | 0 |  | 2 | 2 | 1 | 0 | 0 |  | 2 | 2 | 1 | 0 | 0 |  | 1 | 2 | 2 | 0 | 0 |  | 1 | 2 | 2 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 2 | 0 | 2 | 1 |  | 0 | 1 | 2 | 0 | 2 |  | 0 | 1 | 2 | 0 | 2 |  | 0 | 0 | 2 | 3 | 0 |  | 0 | 0 | 2 | 3 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 4 | 1 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0
|  | Electrical System | Systems |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 0 | 5 | 0 | 0 |  | 0 | 0 | 5 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 5 | 0 |  | 0 | 1 | 0 | 4 | 0 |  | 0 | 0 | 0 | 5 | 0 |  | 0 | 2 | 0 | 3 | 0 |  | 0 | 0 | 0 | 5 | 0
|  | Asset Level | no | Very High | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13
|  | Regulators System | System |  | 4 | 1 | 2 | 2 | 2 |  | 4 | 3 | 2 | 2 | 0 |  | 2 | 3 | 2 | 2 | 2 |  | 4 | 3 | 2 | 2 | 0 |  | 1 | 3 | 2 | 3 | 2
|  | Slam Shut System | System |  | 3 | 3 | 0 | 2 | 1 |  | 4 | 4 | 0 | 1 | 0 |  | 2 | 4 | 0 | 1 | 2 |  | 3 | 3 | 2 | 1 | 0 |  | 1 | 3 | 2 | 1 | 2
|  | Filter System | System |  | 8 | 2 | 0 | 3 | 0 |  | 7 | 3 | 1 | 2 | 0 |  | 6 | 3 | 1 | 3 | 0 |  | 6 | 4 | 2 | 1 | 0 |  | 4 | 4 | 2 | 2 | 1
|  | Pre-heating System | System |  | 5 | 2 | 2 | 1 | 1 |  | 7 | 2 | 1 | 1 | 0 |  | 4 | 2 | 1 | 3 | 1 |  | 6 | 4 | 1 | 0 | 0 |  | 2 | 4 | 1 | 3 | 1
|  | Odorisation System | System |  | 12 | 1 | 0 | 0 | 0 |  | 4 | 9 | 0 | 0 | 0 |  | 3 | 10 | 0 | 0 | 0 |  | 3 | 10 | 0 | 0 | 0 |  | 2 | 11 | 0 | 0 | 0
|  | Metering System | System |  | 3 | 1 | 0 | 8 | 0 |  | 5 | 2 | 0 | 5 | 0 |  | 2 | 2 | 0 | 8 | 0 |  | 9 | 1 | 1 | 1 | 0 |  | 2 | 1 | 1 | 4 | 4
|  | Buildings (no.’s) | Number of |  | 2 | 2 | 4 | 4 | 0 |  | 2 | 3 | 1 | 5 | 1 |  | 1 | 3 | 1 | 5 | 2 |  | 3 | 2 | 2 | 4 | 0 |  | 1 | 2 | 2 | 5 | 1
|  | Fences (no’s -Inc Security) | Number of |  | 1 | 4 | 5 | 2 | 0 |  | 2 | 3 | 5 | 2 | 0 |  | 1 | 3 | 5 | 2 | 1 |  | 3 | 3 | 3 | 3 | 0 |  | 1 | 3 | 3 | 4 | 1
|  | Electrical System | Systems |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 2 | 11 | 0 | 0 |  | 1 | 0 | 13 | 0 | 0
|  | Instrumentation System | Systems |  | 1 | 0 | 0 | 10 | 0 |  | 1 | 1 | 0 | 9 | 0 |  | 1 | 0 | 0 | 10 | 0 |  | 1 | 2 | 0 | 8 | 0 |  | 1 | 0 | 0 | 10 | 0
23 | PRSs | Asset Level | no | Low | [5 empty] | 0 | [11 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | Medium | [5 empty] | 0 | [11 empty] | 0 | [5 empty] | 0 | [5 empty] | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | High | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53
|  | Regulators System | System |  | 1 | 8 | 33 | 8 | 3 |  | 2 | 3 | 34 | 12 | 2 |  | 1 | 3 | 34 | 12 | 3 |  | 2 | 4 | 10 | 36 | 1 |  | 0 | 4 | 10 | 36 | 3
|  | Slam Shut System | System |  | 0 | 17 | 15 | 2 | 19 |  | 1 | 9 | 21 | 4 | 18 |  | 0 | 9 | 21 | 4 | 19 |  | 2 | 5 | 14 | 15 | 17 |  | 0 | 5 | 14 | 15 | 19
|  | Filter System | System |  | 3 | 42 | 7 | 1 | 0 |  | 5 | 28 | 20 | 0 | 0 |  | 3 | 28 | 21 | 1 | 0 |  | 3 | 8 | 40 | 1 | 0 |  | 1 | 8 | 41 | 3 | 0
|  | Pre-heating System | System |  | 1 | 7 | 17 | 7 | 3 |  | 3 | 6 | 10 | 16 | 0 |  | 0 | 6 | 10 | 16 | 3 |  | 5 | 3 | 9 | 18 | 0 |  | 0 | 3 | 9 | 19 | 4
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 18 | 21 | 11 | 0 |  | 1 | 5 | 19 | 22 | 3 |  | 0 | 5 | 19 | 22 | 4 |  | 3 | 3 | 20 | 23 | 2 |  | 1 | 3 | 20 | 23 | 4
|  | Fences (no’s -Inc Security) | Number of |  | 3 | 27 | 19 | 1 | 1 |  | 2 | 16 | 30 | 3 | 0 |  | 1 | 16 | 30 | 3 | 1 |  | 4 | 10 | 30 | 7 | 0 |  | 1 | 10 | 30 | 9 | 1
|  | Electrical System | Systems |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 0 | 52 | 0 | 0 |  | 0 | 0 | 53 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 23 | 30 | 0 |  |  | 1 |  | 52 |  |  | 0 | 0 | 0 | 53 | 0 |  | 0 | 1 | 0 | 53 | 0 |  | 0 | 0 | 0 | 53 | 0
|  | Asset Level | no | Very High | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91
|  | Regulators System | System |  | 10 | 18 | 31 | 20 | 12 |  | 17 | 13 | 30 | 30 | 1 |  | 6 | 13 | 30 | 30 | 12 |  | 20 | 14 | 12 | 45 | 0 |  | 3 | 14 | 12 | 50 | 12
|  | Slam Shut System | System |  | 8 | 17 | 12 | 1 | 53 |  | 18 | 15 | 10 | 6 | 42 |  | 7 | 15 | 10 | 6 | 53 |  | 23 | 12 | 8 | 12 | 36 |  | 6 | 12 | 8 | 12 | 53
|  | Filter System | System |  | 8 | 67 | 8 | 1 | 0 |  | 18 | 43 | 23 | 0 | 0 |  | 7 | 43 | 32 | 2 | 0 |  | 21 | 14 | 49 | 0 | 0 |  | 4 | 14 | 62 | 4 | 0
|  | Pre-heating System | System |  | 13 | 19 | 23 | 18 | 6 |  | 23 | 17 | 13 | 26 | 0 |  | 8 | 17 | 13 | 35 | 6 |  | 31 | 18 | 15 | 15 | 0 |  | 2 | 18 | 15 | 38 | 6
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 5 | 18 | 22 | 29 | 3 |  | 15 | 13 | 15 | 31 | 3 |  | 4 | 13 | 15 | 35 | 10 |  | 21 | 11 | 15 | 23 | 7 |  | 4 | 11 | 15 | 23 | 24
|  | Fences (no’s -Inc Security) | Number of |  | 8 | 26 | 29 | 14 | 0 |  | 14 | 21 | 27 | 15 | 0 |  | 4 | 21 | 27 | 24 | 1 |  | 15 | 12 | 25 | 25 | 0 |  | 4 | 12 | 25 | 35 | 1
|  | Electrical System | Systems |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 14 | 65 | 0 | 0 |  | 0 | 0 | 79 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 9 | 70 | 0 |  | 0 | 11 | 0 | 68 | 0 |  | 0 | 0 | 0 | 79 | 0 |  | 0 | 14 | 0 | 65 | 0 |  | 0 | 0 | 0 | 79 | 0
22 | District Governors | Asset Level | Number of | Low | 31 | 1176 | 42 | 427 | 39 | 1715 | 35 | 1208 | 42 | 0 | 434 | 1719 | 31 | 1176 | 42 | 0 | 466 | 1715 | 39 | 93 | 1176 | 42 | 373 | 1723 | 31 | 0 | 1176 | 42 | 466 | 1715
|  |  |  | Medium | 20 | 416 | 11 | 10 | 19 | 476 | 23 | 445 | 11 | 0 | 0 | 479 | 20 | 416 | 11 | 0 | 29 | 476 | 26 | 29 | 416 | 11 | 0 | 482 | 20 | 0 | 416 | 11 | 29 | 476
|  |  |  | High | 0 | 4 | 1 | 0 | 2 | 7 | 0 | 6 | 1 | 0 | 0 | 7 | 0 | 4 | 1 | 0 | 2 | 7 | 0 | 2 | 4 | 1 | 0 | 7 | 0 | 0 | 4 | 1 | 2 | 7
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | I&C Governors | Asset Level | Number of | Low | 0 | 200 | 0 | 7 | 6 | 213 | 0 | 203 | 0 | 0 | 10 | 213 | 0 | 200 | 0 | 0 | 13 | 213 | 0 | 5 | 200 | 0 | 8 | 213 | 0 | 0 | 200 | 0 | 13 | 213
|  |  |  | Medium | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Service Governors | Asset Level | Number of | Low | 1224 | 459 | 0 | 1060 | 765 | 3508 | 1224 | 1071 | 0 | 448 | 765 | 3508 | 612 | 1071 | 0 | 448 | 1377 | 3508 | 1224 | 1224 | 0 | 295 | 765 | 3508 | 0 | 1224 | 0 | 295 | 1989 | 3508
|  |  |  | Medium | 96 | 36 | 0 | 83 | 60 | 275 | 96 | 84 | 0 | 35 | 60 | 275 | 48 | 84 | 0 | 35 | 108 | 275 | 96 | 96 | 0 | 23 | 60 | 275 | 0 | 96 | 0 | 23 | 156 | 275
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | LPG Storage | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 3
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | LPG Mains | Asset Level | Km | Low | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | LPG Services | Asset Level | Number of | Low | 0 | 846 | 0 | 930 | 0 | 1776 | 80 | 846 | 0 | 872 | 0 | 1798 | 0 | 846 | 0 | 930 | 0 | 1776 | 159 | 846 | 0 | 817 | 0 | 1822 | 0 | 846 | 0 | 930 | 0 | 1776
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | LNG Vessels | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 2 | 18 | 0 | 0 | 20 | 0 | 2 | 14 | 4 | 0 | 20 | 0 | 2 | 14 | 4 | 0 | 20 | 0 | 2 | 9 | 9 | 0 | 20 | 0 | 2 | 9 | 9 | 0 | 20
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## 4.3.2 Asset Health
Asset categories |  | Component | Units | Criticality Index | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index |  |  |  |  | Asset Register | Asset distribution based on estimated asset health index
[5 empty] | RIIO-GD1 Starting Position | [5 empty] | Mid RIIO-GD1 With Proposed Investment (50/50 Estimate) | [5 empty] | Mid RIIO-GD1 Without Investment (50/50 Estimate) | [5 empty] | End RIIO-GD1 With Proposed Investment (50/50 Estimate) | [5 empty] | End RIIO-GD1 Without Investment (50/50 Estimate)
[5 empty] | Asset health index |  |  |  |  | 2013-03-31 | Asset health index |  |  |  |  | 2017-03-31 | Asset health index |  |  |  |  | 2017-03-31 | Asset health index |  |  |  |  | 2021-03-31 | Asset health index |  |  |  |  | 2021-03-31 | Asset health index
[5 empty] | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  | HI1 | HI2 | HI3 | HI4 | HI5 |  |  |  | RI1 | RI2 | RI3 | RI4 | RI5 | RI1 | RI2 | RI3 | RI4 | RI5 | RI1 | RI2 | RI3 | RI4 | RI5 | RI1 | RI2 | RI3 | RI4 | RI5 | RI1 | RI2 | RI3 | RI4 | RI5
1 | Storage Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | Storage Telemetry | Asset Level | Storage TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 0 | 5 | 0 | 5 | 1 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 1 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 0 | 5 | 5 | RI5 | RI4 | RI3 | RI2 | RI2 | Storage Telemetry | Asset Level | Storage TelemetryAsset Level | 0 | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Storage Telemetry | Asset Level | Storage TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Storage Telemetry | Asset Level | Storage TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Above7 bar Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | Above7 bar Telemetry | Asset Level | Above7 bar TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | Above7 bar Telemetry | Asset Level | Above7 bar TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 21 | 35 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | 0 | 0 | 0 | 56 | 0 | 56 | RI5 | RI4 | RI3 | RI2 | RI1 | Above7 bar Telemetry | Asset Level | Above7 bar TelemetryAsset Level | 0 | 35 | 21 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0 | 0 | 56 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 2 | 83 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | 0 | 0 | 0 | 85 | 0 | 85 | RI4 | RI3 | RI2 | RI1 | RI1 | Above7 bar Telemetry | Asset Level | Above7 bar TelemetryAsset Level | 83 | 2 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0 | 85 | 0 | 0 | 0 | 0
3 | Below7 bar Telemetry | Asset Level | System | Low | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | RI5 | RI5 | RI4 | RI3 | RI2 | Below7 bar Telemetry | Asset Level | Below7 bar TelemetryAsset Level | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 6 | 0 | 3 | 9 | 0 | 0 | 3 | 3 | 3 | 9 | 0 | 0 | 3 | 3 | 3 | 9 | 0 | 0 | 0 | 6 | 3 | 9 | 0 | 0 | 0 | 6 | 3 | 9 | RI5 | RI4 | RI3 | RI2 | RI2 | Below7 bar Telemetry | Asset Level | Below7 bar TelemetryAsset Level | 0 | 3 | 6 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 6 | 3 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Below7 bar Telemetry | Asset Level | Below7 bar TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Below7 bar Telemetry | Asset Level | Below7 bar TelemetryAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
4 | Block Valves | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | Block Valves | Asset Level | Block ValvesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 4 | 3 | 0 | 1 | 8 | 0 | 1 | 4 | 2 | 1 | 8 | 0 | 1 | 4 | 2 | 1 | 8 | 0 | 1 | 3 | 3 | 1 | 8 | 0 | 1 | 3 | 3 | 1 | 8 | RI5 | RI4 | RI3 | RI2 | RI2 | Block Valves | Asset Level | Block ValvesAsset Level | 0 | 1 | 3 | 4 | 0 | 0 | 3 | 4 | 1 | 0 | 0 | 3 | 4 | 1 | 0 | 0 | 4 | 3 | 1 | 0 | 0 | 4 | 3 | 1 | 0
|  |  |  | High | 0 | 0 | 7 | 1 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | 0 | 0 | 0 | 8 | 0 | 8 | RI5 | RI4 | RI3 | RI2 | RI1 | Block Valves | Asset Level | Block ValvesAsset Level | 0 | 1 | 7 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 8 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Block Valves | Asset Level | Block ValvesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
5 | Valves | Asset Level | Number of | Low | 8 | 28 | 28 | 14 | 8 | 86 | 8 | 36 | 28 | 14 | 0 | 86 | 8 | 28 | 28 | 14 | 8 | 86 | 8 | 8 | 28 | 42 | 0 | 86 | 8 | 0 | 28 | 42 | 8 | 86 | RI5 | RI5 | RI4 | RI3 | RI2 | Valves | Asset Level | ValvesAsset Level | 0 | 8 | 14 | 28 | 36 | 0 | 0 | 14 | 28 | 44 | 0 | 8 | 14 | 28 | 36 | 0 | 0 | 42 | 28 | 16 | 0 | 8 | 42 | 28 | 8
|  |  |  | Medium | 5 | 99 | 86 | 10 | 4 | 204 | 5 | 113 | 86 | 0 | 0 | 204 | 5 | 99 | 86 | 10 | 4 | 204 | 5 | 4 | 99 | 96 | 0 | 204 | 5 | 0 | 99 | 96 | 4 | 204 | RI5 | RI4 | RI3 | RI2 | RI2 | Valves | Asset Level | ValvesAsset Level | 0 | 14 | 86 | 99 | 5 | 0 | 0 | 86 | 113 | 5 | 0 | 14 | 86 | 99 | 5 | 0 | 96 | 99 | 4 | 5 | 0 | 100 | 99 | 0 | 5
|  |  |  | High | 6 | 56 | 74 | 35 | 3 | 174 | 6 | 94 | 74 | 0 | 0 | 174 | 6 | 56 | 74 | 35 | 3 | 174 | 6 | 108 | 56 | 4 | 0 | 174 | 6 | 0 | 56 | 109 | 3 | 174 | RI5 | RI4 | RI3 | RI2 | RI1 | Valves | Asset Level | ValvesAsset Level | 3 | 35 | 74 | 56 | 6 | 0 | 0 | 74 | 94 | 6 | 3 | 35 | 74 | 56 | 6 | 0 | 4 | 56 | 108 | 6 | 3 | 109 | 56 | 0 | 6
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Valves | Asset Level | ValvesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
6 | Pig Traps | Asset Level | Number of | Low | 0 | 7 | 1 | 0 | 0 | 8 | 6 | 7 | 1 | 0 | 0 | 14 | 0 | 7 | 1 | 0 | 0 | 8 | 10 | 0 | 7 | 1 | 0 | 18 | 0 | 0 | 7 | 1 | 0 | 8 | RI5 | RI5 | RI4 | RI3 | RI2 | Pig Traps | Asset Level | Pig TrapsAsset Level | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 0 | 1 | 13 | 0 | 0 | 0 | 1 | 7 | 0 | 0 | 1 | 7 | 10 | 0 | 0 | 1 | 7 | 0
|  |  |  | Medium | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 3 | 1 | 0 | 0 | 5 | 1 | 0 | 3 | 1 | 0 | 5 | 1 | 0 | 3 | 1 | 0 | 5 | RI5 | RI4 | RI3 | RI2 | RI2 | Pig Traps | Asset Level | Pig TrapsAsset Level | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 1 | 3 | 1 | 0 | 1 | 3 | 0 | 1 | 0 | 1 | 3 | 0 | 1
|  |  |  | High | 0 | 6 | 3 | 0 | 0 | 9 | 0 | 6 | 3 | 0 | 0 | 9 | 0 | 6 | 3 | 0 | 0 | 9 | 0 | 0 | 6 | 3 | 0 | 9 | 0 | 0 | 6 | 3 | 0 | 9 | RI5 | RI4 | RI3 | RI2 | RI1 | Pig Traps | Asset Level | Pig TrapsAsset Level | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 3 | 6 | 0 | 0 | 3 | 6 | 0 | 0 | 0 | 3 | 6 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Pig Traps | Asset Level | Pig TrapsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
7 | Sleeves (Nitrogen & other) | Asset Level | Number of | Low | 11 | 23 | 28 | 0 | 0 | 62 | 11 | 23 | 28 | 0 | 0 | 62 | 11 | 23 | 28 | 0 | 0 | 62 | 11 | 0 | 23 | 28 | 0 | 62 | 11 | 0 | 23 | 28 | 0 | 62 | RI5 | RI5 | RI4 | RI3 | RI2 | Sleeves (Nitrogen & other) | Asset Level | Sleeves (Nitrogen & other)Asset Level | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 0 | 28 | 34 | 0 | 0 | 28 | 23 | 11 | 0 | 0 | 28 | 23 | 11
|  |  |  | Medium | 0 | 268 | 58 | 8 | 0 | 334 | 0 | 290 | 44 | 0 | 0 | 334 | 0 | 268 | 58 | 0 | 8 | 334 | 0 | 51 | 268 | 15 | 0 | 334 | 0 | 0 | 268 | 58 | 8 | 334 | RI5 | RI4 | RI3 | RI2 | RI2 | Sleeves (Nitrogen & other) | Asset Level | Sleeves (Nitrogen & other)Asset Level | 0 | 8 | 58 | 268 | 0 | 0 | 0 | 44 | 290 | 0 | 0 | 8 | 58 | 268 | 0 | 0 | 15 | 268 | 51 | 0 | 0 | 66 | 268 | 0 | 0
|  |  |  | High | 0 | 481 | 0 | 7 | 0 | 488 | 0 | 488 | 0 | 0 | 0 | 488 | 0 | 481 | 0 | 0 | 7 | 488 | 0 | 7 | 481 | 0 | 0 | 488 | 0 | 0 | 481 | 0 | 7 | 488 | RI5 | RI4 | RI3 | RI2 | RI1 | Sleeves (Nitrogen & other) | Asset Level | Sleeves (Nitrogen & other)Asset Level | 0 | 7 | 0 | 481 | 0 | 0 | 0 | 0 | 488 | 0 | 7 | 0 | 0 | 481 | 0 | 0 | 0 | 481 | 7 | 0 | 7 | 0 | 481 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Sleeves (Nitrogen & other) | Asset Level | Sleeves (Nitrogen & other)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
8 | LTS Pipelines - Piggable | Asset Level | Km | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | LTS Pipelines - Piggable | Asset Level | LTS Pipelines - PiggableAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.8 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 9.48 | 331.82 | 144.1 | 0 | 0 | 485.4 | 34.08 | 316.82 | 154.1 | 5 | 0 | 510 | 9.48 | 316.82 | 154.1 | 5 | 0 | 485.4 | 34.08 | 312 | 154.1 | 9.82 | 0 | 510 | 9.48 | 312 | 154.1 | 9.82 | 0 | 485.4 | RI5 | RI4 | RI3 | RI2 | RI2 | LTS Pipelines - Piggable | Asset Level | LTS Pipelines - PiggableAsset Level | 0 | 0 | 144.1 | 331.82 | 9.48 | 0 | 5 | 154.1 | 316.82 | 34.08 | 0 | 5 | 154.1 | 316.82 | 9.48 | 0 | 9.82 | 154.1 | 312 | 34.08 | 0 | 9.82 | 154.1 | 312 | 9.48
|  |  |  | High | 0 | 478.09 | 0 | 10.38 | 0 | 488.47 | 0 | 462.59 | 15.5 | 10.38 | 0 | 488.47 | 0 | 462.59 | 15.5 | 10.38 | 0 | 488.47 | 0 | 459.59 | 18.5 | 10.38 | 0 | 488.47 | 0 | 459.59 | 18.5 | 10.38 | 0 | 488.47 | RI5 | RI4 | RI3 | RI2 | RI1 | LTS Pipelines - Piggable | Asset Level | LTS Pipelines - PiggableAsset Level | 0 | 10.38 | 0 | 478.09 | 0 | 0 | 10.38 | 15.5 | 462.59 | 0 | 0 | 10.38 | 15.5 | 462.59 | 0 | 0 | 10.38 | 18.5 | 459.59 | 0 | 0 | 10.38 | 18.5 | 459.59 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | LTS Pipelines - Piggable | Asset Level | LTS Pipelines - PiggableAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
9 | LTS Pipelines – Non Piggable | Asset Level | Km | Low | 114.98 | 66.19 | 33.39 | 37.67 | 0 | 252.23 | 114.98 | 66.19 | 23.39 | 47.67 | 0 | 252.23 | 114.98 | 66.19 | 23.39 | 47.67 | 0 | 252.23 | 114.98 | 60.19 | 23.39 | 53.67 | 0 | 252.23 | 114.98 | 60.19 | 23.39 | 53.67 | 0 | 252.23 | RI5 | RI5 | RI4 | RI3 | RI2 | LTS Pipelines – Non Piggable | Asset Level | LTS Pipelines – Non PiggableAsset Level | 0 | 0 | 37.67 | 33.39 | 181.17 | 0 | 0 | 47.67 | 23.39 | 181.17 | 0 | 0 | 47.67 | 23.39 | 181.17 | 0 | 0 | 53.67 | 23.39 | 175.17 | 0 | 0 | 53.67 | 23.39 | 175.17
|  |  |  | Medium | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 65.73 | 0 | 5.01 | 0 | 82.81 | 12.07 | 41.73 | 24 | 5.01 | 0 | 82.81 | 12.07 | 41.73 | 24 | 5.01 | 0 | 82.81 | RI5 | RI4 | RI3 | RI2 | RI2 | LTS Pipelines – Non Piggable | Asset Level | LTS Pipelines – Non PiggableAsset Level | 0 | 5.01 | 0 | 65.73 | 12.07 | 0 | 5.01 | 0 | 65.73 | 12.07 | 0 | 5.01 | 0 | 65.73 | 12.07 | 0 | 5.01 | 24 | 41.73 | 12.07 | 0 | 5.01 | 24 | 41.73 | 12.07
|  |  |  | High | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | 4.96 | 11.16 | 0 | 0 | 0 | 16.12 | RI5 | RI4 | RI3 | RI2 | RI1 | LTS Pipelines – Non Piggable | Asset Level | LTS Pipelines – Non PiggableAsset Level | 0 | 0 | 0 | 11.16 | 4.96 | 0 | 0 | 0 | 11.16 | 4.96 | 0 | 0 | 0 | 11.16 | 4.96 | 0 | 0 | 0 | 11.16 | 4.96 | 0 | 0 | 0 | 11.16 | 4.96
|  |  |  | Very High | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | RI4 | RI3 | RI2 | RI1 | RI1 | LTS Pipelines – Non Piggable | Asset Level | LTS Pipelines – Non PiggableAsset Level | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 0 | 0 | 0 | 0 | 1.8 | 0
10 | Cathodic Protection | Asset Level | Number of Schemes | Low | 75 | 258 | 284 | 93 | 0 | 710 | 85 | 273 | 305 | 83 | 0 | 746 | 70 | 241 | 284 | 105 | 46 | 746 | 100 | 253 | 314 | 72 | 12 | 751 | 48 | 235 | 284 | 120 | 64 | 751 | RI5 | RI5 | RI4 | RI3 | RI2 | Cathodic Protection | Asset Level | Cathodic ProtectionAsset Level | 0 | 0 | 93 | 284 | 333 | 0 | 0 | 83 | 305 | 358 | 0 | 46 | 105 | 284 | 311 | 0 | 12 | 72 | 314 | 353 | 0 | 64 | 120 | 284 | 283
|  |  |  | Medium | 31 | 136 | 109 | 45 | 0 | 321 | 47 | 150 | 124 | 32 | 0 | 353 | 26 | 120 | 109 | 75 | 23 | 353 | 52 | 150 | 121 | 32 | 10 | 365 | 23 | 110 | 109 | 92 | 31 | 365 | RI5 | RI4 | RI3 | RI2 | RI2 | Cathodic Protection | Asset Level | Cathodic ProtectionAsset Level | 0 | 45 | 109 | 136 | 31 | 0 | 32 | 124 | 150 | 47 | 0 | 98 | 109 | 120 | 26 | 0 | 42 | 121 | 150 | 52 | 0 | 123 | 109 | 110 | 23
|  |  |  | High | 6 | 163 | 58 | 18 | 0 | 245 | 19 | 162 | 50 | 8 | 0 | 239 | 5 | 142 | 58 | 25 | 9 | 239 | 10 | 161 | 60 | 10 | 3 | 244 | 3 | 134 | 58 | 37 | 12 | 244 | RI5 | RI4 | RI3 | RI2 | RI1 | Cathodic Protection | Asset Level | Cathodic ProtectionAsset Level | 0 | 18 | 58 | 163 | 6 | 0 | 8 | 50 | 162 | 19 | 9 | 25 | 58 | 142 | 5 | 3 | 10 | 60 | 161 | 10 | 12 | 37 | 58 | 134 | 3
|  |  |  | Very High | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | RI4 | RI3 | RI2 | RI1 | RI1 | Cathodic Protection | Asset Level | Cathodic ProtectionAsset Level | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0
11 | Above7 bar Special Crossings | Asset Level | Number of | Low | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | 0 | 0 | 0 | 10 | 0 | 10 | RI5 | RI5 | RI4 | RI3 | RI2 | Above7 bar Special Crossings | Asset Level | Above7 bar Special CrossingsAsset Level | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 10 | 0 | 0
|  |  |  | Medium | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 42 | 0 | 3 | 0 | 46 | 1 | 0 | 42 | 3 | 0 | 46 | 1 | 0 | 42 | 3 | 0 | 46 | RI5 | RI4 | RI3 | RI2 | RI2 | Above7 bar Special Crossings | Asset Level | Above7 bar Special CrossingsAsset Level | 0 | 3 | 0 | 42 | 1 | 0 | 3 | 0 | 42 | 1 | 0 | 3 | 0 | 42 | 1 | 0 | 3 | 42 | 0 | 1 | 0 | 3 | 42 | 0 | 1
|  |  |  | High | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 32 | 6 | 1 | 0 | 39 | 0 | 0 | 32 | 7 | 0 | 39 | 0 | 0 | 32 | 7 | 0 | 39 | RI5 | RI4 | RI3 | RI2 | RI1 | Above7 bar Special Crossings | Asset Level | Above7 bar Special CrossingsAsset Level | 0 | 1 | 6 | 32 | 0 | 0 | 1 | 6 | 32 | 0 | 0 | 1 | 6 | 32 | 0 | 0 | 7 | 32 | 0 | 0 | 0 | 7 | 32 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Above7 bar Special Crossings | Asset Level | Above7 bar Special CrossingsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | Below7 bar Special Crossings | Asset Level | Number of | Low | 46 | 0 | 49 | 77 | 0 | 172 | 46 | 0 | 49 | 77 | 0 | 172 | 23 | 23 | 25 | 63 | 38 | 172 | 46 | 0 | 49 | 77 | 0 | 172 | 0 | 46 | 0 | 49 | 77 | 172 | RI5 | RI5 | RI4 | RI3 | RI2 | Below7 bar Special Crossings | Asset Level | Below7 bar Special CrossingsAsset Level | 0 | 0 | 77 | 49 | 46 | 0 | 0 | 77 | 49 | 46 | 0 | 38 | 63 | 25 | 46 | 0 | 0 | 77 | 49 | 46 | 0 | 77 | 49 | 0 | 46
|  |  |  | Medium | 147 | 0 | 145 | 85 | 0 | 377 | 147 | 0 | 145 | 85 | 0 | 377 | 74 | 73 | 73 | 115 | 42 | 377 | 147 | 0 | 145 | 85 | 0 | 377 | 0 | 147 | 0 | 145 | 85 | 377 | RI5 | RI4 | RI3 | RI2 | RI2 | Below7 bar Special Crossings | Asset Level | Below7 bar Special CrossingsAsset Level | 0 | 85 | 145 | 0 | 147 | 0 | 85 | 145 | 0 | 147 | 0 | 157 | 73 | 73 | 74 | 0 | 85 | 145 | 0 | 147 | 0 | 230 | 0 | 147 | 0
|  |  |  | High | 24 | 0 | 183 | 0 | 0 | 207 | 24 | 0 | 183 | 0 | 0 | 207 | 12 | 12 | 92 | 91 | 0 | 207 | 24 | 0 | 183 | 0 | 0 | 207 | 0 | 24 | 0 | 183 | 0 | 207 | RI5 | RI4 | RI3 | RI2 | RI1 | Below7 bar Special Crossings | Asset Level | Below7 bar Special CrossingsAsset Level | 0 | 0 | 183 | 0 | 24 | 0 | 0 | 183 | 0 | 24 | 0 | 91 | 92 | 12 | 12 | 0 | 0 | 183 | 0 | 24 | 0 | 183 | 0 | 24 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Below7 bar Special Crossings | Asset Level | Below7 bar Special CrossingsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | Distribution Mains (Iron) | Asset Level | Km | Low | 0 | 0 | 0.65895 | 3645.4722 | 1444.7625 | 5090.8936 | 0 | 0 | 0.54852 | 3034.2743 | 1202.6483 | 4237.4711 | 0 | 0 | 0.65895 | 3646.3302 | 1443.9044 | 5090.8936 | 0 | 0 | 0.4381 | 2423.0763 | 960.5342 | 3384.0486 | 0 | 0 | 0.65895 | 3647.1883 | 1443.0464 | 5090.8936 | RI5 | RI5 | RI4 | RI3 | RI2 | Distribution Mains (Iron) | Asset Level | Distribution Mains (Iron)Asset Level | 0 | 1444.7625 | 3645.4722 | 0.65895 | 0 | 0 | 1202.6483 | 3034.2743 | 0.54852 | 0 | 0 | 1443.9044 | 3646.3302 | 0.65895 | 0 | 0 | 960.5342 | 2423.0763 | 0.4381 | 0 | 0 | 1443.0464 | 3647.1883 | 0.65895 | 0
|  |  |  | Medium | 0 | 0 | 0.051 | 387.7529 | 97.4847 | 485.2886 | 0 | 0 | 0.042453 | 322.2415 | 81.1481 | 403.4321 | 0 | 0 | 0.051 | 389.3389 | 95.8987 | 485.2886 | 0 | 0 | 0.033907 | 256.7301 | 64.8116 | 321.5756 | 0 | 0 | 0.051 | 390.9249 | 94.3127 | 485.2886 | RI5 | RI4 | RI3 | RI2 | RI2 | Distribution Mains (Iron) | Asset Level | Distribution Mains (Iron)Asset Level | 0 | 485.2376 | 0.051 | 0 | 0 | 0 | 403.3896 | 0.042453 | 0 | 0 | 0 | 485.2376 | 0.051 | 0 | 0 | 0 | 321.5417 | 0.033907 | 0 | 0 | 0 | 485.2376 | 0.051 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Distribution Mains (Iron) | Asset Level | Distribution Mains (Iron)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Distribution Mains (Iron) | Asset Level | Distribution Mains (Iron)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | Distribution Mains (PE) | Asset Level | Km | Low | 12822.6282 | 5.0716 | 0 | 0 | 0 | 12827.6998 | 14065.2372 | 5.0716 | 0 | 0 | 0 | 14070.3088 | 12822.7977 | 4.9021 | 0 | 0 | 0 | 12827.6998 | 15307.8462 | 5.0716 | 0 | 0 | 0 | 15312.9178 | 12822.9672 | 4.7326 | 0 | 0 | 0 | 12827.6998 | RI5 | RI5 | RI4 | RI3 | RI2 | Distribution Mains (PE) | Asset Level | Distribution Mains (PE)Asset Level | 0 | 0 | 0 | 0 | 12827.6998 | 0 | 0 | 0 | 0 | 14070.3088 | 0 | 0 | 0 | 0 | 12827.6998 | 0 | 0 | 0 | 0 | 15312.9178 | 0 | 0 | 0 | 0 | 12827.6998
|  |  |  | Medium | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2896.4846 | 1.7815 | 0 | 0 | 0 | 2898.2661 | 2895.7099 | 2.5562 | 0 | 0 | 0 | 2898.2661 | 2897.2593 | 1.0068 | 0 | 0 | 0 | 2898.2661 | RI5 | RI4 | RI3 | RI2 | RI2 | Distribution Mains (PE) | Asset Level | Distribution Mains (PE)Asset Level | 0 | 0 | 0 | 2.5562 | 2895.7099 | 0 | 0 | 0 | 2.5562 | 2895.7099 | 0 | 0 | 0 | 1.7815 | 2896.4846 | 0 | 0 | 0 | 2.5562 | 2895.7099 | 0 | 0 | 0 | 1.0068 | 2897.2593
|  |  |  | High | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 227.0409 | -0.12 | 0 | 0 | 0 | 226.9209 | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 227.1609 | -0.24 | 0 | 0 | 0 | 226.9209 | RI5 | RI4 | RI3 | RI2 | RI1 | Distribution Mains (PE) | Asset Level | Distribution Mains (PE)Asset Level | 0 | 0 | 0 | 0 | 226.9209 | 0 | 0 | 0 | 0 | 226.9209 | 0 | 0 | 0 | -0.12 | 227.0409 | 0 | 0 | 0 | 0 | 226.9209 | 0 | 0 | 0 | -0.24 | 227.1609
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Distribution Mains (PE) | Asset Level | Distribution Mains (PE)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | Distribution Mains (Steel) | Asset Level | Km | Low | 0 | 0 | 352.7423 | 192.431 | 54.5418 | 599.7151 | 0 | 0 | 312.6551 | 170.6344 | 48.3639 | 531.6534 | 0 | 0 | 353.3261 | 191.8472 | 54.5418 | 599.7151 | 0 | 0 | 272.5678 | 148.8378 | 42.186 | 463.5916 | 0 | 0 | 353.9099 | 191.2634 | 54.5418 | 599.7151 | RI5 | RI5 | RI4 | RI3 | RI2 | Distribution Mains (Steel) | Asset Level | Distribution Mains (Steel)Asset Level | 0 | 54.5418 | 192.431 | 352.7423 | 0 | 0 | 48.3639 | 170.6344 | 312.6551 | 0 | 0 | 54.5418 | 191.8472 | 353.3261 | 0 | 0 | 42.186 | 148.8378 | 272.5678 | 0 | 0 | 54.5418 | 191.2634 | 353.9099 | 0
|  |  |  | Medium | 0 | 0 | 10.1724 | 179.1802 | 14.032 | 203.3845 | 0 | 0 | 8.1473 | 158.8846 | 12.4426 | 179.4744 | 0 | 0 | 14.0253 | 175.3273 | 14.032 | 203.3845 | 0 | 0 | 6.1222 | 138.5889 | 10.8532 | 155.5643 | 0 | 0 | 17.8783 | 171.4743 | 14.032 | 203.3845 | RI5 | RI4 | RI3 | RI2 | RI2 | Distribution Mains (Steel) | Asset Level | Distribution Mains (Steel)Asset Level | 0 | 193.2122 | 10.1724 | 0 | 0 | 0 | 171.3271 | 8.1473 | 0 | 0 | 0 | 189.3592 | 14.0253 | 0 | 0 | 0 | 149.4421 | 6.1222 | 0 | 0 | 0 | 185.5063 | 17.8783 | 0 | 0
|  |  |  | High | 0 | 0 | 44.7987 | 839.0303 | 13.8193 | 897.6483 | 0 | 0 | 38.4685 | 743.9937 | 12.254 | 794.7162 | 0 | 0 | 50.3423 | 833.4867 | 13.8193 | 897.6483 | 0 | 0 | 32.1383 | 648.957 | 10.6887 | 691.7841 | 0 | 0 | 55.8859 | 827.9431 | 13.8193 | 897.6483 | RI5 | RI4 | RI3 | RI2 | RI1 | Distribution Mains (Steel) | Asset Level | Distribution Mains (Steel)Asset Level | 13.8193 | 839.0303 | 44.7987 | 0 | 0 | 12.254 | 743.9937 | 38.4685 | 0 | 0 | 13.8193 | 833.4867 | 50.3423 | 0 | 0 | 10.6887 | 648.957 | 32.1383 | 0 | 0 | 13.8193 | 827.9431 | 55.8859 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Distribution Mains (Steel) | Asset Level | Distribution Mains (Steel)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
16 | Distribution Mains (other) | Asset Level | Km | Low | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | 0 | 0 | 0.45223 | 0 | 0.62184 | 1.0741 | RI5 | RI5 | RI4 | RI3 | RI2 | Distribution Mains (other) | Asset Level | Distribution Mains (other)Asset Level | 0 | 0.62184 | 0 | 0.45223 | 0 | 0 | 0.62184 | 0 | 0.45223 | 0 | 0 | 0.62184 | 0 | 0.45223 | 0 | 0 | 0.62184 | 0 | 0.45223 | 0 | 0 | 0.62184 | 0 | 0.45223 | 0
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | Distribution Mains (other) | Asset Level | Distribution Mains (other)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Distribution Mains (other) | Asset Level | Distribution Mains (other)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Distribution Mains (other) | Asset Level | Distribution Mains (other)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
17 | Services | Asset Level | Number of | Low | 0 | 760241 | 0 | 1313660 | 0 | 2073901 | 113827 | 760241 | 0 | 1232403 | 0 | 2106471 | 0 | 760241 | 0 | 1313660 | 0 | 2073901 | 225168 | 760241 | 0 | 1153631 | 0 | 2139040 | 0 | 760241 | 0 | 1313660 | 0 | 2073901 | RI5 | RI5 | RI4 | RI3 | RI2 | Services | Asset Level | ServicesAsset Level | 0 | 0 | 1313660 | 0 | 760241 | 0 | 0 | 1232403 | 0 | 874068 | 0 | 0 | 1313660 | 0 | 760241 | 0 | 0 | 1153631 | 0 | 985409 | 0 | 0 | 1313660 | 0 | 760241
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | Services | Asset Level | ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Services | Asset Level | ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Services | Asset Level | ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
18 | MOB Risers | Asset Level | Number of | Low | 1300 | 325 | 0 | 2809 | 2809 | 7243 | 0 | 2941 | 0 | 2060 | 2242 | 7243 | 0 | 1625 | 0 | 2060 | 3558 | 7243 | 0 | 4257 | 0 | 1311 | 1675 | 7243 | 0 | 1625 | 0 | 1311 | 4307 | 7243 | RI5 | RI5 | RI4 | RI3 | RI2 | MOB Risers | Asset Level | MOB RisersAsset Level | 0 | 2809 | 2809 | 0 | 1625 | 0 | 2242 | 2060 | 0 | 2941 | 0 | 3558 | 2060 | 0 | 1625 | 0 | 1675 | 1311 | 0 | 4257 | 0 | 4307 | 1311 | 0 | 1625
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | MOB Risers | Asset Level | MOB RisersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | MOB Risers | Asset Level | MOB RisersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | MOB Risers | Asset Level | MOB RisersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
19 | Operational Holders | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | Operational Holders | Asset Level | Operational HoldersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 1 | 1 | 0 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | 0 | 0 | 1 | 0 | 1 | 2 | RI5 | RI4 | RI3 | RI2 | RI2 | Operational Holders | Asset Level | Operational HoldersAsset Level | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 1 | 1 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Operational Holders | Asset Level | Operational HoldersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Operational Holders | Asset Level | Operational HoldersAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 22 | 22 | 0 | 0 | 0 | 0 | 11 | 11 | 0 | 0 | 0 | 0 | 22 | 22 | RI5 | RI5 | RI4 | RI3 | RI2 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Non Operational Holders (Mothballed & Decommissioned)Asset Level | 0 | 22 | 0 | 0 | 0 | 0 | 17 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 22 | 0 | 0 | 0
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Non Operational Holders (Mothballed & Decommissioned)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Non Operational Holders (Mothballed & Decommissioned)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Non Operational Holders (Mothballed & Decommissioned)Asset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
21 | High Pressure Vessels | Asset Level | Number of | Low | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | 0 | 5 | 1 | 0 | 0 | 6 | RI5 | RI5 | RI4 | RI3 | RI2 | High Pressure Vessels | Asset Level | High Pressure VesselsAsset Level | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 1 | 5 | 0 | 0 | 0 | 1 | 5
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | High Pressure Vessels | Asset Level | High Pressure VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | High Pressure Vessels | Asset Level | High Pressure VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | High Pressure Vessels | Asset Level | High Pressure VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
22 | NTS Offtakes | Asset Level | no | Low | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Asset Level | NTS OfftakesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Regulators System | NTS OfftakesRegulators System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Slam Shut System | NTS OfftakesSlam Shut System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Filter System | NTS OfftakesFilter System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Pre-heating System | NTS OfftakesPre-heating System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Odorisation System | NTS OfftakesOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Metering System | NTS OfftakesMetering System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Buildings (no.’s) | NTS OfftakesBuildings (no.’s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Fences (no’s -Inc Security) | NTS OfftakesFences (no’s -Inc Security) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Electrical System | NTS OfftakesElectrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | NTS Offtakes | Instrumentation System | NTS OfftakesInstrumentation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | Medium | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Asset Level | NTS OfftakesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Regulators System | NTS OfftakesRegulators System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Slam Shut System | NTS OfftakesSlam Shut System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Filter System | NTS OfftakesFilter System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Pre-heating System | NTS OfftakesPre-heating System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Odorisation System | NTS OfftakesOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Metering System | NTS OfftakesMetering System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Buildings (no.’s) | NTS OfftakesBuildings (no.’s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Fences (no’s -Inc Security) | NTS OfftakesFences (no’s -Inc Security) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Electrical System | NTS OfftakesElectrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | NTS Offtakes | Instrumentation System | NTS OfftakesInstrumentation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | High | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5 | [5 empty] | 5 | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Asset Level | NTS OfftakesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 1 | 2 | 0 | 1 | 1 |  | 0 | 1 | 2 | 1 | 1 |  | 0 | 1 | 2 | 1 | 1 |  | 1 | 1 | 1 | 2 | 0 |  | 0 | 1 | 1 | 2 | 1 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Regulators System | NTS OfftakesRegulators System | 1 | 1 | 0 | 2 | 1 | 1 | 1 | 2 | 1 | 0 | 1 | 1 | 2 | 1 | 0 | 0 | 2 | 1 | 1 | 1 | 1 | 2 | 1 | 1 | 0
|  | Slam Shut System | System |  | 0 | 3 | 2 | 0 | 0 |  | 0 | 1 | 3 | 1 | 0 |  | 0 | 1 | 3 | 1 | 0 |  | 1 | 1 | 2 | 1 | 0 |  | 0 | 1 | 2 | 2 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Slam Shut System | NTS OfftakesSlam Shut System | 0 | 0 | 2 | 3 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 1 | 3 | 1 | 0 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 0
|  | Filter System | System |  | 1 | 2 | 2 | 0 | 0 |  | 0 | 2 | 2 | 1 | 0 |  | 0 | 2 | 2 | 1 | 0 |  | 1 | 1 | 2 | 1 | 0 |  | 0 | 1 | 2 | 2 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Filter System | NTS OfftakesFilter System | 0 | 0 | 2 | 2 | 1 | 0 | 1 | 2 | 2 | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 1 | 2 | 1 | 1 | 0 | 2 | 2 | 1 | 0
|  | Pre-heating System | System |  | 2 | 1 | 0 | 0 | 2 |  | 0 | 3 | 0 | 0 | 2 |  | 0 | 3 | 0 | 0 | 2 |  | 2 | 1 | 2 | 0 | 0 |  | 0 | 1 | 2 | 0 | 2 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Pre-heating System | NTS OfftakesPre-heating System | 2 | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 3 | 0 | 0 | 0 | 2 | 1 | 2 | 2 | 0 | 2 | 1 | 0
|  | Odorisation System | System |  | 4 | 0 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 1 | 3 | 0 | 0 | 0 |  | 0 | 4 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Odorisation System | NTS OfftakesOdorisation System | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 3 | 1 | 0 | 0 | 0 | 4 | 0
|  | Metering System | System |  | 3 | 2 | 0 | 0 | 0 |  | 2 | 2 | 1 | 0 | 0 |  | 2 | 2 | 1 | 0 | 0 |  | 1 | 2 | 2 | 0 | 0 |  | 1 | 2 | 2 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Metering System | NTS OfftakesMetering System | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 1 | 2 | 2 | 0 | 0 | 2 | 2 | 1 | 0 | 0 | 2 | 2 | 1
|  | Buildings (no.’s) | Number of |  | 0 | 2 | 0 | 2 | 1 |  | 0 | 1 | 2 | 0 | 2 |  | 0 | 1 | 2 | 0 | 2 |  | 0 | 0 | 2 | 3 | 0 |  | 0 | 0 | 2 | 3 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Buildings (no.’s) | NTS OfftakesBuildings (no.’s) | 1 | 2 | 0 | 2 | 0 | 2 | 0 | 2 | 1 | 0 | 2 | 0 | 2 | 1 | 0 | 0 | 3 | 2 | 0 | 0 | 0 | 3 | 2 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 4 | 1 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | 0 | 1 | 4 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Fences (no’s -Inc Security) | NTS OfftakesFences (no’s -Inc Security) | 0 | 0 | 1 | 4 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 4 | 1 | 0 | 0 | 0 | 4 | 1 | 0
|  | Electrical System | Systems |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 0 | 5 | 0 | 0 |  | 0 | 0 | 5 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | NTS Offtakes | Electrical System | NTS OfftakesElectrical System | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 5 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 5 | 0 |  | 0 | 1 | 0 | 4 | 0 |  | 0 | 0 | 0 | 5 | 0 |  | 0 | 2 | 0 | 3 | 0 |  | 0 | 0 | 0 | 5 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Instrumentation System | NTS OfftakesInstrumentation System | 5 | 0 | 0 | 0 | 0 | 4 | 0 | 1 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 3 | 0 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 0
|  | Asset Level | no | Very High | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13 | [5 empty] | 13 | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Asset Level | NTS OfftakesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 4 | 1 | 2 | 2 | 2 |  | 4 | 3 | 2 | 2 | 0 |  | 2 | 3 | 2 | 2 | 2 |  | 4 | 3 | 2 | 2 | 0 |  | 1 | 3 | 2 | 3 | 2 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Regulators System | NTS OfftakesRegulators System | 4 | 2 | 1 | 4 | 0 | 2 | 2 | 3 | 4 | 0 | 4 | 2 | 3 | 2 | 0 | 2 | 2 | 3 | 4 | 0 | 5 | 2 | 3 | 1 | 0
|  | Slam Shut System | System |  | 3 | 3 | 0 | 2 | 1 |  | 4 | 4 | 0 | 1 | 0 |  | 2 | 4 | 0 | 1 | 2 |  | 3 | 3 | 2 | 1 | 0 |  | 1 | 3 | 2 | 1 | 2 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Slam Shut System | NTS OfftakesSlam Shut System | 3 | 0 | 3 | 3 | 0 | 1 | 0 | 4 | 4 | 0 | 3 | 0 | 4 | 2 | 0 | 1 | 2 | 3 | 3 | 0 | 3 | 2 | 3 | 1 | 0
|  | Filter System | System |  | 8 | 2 | 0 | 3 | 0 |  | 7 | 3 | 1 | 2 | 0 |  | 6 | 3 | 1 | 3 | 0 |  | 6 | 4 | 2 | 1 | 0 |  | 4 | 4 | 2 | 2 | 1 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Filter System | NTS OfftakesFilter System | 3 | 0 | 2 | 8 | 0 | 2 | 1 | 3 | 7 | 0 | 3 | 1 | 3 | 6 | 0 | 1 | 2 | 4 | 6 | 0 | 3 | 2 | 4 | 4 | 0
|  | Pre-heating System | System |  | 5 | 2 | 2 | 1 | 1 |  | 7 | 2 | 1 | 1 | 0 |  | 4 | 2 | 1 | 3 | 1 |  | 6 | 4 | 1 | 0 | 0 |  | 2 | 4 | 1 | 3 | 1 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Pre-heating System | NTS OfftakesPre-heating System | 2 | 2 | 2 | 5 | 0 | 1 | 1 | 2 | 7 | 0 | 4 | 1 | 2 | 4 | 0 | 0 | 1 | 4 | 6 | 0 | 4 | 1 | 4 | 2 | 0
|  | Odorisation System | System |  | 12 | 1 | 0 | 0 | 0 |  | 4 | 9 | 0 | 0 | 0 |  | 3 | 10 | 0 | 0 | 0 |  | 3 | 10 | 0 | 0 | 0 |  | 2 | 11 | 0 | 0 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Odorisation System | NTS OfftakesOdorisation System | 0 | 0 | 1 | 12 | 0 | 0 | 0 | 9 | 4 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 0 | 10 | 3 | 0 | 0 | 0 | 11 | 2 | 0
|  | Metering System | System |  | 3 | 1 | 0 | 8 | 0 |  | 5 | 2 | 0 | 5 | 0 |  | 2 | 2 | 0 | 8 | 0 |  | 9 | 1 | 1 | 1 | 0 |  | 2 | 1 | 1 | 4 | 4 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Metering System | NTS OfftakesMetering System | 8 | 0 | 1 | 3 | 0 | 5 | 0 | 2 | 5 | 0 | 8 | 0 | 2 | 2 | 0 | 1 | 1 | 1 | 9 | 0 | 8 | 1 | 1 | 2 | 0
|  | Buildings (no.’s) | Number of |  | 2 | 2 | 4 | 4 | 0 |  | 2 | 3 | 1 | 5 | 1 |  | 1 | 3 | 1 | 5 | 2 |  | 3 | 2 | 2 | 4 | 0 |  | 1 | 2 | 2 | 5 | 1 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Buildings (no.’s) | NTS OfftakesBuildings (no.’s) | 4 | 4 | 2 | 2 | 0 | 6 | 1 | 3 | 2 | 0 | 7 | 1 | 3 | 1 | 0 | 4 | 2 | 2 | 3 | 0 | 6 | 2 | 2 | 1 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 1 | 4 | 5 | 2 | 0 |  | 2 | 3 | 5 | 2 | 0 |  | 1 | 3 | 5 | 2 | 1 |  | 3 | 3 | 3 | 3 | 0 |  | 1 | 3 | 3 | 4 | 1 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Fences (no’s -Inc Security) | NTS OfftakesFences (no’s -Inc Security) | 2 | 5 | 4 | 1 | 0 | 2 | 5 | 3 | 2 | 0 | 3 | 5 | 3 | 1 | 0 | 3 | 3 | 3 | 3 | 0 | 5 | 3 | 3 | 1 | 0
|  | Electrical System | Systems |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 13 | 0 | 0 | 0 |  | 1 | 2 | 11 | 0 | 0 |  | 1 | 0 | 13 | 0 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Electrical System | NTS OfftakesElectrical System | 0 | 0 | 13 | 1 | 0 | 0 | 0 | 13 | 1 | 0 | 0 | 0 | 13 | 1 | 0 | 0 | 11 | 2 | 1 | 0 | 0 | 13 | 0 | 1 | 0
|  | Instrumentation System | Systems |  | 1 | 0 | 0 | 10 | 0 |  | 1 | 1 | 0 | 9 | 0 |  | 1 | 0 | 0 | 10 | 0 |  | 1 | 2 | 0 | 8 | 0 |  | 1 | 0 | 0 | 10 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | NTS Offtakes | Instrumentation System | NTS OfftakesInstrumentation System | 10 | 0 | 0 | 1 | 0 | 9 | 0 | 1 | 1 | 0 | 10 | 0 | 0 | 1 | 0 | 8 | 0 | 2 | 1 | 0 | 10 | 0 | 0 | 1 | 0
23 | PRSs | Asset Level | no | Low | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Asset Level | PRSsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Regulators System | PRSsRegulators System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Slam Shut System | PRSsSlam Shut System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Filter System | PRSsFilter System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Pre-heating System | PRSsPre-heating System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Odorisation System | PRSsOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Metering System | PRSsMetering System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Buildings (no.’s) | PRSsBuildings (no.’s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Fences (no’s -Inc Security) | PRSsFences (no’s -Inc Security) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Electrical System | PRSsElectrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI5 | RI4 | RI3 | RI2 | PRSs | Instrumentation System | PRSsInstrumentation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | Medium | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | [5 empty] | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Asset Level | PRSsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Regulators System | PRSsRegulators System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Slam Shut System | PRSsSlam Shut System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Filter System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Filter System | PRSsFilter System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Pre-heating System | PRSsPre-heating System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Odorisation System | PRSsOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Metering System | PRSsMetering System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Buildings (no.’s) | PRSsBuildings (no.’s) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Fences (no’s -Inc Security) | PRSsFences (no’s -Inc Security) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Electrical System | PRSsElectrical System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI2 | PRSs | Instrumentation System | PRSsInstrumentation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Asset Level | no | High | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53 | [5 empty] | 53 | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Asset Level | PRSsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 1 | 8 | 33 | 8 | 3 |  | 2 | 3 | 34 | 12 | 2 |  | 1 | 3 | 34 | 12 | 3 |  | 2 | 4 | 10 | 36 | 1 |  | 0 | 4 | 10 | 36 | 3 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Regulators System | PRSsRegulators System | 3 | 8 | 33 | 8 | 1 | 2 | 12 | 34 | 3 | 2 | 3 | 12 | 34 | 3 | 1 | 1 | 36 | 10 | 4 | 2 | 3 | 36 | 10 | 4 | 0
|  | Slam Shut System | System |  | 0 | 17 | 15 | 2 | 19 |  | 1 | 9 | 21 | 4 | 18 |  | 0 | 9 | 21 | 4 | 19 |  | 2 | 5 | 14 | 15 | 17 |  | 0 | 5 | 14 | 15 | 19 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Slam Shut System | PRSsSlam Shut System | 19 | 2 | 15 | 17 | 0 | 18 | 4 | 21 | 9 | 1 | 19 | 4 | 21 | 9 | 0 | 17 | 15 | 14 | 5 | 2 | 19 | 15 | 14 | 5 | 0
|  | Filter System | System |  | 3 | 42 | 7 | 1 | 0 |  | 5 | 28 | 20 | 0 | 0 |  | 3 | 28 | 21 | 1 | 0 |  | 3 | 8 | 40 | 1 | 0 |  | 1 | 8 | 41 | 3 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Filter System | PRSsFilter System | 0 | 1 | 7 | 42 | 3 | 0 | 0 | 20 | 28 | 5 | 0 | 1 | 21 | 28 | 3 | 0 | 1 | 40 | 8 | 3 | 0 | 3 | 41 | 8 | 1
|  | Pre-heating System | System |  | 1 | 7 | 17 | 7 | 3 |  | 3 | 6 | 10 | 16 | 0 |  | 0 | 6 | 10 | 16 | 3 |  | 5 | 3 | 9 | 18 | 0 |  | 0 | 3 | 9 | 19 | 4 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Pre-heating System | PRSsPre-heating System | 3 | 7 | 17 | 7 | 1 | 0 | 16 | 10 | 6 | 3 | 3 | 16 | 10 | 6 | 0 | 0 | 18 | 9 | 3 | 5 | 4 | 19 | 9 | 3 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Odorisation System | PRSsOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Metering System | PRSsMetering System | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 0 | 18 | 21 | 11 | 0 |  | 1 | 5 | 19 | 22 | 3 |  | 0 | 5 | 19 | 22 | 4 |  | 3 | 3 | 20 | 23 | 2 |  | 1 | 3 | 20 | 23 | 4 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Buildings (no.’s) | PRSsBuildings (no.’s) | 0 | 11 | 21 | 18 | 0 | 3 | 22 | 19 | 5 | 1 | 4 | 22 | 19 | 5 | 0 | 2 | 23 | 20 | 3 | 3 | 4 | 23 | 20 | 3 | 1
|  | Fences (no’s -Inc Security) | Number of |  | 3 | 27 | 19 | 1 | 1 |  | 2 | 16 | 30 | 3 | 0 |  | 1 | 16 | 30 | 3 | 1 |  | 4 | 10 | 30 | 7 | 0 |  | 1 | 10 | 30 | 9 | 1 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Fences (no’s -Inc Security) | PRSsFences (no’s -Inc Security) | 1 | 1 | 19 | 27 | 3 | 0 | 3 | 30 | 16 | 2 | 1 | 3 | 30 | 16 | 1 | 0 | 7 | 30 | 10 | 4 | 1 | 9 | 30 | 10 | 1
|  | Electrical System | Systems |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 53 | 0 | 0 | 0 |  | 0 | 0 | 52 | 0 | 0 |  | 0 | 0 | 53 | 0 | 0 |  | RI5 | RI4 | RI3 | RI2 | RI1 | PRSs | Electrical System | PRSsElectrical System | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 0 | 0 | 52 | 0 | 0 | 0 | 0 | 53 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 23 | 30 | 0 |  | 0 | 1 | 0 | 52 | 0 |  | 0 | 0 | 0 | 53 | 0 |  | 0 | 1 | 0 | 53 | 0 |  | 0 | 0 | 0 | 53 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Instrumentation System | PRSsInstrumentation System | 30 | 23 | 0 | 0 | 0 | 52 | 0 | 1 | 0 | 0 | 53 | 0 | 0 | 0 | 0 | 53 | 0 | 1 | 0 | 0 | 53 | 0 | 0 | 0 | 0
|  | Asset Level | no | Very High | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91 | [5 empty] | 91 | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Asset Level | PRSsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Regulators System | System |  | 10 | 18 | 31 | 20 | 12 |  | 17 | 13 | 30 | 30 | 1 |  | 6 | 13 | 30 | 30 | 12 |  | 20 | 14 | 12 | 45 | 0 |  | 3 | 14 | 12 | 50 | 12 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Regulators System | PRSsRegulators System | 32 | 31 | 18 | 10 | 0 | 31 | 30 | 13 | 17 | 0 | 42 | 30 | 13 | 6 | 0 | 45 | 12 | 14 | 20 | 0 | 62 | 12 | 14 | 3 | 0
|  | Slam Shut System | System |  | 8 | 17 | 12 | 1 | 53 |  | 18 | 15 | 10 | 6 | 42 |  | 7 | 15 | 10 | 6 | 53 |  | 23 | 12 | 8 | 12 | 36 |  | 6 | 12 | 8 | 12 | 53 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Slam Shut System | PRSsSlam Shut System | 54 | 12 | 17 | 8 | 0 | 48 | 10 | 15 | 18 | 0 | 59 | 10 | 15 | 7 | 0 | 48 | 8 | 12 | 23 | 0 | 65 | 8 | 12 | 6 | 0
|  | Filter System | System |  | 8 | 67 | 8 | 1 | 0 |  | 18 | 43 | 23 | 0 | 0 |  | 7 | 43 | 32 | 2 | 0 |  | 21 | 14 | 49 | 0 | 0 |  | 4 | 14 | 62 | 4 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Filter System | PRSsFilter System | 1 | 8 | 67 | 8 | 0 | 0 | 23 | 43 | 18 | 0 | 2 | 32 | 43 | 7 | 0 | 0 | 49 | 14 | 21 | 0 | 4 | 62 | 14 | 4 | 0
|  | Pre-heating System | System |  | 13 | 19 | 23 | 18 | 6 |  | 23 | 17 | 13 | 26 | 0 |  | 8 | 17 | 13 | 35 | 6 |  | 31 | 18 | 15 | 15 | 0 |  | 2 | 18 | 15 | 38 | 6 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Pre-heating System | PRSsPre-heating System | 24 | 23 | 19 | 13 | 0 | 26 | 13 | 17 | 23 | 0 | 41 | 13 | 17 | 8 | 0 | 15 | 15 | 18 | 31 | 0 | 44 | 15 | 18 | 2 | 0
|  | Odorisation System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Odorisation System | PRSsOdorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | System |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Metering System | PRSsMetering System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | Number of |  | 5 | 18 | 22 | 29 | 3 |  | 15 | 13 | 15 | 31 | 3 |  | 4 | 13 | 15 | 35 | 10 |  | 21 | 11 | 15 | 23 | 7 |  | 4 | 11 | 15 | 23 | 24 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Buildings (no.’s) | PRSsBuildings (no.’s) | 32 | 22 | 18 | 5 | 0 | 34 | 15 | 13 | 15 | 0 | 45 | 15 | 13 | 4 | 0 | 30 | 15 | 11 | 21 | 0 | 47 | 15 | 11 | 4 | 0
|  | Fences (no’s -Inc Security) | Number of |  | 8 | 26 | 29 | 14 | 0 |  | 14 | 21 | 27 | 15 | 0 |  | 4 | 21 | 27 | 24 | 1 |  | 15 | 12 | 25 | 25 | 0 |  | 4 | 12 | 25 | 35 | 1 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Fences (no’s -Inc Security) | PRSsFences (no’s -Inc Security) | 14 | 29 | 26 | 8 | 0 | 15 | 27 | 21 | 14 | 0 | 25 | 27 | 21 | 4 | 0 | 25 | 25 | 12 | 15 | 0 | 36 | 25 | 12 | 4 | 0
|  | Electrical System | Systems |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 79 | 0 | 0 | 0 |  | 0 | 14 | 65 | 0 | 0 |  | 0 | 0 | 79 | 0 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Electrical System | PRSsElectrical System | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 79 | 0 | 0 | 0 | 65 | 14 | 0 | 0 | 0 | 79 | 0 | 0 | 0
|  | Instrumentation System | Systems |  | 0 | 0 | 9 | 70 | 0 |  | 0 | 11 | 0 | 68 | 0 |  | 0 | 0 | 0 | 79 | 0 |  | 0 | 14 | 0 | 65 | 0 |  | 0 | 0 | 0 | 79 | 0 |  | RI4 | RI3 | RI2 | RI1 | RI1 | PRSs | Instrumentation System | PRSsInstrumentation System | 70 | 9 | 0 | 0 | 0 | 68 | 0 | 11 | 0 | 0 | 79 | 0 | 0 | 0 | 0 | 65 | 0 | 14 | 0 | 0 | 79 | 0 | 0 | 0 | 0
22 | District Governors | Asset Level | Number of | Low | 31 | 1176 | 42 | 427 | 39 | 1715 | 35 | 1208 | 42 | 0 | 434 | 1719 | 31 | 1176 | 42 | 0 | 466 | 1715 | 39 | 93 | 1176 | 42 | 373 | 1723 | 31 | 0 | 1176 | 42 | 466 | 1715 | RI5 | RI5 | RI4 | RI3 | RI2 | District Governors | Asset Level | District GovernorsAsset Level | 0 | 39 | 427 | 42 | 1207 | 0 | 434 | 0 | 42 | 1243 | 0 | 466 | 0 | 42 | 1207 | 0 | 373 | 42 | 1176 | 132 | 0 | 466 | 42 | 1176 | 31
|  |  |  | Medium | 20 | 416 | 11 | 10 | 19 | 476 | 23 | 445 | 11 | 0 | 0 | 479 | 20 | 416 | 11 | 0 | 29 | 476 | 26 | 29 | 416 | 11 | 0 | 482 | 20 | 0 | 416 | 11 | 29 | 476 | RI5 | RI4 | RI3 | RI2 | RI2 | District Governors | Asset Level | District GovernorsAsset Level | 0 | 29 | 11 | 416 | 20 | 0 | 0 | 11 | 445 | 23 | 0 | 29 | 11 | 416 | 20 | 0 | 11 | 416 | 29 | 26 | 0 | 40 | 416 | 0 | 20
|  |  |  | High | 0 | 4 | 1 | 0 | 2 | 7 | 0 | 6 | 1 | 0 | 0 | 7 | 0 | 4 | 1 | 0 | 2 | 7 | 0 | 2 | 4 | 1 | 0 | 7 | 0 | 0 | 4 | 1 | 2 | 7 | RI5 | RI4 | RI3 | RI2 | RI1 | District Governors | Asset Level | District GovernorsAsset Level | 2 | 0 | 1 | 4 | 0 | 0 | 0 | 1 | 6 | 0 | 2 | 0 | 1 | 4 | 0 | 0 | 1 | 4 | 2 | 0 | 2 | 1 | 4 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | District Governors | Asset Level | District GovernorsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
24 | I&C Governors | Asset Level | Number of | Low | 0 | 200 | 0 | 7 | 6 | 213 | 0 | 203 | 0 | 0 | 10 | 213 | 0 | 200 | 0 | 0 | 13 | 213 | 0 | 5 | 200 | 0 | 8 | 213 | 0 | 0 | 200 | 0 | 13 | 213 | RI5 | RI5 | RI4 | RI3 | RI2 | I&C Governors | Asset Level | I&C GovernorsAsset Level | 0 | 6 | 7 | 0 | 200 | 0 | 10 | 0 | 0 | 203 | 0 | 13 | 0 | 0 | 200 | 0 | 8 | 0 | 200 | 5 | 0 | 13 | 0 | 200 | 0
|  |  |  | Medium | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | RI5 | RI4 | RI3 | RI2 | RI2 | I&C Governors | Asset Level | I&C GovernorsAsset Level | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | I&C Governors | Asset Level | I&C GovernorsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | I&C Governors | Asset Level | I&C GovernorsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
25 | Service Governors | Asset Level | Number of | Low | 1224 | 459 | 0 | 1060 | 765 | 3508 | 1224 | 1071 | 0 | 448 | 765 | 3508 | 612 | 1071 | 0 | 448 | 1377 | 3508 | 1224 | 1224 | 0 | 295 | 765 | 3508 | 0 | 1224 | 0 | 295 | 1989 | 3508 | RI5 | RI5 | RI4 | RI3 | RI2 | Service Governors | Asset Level | Service GovernorsAsset Level | 0 | 765 | 1060 | 0 | 1683 | 0 | 765 | 448 | 0 | 2295 | 0 | 1377 | 448 | 0 | 1683 | 0 | 765 | 295 | 0 | 2448 | 0 | 1989 | 295 | 0 | 1224
|  |  |  | Medium | 96 | 36 | 0 | 83 | 60 | 275 | 96 | 84 | 0 | 35 | 60 | 275 | 48 | 84 | 0 | 35 | 108 | 275 | 96 | 96 | 0 | 23 | 60 | 275 | 0 | 96 | 0 | 23 | 156 | 275 | RI5 | RI4 | RI3 | RI2 | RI2 | Service Governors | Asset Level | Service GovernorsAsset Level | 0 | 143 | 0 | 36 | 96 | 0 | 95 | 0 | 84 | 96 | 0 | 143 | 0 | 84 | 48 | 0 | 83 | 0 | 96 | 96 | 0 | 179 | 0 | 96 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | Service Governors | Asset Level | Service GovernorsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | Service Governors | Asset Level | Service GovernorsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
26 | LPG Storage | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | LPG Storage | Asset Level | LPG StorageAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 2 | 1 | 0 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 3 | 0 | 0 | 2 | 1 | 0 | 3 | RI5 | RI4 | RI3 | RI2 | RI2 | LPG Storage | Asset Level | LPG StorageAsset Level | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 1 | 2 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | LPG Storage | Asset Level | LPG StorageAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | LPG Storage | Asset Level | LPG StorageAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
27 | LPG Mains | Asset Level | Km | Low | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.9898 | RI5 | RI5 | RI4 | RI3 | RI2 | LPG Mains | Asset Level | LPG MainsAsset Level | 0 | 0 | 0.367 | 0 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.6228 | 0 | 0 | 0.367 | 0 | 20.6228
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | LPG Mains | Asset Level | LPG MainsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | LPG Mains | Asset Level | LPG MainsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | LPG Mains | Asset Level | LPG MainsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
28 | LPG Services | Asset Level | Number of | Low | 0 | 846 | 0 | 930 | 0 | 1776 | 80 | 846 | 0 | 872 | 0 | 1798 | 0 | 846 | 0 | 930 | 0 | 1776 | 159 | 846 | 0 | 817 | 0 | 1822 | 0 | 846 | 0 | 930 | 0 | 1776 | RI5 | RI5 | RI4 | RI3 | RI2 | LPG Services | Asset Level | LPG ServicesAsset Level | 0 | 0 | 930 | 0 | 846 | 0 | 0 | 872 | 0 | 926 | 0 | 0 | 930 | 0 | 846 | 0 | 0 | 817 | 0 | 1005 | 0 | 0 | 930 | 0 | 846
|  |  |  | Medium | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI2 | LPG Services | Asset Level | LPG ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | LPG Services | Asset Level | LPG ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | LPG Services | Asset Level | LPG ServicesAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
29 | LNG Vessels | Asset Level | Number of | Low | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI5 | RI4 | RI3 | RI2 | LNG Vessels | Asset Level | LNG VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Medium | 0 | 2 | 18 | 0 | 0 | 20 | 0 | 2 | 14 | 4 | 0 | 20 | 0 | 2 | 14 | 4 | 0 | 20 | 0 | 2 | 9 | 9 | 0 | 20 | 0 | 2 | 9 | 9 | 0 | 20 | RI5 | RI4 | RI3 | RI2 | RI2 | LNG Vessels | Asset Level | LNG VesselsAsset Level | 0 | 0 | 18 | 2 | 0 | 0 | 4 | 14 | 2 | 0 | 0 | 4 | 14 | 2 | 0 | 0 | 9 | 9 | 2 | 0 | 0 | 9 | 9 | 2 | 0
|  |  |  | High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI5 | RI4 | RI3 | RI2 | RI1 | LNG Vessels | Asset Level | LNG VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Very High | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | RI4 | RI3 | RI2 | RI1 | RI1 | LNG Vessels | Asset Level | LNG VesselsAsset Level | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | 19253.1717 | 766750.6179 | 2100.3655 | 1325068.2936 | 5475.262 | 2118647.7108 | 133228.3807 | 770106.1179 | 2034.3041 | 1241107.4554 | 4970.4787 | 2151446.7368 | 17131.2359 | 768647.0537 | 1901.8459 | 1323507.7573 | 7521.818 | 2118709.7108 | 245952.7897 | 768626.2978 | 4674.7427 | 1160848.4371 | 4079.6954 | 2184181.9628 | 16311.3001 | 765783.1695 | 4401.8262 | 1323179.041 | 9056.3739 | 2118731.7108 | [8 empty] | 429.8193 | 7322.7962 | 1324344.0622 | 3753.3997 | 782797.6333 | 431.254 | 6554.7345 | 1240592.2039 | 3859.7021 | 900008.8423 | 547.8193 | 9442.5416 | 1322398.233 | 3694.5888 | 782626.528 | 422.6887 | 5766.4928 | 1161465.8456 | 3748.6844 | 1012778.2513 | 595.8193 | 11501.107 | 1322555.9038 | 3521.4579 | 780557.4227
[68 empty] | Start | Mid W | Min WO | End W | End WO | Max | Start | Mid W | Min WO | End W | End WO
1 | Storage Telemetry | Asset Level |  |  | 0 | 0 | 0 | 5 | 0 |  | 1 | 0 | 0 | 0 | 4 |  | 0 | 0 | 0 | 0 | 5 |  | 0 | 1 | 0 | 0 | 4 |  | 0 | 0 | 0 | 0 | 5 | [34 empty] | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0
2 | Above7 bar Telemetry | Asset Level |  |  | 0 | 0 | 23 | 118 | 0 |  | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 141 | 0 |  | 0 | 0 | 0 | 141 | 0 | [34 empty] | 141 | 141 | 141 | 141 | 141 | 141 | 0 | 0 | 0 | 0 | 0
3 | Below7 bar Telemetry | Asset Level |  |  | 0 | 0 | 6 | 0 | 4 |  | 0 | 0 | 3 | 3 | 4 |  | 0 | 0 | 3 | 3 | 4 |  | 0 | 0 | 0 | 6 | 4 |  | 0 | 0 | 0 | 6 | 4 | [34 empty] | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0
4 | Block Valves | Asset Level |  |  | 0 | 4 | 10 | 1 | 1 |  | 0 | 1 | 4 | 10 | 1 |  | 0 | 1 | 4 | 10 | 1 |  | 0 | 1 | 3 | 11 | 1 |  | 0 | 1 | 3 | 11 | 1 | [34 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
5 | Valves | Asset Level |  |  | 19 | 183 | 188 | 59 | 15 |  | 19 | 243 | 188 | 14 | 0 |  | 19 | 183 | 188 | 59 | 15 |  | 19 | 120 | 183 | 142 | 0 |  | 19 | 0 | 183 | 247 | 15 | [34 empty] | 464 | 464 | 464 | 464 | 464 | 464 | 0 | 0 | 0 | 0 | 0
6 | Pig Traps | Asset Level |  |  | 1 | 16 | 5 | 0 | 0 |  | 7 | 16 | 5 | 0 | 0 |  | 1 | 16 | 5 | 0 | 0 |  | 11 | 0 | 16 | 5 | 0 |  | 1 | 0 | 16 | 5 | 0 | [34 empty] | 22 | 28 | 22 | 32 | 22 | 32 | 10 | 4 | 10 | 0 | 10
7 | Sleeves (Nitrogen & other) | Asset Level |  |  | 11 | 772 | 86 | 15 | 0 |  | 11 | 801 | 72 | 0 | 0 |  | 11 | 772 | 86 | 0 | 15 |  | 11 | 58 | 772 | 43 | 0 |  | 11 | 0 | 772 | 86 | 15 | [34 empty] | 884 | 884 | 884 | 884 | 884 | 884 | 0 | 0 | 0 | 0 | 0
8 | LTS Pipelines - Piggable | Asset Level |  |  | 9.48 | 809.91 | 144.1 | 10.38 | 0 |  | 34.08 | 779.41 | 169.6 | 15.38 | 0 |  | 9.48 | 779.41 | 169.6 | 15.38 | 0 |  | 37.88 | 771.59 | 172.6 | 20.2 | 0 |  | 9.48 | 771.59 | 172.6 | 20.2 | 0 | [34 empty] | 973.87 | 998.47 | 973.87 | 1002.27 | 973.87 | 1002.27 | 28.4 | 3.8 | 28.4 | 0 | 28.4
9 | LTS Pipelines – Non Piggable | Asset Level |  |  | 133.81 | 143.08 | 33.39 | 42.68 | 0 |  | 133.81 | 143.08 | 23.39 | 52.68 | 0 |  | 133.81 | 143.08 | 23.39 | 52.68 | 0 |  | 133.81 | 113.08 | 47.39 | 58.68 | 0 |  | 133.81 | 113.08 | 47.39 | 58.68 | 0 | [34 empty] | 352.96 | 352.96 | 352.96 | 352.96 | 352.96 | 352.96 | 0 | 0 | 0 | 0 | 0
10 | Cathodic Protection | Asset Level |  |  | 113 | 557 | 451 | 156 | 0 |  | 152 | 585 | 479 | 123 | 0 |  | 102 | 503 | 451 | 205 | 78 |  | 162 | 565 | 495 | 114 | 25 |  | 74 | 480 | 451 | 249 | 107 | [34 empty] | 1277 | 1339 | 1339 | 1361 | 1361 | 1361 | 84 | 22 | 22 | 0 | 0
11 | Above7 bar Special Crossings | Asset Level |  |  | 1 | 74 | 6 | 14 | 0 |  | 1 | 74 | 6 | 14 | 0 |  | 1 | 74 | 6 | 14 | 0 |  | 1 | 0 | 74 | 20 | 0 |  | 1 | 0 | 74 | 20 | 0 | [34 empty] | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 0 | 0 | 0 | 0
12 | Below7 bar Special Crossings | Asset Level |  |  | 217 | 0 | 377 | 162 | 0 |  | 217 | 0 | 377 | 162 | 0 |  | 109 | 108 | 190 | 269 | 80 |  | 217 | 0 | 377 | 162 | 0 |  | 0 | 217 | 0 | 377 | 162 | [34 empty] | 756 | 756 | 756 | 756 | 756 | 756 | 0 | 0 | 0 | 0 | 0
13 | Distribution Mains (Iron) | Asset Level |  |  | 0 | 0 | 0.70995 | 4033.2251 | 1542.2471 |  | 0 | 0 | 0.59098 | 3356.5158 | 1283.7965 |  | 0 | 0 | 0.70995 | 4035.6692 | 1539.8031 |  | 0 | 0 | 0.472 | 2679.8064 | 1025.3458 |  | 0 | 0 | 0.70995 | 4038.1132 | 1537.359 | [34 empty] | 5576.1822 | 4640.9032 | 5576.1822 | 3705.6242 | 5576.1822 | 5576.1822 | 0 | 935.279 | 0 | 1870.558 | 0
14 | Distribution Mains (PE) | Asset Level |  |  | 15945.2589 | 7.6278 | 0 | 0 | 0 |  | 17187.8679 | 7.6278 | 0 | 0 | 0 |  | 15946.3231 | 6.5636 | 0 | 0 | 0 |  | 18430.4769 | 7.6278 | 0 | 0 | 0 |  | 15947.3873 | 5.4994 | 0 | 0 | 0 | [34 empty] | 15952.8868 | 17195.4958 | 15952.8868 | 18438.1048 | 15952.8868 | 18438.1048 | 2485.218 | 1242.609 | 2485.218 | 0 | 2485.218
15 | Distribution Mains (Steel) | Asset Level |  |  | 0 | 0 | 407.7134 | 1210.6415 | 82.3931 |  | 0 | 0 | 359.2709 | 1073.5126 | 73.0604 |  | 0 | 0 | 417.6937 | 1200.6612 | 82.3931 |  | 0 | 0 | 310.8284 | 936.3837 | 63.7278 |  | 0 | 0 | 427.6741 | 1190.6808 | 82.3931 | [34 empty] | 1700.7479 | 1505.8439 | 1700.7479 | 1310.9399 | 1700.7479 | 1700.7479 | 0 | 194.904 | 0 | 389.808 | 0
16 | Distribution Mains (other) | Asset Level |  |  | 0 | 0 | 0.45223 | 0 | 0.62184 |  | 0 | 0 | 0.45223 | 0 | 0.62184 |  | 0 | 0 | 0.45223 | 0 | 0.62184 |  | 0 | 0 | 0.45223 | 0 | 0.62184 |  | 0 | 0 | 0.45223 | 0 | 0.62184 | [34 empty] | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 0 | 0 | 0 | 0 | 0
17 | Services | Asset Level |  |  | 0 | 760241 | 0 | 1313660 | 0 |  | 113827 | 760241 | 0 | 1232403 | 0 |  | 0 | 760241 | 0 | 1313660 | 0 |  | 225168 | 760241 | 0 | 1153631 | 0 |  | 0 | 760241 | 0 | 1313660 | 0 | [34 empty] | 2073901 | 2106471 | 2073901 | 2139040 | 2073901 | 2139040 | 65139 | 32569 | 65139 | 0 | 65139
18 | MOB Risers | Asset Level |  |  | 1300 | 325 | 0 | 2809 | 2809 |  | 0 | 2941 | 0 | 2060 | 2242 |  | 0 | 1625 | 0 | 2060 | 3558 |  | 0 | 4257 | 0 | 1311 | 1675 |  | 0 | 1625 | 0 | 1311 | 4307 | [34 empty] | 7243 | 7243 | 7243 | 7243 | 7243 | 7243 | 0 | 0 | 0 | 0 | 0
19 | Operational Holders | Asset Level |  |  | 0 | 0 | 1 | 1 | 0 |  | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 1 | 0 | 1 |  | 0 | 0 | 1 | 0 | 1 | [34 empty] | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level |  |  | 0 | 0 | 0 | 0 | 22 |  | 0 | 0 | 0 | 0 | 17 |  | 0 | 0 | 0 | 0 | 22 |  | 0 | 0 | 0 | 0 | 11 |  | 0 | 0 | 0 | 0 | 22 | [34 empty] | 22 | 17 | 22 | 11 | 22 | 22 | 0 | 5 | 0 | 11 | 0
21 | High Pressure Vessels | Asset Level |  |  | 0 | 5 | 1 | 0 | 0 |  | 0 | 5 | 1 | 0 | 0 |  | 0 | 5 | 1 | 0 | 0 |  | 0 | 5 | 1 | 0 | 0 |  | 0 | 5 | 1 | 0 | 0 | [34 empty] | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0
22 | NTS Offtakes | Regulators System |  |  | 5 | 3 | 2 | 3 | 3 |  | 4 | 4 | 4 | 3 | 1 |  | 2 | 4 | 4 | 3 | 3 |  | 5 | 4 | 3 | 4 | 0 |  | 1 | 4 | 3 | 5 | 3 | [34 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System |  |  | 3 | 6 | 2 | 2 | 1 |  | 4 | 5 | 3 | 2 | 0 |  | 2 | 5 | 3 | 2 | 2 |  | 4 | 4 | 4 | 2 | 0 |  | 1 | 4 | 4 | 3 | 2 | [34 empty] | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0
|  | Filter System |  |  | 9 | 4 | 2 | 3 | 0 |  | 7 | 5 | 3 | 3 | 0 |  | 6 | 5 | 3 | 4 | 0 |  | 7 | 5 | 4 | 2 | 0 |  | 4 | 5 | 4 | 4 | 1 | [34 empty] | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System |  |  | 7 | 3 | 2 | 1 | 3 |  | 7 | 5 | 1 | 1 | 2 |  | 4 | 5 | 1 | 3 | 3 |  | 8 | 5 | 3 | 0 | 0 |  | 2 | 5 | 3 | 3 | 3 | [34 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System |  |  | 16 | 1 | 0 | 0 | 0 |  | 5 | 12 | 0 | 0 | 0 |  | 4 | 13 | 0 | 0 | 0 |  | 4 | 13 | 0 | 0 | 0 |  | 2 | 15 | 0 | 0 | 0 | [34 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Metering System |  |  | 6 | 3 | 0 | 8 | 0 |  | 7 | 4 | 1 | 5 | 0 |  | 4 | 4 | 1 | 8 | 0 |  | 10 | 3 | 3 | 1 | 0 |  | 3 | 3 | 3 | 4 | 4 | [34 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) |  |  | 2 | 4 | 4 | 6 | 1 |  | 2 | 4 | 3 | 5 | 3 |  | 1 | 4 | 3 | 5 | 4 |  | 3 | 2 | 4 | 7 | 0 |  | 1 | 2 | 4 | 8 | 1 | [34 empty] | 17 | 17 | 17 | 16 | 16 | 17 | 0 | 0 | 0 | 1 | 1
|  | Fences (no’s -Inc Security) |  |  | 1 | 8 | 6 | 2 | 0 |  | 2 | 4 | 9 | 2 | 0 |  | 1 | 4 | 9 | 2 | 1 |  | 3 | 4 | 7 | 3 | 0 |  | 1 | 4 | 7 | 4 | 1 | [34 empty] | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Electrical System |  |  | 1 | 18 | 0 | 0 | 0 |  | 1 | 18 | 0 | 0 | 0 |  | 1 | 18 | 0 | 0 | 0 |  | 1 | 2 | 16 | 0 | 0 |  | 1 | 0 | 18 | 0 | 0 | [34 empty] | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System |  |  | 1 | 0 | 0 | 15 | 0 |  | 1 | 2 | 0 | 13 | 0 |  | 1 | 0 | 0 | 15 | 0 |  | 1 | 4 | 0 | 11 | 0 |  | 1 | 0 | 0 | 15 | 0 | [34 empty] | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
23 | PRSs | Regulators System |  |  | 11 | 26 | 64 | 28 | 15 |  | 19 | 16 | 64 | 42 | 3 |  | 7 | 16 | 64 | 42 | 15 |  | 22 | 18 | 22 | 81 | 1 |  | 3 | 18 | 22 | 86 | 15 | [34 empty] | 144 | 144 | 144 | 144 | 144 | 144 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System |  |  | 8 | 34 | 27 | 3 | 72 |  | 19 | 24 | 31 | 10 | 60 |  | 7 | 24 | 31 | 10 | 72 |  | 25 | 17 | 22 | 27 | 53 |  | 6 | 17 | 22 | 27 | 72 | [34 empty] | 144 | 144 | 144 | 144 | 144 | 144 | 0 | 0 | 0 | 0 | 0
|  | Filter System |  |  | 11 | 109 | 15 | 2 | 0 |  | 23 | 71 | 43 | 0 | 0 |  | 10 | 71 | 53 | 3 | 0 |  | 24 | 22 | 89 | 1 | 0 |  | 5 | 22 | 103 | 7 | 0 | [34 empty] | 137 | 137 | 137 | 136 | 137 | 137 | 0 | 0 | 0 | 1 | 0
|  | Pre-heating System |  |  | 14 | 26 | 40 | 25 | 9 |  | 26 | 23 | 23 | 42 | 0 |  | 8 | 23 | 23 | 51 | 9 |  | 36 | 21 | 24 | 33 | 0 |  | 2 | 21 | 24 | 57 | 10 | [34 empty] | 114 | 114 | 114 | 114 | 114 | 114 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [34 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System |  |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 0 | 0 | 0 | 1 | 0 |  | 1 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 1 | 0 | [34 empty] | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) |  |  | 5 | 36 | 43 | 40 | 3 |  | 16 | 18 | 34 | 53 | 6 |  | 4 | 18 | 34 | 57 | 14 |  | 24 | 14 | 35 | 46 | 9 |  | 5 | 14 | 35 | 46 | 28 | [34 empty] | 127 | 127 | 127 | 128 | 128 | 128 | 1 | 1 | 1 | 0 | 0
|  | Fences (no’s -Inc Security) |  |  | 11 | 53 | 48 | 15 | 1 |  | 16 | 37 | 57 | 18 | 0 |  | 5 | 37 | 57 | 27 | 2 |  | 19 | 22 | 55 | 32 | 0 |  | 5 | 22 | 55 | 44 | 2 | [34 empty] | 128 | 128 | 128 | 128 | 128 | 128 | 0 | 0 | 0 | 0 | 0
|  | Electrical System |  |  | 0 | 132 | 0 | 0 | 0 |  | 0 | 132 | 0 | 0 | 0 |  | 0 | 132 | 0 | 0 | 0 |  | 0 | 14 | 117 | 0 | 0 |  | 0 | 0 | 132 | 0 | 0 | [34 empty] | 132 | 132 | 132 | 131 | 132 | 132 | 0 | 0 | 0 | 1 | 0
|  | Instrumentation System |  |  | 0 | 0 | 32 | 100 | 0 |  | 0 | 12 | 0 | 120 | 0 |  | 0 | 0 | 0 | 132 | 0 |  | 0 | 15 | 0 | 118 | 0 |  | 0 | 0 | 0 | 132 | 0 | [34 empty] | 132 | 132 | 132 | 133 | 132 | 133 | 1 | 1 | 1 | 0 | 1
22 | District Governors | Asset Level |  |  | 51 | 1596 | 54 | 437 | 60 |  | 58 | 1659 | 54 | 0 | 434 |  | 51 | 1596 | 54 | 0 | 497 |  | 65 | 124 | 1596 | 54 | 373 |  | 51 | 0 | 1596 | 54 | 497 | [34 empty] | 2198 | 2205 | 2198 | 2212 | 2198 | 2212 | 14 | 7 | 14 | 0 | 14
24 | I&C Governors | Asset Level |  |  | 0 | 206 | 0 | 7 | 6 |  | 0 | 209 | 0 | 0 | 10 |  | 0 | 206 | 0 | 0 | 13 |  | 0 | 5 | 206 | 0 | 8 |  | 0 | 0 | 206 | 0 | 13 | [34 empty] | 219 | 219 | 219 | 219 | 219 | 219 | 0 | 0 | 0 | 0 | 0
25 | Service Governors | Asset Level |  |  | 1320 | 495 | 0 | 1143 | 825 |  | 1320 | 1155 | 0 | 483 | 825 |  | 660 | 1155 | 0 | 483 | 1485 |  | 1320 | 1320 | 0 | 318 | 825 |  | 0 | 1320 | 0 | 318 | 2145 | [34 empty] | 3783 | 3783 | 3783 | 3783 | 3783 | 3783 | 0 | 0 | 0 | 0 | 0
26 | LPG Storage | Asset Level |  |  | 0 | 2 | 1 | 0 | 0 |  | 0 | 2 | 1 | 0 | 0 |  | 0 | 2 | 1 | 0 | 0 |  | 0 | 0 | 2 | 1 | 0 |  | 0 | 0 | 2 | 1 | 0 | [34 empty] | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 0
27 | LPG Mains | Asset Level |  |  | 20.6228 | 0 | 0 | 0.367 | 0 |  | 20.6228 | 0 | 0 | 0.367 | 0 |  | 20.6228 | 0 | 0 | 0.367 | 0 |  | 20.6228 | 0 | 0 | 0.367 | 0 |  | 20.6228 | 0 | 0 | 0.367 | 0 | [34 empty] | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 0 | 0 | 0 | 0 | 0
28 | LPG Services | Asset Level |  |  | 0 | 846 | 0 | 930 | 0 |  | 80 | 846 | 0 | 872 | 0 |  | 0 | 846 | 0 | 930 | 0 |  | 159 | 846 | 0 | 817 | 0 |  | 0 | 846 | 0 | 930 | 0 | [34 empty] | 1776 | 1798 | 1776 | 1822 | 1776 | 1822 | 46 | 24 | 46 | 0 | 46
29 | LNG Vessels | Asset Level |  |  | 0 | 2 | 18 | 0 | 0 |  | 0 | 2 | 14 | 4 | 0 |  | 0 | 2 | 14 | 4 | 0 |  | 0 | 2 | 9 | 9 | 0 |  | 0 | 2 | 9 | 9 | 0 | [34 empty] | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0
[5 empty] | 19253.1717 | 766750.6179 | 2100.3655 | 1325068.2936 | 5475.262 |  | 133228.3807 | 770106.1179 | 2034.3041 | 1241107.4554 | 4970.4787 |  | 17131.2359 | 768647.0537 | 1901.8459 | 1323507.7573 | 7521.818 |  | 245952.7897 | 768626.2978 | 4674.7427 | 1160848.4371 | 4079.6954 |  | 16311.3001 | 765783.1695 | 4401.8262 | 1323179.041 | 9056.3739
[5 empty] | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK |  | OK | OK | OK | OK | OK
1 | Storage Telemetry | Asset Level |  |  | 0% | 0% | 0% | 100% | 0% |  | 20% | 0% | 0% | 0% | 80% |  | 0% | 0% | 0% | 0% | 100% |  | 0% | 20% | 0% | 0% | 80% |  | 0% | 0% | 0% | 0% | 100% | [40 empty] | 0% | 0% | 0% | 0% | 0%
2 | Above7 bar Telemetry | Asset Level |  |  | 0% | 0% | 16.31% | 83.69% | 0% |  | 0% | 0% | 0% | 100% | 0% |  | 0% | 0% | 0% | 100% | 0% |  | 0% | 0% | 0% | 100% | 0% |  | 0% | 0% | 0% | 100% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
3 | Below7 bar Telemetry | Asset Level |  |  | 0% | 0% | 60% | 0% | 40% |  | 0% | 0% | 30% | 30% | 40% |  | 0% | 0% | 30% | 30% | 40% |  | 0% | 0% | 0% | 60% | 40% |  | 0% | 0% | 0% | 60% | 40% | [40 empty] | 0% | 0% | 0% | 0% | 0%
4 | Block Valves | Asset Level |  |  | 0% | 25% | 62.5% | 6.25% | 6.25% |  | 0% | 6.25% | 25% | 62.5% | 6.25% |  | 0% | 6.25% | 25% | 62.5% | 6.25% |  | 0% | 6.25% | 18.75% | 68.75% | 6.25% |  | 0% | 6.25% | 18.75% | 68.75% | 6.25% | [40 empty] | 0% | 0% | 0% | 0% | 0%
5 | Valves | Asset Level |  |  | 4.095% | 39.44% | 40.52% | 12.72% | 3.233% |  | 4.095% | 52.37% | 40.52% | 3.017% | 0% |  | 4.095% | 39.44% | 40.52% | 12.72% | 3.233% |  | 4.095% | 25.86% | 39.44% | 30.6% | 0% |  | 4.095% | 0% | 39.44% | 53.23% | 3.233% | [40 empty] | 0% | 0% | 0% | 0% | 0%
6 | Pig Traps | Asset Level |  |  | 3.125% | 50% | 15.62% | 0% | 0% |  | 21.88% | 50% | 15.62% | 0% | 0% |  | 3.125% | 50% | 15.62% | 0% | 0% |  | 34.38% | 0% | 50% | 15.62% | 0% |  | 3.125% | 0% | 50% | 15.62% | 0% | [40 empty] | 31.25% | 12.5% | 31.25% | 0% | 31.25%
7 | Sleeves (Nitrogen & other) | Asset Level |  |  | 1.244% | 87.33% | 9.729% | 1.697% | 0% |  | 1.244% | 90.61% | 8.145% | 0% | 0% |  | 1.244% | 87.33% | 9.729% | 0% | 1.697% |  | 1.244% | 6.561% | 87.33% | 4.864% | 0% |  | 1.244% | 0% | 87.33% | 9.729% | 1.697% | [40 empty] | 0% | 0% | 0% | 0% | 0%
8 | LTS Pipelines - Piggable | Asset Level |  |  | 0.9459% | 80.81% | 14.38% | 1.036% | 0% |  | 3.4% | 77.76% | 16.92% | 1.535% | 0% |  | 0.9459% | 77.76% | 16.92% | 1.535% | 0% |  | 3.779% | 76.98% | 17.22% | 2.015% | 0% |  | 0.9459% | 76.98% | 17.22% | 2.015% | 0% | [40 empty] | 2.834% | 0.3791% | 2.834% | 0% | 2.834%
9 | LTS Pipelines – Non Piggable | Asset Level |  |  | 37.91% | 40.54% | 9.46% | 12.09% | 0% |  | 37.91% | 40.54% | 6.627% | 14.93% | 0% |  | 37.91% | 40.54% | 6.627% | 14.93% | 0% |  | 37.91% | 32.04% | 13.43% | 16.63% | 0% |  | 37.91% | 32.04% | 13.43% | 16.63% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
10 | Cathodic Protection | Asset Level |  |  | 8.303% | 40.93% | 33.14% | 11.46% | 0% |  | 11.17% | 42.98% | 35.19% | 9.037% | 0% |  | 7.494% | 36.96% | 33.14% | 15.06% | 5.731% |  | 11.9% | 41.51% | 36.37% | 8.376% | 1.837% |  | 5.437% | 35.27% | 33.14% | 18.3% | 7.862% | [40 empty] | 6.172% | 1.616% | 1.616% | 0% | 0%
11 | Above7 bar Special Crossings | Asset Level |  |  | 1.053% | 77.89% | 6.316% | 14.74% | 0% |  | 1.053% | 77.89% | 6.316% | 14.74% | 0% |  | 1.053% | 77.89% | 6.316% | 14.74% | 0% |  | 1.053% | 0% | 77.89% | 21.05% | 0% |  | 1.053% | 0% | 77.89% | 21.05% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
12 | Below7 bar Special Crossings | Asset Level |  |  | 28.7% | 0% | 49.87% | 21.43% | 0% |  | 28.7% | 0% | 49.87% | 21.43% | 0% |  | 14.42% | 14.29% | 25.13% | 35.58% | 10.58% |  | 28.7% | 0% | 49.87% | 21.43% | 0% |  | 0% | 28.7% | 0% | 49.87% | 21.43% | [40 empty] | 0% | 0% | 0% | 0% | 0%
13 | Distribution Mains (Iron) | Asset Level |  |  | 0% | 0% | 0.01273% | 72.33% | 27.66% |  | 0% | 0% | 0.0106% | 60.19% | 23.02% |  | 0% | 0% | 0.01273% | 72.37% | 27.61% |  | 0% | 0% | 0.008465% | 48.06% | 18.39% |  | 0% | 0% | 0.01273% | 72.42% | 27.57% | [40 empty] | 0% | 16.77% | 0% | 33.55% | 0%
14 | Distribution Mains (PE) | Asset Level |  |  | 86.48% | 0.04137% | 0% | 0% | 0% |  | 93.22% | 0.04137% | 0% | 0% | 0% |  | 86.49% | 0.0356% | 0% | 0% | 0% |  | 99.96% | 0.04137% | 0% | 0% | 0% |  | 86.49% | 0.02983% | 0% | 0% | 0% | [40 empty] | 13.48% | 6.739% | 13.48% | 0% | 13.48%
15 | Distribution Mains (Steel) | Asset Level |  |  | 0% | 0% | 23.97% | 71.18% | 4.845% |  | 0% | 0% | 21.12% | 63.12% | 4.296% |  | 0% | 0% | 24.56% | 70.6% | 4.845% |  | 0% | 0% | 18.28% | 55.06% | 3.747% |  | 0% | 0% | 25.15% | 70.01% | 4.845% | [40 empty] | 0% | 11.46% | 0% | 22.92% | 0%
16 | Distribution Mains (other) | Asset Level |  |  | 0% | 0% | 42.1% | 0% | 57.9% |  | 0% | 0% | 42.1% | 0% | 57.9% |  | 0% | 0% | 42.1% | 0% | 57.9% |  | 0% | 0% | 42.1% | 0% | 57.9% |  | 0% | 0% | 42.1% | 0% | 57.9% | [40 empty] | 0% | 0% | 0% | 0% | 0%
17 | Services | Asset Level |  |  | 0% | 35.54% | 0% | 61.41% | 0% |  | 5.321% | 35.54% | 0% | 57.61% | 0% |  | 0% | 35.54% | 0% | 61.41% | 0% |  | 10.53% | 35.54% | 0% | 53.93% | 0% |  | 0% | 35.54% | 0% | 61.41% | 0% | [40 empty] | 3.045% | 1.523% | 3.045% | 0% | 3.045%
18 | MOB Risers | Asset Level |  |  | 17.95% | 4.487% | 0% | 38.78% | 38.78% |  | 0% | 40.6% | 0% | 28.44% | 30.95% |  | 0% | 22.44% | 0% | 28.44% | 49.12% |  | 0% | 58.77% | 0% | 18.1% | 23.13% |  | 0% | 22.44% | 0% | 18.1% | 59.46% | [40 empty] | 0% | 0% | 0% | 0% | 0%
19 | Operational Holders | Asset Level |  |  | 0% | 0% | 50% | 50% | 0% |  | 0% | 0% | 50% | 0% | 50% |  | 0% | 0% | 50% | 0% | 50% |  | 0% | 0% | 50% | 0% | 50% |  | 0% | 0% | 50% | 0% | 50% | [40 empty] | 0% | 0% | 0% | 0% | 0%
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level |  |  | 0% | 0% | 0% | 0% | 100% |  | 0% | 0% | 0% | 0% | 77.27% |  | 0% | 0% | 0% | 0% | 100% |  | 0% | 0% | 0% | 0% | 50% |  | 0% | 0% | 0% | 0% | 100% | [40 empty] | 0% | 22.73% | 0% | 50% | 0%
21 | High Pressure Vessels | Asset Level |  |  | 0% | 83.33% | 16.67% | 0% | 0% |  | 0% | 83.33% | 16.67% | 0% | 0% |  | 0% | 83.33% | 16.67% | 0% | 0% |  | 0% | 83.33% | 16.67% | 0% | 0% |  | 0% | 83.33% | 16.67% | 0% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
22 | NTS Offtakes | Regulators System |  |  | 31.25% | 18.75% | 12.5% | 18.75% | 18.75% |  | 25% | 25% | 25% | 18.75% | 6.25% |  | 12.5% | 25% | 25% | 18.75% | 18.75% |  | 31.25% | 25% | 18.75% | 25% | 0% |  | 6.25% | 25% | 18.75% | 31.25% | 18.75% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Slam Shut System |  |  | 21.43% | 42.86% | 14.29% | 14.29% | 7.143% |  | 28.57% | 35.71% | 21.43% | 14.29% | 0% |  | 14.29% | 35.71% | 21.43% | 14.29% | 14.29% |  | 28.57% | 28.57% | 28.57% | 14.29% | 0% |  | 7.143% | 28.57% | 28.57% | 21.43% | 14.29% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Filter System |  |  | 50% | 22.22% | 11.11% | 16.67% | 0% |  | 38.89% | 27.78% | 16.67% | 16.67% | 0% |  | 33.33% | 27.78% | 16.67% | 22.22% | 0% |  | 38.89% | 27.78% | 22.22% | 11.11% | 0% |  | 22.22% | 27.78% | 22.22% | 22.22% | 5.556% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Pre-heating System |  |  | 43.75% | 18.75% | 12.5% | 6.25% | 18.75% |  | 43.75% | 31.25% | 6.25% | 6.25% | 12.5% |  | 25% | 31.25% | 6.25% | 18.75% | 18.75% |  | 50% | 31.25% | 18.75% | 0% | 0% |  | 12.5% | 31.25% | 18.75% | 18.75% | 18.75% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Odorisation System |  |  | 94.12% | 5.882% | 0% | 0% | 0% |  | 29.41% | 70.59% | 0% | 0% | 0% |  | 23.53% | 76.47% | 0% | 0% | 0% |  | 23.53% | 76.47% | 0% | 0% | 0% |  | 11.76% | 88.24% | 0% | 0% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Metering System |  |  | 35.29% | 17.65% | 0% | 47.06% | 0% |  | 41.18% | 23.53% | 5.882% | 29.41% | 0% |  | 23.53% | 23.53% | 5.882% | 47.06% | 0% |  | 58.82% | 17.65% | 17.65% | 5.882% | 0% |  | 17.65% | 17.65% | 17.65% | 23.53% | 23.53% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Buildings (no.’s) |  |  | 11.76% | 23.53% | 23.53% | 35.29% | 5.882% |  | 11.76% | 23.53% | 17.65% | 29.41% | 17.65% |  | 5.882% | 23.53% | 17.65% | 29.41% | 23.53% |  | 17.65% | 11.76% | 23.53% | 41.18% | 0% |  | 5.882% | 11.76% | 23.53% | 47.06% | 5.882% | [40 empty] | 0% | 0% | 0% | 5.882% | 5.882%
|  | Fences (no’s -Inc Security) |  |  | 5.882% | 47.06% | 35.29% | 11.76% | 0% |  | 11.76% | 23.53% | 52.94% | 11.76% | 0% |  | 5.882% | 23.53% | 52.94% | 11.76% | 5.882% |  | 17.65% | 23.53% | 41.18% | 17.65% | 0% |  | 5.882% | 23.53% | 41.18% | 23.53% | 5.882% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Electrical System |  |  | 5.263% | 94.74% | 0% | 0% | 0% |  | 5.263% | 94.74% | 0% | 0% | 0% |  | 5.263% | 94.74% | 0% | 0% | 0% |  | 5.263% | 10.53% | 84.21% | 0% | 0% |  | 5.263% | 0% | 94.74% | 0% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Instrumentation System |  |  | 6.25% | 0% | 0% | 93.75% | 0% |  | 6.25% | 12.5% | 0% | 81.25% | 0% |  | 6.25% | 0% | 0% | 93.75% | 0% |  | 6.25% | 25% | 0% | 68.75% | 0% |  | 6.25% | 0% | 0% | 93.75% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
23 | PRSs | Regulators System |  |  | 7.639% | 18.06% | 44.44% | 19.44% | 10.42% |  | 13.19% | 11.11% | 44.44% | 29.17% | 2.083% |  | 4.861% | 11.11% | 44.44% | 29.17% | 10.42% |  | 15.28% | 12.5% | 15.28% | 56.25% | 0.6944% |  | 2.083% | 12.5% | 15.28% | 59.72% | 10.42% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Slam Shut System |  |  | 5.556% | 23.61% | 18.75% | 2.083% | 50% |  | 13.19% | 16.67% | 21.53% | 6.944% | 41.67% |  | 4.861% | 16.67% | 21.53% | 6.944% | 50% |  | 17.36% | 11.81% | 15.28% | 18.75% | 36.81% |  | 4.167% | 11.81% | 15.28% | 18.75% | 50% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Filter System |  |  | 8.029% | 79.56% | 10.95% | 1.46% | 0% |  | 16.79% | 51.82% | 31.39% | 0% | 0% |  | 7.299% | 51.82% | 38.69% | 2.19% | 0% |  | 17.52% | 16.06% | 64.96% | 0.7299% | 0% |  | 3.65% | 16.06% | 75.18% | 5.109% | 0% | [40 empty] | 0% | 0% | 0% | 0.7299% | 0%
|  | Pre-heating System |  |  | 12.28% | 22.81% | 35.09% | 21.93% | 7.895% |  | 22.81% | 20.18% | 20.18% | 36.84% | 0% |  | 7.018% | 20.18% | 20.18% | 44.74% | 7.895% |  | 31.58% | 18.42% | 21.05% | 28.95% | 0% |  | 1.754% | 18.42% | 21.05% | 50% | 8.772% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Odorisation System |  |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [40 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Metering System |  |  | 0% | 0% | 0% | 100% | 0% |  | 0% | 0% | 0% | 100% | 0% |  | 0% | 0% | 0% | 100% | 0% |  | 100% | 0% | 0% | 0% | 0% |  | 0% | 0% | 0% | 100% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Buildings (no.’s) |  |  | 3.906% | 28.12% | 33.59% | 31.25% | 2.344% |  | 12.5% | 14.06% | 26.56% | 41.41% | 4.688% |  | 3.125% | 14.06% | 26.56% | 44.53% | 10.94% |  | 18.75% | 10.94% | 27.34% | 35.94% | 7.031% |  | 3.906% | 10.94% | 27.34% | 35.94% | 21.88% | [40 empty] | 0.7812% | 0.7812% | 0.7812% | 0% | 0%
|  | Fences (no’s -Inc Security) |  |  | 8.594% | 41.41% | 37.5% | 11.72% | 0.7812% |  | 12.5% | 28.91% | 44.53% | 14.06% | 0% |  | 3.906% | 28.91% | 44.53% | 21.09% | 1.562% |  | 14.84% | 17.19% | 42.97% | 25% | 0% |  | 3.906% | 17.19% | 42.97% | 34.38% | 1.562% | [40 empty] | 0% | 0% | 0% | 0% | 0%
|  | Electrical System |  |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 10.61% | 88.64% | 0% | 0% |  | 0% | 0% | 100% | 0% | 0% | [40 empty] | 0% | 0% | 0% | 0.7576% | 0%
|  | Instrumentation System |  |  | 0% | 0% | 24.06% | 75.19% | 0% |  | 0% | 9.023% | 0% | 90.23% | 0% |  | 0% | 0% | 0% | 99.25% | 0% |  | 0% | 11.28% | 0% | 88.72% | 0% |  | 0% | 0% | 0% | 99.25% | 0% | [40 empty] | 0.7519% | 0.7519% | 0.7519% | 0% | 0.7519%
22 | District Governors | Asset Level |  |  | 2.306% | 72.15% | 2.441% | 19.76% | 2.712% |  | 2.622% | 75% | 2.441% | 0% | 19.62% |  | 2.306% | 72.15% | 2.441% | 0% | 22.47% |  | 2.939% | 5.606% | 72.15% | 2.441% | 16.86% |  | 2.306% | 0% | 72.15% | 2.441% | 22.47% | [40 empty] | 0.6329% | 0.3165% | 0.6329% | 0% | 0.6329%
24 | I&C Governors | Asset Level |  |  | 0% | 94.06% | 0% | 3.196% | 2.74% |  | 0% | 95.43% | 0% | 0% | 4.566% |  | 0% | 94.06% | 0% | 0% | 5.936% |  | 0% | 2.283% | 94.06% | 0% | 3.653% |  | 0% | 0% | 94.06% | 0% | 5.936% | [40 empty] | 0% | 0% | 0% | 0% | 0%
25 | Service Governors | Asset Level |  |  | 34.89% | 13.08% | 0% | 30.21% | 21.81% |  | 34.89% | 30.53% | 0% | 12.77% | 21.81% |  | 17.45% | 30.53% | 0% | 12.77% | 39.25% |  | 34.89% | 34.89% | 0% | 8.406% | 21.81% |  | 0% | 34.89% | 0% | 8.406% | 56.7% | [40 empty] | 0% | 0% | 0% | 0% | 0%
26 | LPG Storage | Asset Level |  |  | 0% | 66.67% | 33.33% | 0% | 0% |  | 0% | 66.67% | 33.33% | 0% | 0% |  | 0% | 66.67% | 33.33% | 0% | 0% |  | 0% | 0% | 66.67% | 33.33% | 0% |  | 0% | 0% | 66.67% | 33.33% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
27 | LPG Mains | Asset Level |  |  | 98.25% | 0% | 0% | 1.748% | 0% |  | 98.25% | 0% | 0% | 1.748% | 0% |  | 98.25% | 0% | 0% | 1.748% | 0% |  | 98.25% | 0% | 0% | 1.748% | 0% |  | 98.25% | 0% | 0% | 1.748% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%
28 | LPG Services | Asset Level |  |  | 0% | 46.43% | 0% | 51.04% | 0% |  | 4.391% | 46.43% | 0% | 47.86% | 0% |  | 0% | 46.43% | 0% | 51.04% | 0% |  | 8.727% | 46.43% | 0% | 44.84% | 0% |  | 0% | 46.43% | 0% | 51.04% | 0% | [40 empty] | 2.525% | 1.317% | 2.525% | 0% | 2.525%
29 | LNG Vessels | Asset Level |  |  | 0% | 10% | 90% | 0% | 0% |  | 0% | 10% | 70% | 20% | 0% |  | 0% | 10% | 70% | 20% | 0% |  | 0% | 10% | 45% | 45% | 0% |  | 0% | 10% | 45% | 45% | 0% | [40 empty] | 0% | 0% | 0% | 0% | 0%

## 4.3.3 Asset Risk
Asset categories |  | Component | Asset distribution based on estimated asset risk index | [5 empty] | Asset distribution based on estimated asset risk index | [5 empty] | Asset distribution based on estimated asset risk index | [5 empty] | Asset distribution based on estimated asset risk index | [5 empty] | Asset distribution based on estimated asset risk index
|  |  | RIIO-GD1 Starting Position | [5 empty] | Mid RIIO-GD1 With Proposed Investment (50/50 Estimate) | [5 empty] | Mid RIIO-GD1 Without Investment (50/50 Estimate) | [5 empty] | End RIIO-GD1 With Proposed Investment (50/50 Estimate) | [5 empty] | End RIIO-GD1 Without Investment (50/50 Estimate)
|  |  | Asset risk index |  |  |  |  | 2013-03-31 | Asset risk index |  |  |  |  | 2017-03-31 | Asset risk index |  |  |  |  | 2017-03-31 | Asset risk index |  |  |  |  | 2021-03-31 | Asset risk index |  |  |  |  | 2021-03-31
|  |  | RI1 | RI2 | RI3 | RI4 | RI5 |  | RI1 | RI2 | RI3 | RI4 | RI5 |  | RI1 | RI2 | RI3 | RI4 | RI5 |  | RI1 | RI2 | RI3 | RI4 | RI5 |  | RI1 | RI2 | RI3 | RI4 | RI5 | [5 empty] | Start | Mid W | Min WO | End W | End WO | Max | Start | Mid W | Min WO | End W | End WO
1 | Storage Telemetry | Asset Level | 0 | 5 | 0 | 0 | 0 |  | 0 | 4 | 0 | 0 | 1 |  | 0 | 5 | 0 | 0 | 0 |  | 0 | 4 | 0 | 1 | 0 |  | 0 | 5 | 0 | 0 | 0 |  | Storage Telemetry | Asset Level | Storage TelemetryAsset Level | Storage Telemetry | 5 | 5 | 5 | 5 | 5 | 5 | 0 | 0 | 0 | 0 | 0
2 | Above7 bar Telemetry | Asset Level | 83 | 37 | 21 | 0 | 0 |  | 85 | 56 | 0 | 0 | 0 |  | 85 | 56 | 0 | 0 | 0 |  | 85 | 56 | 0 | 0 | 0 |  | 85 | 56 | 0 | 0 | 0 |  | Above7 bar Telemetry | Asset Level | Above7 bar TelemetryAsset Level | Above7 bar Telemetry | 141 | 141 | 141 | 141 | 141 | 141 | 0 | 0 | 0 | 0 | 0
3 | Below7 bar Telemetry | Asset Level | 0 | 4 | 6 | 0 | 0 |  | 0 | 7 | 3 | 0 | 0 |  | 0 | 7 | 3 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 |  | 0 | 10 | 0 | 0 | 0 |  | Below7 bar Telemetry | Asset Level | Below7 bar TelemetryAsset Level | Below7 bar Telemetry | 10 | 10 | 10 | 10 | 10 | 10 | 0 | 0 | 0 | 0 | 0
4 | Block Valves | Asset Level | 0 | 2 | 10 | 4 | 0 |  | 0 | 11 | 4 | 1 | 0 |  | 0 | 11 | 4 | 1 | 0 |  | 0 | 12 | 3 | 1 | 0 |  | 0 | 12 | 3 | 1 | 0 |  | Block Valves | Asset Level | Block ValvesAsset Level | Block Valves | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
5 | Valves | Asset Level | 3 | 57 | 174 | 183 | 47 |  | 0 | 0 | 174 | 235 | 55 |  | 3 | 57 | 174 | 183 | 47 |  | 0 | 100 | 197 | 140 | 27 |  | 3 | 217 | 197 | 28 | 19 |  | Valves | Asset Level | ValvesAsset Level | Valves | 464 | 464 | 464 | 464 | 464 | 464 | 0 | 0 | 0 | 0 | 0
6 | Pig Traps | Asset Level | 0 | 0 | 4 | 10 | 8 |  | 0 | 0 | 4 | 10 | 14 |  | 0 | 0 | 4 | 10 | 8 |  | 0 | 4 | 10 | 7 | 11 |  | 0 | 4 | 10 | 7 | 1 |  | Pig Traps | Asset Level | Pig TrapsAsset Level | Pig Traps | 22 | 28 | 22 | 32 | 22 | 32 | 10 | 4 | 10 | 0 | 10
7 | Sleeves (Nitrogen & other) | Asset Level | 0 | 15 | 58 | 777 | 34 |  | 0 | 0 | 44 | 806 | 34 |  | 7 | 8 | 58 | 777 | 34 |  | 0 | 15 | 777 | 81 | 11 |  | 7 | 66 | 777 | 23 | 11 |  | Sleeves (Nitrogen & other) | Asset Level | Sleeves (Nitrogen & other)Asset Level | Sleeves (Nitrogen & other) | 884 | 884 | 884 | 884 | 884 | 884 | 0 | 0 | 0 | 0 | 0
8 | LTS Pipelines - Piggable | Asset Level | 0 | 10.38 | 144.1 | 809.91 | 9.48 |  | 0 | 15.38 | 169.6 | 779.41 | 34.08 |  | 0 | 15.38 | 169.6 | 779.41 | 9.48 |  | 0 | 20.2 | 172.6 | 771.59 | 37.88 |  | 0 | 20.2 | 172.6 | 771.59 | 9.48 |  | LTS Pipelines - Piggable | Asset Level | LTS Pipelines - PiggableAsset Level | LTS Pipelines - Piggable | 973.87 | 998.47 | 973.87 | 1002.27 | 973.87 | 1002.27 | 28.4 | 3.8 | 28.4 | 0 | 28.4
9 | LTS Pipelines – Non Piggable | Asset Level | 0 | 5.01 | 37.67 | 112.08 | 198.2 |  | 0 | 5.01 | 47.67 | 102.08 | 198.2 |  | 0 | 5.01 | 47.67 | 102.08 | 198.2 |  | 0 | 5.01 | 77.67 | 78.08 | 192.2 |  | 0 | 5.01 | 77.67 | 78.08 | 192.2 |  | LTS Pipelines – Non Piggable | Asset Level | LTS Pipelines – Non PiggableAsset Level | LTS Pipelines – Non Piggable | 352.96 | 352.96 | 352.96 | 352.96 | 352.96 | 352.96 | 0 | 0 | 0 | 0 | 0
10 | Cathodic Protection | Asset Level | 0 | 63 | 260 | 584 | 370 |  | 0 | 40 | 257 | 618 | 424 |  | 9 | 169 | 272 | 547 | 342 |  | 3 | 64 | 254 | 625 | 415 |  | 12 | 224 | 288 | 528 | 309 |  | Cathodic Protection | Asset Level | Cathodic ProtectionAsset Level | Cathodic Protection | 1277 | 1339 | 1339 | 1361 | 1361 | 1361 | 84 | 22 | 22 | 0 | 0
11 | Above7 bar Special Crossings | Asset Level | 0 | 4 | 16 | 74 | 1 |  | 0 | 4 | 16 | 74 | 1 |  | 0 | 4 | 16 | 74 | 1 |  | 0 | 10 | 84 | 0 | 1 |  | 0 | 10 | 84 | 0 | 1 |  | Above7 bar Special Crossings | Asset Level | Above7 bar Special CrossingsAsset Level | Above7 bar Special Crossings | 95 | 95 | 95 | 95 | 95 | 95 | 0 | 0 | 0 | 0 | 0
12 | Below7 bar Special Crossings | Asset Level | 0 | 85 | 405 | 49 | 217 |  | 0 | 85 | 405 | 49 | 217 |  | 0 | 286 | 228 | 110 | 132 |  | 0 | 85 | 405 | 49 | 217 |  | 0 | 490 | 49 | 171 | 46 |  | Below7 bar Special Crossings | Asset Level | Below7 bar Special CrossingsAsset Level | Below7 bar Special Crossings | 756 | 756 | 756 | 756 | 756 | 756 | 0 | 0 | 0 | 0 | 0
13 | Distribution Mains (Iron) | Asset Level | 0 | 1930.0001 | 3645.5232 | 0.65895 | 0 |  | 0 | 1606.038 | 3034.3167 | 0.54852 | 0 |  | 0 | 1929.142 | 3646.3812 | 0.65895 | 0 |  | 0 | 1282.0759 | 2423.1102 | 0.4381 | 0 |  | 0 | 1928.284 | 3647.2393 | 0.65895 | 0 |  | Distribution Mains (Iron) | Asset Level | Distribution Mains (Iron)Asset Level | Distribution Mains (Iron) | 5576.1822 | 4640.9032 | 5576.1822 | 3705.6242 | 5576.1822 | 5576.1822 | 0 | 935.279 | 0 | 1870.558 | 0
14 | Distribution Mains (PE) | Asset Level | 0 | 0 | 0 | 2.5562 | 15950.3305 |  | 0 | 0 | 0 | 2.5562 | 17192.9395 |  | 0 | 0 | 0 | 1.6615 | 15951.2252 |  | 0 | 0 | 0 | 2.5562 | 18435.5485 |  | 0 | 0 | 0 | 0.76684 | 15952.1199 |  | Distribution Mains (PE) | Asset Level | Distribution Mains (PE)Asset Level | Distribution Mains (PE) | 15952.8868 | 17195.4958 | 15952.8868 | 18438.1048 | 15952.8868 | 18438.1048 | 2485.218 | 1242.609 | 2485.218 | 0 | 2485.218
15 | Distribution Mains (Steel) | Asset Level | 13.8193 | 1086.7843 | 247.402 | 352.7423 | 0 |  | 12.254 | 963.6847 | 217.2502 | 312.6551 | 0 |  | 13.8193 | 1077.3878 | 256.2148 | 353.3261 | 0 |  | 10.6887 | 840.5851 | 187.0984 | 272.5678 | 0 |  | 13.8193 | 1067.9912 | 265.0275 | 353.9099 | 0 |  | Distribution Mains (Steel) | Asset Level | Distribution Mains (Steel)Asset Level | Distribution Mains (Steel) | 1700.7479 | 1505.8439 | 1700.7479 | 1310.9399 | 1700.7479 | 1700.7479 | 0 | 194.904 | 0 | 389.808 | 0
16 | Distribution Mains (other) | Asset Level | 0 | 0.62184 | 0 | 0.45223 | 0 |  | 0 | 0.62184 | 0 | 0.45223 | 0 |  | 0 | 0.62184 | 0 | 0.45223 | 0 |  | 0 | 0.62184 | 0 | 0.45223 | 0 |  | 0 | 0.62184 | 0 | 0.45223 | 0 |  | Distribution Mains (other) | Asset Level | Distribution Mains (other)Asset Level | Distribution Mains (other) | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 1.0741 | 0 | 0 | 0 | 0 | 0
17 | Services | Asset Level | 0 | 0 | 1313660 | 0 | 760241 |  | 0 | 0 | 1232403 | 0 | 874068 |  | 0 | 0 | 1313660 | 0 | 760241 |  | 0 | 0 | 1153631 | 0 | 985409 |  | 0 | 0 | 1313660 | 0 | 760241 |  | Services | Asset Level | ServicesAsset Level | Services | 2073901 | 2106471 | 2073901 | 2139040 | 2073901 | 2139040 | 65139 | 32569 | 65139 | 0 | 65139
18 | MOB Risers | Asset Level | 0 | 2809 | 2809 | 0 | 1625 |  | 0 | 2242 | 2060 | 0 | 2941 |  | 0 | 3558 | 2060 | 0 | 1625 |  | 0 | 1675 | 1311 | 0 | 4257 |  | 0 | 4307 | 1311 | 0 | 1625 |  | MOB Risers | Asset Level | MOB RisersAsset Level | MOB Risers | 7243 | 7243 | 7243 | 7243 | 7243 | 7243 | 0 | 0 | 0 | 0 | 0
19 | Operational Holders | Asset Level | 0 | 1 | 1 | 0 | 0 |  | 0 | 1 | 1 | 0 | 0 |  | 0 | 1 | 1 | 0 | 0 |  | 0 | 1 | 1 | 0 | 0 |  | 0 | 1 | 1 | 0 | 0 |  | Operational Holders | Asset Level | Operational HoldersAsset Level | Operational Holders | 2 | 2 | 2 | 2 | 2 | 2 | 0 | 0 | 0 | 0 | 0
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | 0 | 22 | 0 | 0 | 0 |  | 0 | 17 | 0 | 0 | 0 |  | 0 | 22 | 0 | 0 | 0 |  | 0 | 11 | 0 | 0 | 0 |  | 0 | 22 | 0 | 0 | 0 |  | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | Non Operational Holders (Mothballed & Decommissioned)Asset Level | Non Operational Holders (Mothballed & Decommissioned) | 22 | 17 | 22 | 11 | 22 | 22 | 0 | 5 | 0 | 11 | 0
21 | High Pressure Vessels | Asset Level | 0 | 0 | 0 | 1 | 5 |  | 0 | 0 | 0 | 1 | 5 |  | 0 | 0 | 0 | 1 | 5 |  | 0 | 0 | 0 | 1 | 5 |  | 0 | 0 | 0 | 1 | 5 |  | High Pressure Vessels | Asset Level | High Pressure VesselsAsset Level | High Pressure Vessels | 6 | 6 | 6 | 6 | 6 | 6 | 0 | 0 | 0 | 0 | 0
22 | NTS Offtakes | Regulators System | 5 | 3 | 1 | 6 | 1 |  | 3 | 3 | 5 | 5 | 0 |  | 5 | 3 | 5 | 3 | 0 |  | 2 | 4 | 4 | 5 | 1 |  | 6 | 4 | 4 | 2 | 0 |  | NTS Offtakes | Regulators System | NTS OfftakesRegulators System | NTS Offtakes-Regulators System | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | 3 | 0 | 5 | 6 | 0 |  | 1 | 1 | 7 | 5 | 0 |  | 3 | 1 | 7 | 3 | 0 |  | 1 | 3 | 5 | 4 | 1 |  | 3 | 4 | 5 | 2 | 0 |  | NTS Offtakes | Slam Shut System | NTS OfftakesSlam Shut System | NTS Offtakes-Slam Shut System | 14 | 14 | 14 | 14 | 14 | 14 | 0 | 0 | 0 | 0 | 0
|  | Filter System | 3 | 0 | 4 | 10 | 1 |  | 2 | 2 | 5 | 9 | 0 |  | 3 | 2 | 5 | 8 | 0 |  | 1 | 3 | 6 | 7 | 1 |  | 3 | 4 | 6 | 5 | 0 |  | NTS Offtakes | Filter System | NTS OfftakesFilter System | NTS Offtakes-Filter System | 18 | 18 | 18 | 18 | 18 | 18 | 0 | 0 | 0 | 0 | 0
|  | Pre-heating System | 4 | 2 | 2 | 6 | 2 |  | 3 | 1 | 2 | 10 | 0 |  | 6 | 1 | 2 | 7 | 0 |  | 0 | 1 | 6 | 7 | 2 |  | 6 | 1 | 6 | 3 | 0 |  | NTS Offtakes | Pre-heating System | NTS OfftakesPre-heating System | NTS Offtakes-Pre-heating System | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | 0 | 0 | 1 | 12 | 4 |  | 0 | 0 | 9 | 7 | 1 |  | 0 | 0 | 10 | 6 | 1 |  | 0 | 0 | 10 | 6 | 1 |  | 0 | 0 | 11 | 6 | 0 |  | NTS Offtakes | Odorisation System | NTS OfftakesOdorisation System | NTS Offtakes-Odorisation System | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Metering System | 8 | 0 | 1 | 5 | 3 |  | 5 | 0 | 3 | 7 | 2 |  | 8 | 0 | 3 | 4 | 2 |  | 1 | 1 | 3 | 11 | 1 |  | 8 | 1 | 3 | 4 | 1 |  | NTS Offtakes | Metering System | NTS OfftakesMetering System | NTS Offtakes-Metering System | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | 5 | 6 | 2 | 4 | 0 |  | 8 | 1 | 5 | 3 | 0 |  | 9 | 1 | 5 | 2 | 0 |  | 4 | 5 | 4 | 3 | 0 |  | 6 | 5 | 4 | 1 | 0 |  | NTS Offtakes | Buildings (no.’s) | NTS OfftakesBuildings (no.’s) | NTS Offtakes-Buildings (no.’s) | 17 | 17 | 17 | 16 | 16 | 17 | 0 | 0 | 0 | 1 | 1
|  | Fences (no’s -Inc Security) | 2 | 5 | 5 | 5 | 0 |  | 2 | 5 | 7 | 3 | 0 |  | 3 | 5 | 7 | 2 | 0 |  | 3 | 3 | 7 | 4 | 0 |  | 5 | 3 | 7 | 2 | 0 |  | NTS Offtakes | Fences (no’s -Inc Security) | NTS OfftakesFences (no’s -Inc Security) | NTS Offtakes-Fences (no’s -Inc Security) | 17 | 17 | 17 | 17 | 17 | 17 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | 0 | 0 | 13 | 6 | 0 |  | 0 | 0 | 13 | 6 | 0 |  | 0 | 0 | 13 | 6 | 0 |  | 0 | 11 | 7 | 1 | 0 |  | 0 | 13 | 5 | 1 | 0 |  | NTS Offtakes | Electrical System | NTS OfftakesElectrical System | NTS Offtakes-Electrical System | 19 | 19 | 19 | 19 | 19 | 19 | 0 | 0 | 0 | 0 | 0
|  | Instrumentation System | 15 | 0 | 0 | 1 | 0 |  | 13 | 0 | 2 | 1 | 0 |  | 15 | 0 | 0 | 1 | 0 |  | 11 | 0 | 4 | 1 | 0 |  | 15 | 0 | 0 | 1 | 0 |  | NTS Offtakes | Instrumentation System | NTS OfftakesInstrumentation System | NTS Offtakes-Instrumentation System | 16 | 16 | 16 | 16 | 16 | 16 | 0 | 0 | 0 | 0 | 0
23 | PRSs | Regulators System | 35 | 39 | 51 | 18 | 1 |  | 33 | 42 | 47 | 20 | 2 |  | 45 | 42 | 47 | 9 | 1 |  | 46 | 48 | 24 | 24 | 2 |  | 65 | 48 | 24 | 7 | 0 |  | PRSs | Regulators System | PRSsRegulators System | PRSs-Regulators System | 144 | 144 | 144 | 144 | 144 | 144 | 0 | 0 | 0 | 0 | 0
|  | Slam Shut System | 73 | 14 | 32 | 25 | 0 |  | 66 | 14 | 36 | 27 | 1 |  | 78 | 14 | 36 | 16 | 0 |  | 65 | 23 | 26 | 28 | 2 |  | 84 | 23 | 26 | 11 | 0 |  | PRSs | Slam Shut System | PRSsSlam Shut System | PRSs-Slam Shut System | 144 | 144 | 144 | 144 | 144 | 144 | 0 | 0 | 0 | 0 | 0
|  | Filter System | 1 | 9 | 74 | 50 | 3 |  | 0 | 23 | 63 | 46 | 5 |  | 2 | 33 | 64 | 35 | 3 |  | 0 | 50 | 54 | 29 | 3 |  | 4 | 65 | 55 | 12 | 1 |  | PRSs | Filter System | PRSsFilter System | PRSs-Filter System | 137 | 137 | 137 | 136 | 137 | 137 | 0 | 0 | 0 | 1 | 0
|  | Pre-heating System | 27 | 30 | 36 | 20 | 1 |  | 26 | 29 | 27 | 29 | 3 |  | 44 | 29 | 27 | 14 | 0 |  | 15 | 33 | 27 | 34 | 5 |  | 48 | 34 | 27 | 5 | 0 |  | PRSs | Pre-heating System | PRSsPre-heating System | PRSs-Pre-heating System | 114 | 114 | 114 | 114 | 114 | 114 | 0 | 0 | 0 | 0 | 0
|  | Odorisation System | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | PRSs | Odorisation System | PRSsOdorisation System | PRSs-Odorisation System | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Metering System | 0 | 1 | 0 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 |  | 0 | 1 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 1 |  | 0 | 1 | 0 | 0 | 0 |  | PRSs | Metering System | PRSsMetering System | PRSs-Metering System | 1 | 1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0
|  | Buildings (no.’s) | 32 | 33 | 39 | 23 | 0 |  | 37 | 37 | 32 | 20 | 1 |  | 49 | 37 | 32 | 9 | 0 |  | 32 | 38 | 31 | 24 | 3 |  | 51 | 38 | 31 | 7 | 1 |  | PRSs | Buildings (no.’s) | PRSsBuildings (no.’s) | PRSs-Buildings (no.’s) | 127 | 127 | 127 | 128 | 128 | 128 | 1 | 1 | 1 | 0 | 0
|  | Fences (no’s -Inc Security) | 15 | 30 | 45 | 35 | 3 |  | 15 | 30 | 51 | 30 | 2 |  | 26 | 30 | 51 | 20 | 1 |  | 25 | 32 | 42 | 25 | 4 |  | 37 | 34 | 42 | 14 | 1 |  | PRSs | Fences (no’s -Inc Security) | PRSsFences (no’s -Inc Security) | PRSs-Fences (no’s -Inc Security) | 128 | 128 | 128 | 128 | 128 | 128 | 0 | 0 | 0 | 0 | 0
|  | Electrical System | 0 | 0 | 79 | 53 | 0 |  | 0 | 0 | 79 | 53 | 0 |  | 0 | 0 | 79 | 53 | 0 |  | 0 | 65 | 66 | 0 | 0 |  | 0 | 79 | 53 | 0 | 0 |  | PRSs | Electrical System | PRSsElectrical System | PRSs-Electrical System | 132 | 132 | 132 | 131 | 132 | 132 | 0 | 0 | 0 | 1 | 0
|  | Instrumentation System | 100 | 32 | 0 | 0 | 0 |  | 120 | 0 | 12 | 0 | 0 |  | 132 | 0 | 0 | 0 | 0 |  | 118 | 0 | 15 | 0 | 0 |  | 132 | 0 | 0 | 0 | 0 |  | PRSs | Instrumentation System | PRSsInstrumentation System | PRSs-Instrumentation System | 132 | 132 | 132 | 133 | 132 | 133 | 1 | 1 | 1 | 0 | 1
22 | District Governors | Asset Level | 2 | 68 | 439 | 462 | 1227 |  | 0 | 434 | 12 | 493 | 1266 |  | 2 | 495 | 12 | 462 | 1227 |  | 0 | 385 | 462 | 1207 | 158 |  | 2 | 507 | 462 | 1176 | 51 |  | District Governors | Asset Level | District GovernorsAsset Level | District Governors | 2198 | 2205 | 2198 | 2212 | 2198 | 2212 | 14 | 7 | 14 | 0 | 14
24 | I&C Governors | Asset Level | 0 | 6 | 7 | 6 | 200 |  | 0 | 10 | 0 | 6 | 203 |  | 0 | 13 | 0 | 6 | 200 |  | 0 | 8 | 6 | 200 | 5 |  | 0 | 13 | 6 | 200 | 0 |  | I&C Governors | Asset Level | I&C GovernorsAsset Level | I&C Governors | 219 | 219 | 219 | 219 | 219 | 219 | 0 | 0 | 0 | 0 | 0
25 | Service Governors | Asset Level | 0 | 908 | 1060 | 36 | 1779 |  | 0 | 860 | 448 | 84 | 2391 |  | 0 | 1520 | 448 | 84 | 1731 |  | 0 | 848 | 295 | 96 | 2544 |  | 0 | 2168 | 295 | 96 | 1224 |  | Service Governors | Asset Level | Service GovernorsAsset Level | Service Governors | 3783 | 3783 | 3783 | 3783 | 3783 | 3783 | 0 | 0 | 0 | 0 | 0
26 | LPG Storage | Asset Level | 0 | 0 | 1 | 2 | 0 |  | 0 | 0 | 1 | 2 | 0 |  | 0 | 0 | 1 | 2 | 0 |  | 0 | 1 | 2 | 0 | 0 |  | 0 | 1 | 2 | 0 | 0 |  | LPG Storage | Asset Level | LPG StorageAsset Level | LPG Storage | 3 | 3 | 3 | 3 | 3 | 3 | 0 | 0 | 0 | 0 | 0
27 | LPG Mains | Asset Level | 0 | 0 | 0.367 | 0 | 20.6228 |  | 0 | 0 | 0.367 | 0 | 20.6228 |  | 0 | 0 | 0.367 | 0 | 20.6228 |  | 0 | 0 | 0.367 | 0 | 20.6228 |  | 0 | 0 | 0.367 | 0 | 20.6228 |  | LPG Mains | Asset Level | LPG MainsAsset Level | LPG Mains | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 20.9898 | 0 | 0 | 0 | 0 | 0
28 | LPG Services | Asset Level | 0 | 0 | 930 | 0 | 846 |  | 0 | 0 | 872 | 0 | 926 |  | 0 | 0 | 930 | 0 | 846 |  | 0 | 0 | 817 | 0 | 1005 |  | 0 | 0 | 930 | 0 | 846 |  | LPG Services | Asset Level | LPG ServicesAsset Level | LPG Services | 1776 | 1798 | 1776 | 1822 | 1776 | 1822 | 46 | 24 | 46 | 0 | 46
29 | LNG Vessels | Asset Level | 0 | 0 | 18 | 2 | 0 |  | 0 | 4 | 14 | 2 | 0 |  | 0 | 4 | 14 | 2 | 0 |  | 0 | 9 | 9 | 2 | 0 |  | 0 | 9 | 9 | 2 | 0 |  | LNG Vessels | Asset Level | LNG VesselsAsset Level | LNG Vessels | 20 | 20 | 20 | 20 | 20 | 20 | 0 | 0 | 0 | 0 | 0
|  |  | 429.8193 | 7322.7962 | 1324344.0622 | 3753.3997 | 782797.6333 | 2118647.7108 | 431.254 | 6554.7345 | 1240592.2039 | 3859.7021 | 900008.8423 | 2151446.7368 | 547.8193 | 9442.5416 | 1322398.233 | 3694.5888 | 782626.528 | 2118709.7108 | 422.6887 | 5766.4928 | 1161465.8456 | 3748.6844 | 1012778.2513 | 2184181.9628 | 595.8193 | 11501.107 | 1322555.9038 | 3521.4579 | 780557.4227 | 2118731.7108
|  |  | 429.8193 | 7322.7962 | 1324344.0622 | 3753.3997 | 782797.6333 | 2118647.7108 | 431.254 | 6554.7345 | 1240592.2039 | 3859.7021 | 900008.8423 | 2151446.7368 | 547.8193 | 9442.5416 | 1322398.233 | 3694.5888 | 782626.528 | 2118709.7108 | 422.6887 | 5766.4928 | 1161465.8456 | 3748.6844 | 1012778.2513 | 2184181.9628 | 595.8193 | 11501.107 | 1322555.9038 | 3521.4579 | 780557.4227 | 2118731.7108
|  | Validation Check | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK | OK
1 | Storage Telemetry | Asset Level | 0% | 100% | 0% | 0% | 0% |  | 0% | 80% | 0% | 0% | 20% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 80% | 0% | 20% | 0% |  | 0% | 100% | 0% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
2 | Above7 bar Telemetry | Asset Level | 58.87% | 26.24% | 14.89% | 0% | 0% |  | 60.28% | 39.72% | 0% | 0% | 0% |  | 60.28% | 39.72% | 0% | 0% | 0% |  | 60.28% | 39.72% | 0% | 0% | 0% |  | 60.28% | 39.72% | 0% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
3 | Below7 bar Telemetry | Asset Level | 0% | 40% | 60% | 0% | 0% |  | 0% | 70% | 30% | 0% | 0% |  | 0% | 70% | 30% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
4 | Block Valves | Asset Level | 0% | 12.5% | 62.5% | 25% | 0% |  | 0% | 68.75% | 25% | 6.25% | 0% |  | 0% | 68.75% | 25% | 6.25% | 0% |  | 0% | 75% | 18.75% | 6.25% | 0% |  | 0% | 75% | 18.75% | 6.25% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
5 | Valves | Asset Level | 0.6466% | 12.28% | 37.5% | 39.44% | 10.13% |  | 0% | 0% | 37.5% | 50.65% | 11.85% |  | 0.6466% | 12.28% | 37.5% | 39.44% | 10.13% |  | 0% | 21.55% | 42.46% | 30.17% | 5.819% |  | 0.6466% | 46.77% | 42.46% | 6.034% | 4.095% | [11 empty] | 0% | 0% | 0% | 0% | 0%
6 | Pig Traps | Asset Level | 0% | 0% | 12.5% | 31.25% | 25% |  | 0% | 0% | 12.5% | 31.25% | 43.75% |  | 0% | 0% | 12.5% | 31.25% | 25% |  | 0% | 12.5% | 31.25% | 21.88% | 34.38% |  | 0% | 12.5% | 31.25% | 21.88% | 3.125% | [11 empty] | 31.25% | 12.5% | 31.25% | 0% | 31.25%
7 | Sleeves (Nitrogen & other) | Asset Level | 0% | 1.697% | 6.561% | 87.9% | 3.846% |  | 0% | 0% | 4.977% | 91.18% | 3.846% |  | 0.7919% | 0.905% | 6.561% | 87.9% | 3.846% |  | 0% | 1.697% | 87.9% | 9.163% | 1.244% |  | 0.7919% | 7.466% | 87.9% | 2.602% | 1.244% | [11 empty] | 0% | 0% | 0% | 0% | 0%
8 | LTS Pipelines - Piggable | Asset Level | 0% | 1.036% | 14.38% | 80.81% | 0.9459% |  | 0% | 1.535% | 16.92% | 77.76% | 3.4% |  | 0% | 1.535% | 16.92% | 77.76% | 0.9459% |  | 0% | 2.015% | 17.22% | 76.98% | 3.779% |  | 0% | 2.015% | 17.22% | 76.98% | 0.9459% | [11 empty] | 2.834% | 0.3791% | 2.834% | 0% | 2.834%
9 | LTS Pipelines – Non Piggable | Asset Level | 0% | 1.419% | 10.67% | 31.75% | 56.15% |  | 0% | 1.419% | 13.51% | 28.92% | 56.15% |  | 0% | 1.419% | 13.51% | 28.92% | 56.15% |  | 0% | 1.419% | 22.01% | 22.12% | 54.45% |  | 0% | 1.419% | 22.01% | 22.12% | 54.45% | [11 empty] | 0% | 0% | 0% | 0% | 0%
10 | Cathodic Protection | Asset Level | 0% | 4.629% | 19.1% | 42.91% | 27.19% |  | 0% | 2.939% | 18.88% | 45.41% | 31.15% |  | 0.6613% | 12.42% | 19.99% | 40.19% | 25.13% |  | 0.2204% | 4.702% | 18.66% | 45.92% | 30.49% |  | 0.8817% | 16.46% | 21.16% | 38.8% | 22.7% | [11 empty] | 6.172% | 1.616% | 1.616% | 0% | 0%
11 | Above7 bar Special Crossings | Asset Level | 0% | 4.211% | 16.84% | 77.89% | 1.053% |  | 0% | 4.211% | 16.84% | 77.89% | 1.053% |  | 0% | 4.211% | 16.84% | 77.89% | 1.053% |  | 0% | 10.53% | 88.42% | 0% | 1.053% |  | 0% | 10.53% | 88.42% | 0% | 1.053% | [11 empty] | 0% | 0% | 0% | 0% | 0%
12 | Below7 bar Special Crossings | Asset Level | 0% | 11.24% | 53.57% | 6.481% | 28.7% |  | 0% | 11.24% | 53.57% | 6.481% | 28.7% |  | 0% | 37.83% | 30.16% | 14.55% | 17.46% |  | 0% | 11.24% | 53.57% | 6.481% | 28.7% |  | 0% | 64.81% | 6.481% | 22.62% | 6.085% | [11 empty] | 0% | 0% | 0% | 0% | 0%
13 | Distribution Mains (Iron) | Asset Level | 0% | 34.61% | 65.38% | 0.01182% | 0% |  | 0% | 28.8% | 54.42% | 0.009837% | 0% |  | 0% | 34.6% | 65.39% | 0.01182% | 0% |  | 0% | 22.99% | 43.45% | 0.007857% | 0% |  | 0% | 34.58% | 65.41% | 0.01182% | 0% | [11 empty] | 0% | 16.77% | 0% | 33.55% | 0%
14 | Distribution Mains (PE) | Asset Level | 0% | 0% | 0% | 0.01386% | 86.51% |  | 0% | 0% | 0% | 0.01386% | 93.25% |  | 0% | 0% | 0% | 0.009011% | 86.51% |  | 0% | 0% | 0% | 0.01386% | 99.99% |  | 0% | 0% | 0% | 0.004159% | 86.52% | [11 empty] | 13.48% | 6.739% | 13.48% | 0% | 13.48%
15 | Distribution Mains (Steel) | Asset Level | 0.8125% | 63.9% | 14.55% | 20.74% | 0% |  | 0.7205% | 56.66% | 12.77% | 18.38% | 0% |  | 0.8125% | 63.35% | 15.06% | 20.77% | 0% |  | 0.6285% | 49.42% | 11% | 16.03% | 0% |  | 0.8125% | 62.8% | 15.58% | 20.81% | 0% | [11 empty] | 0% | 11.46% | 0% | 22.92% | 0%
16 | Distribution Mains (other) | Asset Level | 0% | 57.9% | 0% | 42.1% | 0% |  | 0% | 57.9% | 0% | 42.1% | 0% |  | 0% | 57.9% | 0% | 42.1% | 0% |  | 0% | 57.9% | 0% | 42.1% | 0% |  | 0% | 57.9% | 0% | 42.1% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
17 | Services | Asset Level | 0% | 0% | 61.41% | 0% | 35.54% |  | 0% | 0% | 57.61% | 0% | 40.86% |  | 0% | 0% | 61.41% | 0% | 35.54% |  | 0% | 0% | 53.93% | 0% | 46.07% |  | 0% | 0% | 61.41% | 0% | 35.54% | [11 empty] | 3.045% | 1.523% | 3.045% | 0% | 3.045%
18 | MOB Risers | Asset Level | 0% | 38.78% | 38.78% | 0% | 22.44% |  | 0% | 30.95% | 28.44% | 0% | 40.6% |  | 0% | 49.12% | 28.44% | 0% | 22.44% |  | 0% | 23.13% | 18.1% | 0% | 58.77% |  | 0% | 59.46% | 18.1% | 0% | 22.44% | [11 empty] | 0% | 0% | 0% | 0% | 0%
19 | Operational Holders | Asset Level | 0% | 50% | 50% | 0% | 0% |  | 0% | 50% | 50% | 0% | 0% |  | 0% | 50% | 50% | 0% | 0% |  | 0% | 50% | 50% | 0% | 0% |  | 0% | 50% | 50% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
20 | Non Operational Holders (Mothballed & Decommissioned) | Asset Level | 0% | 100% | 0% | 0% | 0% |  | 0% | 77.27% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 50% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% | [11 empty] | 0% | 22.73% | 0% | 50% | 0%
21 | High Pressure Vessels | Asset Level | 0% | 0% | 0% | 16.67% | 83.33% |  | 0% | 0% | 0% | 16.67% | 83.33% |  | 0% | 0% | 0% | 16.67% | 83.33% |  | 0% | 0% | 0% | 16.67% | 83.33% |  | 0% | 0% | 0% | 16.67% | 83.33% | [11 empty] | 0% | 0% | 0% | 0% | 0%
22 | NTS Offtakes | Regulators System | 31.25% | 18.75% | 6.25% | 37.5% | 6.25% |  | 18.75% | 18.75% | 31.25% | 31.25% | 0% |  | 31.25% | 18.75% | 31.25% | 18.75% | 0% |  | 12.5% | 25% | 25% | 31.25% | 6.25% |  | 37.5% | 25% | 25% | 12.5% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Slam Shut System | 21.43% | 0% | 35.71% | 42.86% | 0% |  | 7.143% | 7.143% | 50% | 35.71% | 0% |  | 21.43% | 7.143% | 50% | 21.43% | 0% |  | 7.143% | 21.43% | 35.71% | 28.57% | 7.143% |  | 21.43% | 28.57% | 35.71% | 14.29% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Filter System | 16.67% | 0% | 22.22% | 55.56% | 5.556% |  | 11.11% | 11.11% | 27.78% | 50% | 0% |  | 16.67% | 11.11% | 27.78% | 44.44% | 0% |  | 5.556% | 16.67% | 33.33% | 38.89% | 5.556% |  | 16.67% | 22.22% | 33.33% | 27.78% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Pre-heating System | 25% | 12.5% | 12.5% | 37.5% | 12.5% |  | 18.75% | 6.25% | 12.5% | 62.5% | 0% |  | 37.5% | 6.25% | 12.5% | 43.75% | 0% |  | 0% | 6.25% | 37.5% | 43.75% | 12.5% |  | 37.5% | 6.25% | 37.5% | 18.75% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Odorisation System | 0% | 0% | 5.882% | 70.59% | 23.53% |  | 0% | 0% | 52.94% | 41.18% | 5.882% |  | 0% | 0% | 58.82% | 35.29% | 5.882% |  | 0% | 0% | 58.82% | 35.29% | 5.882% |  | 0% | 0% | 64.71% | 35.29% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Metering System | 47.06% | 0% | 5.882% | 29.41% | 17.65% |  | 29.41% | 0% | 17.65% | 41.18% | 11.76% |  | 47.06% | 0% | 17.65% | 23.53% | 11.76% |  | 5.882% | 5.882% | 17.65% | 64.71% | 5.882% |  | 47.06% | 5.882% | 17.65% | 23.53% | 5.882% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Buildings (no.’s) | 29.41% | 35.29% | 11.76% | 23.53% | 0% |  | 47.06% | 5.882% | 29.41% | 17.65% | 0% |  | 52.94% | 5.882% | 29.41% | 11.76% | 0% |  | 23.53% | 29.41% | 23.53% | 17.65% | 0% |  | 35.29% | 29.41% | 23.53% | 5.882% | 0% | [11 empty] | 0% | 0% | 0% | 5.882% | 5.882%
|  | Fences (no’s -Inc Security) | 11.76% | 29.41% | 29.41% | 29.41% | 0% |  | 11.76% | 29.41% | 41.18% | 17.65% | 0% |  | 17.65% | 29.41% | 41.18% | 11.76% | 0% |  | 17.65% | 17.65% | 41.18% | 23.53% | 0% |  | 29.41% | 17.65% | 41.18% | 11.76% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Electrical System | 0% | 0% | 68.42% | 31.58% | 0% |  | 0% | 0% | 68.42% | 31.58% | 0% |  | 0% | 0% | 68.42% | 31.58% | 0% |  | 0% | 57.89% | 36.84% | 5.263% | 0% |  | 0% | 68.42% | 26.32% | 5.263% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Instrumentation System | 93.75% | 0% | 0% | 6.25% | 0% |  | 81.25% | 0% | 12.5% | 6.25% | 0% |  | 93.75% | 0% | 0% | 6.25% | 0% |  | 68.75% | 0% | 25% | 6.25% | 0% |  | 93.75% | 0% | 0% | 6.25% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
23 | PRSs | Regulators System | 24.31% | 27.08% | 35.42% | 12.5% | 0.6944% |  | 22.92% | 29.17% | 32.64% | 13.89% | 1.389% |  | 31.25% | 29.17% | 32.64% | 6.25% | 0.6944% |  | 31.94% | 33.33% | 16.67% | 16.67% | 1.389% |  | 45.14% | 33.33% | 16.67% | 4.861% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Slam Shut System | 50.69% | 9.722% | 22.22% | 17.36% | 0% |  | 45.83% | 9.722% | 25% | 18.75% | 0.6944% |  | 54.17% | 9.722% | 25% | 11.11% | 0% |  | 45.14% | 15.97% | 18.06% | 19.44% | 1.389% |  | 58.33% | 15.97% | 18.06% | 7.639% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Filter System | 0.7299% | 6.569% | 54.01% | 36.5% | 2.19% |  | 0% | 16.79% | 45.99% | 33.58% | 3.65% |  | 1.46% | 24.09% | 46.72% | 25.55% | 2.19% |  | 0% | 36.5% | 39.42% | 21.17% | 2.19% |  | 2.92% | 47.45% | 40.15% | 8.759% | 0.7299% | [11 empty] | 0% | 0% | 0% | 0.7299% | 0%
|  | Pre-heating System | 23.68% | 26.32% | 31.58% | 17.54% | 0.8772% |  | 22.81% | 25.44% | 23.68% | 25.44% | 2.632% |  | 38.6% | 25.44% | 23.68% | 12.28% | 0% |  | 13.16% | 28.95% | 23.68% | 29.82% | 4.386% |  | 42.11% | 29.82% | 23.68% | 4.386% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Odorisation System | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | [11 empty] | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0!
|  | Metering System | 0% | 100% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 100% | 0% | 0% | 0% |  | 0% | 0% | 0% | 0% | 100% |  | 0% | 100% | 0% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Buildings (no.’s) | 25% | 25.78% | 30.47% | 17.97% | 0% |  | 28.91% | 28.91% | 25% | 15.62% | 0.7812% |  | 38.28% | 28.91% | 25% | 7.031% | 0% |  | 25% | 29.69% | 24.22% | 18.75% | 2.344% |  | 39.84% | 29.69% | 24.22% | 5.469% | 0.7812% | [11 empty] | 0.7812% | 0.7812% | 0.7812% | 0% | 0%
|  | Fences (no’s -Inc Security) | 11.72% | 23.44% | 35.16% | 27.34% | 2.344% |  | 11.72% | 23.44% | 39.84% | 23.44% | 1.562% |  | 20.31% | 23.44% | 39.84% | 15.62% | 0.7812% |  | 19.53% | 25% | 32.81% | 19.53% | 3.125% |  | 28.91% | 26.56% | 32.81% | 10.94% | 0.7812% | [11 empty] | 0% | 0% | 0% | 0% | 0%
|  | Electrical System | 0% | 0% | 59.85% | 40.15% | 0% |  | 0% | 0% | 59.85% | 40.15% | 0% |  | 0% | 0% | 59.85% | 40.15% | 0% |  | 0% | 49.24% | 50% | 0% | 0% |  | 0% | 59.85% | 40.15% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0.7576% | 0%
|  | Instrumentation System | 75.19% | 24.06% | 0% | 0% | 0% |  | 90.23% | 0% | 9.023% | 0% | 0% |  | 99.25% | 0% | 0% | 0% | 0% |  | 88.72% | 0% | 11.28% | 0% | 0% |  | 99.25% | 0% | 0% | 0% | 0% | [11 empty] | 0.7519% | 0.7519% | 0.7519% | 0% | 0.7519%
22 | District Governors | Asset Level | 0.09042% | 3.074% | 19.85% | 20.89% | 55.47% |  | 0% | 19.62% | 0.5425% | 22.29% | 57.23% |  | 0.09042% | 22.38% | 0.5425% | 20.89% | 55.47% |  | 0% | 17.41% | 20.89% | 54.57% | 7.143% |  | 0.09042% | 22.92% | 20.89% | 53.16% | 2.306% | [11 empty] | 0.6329% | 0.3165% | 0.6329% | 0% | 0.6329%
24 | I&C Governors | Asset Level | 0% | 2.74% | 3.196% | 2.74% | 91.32% |  | 0% | 4.566% | 0% | 2.74% | 92.69% |  | 0% | 5.936% | 0% | 2.74% | 91.32% |  | 0% | 3.653% | 2.74% | 91.32% | 2.283% |  | 0% | 5.936% | 2.74% | 91.32% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
25 | Service Governors | Asset Level | 0% | 24% | 28.02% | 0.9516% | 47.03% |  | 0% | 22.73% | 11.84% | 2.22% | 63.2% |  | 0% | 40.18% | 11.84% | 2.22% | 45.76% |  | 0% | 22.42% | 7.798% | 2.538% | 67.25% |  | 0% | 57.31% | 7.798% | 2.538% | 32.36% | [11 empty] | 0% | 0% | 0% | 0% | 0%
26 | LPG Storage | Asset Level | 0% | 0% | 33.33% | 66.67% | 0% |  | 0% | 0% | 33.33% | 66.67% | 0% |  | 0% | 0% | 33.33% | 66.67% | 0% |  | 0% | 33.33% | 66.67% | 0% | 0% |  | 0% | 33.33% | 66.67% | 0% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%
27 | LPG Mains | Asset Level | 0% | 0% | 1.748% | 0% | 98.25% |  | 0% | 0% | 1.748% | 0% | 98.25% |  | 0% | 0% | 1.748% | 0% | 98.25% |  | 0% | 0% | 1.748% | 0% | 98.25% |  | 0% | 0% | 1.748% | 0% | 98.25% | [11 empty] | 0% | 0% | 0% | 0% | 0%
28 | LPG Services | Asset Level | 0% | 0% | 51.04% | 0% | 46.43% |  | 0% | 0% | 47.86% | 0% | 50.82% |  | 0% | 0% | 51.04% | 0% | 46.43% |  | 0% | 0% | 44.84% | 0% | 55.16% |  | 0% | 0% | 51.04% | 0% | 46.43% | [11 empty] | 2.525% | 1.317% | 2.525% | 0% | 2.525%
29 | LNG Vessels | Asset Level | 0% | 0% | 90% | 10% | 0% |  | 0% | 20% | 70% | 10% | 0% |  | 0% | 20% | 70% | 10% | 0% |  | 0% | 45% | 45% | 10% | 0% |  | 0% | 45% | 45% | 10% | 0% | [11 empty] | 0% | 0% | 0% | 0% | 0%

## 3.16a Capacity Output Data
Scotland GDN
No. of sites where capacity utilisation exceeds the parameter
capacity utilisation | As at 1/4/2013 | As at 31/3/2017 without network intervention | As at 31/3/2017 with network intervention | As at 31/3/2021 without network intervention | As at 31/3/2021 with network intervention
</= 50% | 96 | 89 | 89 | 91 | 91
>50% to </=70% | 29 | 27 | 28 | 28 | 29
>70% to </=80% | 5 | 11 | 17 | 7 | 15
>80% to </=100% | 14 | 13 | 13 | 14 | 12
>100% | 3 | 7 | 0 | 7 | 0
Total no. of sites | 147 | 147 | 147 | 147 | 147