## New project
|  | Design Availability Spreadsheet | [6 empty] | No. 1 | Weather Sensitivity |  | Asset Classes
[10 empty] | Average | Typical North Sea Weather around UK - Average 65 days MTTR for cable | Converter
Project: | [9 empty] | Restricted access | Average 90 days MTTR for cable | Cables
Size: XXXMW | [11 empty] | Other
Timing: 20XX | [9 empty] | Maintenance Sensitivity
Location: Example | [9 empty] | Less frequent | Fewer Maintenance requirements equating to 24 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Units | Circuit Length (km) | Class | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability | % Tot | Available Capacity %
1 |  | Converter | Bipole with earth return (Onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 9.2391 | 50% | Sensitivities
1 | 150 | Cables | Offshore Bipole with Metallic Return Cable | 0.078 | 12.8205 | 65 | 0.0069452 | 39.446 | 50% | Weather | Average
1 | 20 | Cables | Onshore Bipole No Return Cable | 0.0176 | 56.8182 | 40 | 0.0019288 | 10.9546 | 0% | Maintenance | Average
1 |  | Converter | Bipole no earth return (onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 9.2391 | 50% | Converter Outages | Medium Case
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
#N/A
|  |  |  | #N/A | Total |  | 0.012127
#N/A
#N/A
Availability Calculation - Scheduled Maintenance
Units |  | Class | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Unavailability | % Tot | Available Capacity %
1 |  | Other | Scheduled Maintenance Medium Case (1) | 1 | 1 | 2 | 0.0054795 | 31.1211 | 0%
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.0054795 | 100
[5 empty] | Total unavailability |  | 0.017607
[5 empty] | Overall availability |  | 98.24%
Note on E40: mhook: These will have no direct impact on availability but have been included here for completeness
Note on E45: mhook: These will have no direct impact on availability but have been included here for completeness

## Project 1
|  | Design Availability Spreadsheet | [6 empty] | No. 1 | Weather Sensitivity |  |  | Asset Classes
[10 empty] | Average | Typical North Sea Weather around UK - Average 65 days MTTR for cable |  | Converter
Project: | [9 empty] | Restricted access | Average 90 days MTTR for cable |  | Cables
Size: XXXMW | [12 empty] | Other
Timing: 20XX | [9 empty] | Maintenance Sensitivity
Location: Example | [9 empty] | Less frequent | Fewer Maintenance requirements equating to 24 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Units | Circuit Length (km) | Class | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability | % Tot | Available Capacity %
1 |  | Converter | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 13.0297 | 0% | Sensitivities
1 | 110 | Cables | Project 1 Offshore Cable Section | 0.0572 | 17.4825 | 65 | 0.010186 | 40.7953 | 0% | Weather | Average
1 | 29 | Cables | Project 1 Onshore Cable Section | 0.02552 | 39.185 | 40 | 0.0027967 | 11.2006 | 0% | Maintenance | Average
1 |  | Converter | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 13.0297 | 0% | Converter Outages | Medium Case | To vary converter MTBF, change sensitivity in New Project
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A | Project 1 – 1000 MW Symmetrical Monopole, 139 km connection with 110km offshore and 29 km onshore.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A | This is similar to that envisaged for the NEMO project.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
#N/A
|  |  |  | #N/A | Total |  | 0.01949
#N/A
#N/A
Availability Calculation - Scheduled Maintenance
Units |  | Class | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Unavailability | % Tot | Available Capacity %
1 |  | Other | Scheduled Maintenance Medium Case (1) | 1 | 1 | 2 | 0.0054795 | 21.9447 | 0%
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.0054795 | 100
[5 empty] | Total unavailability |  | 0.024969
[5 empty] | Overall availability |  | 97.5%
Note on E40: mhook: These will have no direct impact on availability but have been included here for completeness
Note on E45: mhook: These will have no direct impact on availability but have been included here for completeness

## Project 2
|  | Design Availability Spreadsheet | [6 empty] | No. 1 | Weather Sensitivity |  |  | Asset Classes
[10 empty] | Average | Typical North Sea Weather around UK - Average 65 days MTTR for cable |  | Converter
Project: | [9 empty] | Restricted access | Average 90 days MTTR for cable |  | Cables
Size: XXXMW | [12 empty] | Other
Timing: 20XX | [9 empty] | Maintenance Sensitivity
Location: Example | [9 empty] | Less frequent | Fewer Maintenance requirements equating to 24 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Units | Circuit Length (km) | Class | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability | % Tot | Available Capacity %
1 |  | Converter | Bipole with earth return (Onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 3.9856 | 50% | Sensitivities
1 | 700 | Cables | Project 2 offshore | 0.364 | 2.7473 | 65 | 0.032411 | 79.4093 | 50% | Weather | Average
1 | 50 | Cables | Project 2 onshore | 0.044 | 22.7273 | 40 | 0.002411 | 5.907 | 50% | Maintenance | Average
1 |  | Converter | Bipole with earth return (Onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 3.9856 | 50% | Converter Outages | Medium Case | To vary converter MTBF, change sensitivity in New Project
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A | Project 2 – 1400 MW Bipole, 750 km with 700 km of offshore cable and 50 km of onshore cable, a possible long interconnection.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.038075
Availability Calculation - Scheduled Maintenance
Units |  | Class | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Unavailability | % Tot | Available Capacity %
1 |  | Other | Scheduled Maintenance Medium Case (2) | 1 | 1 | 2 | 0.0027397 | 6.7125 | 50%
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.0027397 | 100
[5 empty] | Total unavailability |  | 0.040815
[5 empty] | Overall availability |  | 95.92%
Note on E40: mhook: These will have no direct impact on availability but have been included here for completeness
Note on E45: mhook: These will have no direct impact on availability but have been included here for completeness

## Project 3 (1)
|  | Design Availability Spreadsheet | [6 empty] | No. 1 | Weather Sensitivity |  |  | Asset Classes
[10 empty] | Average | Typical North Sea Weather around UK - Average 65 days MTTR for cable |  | Converter
Project: | [9 empty] | Restricted access | Average 90 days MTTR for cable |  | Cables
Size: XXXMW | [12 empty] | Other
Timing: 20XX | [9 empty] | Maintenance Sensitivity
Location: Example | [9 empty] | Less frequent | Fewer Maintenance requirements equating to 24 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Units | Circuit Length (km) | Class | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability | % Tot | Available Capacity %
1 |  | Converter | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 7.7994 | 0% | Sensitivities
1 | 140 | Cables | Project 3-1 Offshore | 0.0728 | 13.7363 | 65 | 0.012964 | 31.0794 | 0% | Weather | Average
1 | 10 | Cables | Project 3-1 Onshore | 0.0088 | 113.6364 | 40 | 0.00096438 | 2.3119 | 0% | Maintenance | Average
3 |  | Other | HVDC Circuit Breaker (3-1) | 0.0273 | 36.63 | 25 | 0.0018699 | 4.4826 | 0% | Converter Outages | Medium Case | To vary converter MTBF, change sensitivity in New Project
1 | 140 | Cables | Project 3-1 Offshore | 0.0728 | 13.7363 | 65 | 0.012964 | 31.0794 | 0%
1 | 10 | Cables | Project 3-1 Onshore | 0.0088 | 113.6364 | 40 | 0.00096438 | 2.3119 | 0% | Project 3 (1) - 1800 MW symmetrical monopole, 300km interconnector with an onshore HVDC node consisting
1 |  | Converter | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 7.7994 | 0% | of 3 HVDC circuit breakers (CBs) splitting the connection into two 150 km sections.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A | Each 150 km section consists of 140 km offshore and 10 km onshore.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A | At this first stage, the project will be considered as a point to point 1800 MW interconnector.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.036234
Availability Calculation - Scheduled Maintenance
Units |  | Class | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Unavailability | % Tot | Available Capacity %
1 |  | Other | Scheduled Maintenance Medium Case (3-1) | 1 | 1 | 2 | 0.0054795 | 13.1359 | 0%
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.0054795 | 100
[5 empty] | Total unavailability |  | 0.041714
[5 empty] | Overall availability |  | 95.83%
Note on E40: mhook: These will have no direct impact on availability but have been included here for completeness
Note on E45: mhook: These will have no direct impact on availability but have been included here for completeness

## Project 3 (2)
|  | Design Availability Spreadsheet | [6 empty] | No. 1 | Weather Sensitivity |  |  | Asset Classes
[10 empty] | Average | Typical North Sea Weather around UK - Average 65 days MTTR for cable |  | Converter
Project: | [9 empty] | Restricted access | Average 90 days MTTR for cable |  | Cables
Size: XXXMW | [12 empty] | Other
Timing: 20XX | [9 empty] | Maintenance Sensitivity
Location: Example | [9 empty] | Less frequent | Fewer Maintenance requirements equating to 24 hours per year
[10 empty] | Average | Typical expected maintenance of 48 hours per year
Availability Calculation - Unplanned Outages | [9 empty] | More frequent | Higher Maintenance requirements equating to 72 hours per year
Units | Circuit Length (km) | Class | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability | % Tot | Available Capacity %
1 |  | Converter | Symmetrical Monopole (Onshore) 3-2 | 2 | 0.5 | 0.59375 | 0.0016267 | 5.8174 | 50% | Sensitivities
1 | 140 | Cables | Project 3-2 Offshore | 0.0728 | 13.7363 | 65 | 0.0064822 | 23.1813 | 50% | Weather | Average
1 | 10 | Cables | Project 3-2 Onshore | 0.0088 | 113.6364 | 40 | 0.00048219 | 1.7244 | 50% | Maintenance | Average
3 |  | Other | HVDC Circuit Breaker (3-2) | 0.0273 | 36.63 | 25 | 0.00093493 | 3.3435 | 50% | Converter Outages | Medium Case | To vary converter MTBF, change sensitivity in New Project
1 | 140 | Cables | Project 3-2 Offshore | 0.0728 | 13.7363 | 65 | 0.0064822 | 23.1813 | 50%
1 | 10 | Cables | Project 3-2 Onshore | 0.0088 | 113.6364 | 40 | 0.00048219 | 1.7244 | 50% | Project 3 (2) - 600 MW of generation is connected to the HVDC node via an HVDC converter forming a multi-terminal arrangement.
1 |  | Converter | Symmetrical Monopole (Onshore) 3-2 | 2 | 0.5 | 0.59375 | 0.0016267 | 5.8174 | 50% | The interconnector now has a capacity of 3600 MW during normal operation (with 1800 MW delivered to each side of the interconnector).
1 |  | Converter | Symmetrical Monopole (Onshore) 3-2 | 2 | 0.5 | 0.59375 | 0.0016267 | 5.8174 | 50% | During an outage of either of the 150 km sections, the capacity of the interconnector is restricted to 1800 MW.
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.019744
Availability Calculation - Scheduled Maintenance
Units |  | Class | Maintenance Case (H/M/L) | Maintenance Rate/year | Maintenance Period (years) | Maintenance Duration (Days) | Unavailability | % Tot | Available Capacity %
3 |  | Other | Scheduled Maintenance Medium Case (3-2) | 3 | 0.33333 | 2 | 0.0082192 | 29.393 | 50%
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
|  |  |  | #N/A | - | #N/A | 0 | 0 | #N/A
[5 empty] | Total |  | 0.0082192 | 100
[5 empty] | Total unavailability |  | 0.027963
[5 empty] | Overall availability |  | 97.2%
Note on E40: mhook: These will have no direct impact on availability but have been included here for completeness
Note on E45: mhook: These will have no direct impact on availability but have been included here for completeness

## Converter Data
Converter Outage Factors
Unplanned Outage
Range | MTTR Factor | MTBF Factor (x No of faults/year)
Worst Case | 1 | 1.5
Medium Case | 1 | 1
Best Case | 1 | 0.5
Project Converter Database
Converter Unscheduled Outages
Converter Type | MTTR | MTBF | MTBF | MTTR | Failure Rate (PU) | Unavailability (per Unit) | Available Capacity %
Monopole (Onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0032534 | 0%
Monopole (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0065068 | 0%
Symmetrical Monopole (Onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0032534 | 0%
Symmetrical Monopole (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0065068 | 0%
Bipole with earth return (Onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0016267 | 50%
Bipole with earth return (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0032534 | 50%
Bipole no earth return (onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0016267 | 50%
Bipole no earth return (offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0032534 | 50%
Symmetrical Monopole (Onshore) 3-2 | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0016267 | 50%
User Defined 1 (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0065068 | 0%
User Defined 2 (Onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0016267 | 50%
User Defined 2 (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0032534 | 50%
User Defined 3 (Onshore) | Medium Case | Medium Case | 0.5 | 0.59375 | 2 | 0.0032534 | 0%
User Defined 3 (Offshore) | Medium Case | Medium Case | 0.5 | 1.1875 | 2 | 0.0065068 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
|  | Medium Case |  | 0 | 0 | 0 | 0%
Base Converter Component Availability Data
Unplanned Outage
Component | MTBF (years) | MTTR (Days)
Monopole (Onshore) | 0.5 | 0.59375
Monopole (Offshore) | 0.5 | 1.1875
Symmetrical Monopole (Onshore) | 0.5 | 0.59375
Symmetrical Monopole (Offshore) | 0.5 | 1.1875
Bipole with earth return (Onshore) | 0.5 | 0.59375
Bipole with earth return (Offshore) | 0.5 | 1.1875
Bipole no earth return (onshore) | 0.5 | 0.59375
Bipole no earth return (offshore) | 0.5 | 1.1875
Symmetrical Monopole (Onshore) 3-2 | 0.5 | 0.59375
User Defined 1 (Offshore) | 0.5 | 1.1875
User Defined 2 (Onshore) | 0.5 | 0.59375
User Defined 2 (Offshore) | 0.5 | 1.1875
User Defined 3 (Onshore) | 0.5 | 0.59375
User Defined 3 (Offshore) | 0.5 | 1.1875
AC Filter
Energisation Resistor/Short Switch
DC Converter
DC Reactor
DC Filter
Converter Design Database
Monopole (Onshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 0.59375 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 100% | 0% | 1.1875 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Monopole (Offshore) | Total Unavailability | 0.0065068 | [5 empty] | Total Unscheduled | 0.0065068 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.35% | [7 empty] | 2 | 1.1875 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Monopole (Offshore) | 2 | 0.5 | 1.1875 | 0.0065068 | 100% | 0% | 2.375 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Symmetrical Monopole (Onshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 0.59375 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Symmetrical Monopole (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 100% | 0% | 1.1875 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Symmetrical Monopole (Offshore) | Total Unavailability | 0.0065068 | [5 empty] | Total Unscheduled | 0.0065068 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.35% | [7 empty] | 2 | 1.1875 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Symmetrical Monopole (Offshore) | 2 | 0.5 | 1.1875 | 0.0065068 | 100% | 0% | 2.375 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Bipole with earth return (Onshore) | Total Unavailability | 0.0016267 | [5 empty] | Total Unscheduled | 0.0016267 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.84% | [7 empty] | 2 | 0.59375 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Bipole with earth return (Onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 100% | 50% | 1.1875 | 0.59375
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Bipole with earth return (Offshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 1.1875 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Bipole with earth return (Offshore) | 2 | 0.5 | 1.1875 | 0.0032534 | 100% | 50% | 2.375 | 1.1875
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Bipole no earth return (onshore) | Total Unavailability | 0.0016267 | [5 empty] | Total Unscheduled | 0.0016267 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.84% | [7 empty] | 2 | 0.59375 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Bipole no earth return (onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 100% | 50% | 1.1875 | 0.59375
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Bipole no earth return (offshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 1.1875 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Bipole no earth return (offshore) | 2 | 0.5 | 1.1875 | 0.0032534 | 100% | 50% | 2.375 | 1.1875
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
Symmetrical Monopole (Onshore) 3-2 | Total Unavailability | 0.0016267 | [5 empty] | Total Unscheduled | 0.0016267 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.84% | [7 empty] | 2 | 0.59375 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | Symmetrical Monopole (Onshore) 3-2 | 2 | 0.5 | 0.59375 | 0.0016267 | 100% | 50% | 1.1875 | 0.59375
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
User Defined 1 (Offshore) | Total Unavailability | 0.0065068 | [5 empty] | Total Unscheduled | 0.0065068 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.35% | [7 empty] | 2 | 1.1875 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | User Defined 1 (Offshore) | 2 | 0.5 | 1.1875 | 0.0065068 | 100% | 0% | 2.375 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
User Defined 2 (Onshore) | Total Unavailability | 0.0016267 | [5 empty] | Total Unscheduled | 0.0016267 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.84% | [7 empty] | 2 | 0.59375 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | User Defined 2 (Onshore) | 2 | 0.5 | 0.59375 | 0.0016267 | 100% | 50% | 1.1875 | 0.59375
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
User Defined 2 (Offshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 1.1875 | 50%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | User Defined 2 (Offshore) | 2 | 0.5 | 1.1875 | 0.0032534 | 100% | 50% | 2.375 | 1.1875
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
User Defined 3 (Onshore) | Total Unavailability | 0.0032534 | [5 empty] | Total Unscheduled | 0.0032534 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.67% | [7 empty] | 2 | 0.59375 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | User Defined 3 (Onshore) | 2 | 0.5 | 0.59375 | 0.0032534 | 100% | 0% | 1.1875 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
User Defined 3 (Offshore) | Total Unavailability | 0.0065068 | [5 empty] | Total Unscheduled | 0.0065068 | Overall unscheduled Failure Rate | Overall unscheduled MTTR | Overall unscheduled capacity availability
| Avaialability | 99.35% | [7 empty] | 2 | 1.1875 | 0%
Converter Unscheduled Outages | [7 empty] | Overall Availability calculations
Units | Equipment | Failure Rate | MTBF Years | MTTR Days | Unavailability (per Unit) | % Tot | Available Capacity % | Unscheduled Overall MTTR | Unscheduled Overall Capacity Avilability
1 | User Defined 3 (Offshore) | 2 | 0.5 | 1.1875 | 0.0065068 | 100% | 0% | 2.375 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0
|  | 0 | 0 | 0 | 0 | 0% |  | 0 | 0

## Cable Data
Project Cable Database
| Selection factors | [6 empty] | External Failures |  |  |  | Internal Failures |  |  | Total Failures | [6 empty] | #REF! | Monopole
Cable Name | Technology | Failure Rate (H/M/L) | Installation Risk | Burial Depth | MTTR | Converter arrangement | Cable Configuration | Failure Rate (PA) |  | MTTR | Available Capacity (%) | Failure Rate | MTTR | Availability Capacity | Failure Rate (PA) | MTTR | Available Capacity |  |  |  |  | #REF! | Monopole
Project 1 Offshore Cable Section | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00025 |  | 65 | 0% | 0.00027 | 65 | 0% | 0.00052 | 65 | 0% |  |  |  |  | #REF! | Symetrical Monopole
Project 1 Onshore Cable Section | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00058 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.00088 | 40 | 0% |  |  |  |  | #REF! | Symetrical Monopole
Project 2 onshore | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Bipole with earth rerun | Unbundled | 0.00058 |  | 40 | 50% | 0.0003 | 40 | 50% | 0.00088 | 40 | 50% |  |  |  |  | #REF! | Bipole no earth return
Project 2 offshore | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Bipole with earth rerun | Unbundled | 0.00025 |  | 65 | 50% | 0.00027 | 65 | 50% | 0.00052 | 65 | 50% |  |  |  |  | #REF! | Bipole no earth return
Project 3-1 Offshore | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00025 |  | 65 | 0% | 0.00027 | 65 | 0% | 0.00052 | 65 | 0% |  |  |  |  | #REF! | Bipole with earth rerun
Project 3-1 Onshore | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00058 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.00088 | 40 | 0% |  |  |  |  | #REF! | Bipole with earth rerun
Project 3-2 Onshore | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | User Defined 1 | Unbundled | 0.00058 |  | 40 | 50% | 0.0003 | 40 | 50% | 0.00088 | 40 | 50% |  |  |  |  | #REF! | User Defined 1
Project 3-2 Offshore | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | User Defined 1 | Unbundled | 0.00025 |  | 65 | 50% | 0.00027 | 65 | 50% | 0.00052 | 65 | 50% |  |  |  |  | #REF! | User Defined 1
Offshore Symmetrical Monopole Cable | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00025 |  | 65 | 0% | 0.00027 | 65 | 0% | 0.00052 | 65 | 0% |  |  |  |  | #REF! | User Defined 2
Onshore Symmetrical Monople Cable | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Symetrical Monopole | Unbundled | 0.00058 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.00088 | 40 | 0% |  |  |  |  | #REF! | User Defined 2
Offshore Bipole with Metallic Return Cable | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Bipole with earth rerun | Unbundled | 0.00025 |  | 65 | 50% | 0.00027 | 65 | 50% | 0.00052 | 65 | 50% |  |  |  |  | #REF! | User Defined 3
Onshore Bipole with Metallic Return Cable | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Bipole with earth rerun | Unbundled | 0.00058 |  | 40 | 50% | 0.0003 | 40 | 50% | 0.00088 | 40 | 50% |  |  |  |  | #REF! | User Defined 3
Offshore Bipole No Return Cable | HVDC subsea MIND Cable | Average | Average | Normal Burial | Average | Bipole no earth return | Unbundled | 0.00025 |  | 65 | 0% | 0.00027 | 65 | 0% | 0.00052 | 65 | 0%
Onshore Bipole No Return Cable | HVDC Onshore MIND Cable | Average | Average | Normal Burial | Average | Bipole no earth return | Unbundled | 0.00058 |  | 40 | 0% | 0.0003 | 40 | 0% | 0.00088 | 40 | 0%
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
[8 empty] | ---- |  | ---- | ---- | ---- | ---- | ---- | ---- | ---- | ----
Base Availability Data | [13 empty] | Cable Factors
| External Failures (No/km/year) |  |  | MTTR (Days) |  | Internal Failures (No/km/year) |  |  | MTTR (Days) |  |  |  |  | Converter Arrangement |  |  |  | Cable Bundling Arrangement |  | Installation Risk Factor
Cable Type | High | Low | Average | Average | High | High | Low | Average | Average | High |  |  |  | Converter Arrangement | Available Capacity (%) |  |  | Arrangement | Factor | Risk | Factor
AC subsea XLPE Cable | 0.000375 | 0.0001875 | 0.00025 | 65 | 90 | 0.000405 | 0.0002025 | 0.00027 | 65 | 90 |  |  |  | Monopole | 0% |  |  | Bundled | 0 | High | 1.2
AC Onshore XLPE Cable | 0.00087 | 0.000435 | 0.00058 | 20 | 30 | 0.00045 | 0.000225 | 0.0003 | 20 | 30 |  |  |  | Symetrical Monopole | 0% |  |  | Unbundled | 1 | Low | 0.8
HVDC subsea XLPE Cable | 0.000375 | 0.0001875 | 0.00025 | 65 | 90 | 0.000405 | 0.0002025 | 0.00027 | 65 | 90 |  |  |  | Bipole no earth return | 0% |  |  |  |  | Average | 1
HVDC Onshore XLPE Cable | 0.00087 | 0.000435 | 0.00058 | 20 | 30 | 0.00045 | 0.000225 | 0.0003 | 20 | 30 |  |  |  | Bipole with earth rerun | 50%
HVDC subsea MIND Cable | 0.000375 | 0.0001875 | 0.00025 | 65 | 90 | 0.000405 | 0.0002025 | 0.00027 | 65 | 90 |  |  |  | User Defined 1 | 50% |  |  | Burial Depth
HVDC Onshore MIND Cable | 0.00087 | 0.000435 | 0.00058 | 40 | 65 | 0.00045 | 0.000225 | 0.0003 | 40 | 65 |  |  |  | User Defined 2 | 50% |  |  | Burial Depth | Factor
[14 empty] | User Defined 3 | 75% |  |  | Deep Buried (>1.5m) | 0.8
[14 empty] | AC 1 | 0% |  |  | Normal Burial | 1
[14 empty] | AC2 | 86.4% |  |  | Unburied | 1.2
[14 empty] | AC3 | 66.67%
[14 empty] | Converter Type | Symmetrical Monopole (Onshore)

## Other
Other Equipment Database
| Unplanned Outage |  | Scheduled Maintenance |  | Available Capacity (%)
Component | Failure Rate (PA) | MTTR (Days) | Maintainence Rate (PA) | MTTR (Days)
Scheduled Maintenance Less frequent Case (1) | 0 | 0 | 1 | 1 | 0%
Scheduled Maintenance Medium Case (1) | 0 | 0 | 1 | 2 | 0%
Scheduled Maintenance more frequent Case (1) | 0 | 0 | 1 | 3 | 0%
HVDC Circuit Breaker (3-1) | 0.0091 | 25 | 0 | 0 | 0%
Scheduled Maintenance less frequent Case (3-2) | 0 | 0 | 1 | 1 | 50%
Scheduled Maintenance Medium Case (3-2) | 0 | 0 | 1 | 2 | 50%
Scheduled Maintenance more frequent Case (3-2) | 0 | 0 | 1 | 3 | 50%
HVDC Circuit Breaker (3-2) | 0.0091 | 25 | 0 | 0 | 50%
Scheduled Maintenance less frequent Case (2) | 0 | 0 | 1 | 1 | 50%
Scheduled Maintenance Medium Case (2) | 0 | 0 | 1 | 2 | 50%
Scheduled Maintenance more frequent Case (2) | 0 | 0 | 1 | 3 | 50%
Scheduled Maintenance less frequent Case (3-1) | 0 | 0 | 1 | 1 | 0%
Scheduled Maintenance Medium Case (3-1) | 0 | 0 | 1 | 2 | 0%
Scheduled Maintenance more frequent Case (3-1) | 0 | 0 | 1 | 3 | 0%
Converter Transformer | 0.03276 | 7.5 | 0 | 0 | 0%
Transformer Failure Rate Breakdown
Name | Outage Type | Failure Rate (PA) | MTTR (Days)
Transformers - Unplanned Outages
Converter Transformer | In-Situ Repair | 0.02637 | 7.5
| BTWR | 0.00639 | 90
| Overall | 0.03276 | 23.592