## Schedule 2
Schedule 2D: Network Assets Workbook
| DNO Name: | WPD
| Reporting price base: | Price base (2012/13)
DNO Name
[DNO]
WPD
ENWL
NPG
SP
SSE
UKPN

## NAW1 - DPCR5 View - EMID
HI1: Network Outputs DPCR5
EMID
Price base (2012/13)
| ASSET CATEGORIES | ASSET REGISTER |  | HEALTH INDEX - CURRENT (as at 31 March) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with no further DPCR5 intervention) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with DPCR5 actual & forecast intervention) |  |  |  |  | DATA QUALITY - CURRENT (as at 31 March)
[19 empty] | Number of assets included for HI output measure | Primary form of measure | Number of assets actually observed | Average age of data used | Description of the form of measure used to assign a HI, the quality of data used, and any other relevant information | Degradation assumption adopted
|  | Current (as at 31 March) | Forecast (as at 31 March 2015) | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | Assets | Health Condition Age Other | % | Years | Commentary | Description
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 115545 | 115445 | 42847 | 38701 | 20724 | 3675 | 9598 | 37247 | 38701 | 21004 | 4515 | 14078 | 42847 | 38701 | 20624 | 3675 | 9598 | 115545 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
| LV Switchgear (at s/s) | 18398 | 18593 | 9913 | 3637 | 4702 | 91 | 55 | 9542 | 3116 | 5505 | 163 | 72 | 10069 | 3050 | 5387 | 66 | 21 | 18398 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| LV UGB and LV Pillar OD (not at s/s) | 28908 | 29009 | 5447 | 6890 | 15535 | 481 | 555 | 5279 | 5332 | 16865 | 586 | 846 | 5830 | 5315 | 16813 | 586 | 465 | 28908 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV Network
| HV Switchgear (GM) - Primary | 4317 | 4332 | 1532 | 607 | 2111 | 36 | 31 | 1375 | 614 | 2197 | 98 | 33 | 1489 | 609 | 2135 | 97 | 2 | 4317 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Switchgear (GM) - Distribution | 28757 | 27893 | 13671 | 4727 | 9545 | 608 | 206 | 12540 | 5417 | 9351 | 938 | 511 | 14355 | 4912 | 8599 | 27 | 0 | 28757 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Transformer (GM) | 19563 | 19718 | 10860 | 3939 | 4321 | 216 | 227 | 10346 | 3613 | 4952 | 312 | 340 | 10640 | 3588 | 4926 | 312 | 252 | 19563 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV UG Cable
| HV OHL Support - Poles | 147489 | 148096 | 31233 | 60541 | 28601 | 5426 | 21688 | 25850 | 60541 | 28870 | 6233 | 25995 | 31840 | 60541 | 28601 | 5426 | 21688 | 147489 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
EHV Network
| EHV Switchgear (GM) | 1306 | 1318 | 734 | 148 | 418 | 2 | 4 | 645 | 237 | 413 | 7 | 4 | 702 | 224 | 387 | 5 | 0 | 1306 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV Transformer | 711 | 712 | 181 | 117 | 385 | 19 | 9 | 144 | 130 | 378 | 45 | 14 | 163 | 127 | 366 | 45 | 11 | 711 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Oil) | 160.71 | 160.71 | 22.402 | 111.235 | 27.073 | 0 | 0 | 21.971 | 103.424 | 35.315 | 0 | 0 | 21.971 | 103.424 | 35.315 | 0 | 0 | 160.71 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 1140 | 1138 | 1 | 792 | 136 | 125 | 86 | 1 | 792 | 67 | 97 | 183 | 192 | 804 | 65 | 77 | 0 | 1140 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Support - Poles | 27573 | 27573 | 2775 | 6429 | 13100 | 2149 | 3120 | 1875 | 6429 | 13145 | 2284 | 3840 | 2775 | 6429 | 13100 | 2149 | 3120 | 27573 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 2280 | 2272 | 126 | 554 | 823 | 101 | 676 | 126 | 554 | 738 | 93 | 769 | 126 | 551 | 733 | 93 | 769 | 2280 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Conductor (Tower Lines) | 842.96 | 861.25 | 0 | 66.877 | 736.872 | 39.211 | 0 | 0 | 66.877 | 736.873 | 0 | 39.21 | 58 | 66.834 | 736.416 | 0 | 0 | 842.96 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV Network
| 132kV CBs | 255 | 263 | 106 | 32 | 69 | 43 | 5 | 86 | 52 | 51 | 58 | 8 | 98 | 52 | 51 | 54 | 8 | 255 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV Transformer | 194 | 193 | 55 | 20 | 111 | 7 | 1 | 48 | 23 | 111 | 6 | 6 | 57 | 23 | 106 | 4 | 3 | 194 | Health | 1 | 1.5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Oil) | 162 | 149.27 | 20.093 | 70.692 | 58.486 | 12.729 | 0 | 20.093 | 56.855 | 72.323 | 12.729 | 0 | 20.093 | 56.855 | 72.322 | 0 | 0 | 162 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 4562 | 4552 | 171 | 3685 | 492 | 211 | 3 | 171 | 3684 | 445 | 99 | 163 | 296 | 3720 | 445 | 91 | 0 | 4562 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 9124 | 9084 | 850 | 1425 | 5084 | 1210 | 555 | 850 | 1000 | 4782 | 1280 | 1212 | 844 | 993 | 4755 | 1280 | 1212 | 9124 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV OHL Conductor (Tower Lines) | 2243 | 2239.4 | 80.618 | 292.298 | 1665.202 | 133.082 | 71.8 | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 | 2243 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
Other
Submarine Cables
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required
Note on U7: Ofgem: Insert one of the following: Health; Condition; Age; or Other.

## NAW2 - Total - EMID
HI2: Secondary deliverables RIIO-ED1
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) with investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) with investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | Yes | Expenditure on Health Index asset categories | LV | 13.3622 | 26.8534 | 52.2517
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | No | Expenditure on Health Index asset categories | HV | 28.269 | 53.854 | 106.605
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | EHV | 25.334 | 45.0176 | 81.8724
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | 132kV | 28.3645 | 72.4497 | 117.1772
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Health Index asset categories | Total | 95.3297 | 198.1747 | 357.9064
| LV UGB |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 8614 | 3150 | 5410 | 57 | 0 | 17231 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 7730 | 3979 | 5448 | 74 | 0 | 17231 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 537 | 190 | 618 | 9 | 0 | 1354 | 458 | 195 | 655 | 23 | 23 | 1354 | 551 | 188 | 595 | 20 | 0 | 1354 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 9158 | 3340 | 6029 | 66 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 8288 | 4167 | 6044 | 94 | 0 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 5839 | 3898 | 15993 | 1531 | 726 | 27987 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 6038 | 2592 | 12989 | 3687 | 2681 | 27987 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 101 | 198 | 645 | 52 | 26 | 1022 | 75 | 199 | 649 | 52 | 47 | 1022 | 107 | 115 | 550 | 155 | 95 | 1022 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 | 30004 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 5940 | 4096 | 16638 | 1583 | 752 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 6145 | 2707 | 13539 | 3842 | 2776 |  | 4361 | 2740 | 13705 | 3889 | 4314
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 266 | 167 | 292 | 84 | 0 | 809 | 232 | 167 | 301 | 84 | 25 | 809 | 287 | 150 | 215 | 121 | 36 | 809 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 1003 | 449 | 1006 | 165 | 0 | 2623 | 808 | 449 | 1049 | 261 | 56 | 2623 | 1141 | 379 | 728 | 364 | 11 | 2623 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 314 | 147 | 365 | 54 | 0 | 880 | 209 | 147 | 377 | 127 | 20 | 880 | 371 | 131 | 248 | 127 | 3 | 880 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 8 | 5 | 7 | 0 | 0 | 20 | 6 | 5 | 7 | 1 | 1 | 20 | 10 | 5 | 3 | 2 | 0 | 20 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 1591 | 768 | 1670 | 303 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 1809 | 665 | 1194 | 614 | 50 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 6016 | 941 | 2202 | 347 | 0 | 9506 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 5152 | 1779 | 1626 | 874 | 3 | 9434 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 4968 | 4108 | 3246 | 567 | 0 | 12889 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 4837 | 4320 | 2524 | 1090 | 3 | 12774 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 2198 | 1320 | 1566 | 20 | 0 | 5104 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 2250 | 1456 | 983 | 352 | 0 | 5041 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 69 | 9 | 64 | 0 | 0 | 142 | 61 | 18 | 64 | 0 | 0 | 143 | 71 | 2 | 43 | 24 | 0 | 140 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 13251 | 6378 | 7078 | 934 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 12310 | 7557 | 5176 | 2340 | 6 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 1817 | 514 | 894 | 79 | 2 | 3306 | 1646 | 518 | 900 | 91 | 151 | 3306 | 1665 | 725 | 804 | 107 | 5 | 3306 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 6778 | 2781 | 3302 | 167 | 0 | 13028 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 6139 | 3376 | 3287 | 226 | 0 | 13028 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 1354 | 545 | 1309 | 58 | 0 | 3266 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 1405 | 619 | 1153 | 88 | 1 | 3266 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 62 | 14 | 35 | 7 | 0 | 118 | 46 | 14 | 35 | 13 | 10 | 118 | 64 | 27 | 25 | 2 | 0 | 118 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 10011 | 3854 | 5540 | 311 | 2 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 9273 | 4747 | 5269 | 423 | 6 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 27866 | 52987 | 25032 | 4749 | 18981 | 129615 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 54 | 103 | 49 | 9 | 38 | 253 | 31 | 103 | 50 | 13 | 56 | 253 | 54 | 104 | 49 | 9 | 37 | 253 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 4267 | 60541 | 29980 | 9562 | 43746
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 399 | 147 | 52 | 62 | 8 | 668 | 336 | 158 | 52 | 95 | 17 | 658 | 386 | 193 | 49 | 13 | 36 | 677 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 234 | 76 | 79 | 49 | 0 | 438 | 179 | 80 | 79 | 92 | 2 | 432 | 313 | 82 | 21 | 29 | 1 | 446 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 89 | 15 | 35 | 4 | 0 | 143 | 62 | 18 | 35 | 17 | 5 | 137 | 119 | 10 | 14 | 8 | 0 | 151 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 54 | 24 | 13 | 0 | 0 | 91 | 17 | 24 | 27 | 23 | 0 | 91 | 60 | 21 | 7 | 3 | 0 | 91 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 776 | 262 | 179 | 115 | 8 |  | 594 | 280 | 193 | 227 | 24 |  | 878 | 306 | 91 | 53 | 37 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 54 | 52 | 82 | 31 | 15 | 234 | 46 | 53 | 82 | 31 | 22 | 234 | 59 | 61 | 65 | 24 | 25 | 234 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 100 | 40 | 143 | 13 | 3 | 299 | 62 | 40 | 146 | 13 | 29 | 290 | 104 | 47 | 75 | 72 | 5 | 303 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 57 | 31 | 80 | 11 | 0 | 179 | 32 | 37 | 84 | 18 | 8 | 179 | 71 | 29 | 52 | 25 | 2 | 179 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 1 | 6 | 2 | 0 | 9 | 2 | 1 | 4 | 2 | 0 | 9 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 211 | 124 | 311 | 57 | 18 |  | 140 | 131 | 318 | 64 | 59 |  | 236 | 138 | 196 | 123 | 32 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 26 | 87 | 9 | 18 | 0 | 140 | 24 | 85 | 9 | 20 | 2 | 140 | 26 | 85 | 10 | 19 | 0 | 140 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 104 | 383 | 23 | 44 | 3 | 557 | 100 | 373 | 23 | 54 | 7 | 557 | 105 | 392 | 24 | 36 | 0 | 557 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 68 | 320 | 39 | 13 | 1 | 441 | 68 | 308 | 39 | 25 | 1 | 441 | 68 | 329 | 40 | 4 | 0 | 441 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 198 | 790 | 71 | 75 | 4 |  | 192 | 766 | 71 | 99 | 10 |  | 199 | 806 | 74 | 59 | 0 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 501 | 845 | 1680 | 242 | 354 | 3622 | 198 | 845 | 1735 | 297 | 547 | 3622 | 649 | 844 | 1635 | 198 | 296 | 3622 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 3595 | 5027 | 9998 | 1435 | 2115 | 22170 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 4695 | 5028 | 9637 | 1171 | 1760 | 22291 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 328 | 553 | 1100 | 158 | 234 | 2373 | 129 | 553 | 1138 | 195 | 358 | 2373 | 425 | 553 | 1071 | 129 | 195 | 2373 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 4 | 4 | 9 | 1 | 0 | 18 | 0 | 4 | 9 | 2 | 3 | 18 | 3 | 4 | 9 | 0 | 2 | 18 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 4428 | 6429 | 12787 | 1836 | 2703 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 5772 | 6429 | 12352 | 1498 | 2253 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 59 | 71 | 171 | 0 | 69 | 370 | 51 | 71 | 171 | 0 | 77 | 370 | 128 | 71 | 96 | 75 | 0 | 370 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 633 | 180 | 840 | 22 | 227 | 1902 | 75 | 180 | 840 | 22 | 785 | 1902 | 882 | 38 | 408 | 574 | 0 | 1902 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 692 | 251 | 1011 | 22 | 296 |  | 126 | 251 | 1011 | 22 | 862 |  | 1010 | 109 | 504 | 649 | 0 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 67.017 | 0 | 74.589 | 14 | 0 | 155.606 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 81.017 | 0 | 0 | 74.589 | 0 | 155.606 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0.158 | 0 | 705.486 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0.158 | 0 | 66.819 | 638.667 | 0 | 705.644 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 67.175 | 0 | 780.075 | 14 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 81.175 | 0 | 66.819 | 713.256 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 46 | 14 | 16 | 21 | 18 | 115 | 33 | 25 | 16 | 21 | 20 | 115 | 68 | 13 | 7 | 16 | 18 | 122 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 51 | 11 | 13 | 5 | 8 | 88 | 35 | 21 | 15 | 5 | 12 | 88 | 70 | 12 | 0 | 12 | 0 | 94 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 25 | 0 | 4 | 1 | 0 | 30 | 8 | 1 | 4 | 1 | 16 | 30 | 33 | 0 | 0 | 1 | 0 | 34 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 10 | 14 | 5 | 1 | 0 | 30 | 3 | 19 | 5 | 1 | 2 | 30 | 11 | 13 | 5 | 1 | 0 | 30 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 132 | 39 | 38 | 28 | 26 |  | 79 | 66 | 40 | 28 | 50 |  | 182 | 38 | 12 | 30 | 18 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 17 | 8 | 34 | 4 | 0 | 63 | 14 | 8 | 34 | 4 | 3 | 63 | 21 | 8 | 19 | 14 | 1 | 63 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 40 | 2 | 30 | 1 | 0 | 73 | 24 | 2 | 31 | 10 | 0 | 67 | 52 | 4 | 14 | 3 | 0 | 73 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 12 | 12 | 31 | 0 | 0 | 55 | 6 | 12 | 32 | 1 | 3 | 54 | 13 | 12 | 23 | 7 | 0 | 55 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 1 | 7 | 1 | 0 | 0 | 9 | 1 | 7 | 1 | 0 | 0 | 9 | 1 | 6 | 2 | 0 | 0 | 9 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 70 | 29 | 96 | 5 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 87 | 30 | 58 | 24 | 1 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 2.543 | 16.153 | 27.394 | 0 | 0 | 46.09 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 2.127 | 8.62 | 34.755 | 0 | 0 | 45.502 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 1.675 | 20.001 | 37.476 | 0 | 0 | 59.152 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0.052 | 16.899 | 41.393 | 0 | 0 | 58.344 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 6.683 | 11.746 | 22.895 | 0 | 0 | 41.324 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 2.06 | 14.111 | 24.549 | 0 | 0 | 40.72 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0.005 | 0.032 | 0 | 0 | 0 | 0.037 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.032 | 0 | 0 | 0 | 0.037 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 10.906 | 47.932 | 87.765 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 4.244 | 39.662 | 100.697 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 114 | 1171 | 141 | 12 | 3 | 1441 | 111 | 1145 | 141 | 38 | 6 | 1441 | 117 | 1160 | 142 | 22 | 0 | 1441 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 93 | 1610 | 223 | 0 | 0 | 1926 | 91 | 1590 | 223 | 20 | 2 | 1926 | 115 | 1610 | 198 | 3 | 0 | 1926 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 89 | 911 | 44 | 0 | 1 | 1045 | 89 | 871 | 44 | 40 | 1 | 1045 | 96 | 894 | 53 | 2 | 0 | 1045 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 5 | 85 | 50 | 0 | 0 | 140 | 5 | 79 | 50 | 6 | 0 | 140 | 5 | 87 | 48 | 0 | 0 | 140 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 301 | 3777 | 458 | 12 | 4 |  | 296 | 3685 | 458 | 104 | 9 |  | 333 | 3751 | 441 | 27 | 0 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 987 | 143 | 985 | 237 | 415 | 2767 | 419 | 143 | 985 | 237 | 979 | 2763 | 1550 | 92 | 624 | 499 | 0 | 2765 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 767 | 223 | 2553 | 208 | 245 | 3996 | 322 | 223 | 2553 | 216 | 678 | 3992 | 1122 | 79 | 2081 | 715 | 0 | 3997 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 483 | 42 | 1077 | 16 | 379 | 1997 | 94 | 42 | 1077 | 16 | 767 | 1996 | 895 | 21 | 843 | 239 | 0 | 1998 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 59 | 50 | 186 | 0 | 38 | 333 | 9 | 50 | 186 | 0 | 88 | 333 | 103 | 49 | 100 | 81 | 0 | 333 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 2296 | 458 | 4801 | 461 | 1077 |  | 844 | 458 | 4801 | 469 | 2512 |  | 3670 | 241 | 3648 | 1534 | 0 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 70.88 | 37.226 | 531.437 | 16.886 | 23.378 | 679.807 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 114.78 | 36.988 | 240.883 | 287.157 | 0 | 679.808 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 52.126 | 15.055 | 855.192 | 22.609 | 40.052 | 985.034 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 120.349 | 14.959 | 219.285 | 630.441 | 0 | 985.034 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 3.14 | 28.185 | 444.982 | 0.654 | 15.399 | 492.36 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 22.217 | 28.005 | 139.8 | 302.338 | 0 | 492.36 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0.004 | 0 | 57.216 | 24.979 | 0 | 82.199 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 23.404 | 0 | 3.149 | 55.646 | 0 | 82.199 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 126.15 | 80.466 | 1888.827 | 65.128 | 78.829 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 280.75 | 79.952 | 603.117 | 1275.582 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 431571.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 123964.541 | 130037.065 | 108759.4 | 14988.128 | 36254.829 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 125255.355 | 131118.446 | 98678.325 | 22399.838 | 36465 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW3 - Asset Repl - EMID
HI3: Secondary deliverables RIIO-ED1 - Asset replacement
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Asset Replacement associated with HI Categories | LV | 12.741 | 25.551 | 49.575
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Asset Replacement associated with HI Categories | HV | 26.893 | 50.883 | 100.378
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | EHV | 15.571 | 31.321 | 62.145
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | 132kV | 16.599 | 25.337 | 52.99
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Asset Replacement associated with HI Categories | Total | 71.804 | 133.092 | 265.088
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 11440 | 0 | -572 | -1716 | -9152 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 22524 | 0 | -1126 | -3379 | -18019 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 11440 | 0 | -572 | -1716 | -9152 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 22524 | 0 | -1126 | -3379 | -18019 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 598 | -107 | -316 | -109 | -66 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 1190 | -207 | -96 | -619 | -268 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 78 | -5 | -36 | -14 | -23 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 161 | -17 | -21 | -74 | -49 | 0 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 676 | -112 | -352 | -123 | -89 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 1351 | -224 | -117 | -693 | -317 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 731 | 0 | 0 | 0 | -731 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 1456 | 0 | 0 | 0 | -1456 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 21 | 0 | 0 | 0 | -21 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 48 | 0 | 0 | 0 | -48 | 0 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 | 30004 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 752 | 0 | 0 | 0 | -752 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 1504 | 0 | 0 | 0 | -1504 |  | 4361 | 2740 | 13705 | 3889 | 4314
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 34 | 0 | -9 | 0 | -25 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 91 | -18 | 0 | 0 | -73 | 0 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 195 | 0 | -43 | -96 | -56 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 397 | -85 | 0 | 0 | -312 | 0 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 105 | 0 | -12 | -73 | -20 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 181 | -25 | 0 | -11 | -145 | 0 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 2 | 0 | 0 | -1 | -1 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 4 | 0 | 0 | -2 | -2 | 0 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 336 | 0 | -64 | -170 | -102 |  | 1255 | 768 | 1734 | 473 | 102 |  | 673 | -128 | 0 | -13 | -532 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 370 | -156 | -1 | -276 | 0 | -63 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 795 | -330 | 0 | -119 | -481 | -135 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 614 | -81 | 0 | -638 | 0 | -105 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 1288 | -146 | 0 | -411 | -951 | -220 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 483 | -10 | -41 | -515 | 0 | -83 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 860 | -18 | 0 | -616 | -372 | -146 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 8 | -9 | 0 | 0 | 0 | -1 | 61 | 18 | 64 | 0 | 0 | 143 | 18 | -18 | 0 | -3 | 0 | -3 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 1475 | -256 | -42 | -1429 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 2961 | -512 | 0 | -1149 | -1804 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 161 | 0 | 0 | -12 | -149 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 286 | 0 | 0 | -20 | -266 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 436 | 0 | 0 | -93 | -343 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 895 | 0 | 0 | -213 | -682 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 224 | 0 | 0 | -67 | -157 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 461 | 0 | 0 | -123 | -338 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 16 | 0 | 0 | -6 | -10 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 33 | 0 | 0 | -7 | -26 | 0 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 837 | 0 | 0 | -178 | -659 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 1675 | 0 | 0 | -363 | -1312 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 11938 | 0 | -598 | -1790 | -9550 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 24132 | 0 | -1207 | -3620 | -19305 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 1680 | 0 | -83 | -252 | -1345 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 3394 | 0 | -170 | -509 | -2715 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 23 | 0 | -1 | -4 | -18 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 47 | 0 | -2 | -7 | -38 | 0 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 13641 | 0 | -682 | -2046 | -10913 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 27573 | 0 | -1379 | -4136 | -22058 |  | 4267 | 60541 | 29980 | 9562 | 43746
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 42 | 0 | 0 | -33 | -9 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 81 | 0 | 0 | 0 | -81 | 0 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 45 | 0 | 0 | -43 | -2 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 125 | 0 | 0 | -20 | -105 | 0 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 18 | 0 | 0 | -13 | -5 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 37 | 0 | 0 | -4 | -33 | 0 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 37 | 0 | -14 | -23 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 40 | 0 | 0 | -11 | -29 | 0 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 142 | 0 | -14 | -112 | -16 |  | 594 | 280 | 193 | 227 | 24 |  | 283 | 0 | 0 | -35 | -248 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 7 | 0 | 0 | 0 | -7 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 28 | 0 | 0 | 0 | -28 | 0 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 26 | 0 | 0 | 0 | -26 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 38 | 0 | 0 | 0 | -38 | 0 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 15 | 0 | 0 | -7 | -8 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 28 | 0 | 0 | -4 | -24 | 0 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 48 | 0 | 0 | -7 | -41 |  | 140 | 131 | 318 | 64 | 59 |  | 96 | 0 | 0 | -4 | -92 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 2 | 0 | 0 | 0 | -2 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 4 | 0 | 0 | 0 | -4 | 0 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 4 | 0 | 0 | 0 | -4 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 10 | 0 | 0 | 0 | -10 | 0 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 5 | 0 | 0 | 0 | -5 | 0 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 6 | 0 | 0 | 0 | -6 |  | 192 | 766 | 71 | 99 | 10 |  | 19 | 0 | 0 | 0 | -19 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 303 | 0 | -55 | -55 | -193 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 631 | 0 | -116 | -116 | -399 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 1811 | 0 | -335 | -336 | -1140 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 3769 | 0 | -696 | -697 | -2376 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 199 | 0 | -38 | -37 | -124 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 415 | 0 | -78 | -77 | -260 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 4 | 0 | 0 | -1 | -3 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 3 | 0 | 0 | -2 | -1 | 0 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 2317 | 0 | -428 | -429 | -1460 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 4818 | 0 | -890 | -892 | -3036 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 8 | 0 | 0 | 0 | -8 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 77 | 0 | 0 | 0 | -77 | 0 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 558 | 0 | 0 | 0 | -558 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 807 | 0 | 0 | 0 | -807 | 0 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 566 | 0 | 0 | 0 | -566 |  | 126 | 251 | 1011 | 22 | 862 |  | 884 | 0 | 0 | 0 | -884 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 9 | 0 | 0 | -9 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 23 | 0 | 0 | 0 | -23 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 9 | 0 | 0 | -9 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 23 | 0 | 0 | 0 | -23 |  | 58 | 0 | 66.834 | 713.416 | 23
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 1 | 0 | 0 | 0 | -1 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 11 | 0 | 0 | 0 | -11 | 0 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 4 | 0 | 0 | 0 | -4 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 16 | 0 | 0 | 0 | -16 | 0 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 16 | 0 | 0 | 0 | -16 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 17 | 0 | 0 | 0 | -17 | 0 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 23 | 0 | 0 | 0 | -23 |  | 79 | 66 | 40 | 28 | 50 |  | 47 | 0 | 0 | 0 | -47 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 3 | 0 | 0 | 0 | -3 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 7 | 0 | 0 | 0 | -7 | 0 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 9 | 0 | 0 | -9 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 23 | 0 | 0 | -11 | -12 | 0 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 4 | 0 | 0 | -1 | -3 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 5 | 0 | 0 | -1 | -4 | 0 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 16 | 0 | 0 | -10 | -6 |  | 45 | 29 | 98 | 15 | 6 |  | 35 | 0 | 0 | -12 | -23 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 3 | 0 | 0 | 0 | -3 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 6 | 0 | 0 | 0 | -6 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 2 | 0 | 0 | 0 | -2 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 2 | 0 | 0 | 0 | -2 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 7 | 0 | 0 | 0 | -7 | 0 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 5 | 0 | 0 | 0 | -5 |  | 296 | 3685 | 458 | 104 | 9 |  | 15 | 0 | 0 | 0 | -15 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 564 | 0 | 0 | 0 | -564 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 1093 | 0 | 0 | 0 | -1093 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 441 | 0 | 0 | -8 | -433 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 713 | 0 | 0 | 0 | -713 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 388 | 0 | 0 | 0 | -388 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 767 | 0 | 0 | 0 | -767 | 0 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 50 | 0 | 0 | 0 | -50 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 88 | 0 | 0 | 0 | -88 | 0 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 1443 | 0 | 0 | -8 | -1435 |  | 844 | 458 | 4801 | 469 | 2512 |  | 2661 | 0 | 0 | 0 | -2661 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 70.837 | 0 | 0 | 0 | -70.837 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 111.102 | 0 | 0 | -16.886 | -94.215 | 0.001 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 52.059 | 0 | 0 | 0 | -52.059 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 114.72 | 0 | 0 | -19.967 | -94.753 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 3.104 | 0 | 0 | 0 | -3.104 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 19.157 | 0 | 0 | -0.654 | -18.503 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 23.021 | 0 | 0 | -23.021 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 126 | 0 | 0 | 0 | -126 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 268 | 0 | 0 | -60.528 | -207.471 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 431571.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 33858 | -368 | -2154 | -6237 | -25351 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 67410 | -864 | -3512 | -10736.528 | -52801.471 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW4 - Refurb - EMID
HI4: Secondary deliverables RIIO-ED1 - refurbishment
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV | 0.252 | 0.564 | 1.2
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV | 0.769 | 1.757 | 3.799
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV | 0.638 | 1.251 | 2.461
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV | 2.622 | 7.017 | 14.185
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 4.281 | 10.589 | 21.645
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 0 | 0 | 0 | 0 | 0 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 0 | 0 | 0 | 0 | 0 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 0 | 0 | 0 | 0 | 0 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 0 | 0 | 0 | 0 | 0 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 0 | 0 | 0 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 0 | 0 | 0 | 0 | 0 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 0 | 0 | 0 | 0 | 0 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 | 30004 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 0 | 0 | 0 | 0 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 0 | 0 | 0 | 0 | 0 |  | 4361 | 2740 | 13705 | 3889 | 4314
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 0 | 0 | 0 | 0 | 0 | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 0 | 0 | 0 | 0 | 0 | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 0 | 0 | 0 | 0 | 0 | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 0 | 0 | 0 | 0 | 0 | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 0 | 0 | 0 | 0 | 0 | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 64 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 0 | 0 | 0 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 0 | 0 | 0 | 0 | 0 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 0 | 0 | 0 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 0 | 0 | 0 | 0 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 0 | 0 | 0 | 0 | 0 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 0 | 0 | 0 | 0 | 0 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 0 | 0 | 0 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 0 | 0 | 0 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 2 | 0 | -2 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 4 | 0 | -4 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 10 | 0 | -10 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 20 | 0 | -20 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 12 | 0 | -12 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 24 | 0 | -24 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 24 | 0 | -24 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 48 | 0 | -48 | 0 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 0 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 0 | 0 | 0 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 79 | 66 | 40 | 28 | 50 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 26 | 0 | -26 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 48 | 0 | -48 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 20 | 0 | -20 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 0 | 62 | 0 | -62 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 40 | 0 | -40 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 66 | 0 | -66 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 6 | 0 | -6 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 8 | 0 | -8 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 92 | 0 | -92 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 0 | 184 | 0 | -184 | 0 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 0 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 0 | 0 | 0 | 0 | 0 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 431571.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 0 | 116 | 0 | -116 | 0 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 0 | 232 | 0 | -232 | 0 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW5 - General Reinfor - EMID
HI5: Secondary deliverables RIIO-ED1 - General reinforcement
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on General Reinforcement associated with HI Categories | LV
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on General Reinforcement associated with HI Categories | HV
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | EHV | 9.125 | 12.4456 | 17.2664
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | 132kV | 9.1435 | 40.0957 | 50.0022
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on General Reinforcement associated with HI Categories | Total | 18.2685 | 52.5413 | 67.2687
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | [5 empty] | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | [5 empty] | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | [5 empty] | 0 | 7 | 0 | 1 | 0 | 0 | 8 | [5 empty] | 0 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | [5 empty] | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | [5 empty] | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | [5 empty] | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | [5 empty] | 0 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 0 | 0 | 0 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | [5 empty] | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | [5 empty] | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | [5 empty] | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | [5 empty] | 0 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 | 30004 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 0 | 0 | 0 | 0 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 0 | 0 | 0 | 0 | 0 |  | 4361 | 2740 | 13705 | 3889 | 4314
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | [5 empty] | 0 | 232 | 167 | 301 | 84 | 25 | 809 | [5 empty] | 0 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | [5 empty] | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | [5 empty] | 0 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | [5 empty] | 0 | 209 | 147 | 377 | 127 | 20 | 880 | [5 empty] | 0 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | [5 empty] | 0 | 6 | 5 | 7 | 1 | 1 | 20 | [5 empty] | 0 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | [5 empty] | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | [5 empty] | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | [5 empty] | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | [5 empty] | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | [5 empty] | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | [5 empty] | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | [5 empty] | 0 | 61 | 18 | 64 | 0 | 0 | 143 | [5 empty] | 0 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 0 | 0 | 0 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | [5 empty] | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | [5 empty] | 0 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | [5 empty] | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | [5 empty] | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | [5 empty] | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | [5 empty] | 0 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | [5 empty] | 0 | 46 | 14 | 35 | 13 | 10 | 118 | [5 empty] | 0 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 0 | 0 | 0 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 0 | 0 | 0 | 0 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | [5 empty] | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | [5 empty] | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | [5 empty] | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | [5 empty] | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | [5 empty] | 0 | 31 | 103 | 50 | 13 | 56 | 253 | [5 empty] | 0 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 21 | -11 | 0 | 0 | 0 | 10 | 336 | 158 | 52 | 95 | 17 | 658 | 31 | -12 | 0 | 0 | 0 | 19 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 10 | -4 | 0 | 0 | 0 | 6 | 179 | 80 | 79 | 92 | 2 | 432 | 23 | -9 | 0 | 0 | 0 | 14 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 9 | -3 | 0 | 0 | 0 | 6 | 62 | 18 | 35 | 17 | 5 | 137 | 20 | -6 | 0 | 0 | 0 | 14 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 3 | -3 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 40 | -18 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 77 | -30 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 1 | -1 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 1 | -1 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 12 | 0 | -3 | 0 | 0 | 9 | 62 | 40 | 146 | 13 | 29 | 290 | 16 | 0 | -3 | 0 | 0 | 13 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 10 | -6 | -4 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 13 | -9 | -4 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 23 | -7 | -7 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 30 | -10 | -7 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 0 | 0 | 0 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 610 | 0 | 0 | 0 | 0 | 610 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 829 | 0 | -98 | 0 | 0 | 731 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 610 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 829 | 0 | -98 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0.017 | 0 | -0.017 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0.017 | 0 | 0 | -0.017 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0.158 | 0 | -0.158 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0.158 | 0 | -0.015 | -0.143 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0.175 | 0 | -0.175 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0.175 | 0 | -0.015 | -0.16 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 12 | -11 | 0 | 0 | -1 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 25 | -11 | 0 | -2 | -5 | 7 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 12 | -10 | -2 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 20 | -10 | 0 | -4 | 0 | 6 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 1 | -1 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 8 | -1 | 0 | -3 | 0 | 4 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 5 | -5 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 5 | -5 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 30 | -27 | -2 | 0 | -1 |  | 79 | 66 | 40 | 28 | 50 |  | 58 | -27 | 0 | -9 | -5 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 7 | 0 | -1 | 0 | 0 | 6 | 24 | 2 | 31 | 10 | 0 | 67 | 7 | 0 | -1 | 0 | 0 | 6 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 2 | 0 | -1 | 0 | 0 | 1 | 6 | 12 | 32 | 1 | 3 | 54 | 2 | 0 | -1 | 0 | 0 | 1 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 9 | 0 | -2 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 9 | 0 | -2 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | -0.317 | -0.538 | 0 | 0 | -0.855 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | -0.287 | -1.156 | 0 | 0 | -1.443 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | -0.393 | -0.737 | 0 | 0 | -1.13 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | -0.562 | -1.376 | 0 | 0 | -1.938 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | -0.231 | -0.45 | 0 | 0 | -0.681 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | -0.469 | -0.816 | 0 | 0 | -1.285 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | -0.001 | 0 | 0 | 0 | -0.001 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | -0.001 | 0 | 0 | 0 | -0.001 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | -0.942 | -1.725 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | -1.319 | -3.348 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 22 | 0 | -22 | 0 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 22 | 0 | -22 | 0 | 0 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 4 | 0 | 0 | 0 | 0 | 4 | 419 | 143 | 985 | 237 | 979 | 2763 | 37 | -3 | -18 | -14 | 0 | 2 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 4 | 0 | 0 | 0 | 0 | 4 | 322 | 223 | 2553 | 216 | 678 | 3992 | 86 | -2 | -59 | -20 | 0 | 5 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 1 | 0 | 0 | 0 | 0 | 1 | 94 | 42 | 1077 | 16 | 767 | 1996 | 34 | -1 | -24 | -7 | 0 | 2 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 6 | -1 | -3 | -2 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 9 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 163 | -7 | -104 | -43 | 0 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0.043 | -0.003 | -0.04 | 0 | 0 | -6.9389e-18 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 3.678 | -0.241 | -1.568 | -1.869 | 0 | -2.2204e-16 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0.067 | -0.001 | -0.066 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 5.629 | -0.097 | -1.428 | -4.104 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0.036 | -0.002 | -0.034 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 3.06 | -0.182 | -0.91 | -1.968 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0.004 | 0 | -0.004 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0.383 | 0 | -0.021 | -0.362 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0.15 | -0.006 | -0.144 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 12.75 | -0.52 | -3.927 | -8.303 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 431571.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 721.325 | -52.948 | -13.044 | 0 | -1 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 1200.925 | -75.839 | -240.29 | -60.463 | -5 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW6 - Faults - EMID
HI6: Secondary deliverables RIIO-ED1 - Faults
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Faults associated with HI Categories | LV | 0.36918 | 0.73835 | 1.4767
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Faults associated with HI Categories | HV | 0.60701 | 1.214 | 2.428
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | EHV | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | 132kV | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Faults associated with HI Categories | Total | 0.97619 | 1.9524 | 3.9048
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 0 | 0 | 0 | 0 | 0 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 0 | 0 | 0 | 0 | 0 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 15 | -6 | -9 | 0 | 0 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 29 | -12 | -17 | 0 | 0 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 1 | 0 | -1 | 0 | 0 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 3 | -1 | -2 | 0 | 0 | 0 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 16 | -6 | -10 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 32 | -13 | -19 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 135 | -24 | -101 | -10 | 0 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 269 | -32 | -159 | -45 | -33 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 5 | -1 | -4 | 0 | 0 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 11 | -1 | -7 | -2 | -1 | 0 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 |  |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 140 | -25 | -105 | -10 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 280 | -33 | -166 | -47 | -34 |  | 4361 | 2740 | 13705 | 3889 | 4314
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 15 | -4 | -11 | 0 | 0 | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 36 | -15 | -14 | -7 | 0 | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 36 | -20 | -16 | 0 | 0 | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 69 | -37 | -23 | -9 | 0 | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 13 | -7 | -6 | 0 | 0 | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 23 | -12 | -8 | -3 | 0 | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 64 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 64 | -31 | -33 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 128 | -64 | -45 | -19 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 10 | -4 | -6 | 0 | 0 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 20 | -9 | -10 | -1 | 0 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 42 | -20 | -22 | 0 | 0 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 85 | -41 | -41 | -3 | 0 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 12 | -4 | -8 | 0 | 0 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 23 | -8 | -14 | -1 | 0 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 64 | -28 | -36 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 128 | -58 | -65 | -5 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 0 | 0 | 0 | 0 | 0 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 0 | 0 | 0 | 0 | 0 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 0 | 0 | 0 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 0 | 0 | 0 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 0 | 0 | 0 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 0 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 0 | 0 | 0 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 79 | 66 | 40 | 28 | 50 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 0 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 0 | 0 | 0 | 0 | 0 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 401567.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 284 | -90 | -184 | -10 | 0 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 568 | -168 | -295 | -71 | -34 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW7 - HVP - EMID
HI7: Secondary deliverables RIIO-ED1 - HVP
EMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV |  | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV |  | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV |  | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV |  | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 0 | 0 | 0
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 0 | 0 | 0 | 0 | 0 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 0 | 0 | 0 | 0 | 0 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 115445 | 124041 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617
| LV Switchgear (at s/s) |  |  |  | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8
[5 empty] | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 0 | 0 | 0 | 0 | 0 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 0 | 0 | 0 | 0 | 0 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231
[5 empty] | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 206 | 618 | 94 | 49 | 1354
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 18593 | 20964 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 0 | 0 | 0 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 0 | 0 | 0 | 0 | 0 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 0 | 0 | 0 | 0 | 0 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987
[5 empty] | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 116 | 557 | 157 | 144 | 1022
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29009 | 30004 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 0 | 0 | 0 | 0 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 0 | 0 | 0 | 0 | 0 |  | 4361 | 2740 | 13705 | 3889 | 4314
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 168 | 215 | 121 | 109 | 809
[5 empty] | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 464 | 728 | 364 | 323 | 2623
[5 empty] | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 156 | 248 | 138 | 148 | 880
[5 empty] | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 3 | 4 | 2 | 20
|  | Yes | 4332 | 4514 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 0 | 0 | 0 | 0 | 0 | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 0 | 0 | 0 | 0 | 0 | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569
[5 empty] | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 0 | 0 | 0 | 0 | 0 | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994
[5 empty] | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 0 | 0 | 0 | 0 | 0 | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 0 | 0 | 0 | 0 | 0 | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187
[5 empty] | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 64 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 20 | 43 | 27 | 0 | 143
|  | Yes | 27893 | 28471 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 0 | 0 | 0 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810
| HV Transformer (GM) |  |  |  | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306
[5 empty] | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 0 | 0 | 0 | 0 | 0 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028
[5 empty] | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266
[5 empty] | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 27 | 25 | 9 | 26 | 118
|  | Yes | 19718 | 20507 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 0 | 0 | 0 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 0 | 0 | 0 | 0 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318
| HV UG Cable |  |  |  | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 0 | 0 | 0 | 0 | 0 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 0 | 0 | 0 | 0 | 0 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615
[5 empty] | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228
[5 empty] | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 104 | 51 | 16 | 75 | 253
|  | Yes | 148096 | 151721 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 205 | 49 | 13 | 117 | 658
[5 empty] | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 91 | 21 | 49 | 106 | 432
[5 empty] | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 14 | 12 | 33 | 137
[5 empty] | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91
|  | Yes | 1318 | 1416 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285
| EHV Transformer |  |  |  | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234
[5 empty] | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 47 | 78 | 72 | 43 | 290
[5 empty] | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179
[5 empty] | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9
|  | Yes | 712 | 733 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 0 | 0 | 0 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 0 | 0 | 0 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569
[5 empty] | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77
[5 empty] | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371
|  | Yes | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140
[5 empty] | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557
[5 empty] | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1138 | 1135 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 0 | 0 | 0 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 180 | 758 | 74 | 107 | 19
| EHV OHL Support - Poles |  |  |  | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622
[5 empty] | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560
[5 empty] | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373
[5 empty] | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18
|  | Yes | 27573 | 28313 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 0 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 0 | 0 | 0 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370
[5 empty] | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2272 | 2260 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606
[5 empty] | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 861.25 | 860.5 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 7 | 18 | 34 | 115
[5 empty] | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22 | 0 | 16 | 16 | 88
[5 empty] | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 4 | 17 | 30
[5 empty] | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30
|  | Yes | 263 | 280 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 79 | 66 | 40 | 28 | 50 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 65 | 12 | 39 | 70
| 132kV Transformer |  |  |  | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63
[5 empty] | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 15 | 14 | 12 | 67
[5 empty] | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 24 | 8 | 4 | 54
[5 empty] | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9
|  | Yes | 193 | 200 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945
[5 empty] | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282
[5 empty] | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005
[5 empty] | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038
|  | Yes | 149.27 | 144.603 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441
[5 empty] | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926
[5 empty] | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045
[5 empty] | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140
|  | Yes | 4552 | 4545 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3567 | 463 | 211 | 15
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763
[5 empty] | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992
[5 empty] | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 867 | 246 | 767 | 1996
[5 empty] | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333
|  | Yes | 9084 | 9065 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 0 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 0 | 0 | 0 | 0 | 0 |  | 846 | 248 | 3752 | 1577 | 2661
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807
[5 empty] | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034
[5 empty] | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36
[5 empty] | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199
|  | Yes | 2239.4 | 2236.7 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 413601.63 | 431571.513 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 0 | 0 | 0 | 0 | 0 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 0 | 0 | 0 | 0 | 0 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW8 - Average Crit - EMID
HI8: Secondary deliverables RIIO-ED1
EMID
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 416 | 1405 | 278 | 2688 | 4787
| LV Switchgear (at s/s) | 1896 | 787 | 488 | 3927 | 7098
| LV UGB and LV Pillar OD (not at s/s) | 2150 | 658 | 488 | 2485 | 5781
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 64745 | 1264 | 1985 | 12468 | 80462
| HV Switchgear (GM) - Distribution | 14058 | 1629 | 2438 | 4811 | 22936
| HV Transformer (GM) | 13028 | 1236 | 3658 | 4718 | 22640
| HV UG Cable | 37546 | 142 | 1102 | 10500 | 49290
| HV OHL Support - Poles | 3217 | 1464 | 478 | 2920 | 8079
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 131429 | 841 | 3729 | 22060 | 158059
| EHV Transformer | 292683 | 1178 | 24219 | 153107 | 471187
EHV UG Cable (Gas)
| EHV UG Cable (Oil) | 4735 | 710 | 8805 | 9003 | 23253
| EHV UG Cable (Non Pressurised) | 53870 | 142 | 1602 | 13000 | 68614
| EHV OHL Support - Towers | 151019 | 25436 | 2230 | 63510 | 242195
| EHV OHL Support - Poles | 7888 | 1448 | 478 | 4100 | 13914
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 100002 | 12718 | 880 | 4000 | 117600
| EHV OHL Conductor (Tower Lines) | 100029 | 12718 | 880 | 4000 | 117627
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 295844 | 1106 | 7395 | 21512 | 325857
| 132kV Transformer | 1745086 | 1273 | 60737 | 316056 | 2123152
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 73590 | 710 | 8805 | 18006 | 101111
| 132kV UG Cable (Non Pressurised) | 408508 | 710 | 2501 | 225000 | 636719
| 132kV OHL Support - Tower | 1067827 | 25436 | 2230 | 137123 | 1232616
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 554281 | 12718 | 880 | 4000 | 571879
| 132kV OHL Conductor (Tower Lines) | 555722 | 12718 | 880 | 4000 | 573320
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]

## NAW1 - DPCR5 View - SWALES
HI1: Network Outputs DPCR5
SWALES
Price base (2012/13)
| ASSET CATEGORIES | ASSET REGISTER |  | HEALTH INDEX - CURRENT (as at 31 March) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with no further DPCR5 intervention) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with DPCR5 actual & forecast intervention) |  |  |  |  | DATA QUALITY - CURRENT (as at 31 March)
[19 empty] | Number of assets included for HI output measure | Primary form of measure | Number of assets actually observed | Average age of data used | Description of the form of measure used to assign a HI, the quality of data used, and any other relevant information | Degradation assumption adopted
|  | Current (as at 31 March) | Forecast (as at 31 March 2015) | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | Assets | Health Condition Age Other | % | Years | Commentary | Description
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 101931 | 101791 | 8724 | 76515 | 3589 | 8177 | 4926 | 4524 | 76515 | 3799 | 8807 | 8286 | 8724 | 76515 | 3589 | 8037 | 4926 | 101931 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
| LV Switchgear (at s/s) | 7750 | 7865 | 3924 | 1261 | 2140 | 238 | 187 | 3810 | 1132 | 2233 | 303 | 272 | 4118 | 1126 | 2210 | 284 | 127 | 7750 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| LV UGB and LV Pillar OD (not at s/s) | 4313 | 4319 | 581 | 729 | 2583 | 274 | 146 | 580 | 522 | 2723 | 280 | 208 | 638 | 522 | 2721 | 280 | 158 | 4313 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 2289 | 2263 | 1417 | 349 | 417 | 66 | 40 | 1282 | 468 | 361 | 125 | 53 | 1294 | 466 | 358 | 105 | 40 | 2289 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Switchgear (GM) - Distribution | 10508 | 10609 | 6690 | 1989 | 1082 | 241 | 506 | 6146 | 2268 | 1223 | 203 | 668 | 6357 | 2238 | 1209 | 193 | 612 | 10508 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Transformer (GM) | 8258 | 8341 | 4232 | 1271 | 2088 | 262 | 405 | 4081 | 1275 | 2130 | 288 | 484 | 4413 | 1260 | 2109 | 287 | 272 | 8258 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV UG Cable
| HV OHL Support - Poles | 159957 | 160231 | 10352 | 122904 | 2563 | 11561 | 12577 | 4552 | 122904 | 2853 | 12431 | 17217 | 10625 | 122904 | 2563 | 11561 | 12578 | 159957 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 693 | 707 | 456 | 38 | 194 | 4 | 1 | 427 | 56 | 198 | 9 | 3 | 471 | 56 | 171 | 7 | 2 | 693 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV Transformer | 286 | 286 | 95 | 19 | 101 | 67 | 4 | 95 | 13 | 96 | 57 | 25 | 118 | 11 | 89 | 51 | 17 | 286 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Gas) | 8.564 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 0 | 0.682 | 2.133 | 5.749 | 0 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Oil) | 2 | 2 | 1.26 | 0.74 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 254 | 254 | 34 | 132 | 62 | 18 | 8 | 33 | 118 | 77 | 18 | 8 | 41 | 122 | 77 | 14 | 0 | 254 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Support - Poles | 20254 | 20249 | 1854 | 9681 | 1562 | 3573 | 3584 | 984 | 9681 | 1606 | 3703 | 4280 | 1854 | 9681 | 1562 | 3573 | 3579 | 20254 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition | 0
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 597 | 597 | 29 | 0 | 496 | 72 | 0 | 0 | 29 | 496 | 72 | 0 | 0 | 29 | 496 | 72 | 0 | 597 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Conductor (Tower Lines) | 69 | 69 | 7.262 | 0 | 50.522 | 0 | 11.216 | 7.262 | 0 | 49.738 | 0 | 12 | 19.262 | 0 | 49.738 | 0 | 0 | 69 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 231 | 229 | 138 | 78 | 13 | 2 | 0 | 110 | 101 | 18 | 2 | 0 | 111 | 101 | 16 | 1 | 0 | 231 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV Transformer | 130 | 131 | 70 | 30 | 10 | 20 | 0 | 62 | 34 | 13 | 11 | 10 | 63 | 34 | 13 | 11 | 10 | 130 | Health | 1 | 1.5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Oil) | 57.4847 | 55.1747 | 26.993 | 24.828 | 3.353 | 2.311 | 0 | 26.805 | 24.256 | 4.115 | 2.309 | 0 | 26.804 | 24.256 | 4.115 | 0 | 0 | 57.485 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 2378 | 2378 | 277 | 1251 | 581 | 269 | 0 | 274 | 1243 | 591 | 270 | 0 | 298 | 1243 | 591 | 246 | 0 | 2378 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 4714 | 4720 | 134 | 102 | 4320 | 145 | 13 | 134 | 98 | 4279 | 49 | 154 | 292 | 98 | 4279 | 49 | 2 | 4714 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV OHL Conductor (Tower Lines) | 1089 | 1089 | 234.554 | 355.332 | 499.114 | 0 | 0 | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 | 224.774 | 389.017 | 475.209 | 0 | 0 | 1089 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
0
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required
Note on U7: Ofgem: Insert one of the following: Health; Condition; Age; or Other.

## NAW2 - Total - SWALES
HI2: Secondary deliverables RIIO-ED1
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) with investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) with investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | Yes | Expenditure on Health Index asset categories | LV | 8.335 | 16.836 | 33.354
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | No | Expenditure on Health Index asset categories | HV | 15.6961 | 39.0103 | 77.4925
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | EHV | 12.35 | 19.6124 | 37.2941
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | 132kV | 4.8466 | 19.3996 | 46.165
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Health Index asset categories | Total | 41.2277 | 94.8583 | 194.3056
| LV UGB |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 13724 | 76515 | 3589 | 5037 | 2926 | 101791 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 18849 | 76515 | 3589 | 1962 | 876 | 101791 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 13724 | 76515 | 3589 | 5037 | 2926 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 18849 | 76515 | 3589 | 1962 | 876 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 278 | 0 | 0 | 0 | 0 | 278 | 278 | 0 | 0 | 0 | 0 | 278 | 278 | 0 | 0 | 0 | 0 | 278 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 3539 | 1368 | 2108 | 440 | 56 | 7511 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 3129 | 1850 | 1860 | 602 | 70 | 7511 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 36 | 11 | 25 | 2 | 2 | 76 | 30 | 13 | 26 | 2 | 5 | 76 | 35 | 14 | 19 | 8 | 0 | 76 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 3853 | 1379 | 2133 | 442 | 58 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 3442 | 1864 | 1879 | 610 | 70 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 565 | 306 | 2157 | 340 | 267 | 3635 | 442 | 306 | 2157 | 340 | 390 | 3635 | 684 | 78 | 2062 | 443 | 368 | 3635 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 30 | 1 | 548 | 1 | 1 | 581 | 25 | 1 | 548 | 1 | 6 | 581 | 31 | 0 | 544 | 6 | 0 | 581 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 698 | 307 | 2705 | 341 | 268 |  | 570 | 307 | 2705 | 341 | 396 |  | 818 | 78 | 2606 | 449 | 368 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 311 | 210 | 69 | 29 | 12 | 631 | 290 | 210 | 69 | 37 | 25 | 631 | 248 | 260 | 61 | 44 | 18 | 631 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 725 | 400 | 192 | 64 | 35 | 1416 | 665 | 400 | 198 | 86 | 67 | 1416 | 667 | 467 | 141 | 105 | 36 | 1416 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 7 | 5 | 14 | 4 | 1 | 31 | 7 | 5 | 14 | 4 | 1 | 31 | 12 | 4 | 8 | 7 | 0 | 31 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 82 | 57 | 27 | 15 | 4 | 185 | 75 | 57 | 27 | 17 | 9 | 185 | 83 | 67 | 20 | 15 | 0 | 185 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 1125 | 672 | 302 | 112 | 52 |  | 1037 | 672 | 308 | 144 | 102 |  | 1010 | 798 | 230 | 171 | 54 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 225 | 26 | 3 | 0 | 0 | 254 | 225 | 26 | 3 | 0 | 0 | 254 | 169 | 79 | 6 | 0 | 0 | 254 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 4732 | 2872 | 1124 | 162 | 347 | 9237 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 4176 | 3260 | 1291 | 230 | 246 | 9203 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 487 | 294 | 221 | 18 | 54 | 1074 | 367 | 298 | 224 | 22 | 173 | 1084 | 480 | 309 | 211 | 47 | 21 | 1068 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 3 | 1 | 0 | 4 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 5444 | 3192 | 1352 | 180 | 401 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 4825 | 3648 | 1511 | 278 | 267 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 462 | 132 | 580 | 123 | 34 | 1331 | 332 | 134 | 589 | 124 | 152 | 1331 | 506 | 140 | 521 | 137 | 27 | 1331 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 3136 | 995 | 1461 | 232 | 0 | 5824 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 2962 | 1251 | 1472 | 94 | 45 | 5824 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 756 | 227 | 179 | 22 | 0 | 1184 | 715 | 231 | 181 | 26 | 31 | 1184 | 689 | 283 | 199 | 4 | 9 | 1184 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 4354 | 1356 | 2220 | 377 | 34 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 4157 | 1676 | 2192 | 235 | 81 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 18535 | 114507 | 2388 | 7317 | 6538 | 149285 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 26787 | 114507 | 2388 | 4016 | 1587 | 149285 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 1340 | 8283 | 172 | 528 | 474 | 10797 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 1937 | 8283 | 172 | 291 | 114 | 10797 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 18 | 114 | 3 | 9 | 5 | 149 | 6 | 114 | 3 | 12 | 14 | 149 | 27 | 114 | 3 | 4 | 1 | 149 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 19893 | 122904 | 2563 | 7854 | 7017 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 28751 | 122904 | 2563 | 4311 | 1702 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 180 | 80 | 0 | 25 | 0 | 285 | 171 | 80 | 0 | 25 | 9 | 285 | 151 | 117 | 7 | 0 | 12 | 287 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 240 | 22 | 28 | 28 | 0 | 318 | 190 | 22 | 36 | 65 | 1 | 314 | 239 | 57 | 16 | 5 | 1 | 318 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 43 | 4 | 6 | 10 | 0 | 63 | 32 | 4 | 7 | 19 | 1 | 63 | 52 | 8 | 2 | 1 | 0 | 63 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 30 | 0 | 15 | 0 | 0 | 45 | 22 | 0 | 16 | 7 | 0 | 45 | 28 | 4 | 13 | 0 | 0 | 45 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 493 | 106 | 49 | 63 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 470 | 186 | 38 | 6 | 13 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 48 | 5 | 19 | 17 | 14 | 103 | 46 | 5 | 19 | 19 | 14 | 103 | 55 | 6 | 13 | 10 | 19 | 103 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 52 | 13 | 21 | 11 | 16 | 113 | 34 | 13 | 21 | 11 | 34 | 113 | 60 | 12 | 11 | 18 | 12 | 113 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 25 | 5 | 20 | 8 | 4 | 62 | 18 | 5 | 20 | 9 | 10 | 62 | 30 | 6 | 15 | 8 | 3 | 62 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 6 | 2 | 0 | 0 | 0 | 8 | 6 | 2 | 0 | 0 | 0 | 8 | 4 | 4 | 0 | 0 | 0 | 8 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 131 | 25 | 60 | 36 | 34 |  | 104 | 25 | 60 | 39 | 58 |  | 149 | 28 | 39 | 36 | 34 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 2.815 | 0 | 3.589 | 6.404 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0.723 | 2.092 | 1.429 | 4.244 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 2.815 | 0 | 3.589 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0.723 | 2.092 | 1.429 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 31 | 76 | 76 | 5 | 0 | 188 | 31 | 68 | 76 | 13 | 0 | 188 | 30 | 81 | 71 | 6 | 0 | 188 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 10 | 30 | 25 | 1 | 0 | 66 | 10 | 30 | 25 | 1 | 0 | 66 | 10 | 26 | 30 | 0 | 0 | 66 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 41 | 106 | 101 | 6 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 40 | 107 | 101 | 6 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 356 | 1183 | 191 | 385 | 360 | 2475 | 133 | 1183 | 191 | 464 | 504 | 2475 | 488 | 1183 | 191 | 332 | 281 | 2475 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 2704 | 8372 | 1351 | 2724 | 2546 | 17697 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 3700 | 8371 | 1351 | 2350 | 1984 | 17756 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 38 | 127 | 20 | 41 | 38 | 264 | 14 | 127 | 20 | 49 | 54 | 264 | 52 | 127 | 20 | 35 | 30 | 264 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 3098 | 9682 | 1562 | 3150 | 2944 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 4240 | 9681 | 1562 | 2717 | 2295 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 41 | 29 | 40 | 42 | 12 | 164 | 0 | 29 | 40 | 42 | 53 | 164 | 55 | 29 | 0 | 73 | 7 | 164 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 59 | 0 | 187 | 34 | 0 | 280 | 0 | 0 | 187 | 85 | 8 | 280 | 117 | 0 | 6 | 157 | 0 | 280 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 35 | 0 | 118 | 0 | 0 | 153 | 0 | 0 | 118 | 0 | 35 | 153 | 57 | 0 | 15 | 81 | 0 | 153 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 135 | 29 | 345 | 76 | 12 |  | 0 | 29 | 345 | 127 | 96 |  | 229 | 29 | 21 | 311 | 7 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 5.684 | 0 | 12.301 | 18.204 | 0 | 36.189 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 13.684 | 0 | 12.301 | 18.204 | 0 | 44.189 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 16.5 | 7.262 | 15.825 | 33.913 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 24.5 | 7.262 | 14.061 | 35.677 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 34 | 44 | 13 | 2 | 0 | 93 | 33 | 44 | 13 | 3 | 0 | 93 | 13 | 60 | 16 | 2 | 2 | 93 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 35 | 35 | 6 | 1 | 0 | 77 | 31 | 35 | 6 | 3 | 0 | 75 | 31 | 37 | 12 | 0 | 0 | 80 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 15 | 32 | 4 | 0 | 1 | 52 | 15 | 32 | 4 | 0 | 1 | 52 | 13 | 31 | 6 | 0 | 2 | 52 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 4 | 5 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 0 | 0 | 9 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 88 | 116 | 23 | 3 | 1 |  | 83 | 116 | 23 | 6 | 1 |  | 61 | 133 | 34 | 2 | 4 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 22 | 20 | 5 | 1 | 6 | 54 | 22 | 20 | 5 | 1 | 6 | 54 | 19 | 27 | 5 | 0 | 3 | 54 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 26 | 18 | 8 | 0 | 4 | 56 | 22 | 18 | 8 | 0 | 8 | 56 | 32 | 12 | 15 | 0 | 0 | 59 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 7 | 1 | 3 | 0 | 0 | 11 | 4 | 1 | 3 | 0 | 3 | 11 | 5 | 3 | 2 | 1 | 0 | 11 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 6 | 2 | 1 | 1 | 0 | 10 | 4 | 2 | 1 | 1 | 2 | 10 | 7 | 1 | 2 | 0 | 0 | 10 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 61 | 41 | 17 | 2 | 10 |  | 52 | 41 | 17 | 2 | 19 |  | 63 | 43 | 24 | 1 | 3 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 72 | 364 | 231 | 36 | 1 | 704 | 72 | 364 | 231 | 36 | 1 | 704 | 71 | 378 | 233 | 22 | 0 | 704 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 175 | 508 | 236 | 84 | 3 | 1006 | 165 | 480 | 236 | 112 | 13 | 1006 | 187 | 525 | 247 | 47 | 0 | 1006 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 57 | 374 | 169 | 67 | 1 | 668 | 57 | 354 | 169 | 87 | 1 | 668 | 62 | 381 | 168 | 57 | 0 | 668 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 304 | 1246 | 636 | 187 | 5 |  | 294 | 1198 | 636 | 235 | 15 |  | 320 | 1284 | 648 | 126 | 0 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 87 | 14 | 1130 | 59 | 1 | 1291 | 12 | 14 | 1130 | 131 | 4 | 1291 | 147 | 0 | 21 | 1123 | 0 | 1291 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 229 | 4 | 1621 | 183 | 0 | 2037 | 79 | 4 | 1621 | 333 | 0 | 2037 | 412 | 0 | 10 | 1615 | 0 | 2037 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 300 | 28 | 927 | 90 | 34 | 1379 | 201 | 28 | 927 | 174 | 49 | 1379 | 424 | 20 | 60 | 875 | 0 | 1379 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 13 | 0 | 13 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 616 | 46 | 3691 | 332 | 35 |  | 292 | 46 | 3691 | 638 | 53 |  | 983 | 20 | 91 | 3626 | 0 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 57.049 | 134.058 | 102.342 | 0.027 | 0 | 293.476 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 51.119 | 142.817 | 66.759 | 32.781 | 0 | 293.476 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 49.382 | 140.584 | 271.178 | 0.016 | 0 | 461.16 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 63.842 | 134.123 | 219.149 | 44.045 | 0 | 461.159 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 98.695 | 139.56 | 82.502 | 10.263 | 0 | 331.02 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 93.229 | 97.971 | 117.519 | 22.301 | 0 | 331.02 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 205.126 | 414.202 | 459.366 | 10.306 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 208.19 | 374.911 | 406.771 | 99.127 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 54307.373 | 218167.399 | 21831.499 | 18242.219 | 13800.589 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 68664.993 | 219397.973 | 17559.627 | 14983.896 | 5775.429 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW3 - Asset Rep - SWALES
HI3: Secondary deliverables RIIO-ED1 - Asset replacement
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Asset Replacement associated with HI Categories | LV | 8.115 | 16.388 | 32.441
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Asset Replacement associated with HI Categories | HV | 13.037 | 33.153 | 65.804
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | EHV | 8.22 | 16.473 | 32.403
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | 132kV | 2.362 | 10.592 | 22.466
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Asset Replacement associated with HI Categories | Total | 31.734 | 76.606 | 153.114
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 8621 | 0 | 0 | -4035 | -4586 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 17457 | 0 | 0 | -8170 | -9287 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 8621 | 0 | 0 | -4035 | -4586 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 17457 | 0 | 0 | -8170 | -9287 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 368 | -24 | -62 | -11 | -271 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 736 | -52 | -94 | -47 | -543 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 6 | -2 | -1 | 0 | -3 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 12 | -2 | -3 | -1 | -6 | 0 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 374 | -26 | -63 | -11 | -274 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 748 | -54 | -97 | -48 | -549 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 123 | 0 | 0 | 0 | -123 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 250 | 0 | 0 | 0 | -250 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 5 | 0 | 0 | 0 | -5 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 6 | 0 | 0 | 0 | -6 | 0 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 128 | 0 | 0 | 0 | -128 |  | 570 | 307 | 2705 | 341 | 396 |  | 256 | 0 | 0 | 0 | -256 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 21 | 0 | 0 | -8 | -13 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 31 | 0 | 0 | -1 | -30 | 0 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 60 | 0 | -6 | -22 | -32 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 117 | 0 | -2 | -14 | -101 | 0 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 5 | 0 | 0 | -1 | -4 | 0 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 7 | 0 | 0 | -2 | -5 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 24 | 0 | 0 | -1 | -23 | 0 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 88 | 0 | -6 | -32 | -50 |  | 1037 | 672 | 308 | 144 | 102 |  | 177 | 0 | -2 | -17 | -158 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 373 | -60 | -3 | 0 | -340 | -30 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 788 | -112 | -25 | -47 | -668 | -64 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 114 | -1 | 0 | -4 | -119 | -10 | 367 | 298 | 224 | 22 | 173 | 1084 | 190 | -11 | -1 | -2 | -192 | -16 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 487 | -61 | -3 | -4 | -459 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 978 | -123 | -26 | -49 | -860 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 118 | 0 | 0 | 0 | -118 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 207 | 0 | 0 | -15 | -192 | 0 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 281 | 0 | 0 | -15 | -266 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 594 | 0 | 0 | -224 | -370 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 35 | 0 | 0 | -4 | -31 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 69 | 0 | 0 | -31 | -38 | 0 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 434 | 0 | 0 | -19 | -415 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 870 | 0 | 0 | -270 | -600 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 12699 | 0 | 0 | -4978 | -7721 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 25798 | 0 | 0 | -9850 | -15948 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 918 | 0 | 0 | -361 | -557 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 1866 | 0 | 0 | -712 | -1154 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 12 | 0 | 0 | -3 | -9 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 26 | 0 | 0 | -10 | -16 | 0 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 13629 | 0 | 0 | -5342 | -8287 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 27690 | 0 | 0 | -10572 | -17118 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 9 | 0 | 0 | 0 | -9 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 22 | 0 | 0 | 0 | -22 | 0 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 38 | 0 | 0 | -37 | -1 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 77 | 0 | 0 | -8 | -69 | 0 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 10 | 0 | 0 | -9 | -1 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 23 | 0 | 0 | -2 | -21 | 0 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 8 | 0 | -1 | -7 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 10 | 0 | 0 | -3 | -7 | 0 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 65 | 0 | -1 | -53 | -11 |  | 415 | 106 | 59 | 116 | 11 |  | 132 | 0 | 0 | -13 | -119 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 9 | 0 | 0 | 0 | -9 | 0 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 18 | 0 | 0 | 0 | -18 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 28 | 0 | 0 | 0 | -28 | 0 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 7 | 0 | 0 | -1 | -6 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 13 | 0 | 0 | 0 | -13 | 0 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 25 | 0 | 0 | -1 | -24 |  | 104 | 25 | 60 | 39 | 58 |  | 50 | 0 | 0 | 0 | -50 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | -2.16 | -2.16 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | -4.32 | -4.32 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | -2.16 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | -4.32 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 223 | 0 | 0 | -79 | -144 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 451 | 0 | 0 | -159 | -292 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 1577 | 0 | 0 | -555 | -1022 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 3191 | 0 | 0 | -1123 | -2068 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 24 | 0 | 0 | -8 | -16 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 48 | 0 | 0 | -17 | -31 | 0 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 1824 | 0 | 0 | -642 | -1182 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 3690 | 0 | 0 | -1299 | -2391 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 41 | 0 | 0 | 0 | -41 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 55 | 0 | 0 | 0 | -55 | 0 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 59 | 0 | 0 | -51 | -8 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 117 | 0 | 0 | -97 | -20 | 0 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 35 | 0 | 0 | 0 | -35 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 57 | 0 | 0 | -22 | -35 | 0 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 135 | 0 | 0 | -51 | -84 |  | 0 | 29 | 345 | 127 | 96 |  | 229 | 0 | 0 | -119 | -110 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 1 | 0 | 0 | -1 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 2 | 0 | 0 | -2 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 3 | 0 | 0 | 0 | -3 | 0 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 2 | 0 | 0 | 0 | -2 | 0 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 3 | 0 | 0 | -3 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 6 | 0 | 0 | 0 | -6 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 4 | 0 | 0 | 0 | -4 | 0 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 4 | 0 | 0 | 0 | -4 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 8 | 0 | 0 | 0 | -8 | 0 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 2 | 0 | 0 | 0 | -2 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 9 | 0 | 0 | 0 | -9 |  | 52 | 41 | 17 | 2 | 19 |  | 18 | 0 | 0 | 0 | -18 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 5 | 0 | 0 | 0 | -5 | 0 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 10 | 0 | 0 | 0 | -10 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 23 | 0 | 0 | 0 | -23 | 0 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 5 | 0 | 0 | 0 | -5 | 0 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 10 | 0 | 0 | 0 | -10 |  | 294 | 1198 | 636 | 235 | 15 |  | 33 | 0 | 0 | 0 | -33 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 75 | 0 | 0 | -72 | -3 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 135 | 0 | 0 | 0 | -135 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 150 | 0 | 0 | -150 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 333 | 0 | 0 | 0 | -333 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 99 | 0 | 0 | -84 | -15 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 223 | 0 | 0 | 0 | -223 | 0 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 324 | 0 | 0 | -306 | -18 |  | 292 | 46 | 3691 | 638 | 53 |  | 691 | 0 | 0 | 0 | -691 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 13.845 | 0 | 0 | -13.845 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 22.579 | 0 | 0 | -8.707 | -13.872 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 7.916 | 0 | 0 | -7.916 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 35.264 | 0 | 0 | -8.813 | -26.452 | -0.001 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 24.14 | 0 | 0 | -24.14 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 42.756 | 0 | 0 | -1.652 | -41.104 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 45.901 | 0 | 0 | -45.901 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 100.599 | 0 | 0 | -19.172 | -81.428 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 26201.901 | -87 | -73 | -10544.901 | -15539.16 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 53125.599 | -177 | -125 | -20576.172 | -32331.748 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW4 - Refurb - SWALES
HI4: Secondary deliverables RIIO-ED1 - refurbishment
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV | 0.22 | 0.448 | 0.913
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV | 2.128 | 4.795 | 9.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV | 0.374 | 0.927 | 1.917
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV | 1.756 | 3.533 | 6.94
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 4.478 | 9.703 | 19.334
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 0 | 0 | 0 | 0 | 0 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 0 | 0 | 0 | 0 | 0 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 0 | 0 | 0 | 0 | 0 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 0 | 0 | 0 | 0 | 0 | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 0 | 0 | 0 | 0 | 0 | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 0 | 0 | 0 | 0 | 0 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 0 | 0 | 0 | 0 | 0 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 0 | 0 | 0 | 0 | 0 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 0 | 0 | 0 | 0 | 0 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 0 | 0 | 0 | 0 | 0 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 0 | 0 | 0 | 0 | 0 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 0 | 0 | 0 | 0 | 0 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 0 | 0 | 0 | 0 | 0 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 8 | 0 | -8 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 14 | 0 | -14 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 2 | 0 | -2 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 8 | 0 | -8 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 16 | 0 | -16 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 0 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 0 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 10 | 0 | -10 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 28 | 0 | -28 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 55 | 0 | -55 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 20 | 0 | -20 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 31 | 0 | -31 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 48 | 0 | -48 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 96 | 0 | -96 | 0 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 0 | 56 | 0 | -56 | 0 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 0 | 112 | 0 | -112 | 0 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW5 - General Reinf - SWALES
HI5: Secondary deliverables RIIO-ED1 - General reinforcement
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on General Reinforcement associated with HI Categories | LV
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on General Reinforcement associated with HI Categories | HV
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | EHV | 3.756 | 2.2124 | 2.9741
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | 132kV | 0.72856 | 5.2746 | 16.759
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on General Reinforcement associated with HI Categories | Total | 4.4846 | 7.487 | 19.7331
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | [5 empty] | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | [5 empty] | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | [5 empty] | 0 | 278 | 0 | 0 | 0 | 0 | 278 | [5 empty] | 0 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | [5 empty] | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | [5 empty] | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | [5 empty] | 0 | 30 | 13 | 26 | 2 | 5 | 76 | [5 empty] | 0 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | [5 empty] | 0 | 103 | 0 | 0 | 0 | 0 | 103 | [5 empty] | 0 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | [5 empty] | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | [5 empty] | 0 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | [5 empty] | 0 | 25 | 1 | 548 | 1 | 6 | 581 | [5 empty] | 0 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | [5 empty] | 0 | 290 | 210 | 69 | 37 | 25 | 631 | [5 empty] | 0 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | [5 empty] | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | [5 empty] | 0 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | [5 empty] | 0 | 7 | 5 | 14 | 4 | 1 | 31 | [5 empty] | 0 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | [5 empty] | 0 | 75 | 57 | 27 | 17 | 9 | 185 | [5 empty] | 0 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | [5 empty] | 0 | 225 | 26 | 3 | 0 | 0 | 254 | [5 empty] | 0 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | [5 empty] | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | [5 empty] | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | [5 empty] | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | [5 empty] | 0 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | [5 empty] | 0 | 0 | 0 | 4 | 0 | 0 | 4 | [5 empty] | 0 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 0 | 0 | 0 | 0 | 0 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 0 | 0 | 0 | 0 | 0 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | [5 empty] | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | [5 empty] | 0 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | [5 empty] | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | [5 empty] | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | [5 empty] | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | [5 empty] | 0 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | [5 empty] | 0 | 0 | 2 | 0 | 0 | 0 | 2 | [5 empty] | 0 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 0 | 0 | 0 | 0 | 0 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | [5 empty] | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | [5 empty] | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | [5 empty] | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | [5 empty] | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | [5 empty] | 0 | 6 | 114 | 3 | 12 | 14 | 149 | [5 empty] | 0 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 2 | 0 | 0 | 0 | 0 | 2 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 12 | 0 | -8 | 0 | 0 | 4 | 190 | 22 | 36 | 65 | 1 | 314 | 12 | 0 | -4 | -4 | 0 | 4 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 1 | 0 | -1 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 1 | 0 | 0 | -1 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 13 | 0 | -9 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 15 | 0 | -4 | -5 | 0 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 2 | 0 | 0 | -2 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 2 | 0 | 0 | 0 | -2 | 0 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 2 | 0 | 0 | -2 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 2 | 0 | 0 | 0 | -2 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 186 | 0 | 0 | 0 | 0 | 186 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 246 | 0 | 0 | 0 | 0 | 246 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 186 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 246 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 4.5 | 0 | 0 | 0 | 0 | 4.5 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 12.5 | 0 | 0 | 0 | 0 | 12.5 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 4.5 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 12.5 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 2 | 0 | 0 | 0 | 0 | 2 | 31 | 35 | 6 | 3 | 0 | 75 | 5 | 0 | 0 | 0 | 0 | 5 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 2 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 5 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 3 | 0 | 0 | 0 | 0 | 3 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 3 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 0 | 0 | 0 | 0 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 207.5 | 0 | -9 | -2 | 0 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 283.5 | 0 | -4 | -5 | -2 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW6 - Faults - SWALES
HI6: Secondary deliverables RIIO-ED1 - Faults
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Faults associated with HI Categories | LV | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Faults associated with HI Categories | HV | 0.53114 | 1.0623 | 2.1245
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | EHV | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | 132kV | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Faults associated with HI Categories | Total | 0.53114 | 1.0623 | 2.1245
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 0 | 0 | 0 | 0 | 0 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 0 | 0 | 0 | 0 | 0 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 0 | 0 | 0 | 0 | 0 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 2 | -2 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 50 | -34 | -14 | -1 | -1 | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 99 | -64 | -26 | -4 | -5 | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 6 | -3 | -3 | 0 | 0 | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | 11 | -6 | -4 | -1 | 0 | 0 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 56 | -37 | -17 | -1 | -1 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 112 | -72 | -30 | -5 | -5 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 12 | -2 | -9 | -1 | 0 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 23 | -4 | -14 | -4 | -1 | 0 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 38 | -16 | -21 | -1 | 0 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 76 | -34 | -39 | -2 | -1 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 6 | -4 | -2 | 0 | 0 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 13 | -8 | -5 | 0 | 0 | 0 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 56 | -22 | -32 | -2 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 112 | -46 | -58 | -6 | -2 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 0 | 0 | 0 | 0 | 0 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 0 | 0 | 0 | 0 | 0 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 0 | 0 | 0 | 0 | 0 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 0 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 0 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 0 | 0 | 0 | 0 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 112 | -59 | -49 | -3 | -1 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 224 | -118 | -88 | -11 | -7 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW7 - HVP - SWALES
HI7: Secondary deliverables RIIO-ED1 - HVP
SWALES
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV |  | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV |  | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV |  | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV |  | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 0 | 0 | 0
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 0 | 0 | 0 | 0 | 0 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 101791 | 102791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163
| LV Switchgear (at s/s) |  |  |  | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278
[5 empty] | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 0 | 0 | 0 | 0 | 0 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 0 | 0 | 0 | 0 | 0 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511
[5 empty] | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 22 | 9 | 6 | 76
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 7865 | 8481 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103
[5 empty] | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635
[5 empty] | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 544 | 6 | 6 | 581
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 4319 | 4411 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 260 | 61 | 45 | 48 | 631
[5 empty] | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 467 | 143 | 119 | 137 | 1416
[5 empty] | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 8 | 8 | 4 | 31
[5 empty] | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 67 | 20 | 16 | 23 | 185
|  | Yes | 2263 | 2290 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254
[5 empty] | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 0 | 0 | 0 | 0 | 0 | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 0 | 0 | 0 | 0 | 0 | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267
[5 empty] | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 326 | 216 | 50 | 213 | 1084
[5 empty] | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4
|  | Yes | 10609 | 10973 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 0 | 0 | 0 | 0 | 0 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 0 | 0 | 0 | 0 | 0 |  | 3735 | 3843 | 1567 | 332 | 1132
| HV Transformer (GM) |  |  |  | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 144 | 535 | 156 | 220 | 1331
[5 empty] | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 0 | 0 | 0 | 0 | 0 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 0 | 0 | 0 | 0 | 0 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824
[5 empty] | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 291 | 204 | 35 | 47 | 1184
[5 empty] | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2
|  | Yes | 8341 | 8711 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 0 | 0 | 0 | 0 | 0 |  | 3175 | 1722 | 2250 | 511 | 683
| HV UG Cable |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 0 | 0 | 0 | 0 | 0 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 0 | 0 | 0 | 0 | 0 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285
[5 empty] | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797
[5 empty] | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 3 | 14 | 17 | 149
|  | Yes | 160231 | 161619 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 117 | 7 | 0 | 34 | 285
[5 empty] | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 57 | 20 | 17 | 70 | 314
[5 empty] | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63
[5 empty] | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45
|  | Yes | 707 | 778 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 323 | 186 | 42 | 24 | 132
| EHV Transformer |  |  |  | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 6 | 13 | 10 | 30 | 103
[5 empty] | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113
[5 empty] | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62
[5 empty] | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8
|  | Yes | 286 | 294 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 0 | 0 | 0 | 0 | 0 |  | 97 | 28 | 39 | 36 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749
| EHV UG Cable (Oil) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188
[5 empty] | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0
| EHV OHL Support - Poles |  |  |  | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475
[5 empty] | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510
[5 empty] | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20249 | 20457 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 0 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 0 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164
[5 empty] | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280
[5 empty] | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103
[5 empty] | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689
[5 empty] | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297
[5 empty] | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911
|  | Yes | 69 | 81.5 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93
[5 empty] | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 37 | 12 | 0 | 3 | 75
[5 empty] | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52
[5 empty] | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9
|  | Yes | 229 | 234 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10
| 132kV Transformer |  |  |  | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54
[5 empty] | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 15 | 0 | 8 | 56
[5 empty] | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11
[5 empty] | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10
|  | Yes | 131 | 134 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74
[5 empty] | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539
[5 empty] | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188
[5 empty] | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708
|  | Yes | 55.1747 | 55.1747 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704
[5 empty] | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006
[5 empty] | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2378 | 2361 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 0 | 0 | 0 | 0 |  | 287 | 1188 | 648 | 222 | 33
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291
[5 empty] | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037
[5 empty] | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379
[5 empty] | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13
|  | Yes | 4720 | 4652 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476
[5 empty] | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16
[5 empty] | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02
[5 empty] | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344
|  | Yes | 1089 | 1083.9 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 326193.7387 | 330263.8187 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 0 | 0 | 0 | 0 | 0 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 0 | 0 | 0 | 0 | 0 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW8 - Average Crit - SWALES
HI8: Secondary deliverables RIIO-ED1
SWALES
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 344 | 1405 | 278 | 2688 | 4715
| LV Switchgear (at s/s) | 1107 | 675 | 491 | 3823 | 6096
| LV UGB and LV Pillar OD (not at s/s) | 1273 | 782 | 494 | 2670 | 5219
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 37966 | 1198 | 1888 | 11397 | 52450
| HV Switchgear (GM) - Distribution | 5682 | 1668 | 2423 | 4920 | 14693
| HV Transformer (GM) | 5679 | 1241 | 3666 | 4703 | 15289
| HV UG Cable | 19048 | 142 | 1102 | 10500 | 30792
| HV OHL Support - Poles | 1964 | 1475 | 478 | 2920 | 6837
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 101815 | 752 | 3572 | 18941 | 125080
| EHV Transformer | 173351 | 951 | 18221 | 101562 | 294085
| EHV UG Cable (Gas) | 1726 | 7 | 390 | 6109 | 8232
| EHV UG Cable (Oil) | 44728 | 708 | 3833 | 25805 | 75074
| EHV UG Cable (Non Pressurised) | 36497 | 142 | 1602 | 15000 | 53241
| EHV OHL Support - Towers | 175157 | 25436 | 2484 | 82888 | 285965
| EHV OHL Support - Poles | 6668 | 1467 | 478 | 4100 | 12713
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 99549 | 12718 | 880 | 4000 | 117147
| EHV OHL Conductor (Tower Lines) | 91579 | 12718 | 880 | 4000 | 109177
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 231710 | 796 | 5943 | 24834 | 263283
| 132kV Transformer | 949275 | 1277 | 52400 | 274907 | 1277859
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 48235 | 708 | 10706 | 25805 | 85454
| 132kV UG Cable (Non Pressurised) | 224723 | 710 | 2501 | 225000 | 452934
| 132kV OHL Support - Tower | 757448 | 25436 | 3901 | 137123 | 923908
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 429529 | 12718 | 880 | 4000 | 447127
| 132kV OHL Conductor (Tower Lines) | 437701 | 12718 | 880 | 4000 | 455299
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]

## NAW1 - DPCR5 View - SWEST
HI1: Network Outputs DPCR5
SWEST
Price base (2012/13)
| ASSET CATEGORIES | ASSET REGISTER |  | HEALTH INDEX - CURRENT (as at 31 March) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with no further DPCR5 intervention) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with DPCR5 actual & forecast intervention) |  |  |  |  | DATA QUALITY - CURRENT (as at 31 March)
[19 empty] | Number of assets included for HI output measure | Primary form of measure | Number of assets actually observed | Average age of data used | Description of the form of measure used to assign a HI, the quality of data used, and any other relevant information | Degradation assumption adopted
|  | Current (as at 31 March) | Forecast (as at 31 March 2015) | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | Assets | Health Condition Age Other | % | Years | Commentary | Description
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 198508 | 198539 | 23606 | 137079 | 3676 | 26775 | 7372 | 16806 | 137079 | 4016 | 27795 | 12812 | 23637 | 137079 | 3676 | 26775 | 7372 | 198508 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
| LV Switchgear (at s/s) | 12069 | 12228 | 6113 | 2119 | 3365 | 219 | 253 | 5696 | 2076 | 3678 | 260 | 359 | 6309 | 2052 | 3517 | 253 | 97 | 12069 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| LV UGB and LV Pillar OD (not at s/s) | 12352 | 12333 | 2452 | 3219 | 6318 | 14 | 349 | 2370 | 2555 | 7047 | 19 | 361 | 2485 | 2555 | 7047 | 19 | 227 | 12352 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 2959 | 3046 | 1120 | 242 | 1283 | 127 | 187 | 1026 | 298 | 1193 | 221 | 221 | 1163 | 298 | 1190 | 217 | 178 | 2959 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Switchgear (GM) - Distribution | 16807 | 16802 | 7383 | 3218 | 3855 | 1126 | 1225 | 6539 | 3817 | 3774 | 1114 | 1563 | 6962 | 3723 | 3708 | 1112 | 1297 | 16807 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Transformer (GM) | 13020 | 13065 | 5572 | 2870 | 3391 | 322 | 865 | 5468 | 2659 | 3699 | 318 | 876 | 5940 | 2621 | 3631 | 318 | 555 | 13020 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV UG Cable
| HV OHL Support - Poles | 213180 | 213302 | 36727 | 147938 | 4459 | 18367 | 5689 | 29728 | 147937 | 4809 | 19416 | 11290 | 36850 | 147938 | 4458 | 18367 | 5689 | 213180 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition | 0
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 1011 | 1026 | 563 | 98 | 276 | 52 | 22 | 544 | 112 | 263 | 60 | 32 | 559 | 112 | 263 | 60 | 32 | 1011 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV Transformer | 592 | 597 | 224 | 53 | 234 | 67 | 14 | 214 | 54 | 227 | 69 | 28 | 228 | 54 | 225 | 66 | 24 | 592 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Gas) | 34 | 34 | 0 | 0 | 0 | 34 | 0 | 0 | 0 | 0 | 32.735 | 1.265 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Oil) | 60.2782 | 60.2782 | 0.738 | 38.421 | 21.119 | 0 | 0 | 0.738 | 28.776 | 30.764 | 0 | 0 | 0.738 | 28.776 | 30.764 | 0 | 0 | 60.278 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 494 | 489 | 120 | 304 | 47 | 17 | 6 | 113 | 281 | 77 | 17 | 6 | 119 | 282 | 75 | 13 | 0 | 494 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Support - Poles | 29611 | 29607 | 3581 | 18537 | 1465 | 3572 | 2456 | 2831 | 18537 | 1503 | 3684 | 3056 | 3577 | 18537 | 1465 | 3572 | 2456 | 29611 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition | 0
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 1045 | 1025 | 626 | 0 | 241 | 178 | 0 | 626 | 0 | 186 | 55 | 178 | 606 | 0 | 186 | 55 | 178 | 1045 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Conductor (Tower Lines) | 109 | 107.75 | 73.525 | 3.183 | 32.292 | 0 | 0 | 73.525 | 3.183 | 32.292 | 0 | 0 | 72.682 | 3.146 | 31.922 | 0 | 0 | 109 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 155 | 166 | 106 | 9 | 24 | 11 | 5 | 105 | 10 | 23 | 11 | 6 | 120 | 10 | 23 | 11 | 2 | 155 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV Transformer | 93 | 94 | 39 | 15 | 35 | 4 | 0 | 39 | 13 | 32 | 9 | 0 | 42 | 13 | 32 | 7 | 0 | 93 | Health | 1 | 1.5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Oil) | 64.8699 | 61.6699 | 12.541 | 48.698 | 0.029 | 3.602 | 0 | 12.541 | 45.196 | 3.533 | 3.6 | 0 | 12.541 | 45.196 | 3.533 | 0.4 | 0 | 64.87 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 3088 | 3088 | 751 | 1898 | 296 | 140 | 3 | 747 | 1896 | 298 | 144 | 3 | 750 | 1926 | 298 | 114 | 0 | 3088 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 4764 | 4764 | 2221 | 1324 | 922 | 248 | 49 | 2221 | 1293 | 858 | 98 | 294 | 2521 | 1293 | 858 | 92 | 0 | 4764 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV OHL Conductor (Tower Lines) | 1373.13 | 1369.13 | 370.308 | 454.927 | 547.895 | 0 | 0 | 359.38 | 350.553 | 659.831 | 3.366 | 0 | 358.252 | 349.453 | 658.059 | 3.366 | 0 | 1373.13 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required
Note on U7: Ofgem: Insert one of the following: Health; Condition; Age; or Other.

## NAW2 - Total - SWEST
HI2: Secondary deliverables RIIO-ED1
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) with investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) with investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | Yes | Expenditure on Health Index asset categories | LV | 15.327 | 28.785 | 56.978
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | No | Expenditure on Health Index asset categories | HV | 25.0499 | 55.2518 | 109.8316
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | EHV | 6.408 | 27.8776 | 56.2271
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | 132kV | 6.9664 | 17.8027 | 38.8234
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Health Index asset categories | Total | 53.7513 | 129.717 | 261.8601
| LV UGB |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 27885 | 137079 | 2401 | 25501 | 5673 | 198539 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 32287 | 137079 | 1080 | 24180 | 3913 | 198539 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 27885 | 137079 | 2401 | 25501 | 5673 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 32287 | 137079 | 1080 | 24180 | 3913 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 635 | 142 | 61 | 9 | 10 | 857 | 630 | 142 | 61 | 9 | 15 | 857 | 593 | 148 | 93 | 10 | 13 | 857 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 4995 | 2354 | 3623 | 228 | 64 | 11264 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 4736 | 2697 | 3353 | 352 | 126 | 11264 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 35 | 15 | 52 | 5 | 0 | 107 | 18 | 15 | 53 | 6 | 15 | 107 | 48 | 16 | 33 | 10 | 0 | 107 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 5665 | 2511 | 3736 | 242 | 74 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 5377 | 2861 | 3479 | 372 | 139 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 179 | 0 | 0 | 1 | 0 | 180 | 179 | 0 | 0 | 1 | 0 | 180 | 180 | 0 | 0 | 0 | 0 | 180 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 2277 | 2099 | 6959 | 626 | 13 | 11974 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 2113 | 1533 | 6200 | 1745 | 383 | 11974 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 31 | 16 | 125 | 7 | 0 | 179 | 15 | 16 | 125 | 7 | 16 | 179 | 38 | 9 | 114 | 18 | 0 | 179 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 2487 | 2115 | 7084 | 634 | 13 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 2331 | 1542 | 6314 | 1763 | 383 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 351 | 61 | 196 | 59 | 33 | 700 | 289 | 61 | 217 | 68 | 65 | 700 | 374 | 98 | 135 | 67 | 26 | 700 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 845 | 198 | 553 | 210 | 62 | 1868 | 661 | 198 | 586 | 232 | 191 | 1868 | 960 | 255 | 344 | 234 | 75 | 1868 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 196 | 51 | 157 | 42 | 9 | 455 | 122 | 51 | 162 | 60 | 60 | 455 | 236 | 57 | 94 | 55 | 13 | 455 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 8 | 3 | 12 | 0 | 0 | 23 | 7 | 3 | 12 | 1 | 0 | 23 | 11 | 4 | 6 | 2 | 0 | 23 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 1400 | 313 | 918 | 311 | 104 |  | 1079 | 313 | 977 | 361 | 316 |  | 1581 | 414 | 579 | 358 | 114 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 652 | 8 | 2 | 5 | 0 | 667 | 644 | 18 | 2 | 5 | 0 | 669 | 645 | 18 | 1 | 0 | 2 | 666 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 5817 | 3934 | 2814 | 1222 | 693 | 14480 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 6071 | 3858 | 2733 | 1111 | 531 | 14304 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 291 | 384 | 357 | 234 | 126 | 1392 | 82 | 398 | 360 | 235 | 356 | 1431 | 482 | 330 | 332 | 156 | 54 | 1354 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 35 | 9 | 0 | 1 | 1 | 46 | 15 | 9 | 0 | 1 | 25 | 50 | 35 | 9 | 0 | 0 | 2 | 46 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 6795 | 4335 | 3173 | 1462 | 820 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 7233 | 4215 | 3066 | 1267 | 589 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 1073 | 355 | 651 | 70 | 71 | 2220 | 910 | 359 | 660 | 88 | 203 | 2220 | 1120 | 312 | 667 | 112 | 9 | 2220 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 4069 | 1590 | 2887 | 271 | 166 | 8983 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 4130 | 1551 | 2927 | 305 | 70 | 8983 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 945 | 319 | 530 | 30 | 24 | 1848 | 861 | 323 | 535 | 56 | 73 | 1848 | 940 | 353 | 514 | 36 | 5 | 1848 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 6 | 3 | 0 | 0 | 14 | 3 | 6 | 3 | 0 | 2 | 14 | 5 | 5 | 4 | 0 | 0 | 14 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 6092 | 2270 | 4071 | 371 | 261 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 6195 | 2221 | 4112 | 453 | 84 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 41030 | 146348 | 3037 | 16797 | 3799 | 211011 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 45896 | 146349 | 1577 | 15338 | 1851 | 211011 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 445 | 1590 | 33 | 182 | 41 | 2291 | 280 | 1590 | 58 | 219 | 144 | 2291 | 498 | 1589 | 17 | 166 | 21 | 2291 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 41475 | 147938 | 3070 | 16979 | 3840 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 46394 | 147938 | 1594 | 15504 | 1872 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 265 | 56 | 22 | 22 | 4 | 369 | 248 | 57 | 24 | 22 | 18 | 369 | 244 | 77 | 27 | 11 | 10 | 369 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 238 | 76 | 75 | 73 | 9 | 471 | 184 | 76 | 83 | 86 | 46 | 475 | 254 | 89 | 63 | 32 | 38 | 476 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 55 | 16 | 27 | 25 | 4 | 127 | 44 | 16 | 27 | 26 | 14 | 127 | 74 | 21 | 9 | 18 | 5 | 127 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 26 | 10 | 11 | 6 | 2 | 55 | 19 | 10 | 12 | 9 | 5 | 55 | 23 | 16 | 8 | 5 | 3 | 55 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 584 | 158 | 135 | 126 | 19 |  | 495 | 159 | 146 | 143 | 83 |  | 595 | 203 | 107 | 66 | 56 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 127 | 37 | 45 | 17 | 20 | 246 | 111 | 37 | 45 | 18 | 35 | 246 | 140 | 39 | 36 | 15 | 16 | 246 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 67 | 31 | 99 | 34 | 17 | 248 | 46 | 33 | 99 | 35 | 35 | 248 | 79 | 34 | 71 | 37 | 27 | 248 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 36 | 4 | 19 | 9 | 5 | 73 | 25 | 4 | 21 | 9 | 14 | 73 | 45 | 7 | 12 | 7 | 2 | 73 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 25 | 0 | 3 | 2 | 0 | 30 | 22 | 0 | 3 | 4 | 1 | 30 | 21 | 4 | 2 | 1 | 2 | 30 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 255 | 72 | 166 | 62 | 42 |  | 204 | 74 | 168 | 66 | 85 |  | 285 | 84 | 121 | 60 | 47 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 17 | 17 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 17 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.134 | 4.346 | 10.62 | 7.601 | 0 | 22.701 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 3.051 | 11.414 | 0.635 | 0.401 | 15.501 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 7.601 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 0.401 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 29 | 70 | 20 | 6 | 0 | 125 | 27 | 70 | 20 | 6 | 2 | 125 | 31 | 76 | 18 | 0 | 0 | 125 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 69 | 175 | 55 | 0 | 0 | 299 | 69 | 166 | 55 | 9 | 0 | 299 | 62 | 186 | 51 | 0 | 0 | 299 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 17 | 36 | 12 | 0 | 0 | 65 | 16 | 34 | 12 | 2 | 1 | 65 | 15 | 36 | 14 | 0 | 0 | 65 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 115 | 281 | 87 | 6 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 108 | 298 | 83 | 0 | 0 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 736 | 3064 | 199 | 547 | 348 | 4894 | 374 | 3064 | 249 | 619 | 588 | 4894 | 887 | 3064 | 153 | 502 | 288 | 4894 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 3568 | 14261 | 872 | 2546 | 1620 | 22867 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 4298 | 14261 | 634 | 2335 | 1339 | 22867 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 291 | 1212 | 79 | 216 | 138 | 1936 | 148 | 1212 | 99 | 245 | 232 | 1936 | 351 | 1212 | 61 | 198 | 114 | 1936 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 4595 | 18537 | 1150 | 3309 | 2106 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 5536 | 18537 | 848 | 3035 | 1741 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 17 | 290 | 0 | 120 | 0 | 427 | 0 | 290 | 0 | 132 | 5 | 427 | 137 | 290 | 0 | 0 | 0 | 427 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 289 | 167 | 0 | 0 | 0 | 456 | 117 | 167 | 0 | 0 | 172 | 456 | 289 | 167 | 0 | 0 | 0 | 456 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 54 | 1 | 0 | 0 | 0 | 55 | 0 | 1 | 0 | 0 | 54 | 55 | 54 | 1 | 0 | 0 | 0 | 55 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 34 | 31 | 10 | 12 | 0 | 87 | 0 | 31 | 10 | 12 | 34 | 87 | 56 | 31 | 0 | 0 | 0 | 87 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 394 | 489 | 10 | 132 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 536 | 489 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 60 | -1 | 11 | 1 | 1 | 72 | 47 | 8 | 11 | 1 | 5 | 72 | 53 | 9 | 9 | 1 | 0 | 72 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 46 | 6 | 4 | 4 | 1 | 61 | 43 | 8 | 4 | 4 | 2 | 61 | 44 | 14 | 2 | 2 | 0 | 62 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 21 | 1 | 0 | 1 | 3 | 26 | 13 | 4 | 0 | 3 | 6 | 26 | 23 | 3 | 0 | 0 | 0 | 26 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 5 | 2 | 0 | 0 | 0 | 7 | 4 | 3 | 0 | 0 | 0 | 7 | 3 | 4 | 0 | 0 | 0 | 7 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 132 | 8 | 15 | 6 | 5 |  | 107 | 23 | 15 | 8 | 13 |  | 123 | 30 | 11 | 3 | 0 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 14 | 4 | 8 | 1 | 0 | 27 | 13 | 4 | 8 | 1 | 1 | 27 | 13 | 4 | 8 | 2 | 0 | 27 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 21 | 5 | 17 | 4 | 1 | 48 | 19 | 5 | 18 | 5 | 1 | 48 | 25 | 5 | 12 | 6 | 1 | 49 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 6 | 2 | 3 | 2 | 0 | 13 | 5 | 2 | 3 | 3 | 0 | 13 | 7 | 3 | 2 | 1 | 0 | 13 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 1 | 3 | 1 | 0 | 6 | 0 | 1 | 4 | 1 | 0 | 6 | 2 | 1 | 2 | 1 | 0 | 6 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 42 | 12 | 31 | 8 | 1 |  | 37 | 12 | 33 | 10 | 2 |  | 47 | 13 | 24 | 10 | 1 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 8.042 | 0.632 | 16.765 | 0 | 0.2 | 25.639 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 5.449 | 2.857 | 17.333 | 0 | 0 | 25.639 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 11.38 | 21.502 | 28.588 | 0 | 0.2 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 5.561 | 14.005 | 42.104 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 299 | 693 | 128 | 28 | 0 | 1148 | 298 | 676 | 128 | 45 | 1 | 1148 | 270 | 748 | 125 | 5 | 0 | 1148 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 302 | 792 | 125 | 33 | 0 | 1252 | 298 | 755 | 125 | 70 | 4 | 1252 | 306 | 812 | 132 | 2 | 0 | 1252 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 39 | 375 | 81 | 6 | 0 | 501 | 39 | 366 | 81 | 15 | 0 | 501 | 37 | 361 | 101 | 2 | 0 | 501 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 63 | 104 | 20 | 0 | 0 | 187 | 63 | 104 | 20 | 0 | 0 | 187 | 60 | 94 | 33 | 0 | 0 | 187 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 703 | 1964 | 354 | 67 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 673 | 2015 | 391 | 9 | 0 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 1139 | 200 | 455 | 145 | 35 | 1974 | 881 | 200 | 455 | 401 | 37 | 1974 | 1332 | 153 | 489 | 0 | 0 | 1974 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 966 | 104 | 261 | 78 | 0 | 1409 | 820 | 104 | 261 | 224 | 0 | 1409 | 1080 | 99 | 230 | 0 | 0 | 1409 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 575 | 33 | 255 | 81 | 1 | 945 | 507 | 33 | 255 | 149 | 1 | 945 | 682 | 32 | 231 | 0 | 0 | 945 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 317 | 11 | 92 | 16 | 0 | 436 | 313 | 11 | 92 | 20 | 0 | 436 | 339 | 8 | 89 | 0 | 0 | 436 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 2997 | 348 | 1063 | 320 | 36 |  | 2521 | 348 | 1063 | 794 | 38 |  | 3433 | 292 | 1039 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 95.344 | 82.501 | 378.804 | 26.094 | 0 | 582.743 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 77.335 | 114.53 | 335.821 | 55.057 | 0 | 582.743 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 156.43 | 21.698 | 167.759 | 26.486 | 0 | 372.373 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 42.795 | 152.391 | 160.951 | 16.236 | 0 | 372.373 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 4.613 | 82.052 | 175.652 | 20.01 | 0 | 282.327 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 361.05 | 219.014 | 721.468 | 67.598 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 167.174 | 409.54 | 701.112 | 91.303 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 102000.372 | 318751.121 | 28257.545 | 49628.39 | 13011.2 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 112918.523 | 318722.705 | 23635.74 | 47200.058 | 8939.401 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW3 - Asset Repl - SWEST
HI3: Secondary deliverables RIIO-ED1 - Asset replacement
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Asset Replacement associated with HI Categories | LV | 14.225 | 26.603 | 52.903
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Asset Replacement associated with HI Categories | HV | 22.121 | 49.229 | 98.269
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | EHV | 5.079 | 24.271 | 47.742
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | 132kV | 3.566 | 8.551 | 21.026
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Asset Replacement associated with HI Categories | Total | 44.991 | 108.654 | 219.94
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 14161 | 0 | -2266 | -3115 | -8780 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 28834 | 0 | -4614 | -6343 | -17877 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 14161 | 0 | -2266 | -3115 | -8780 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 28834 | 0 | -4614 | -6343 | -17877 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 5 | 0 | 0 | 0 | -5 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 7 | 0 | 0 | 0 | -7 | 0 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 474 | -25 | -59 | -92 | -298 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 954 | -56 | -82 | -122 | -694 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 17 | 0 | -1 | -1 | -15 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 32 | 0 | -2 | -6 | -24 | 0 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 496 | -25 | -60 | -93 | -318 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 993 | -56 | -84 | -128 | -725 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 1 | 0 | 0 | 0 | -1 | 0 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 348 | 0 | 0 | -115 | -233 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 703 | 0 | 0 | 0 | -703 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 16 | 0 | 0 | 0 | -16 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 24 | 0 | 0 | 0 | -24 | 0 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 364 | 0 | 0 | -115 | -249 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 728 | 0 | 0 | 0 | -728 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 62 | 0 | -21 | -9 | -32 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 127 | 0 | -28 | -5 | -94 | 0 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 184 | 0 | -33 | -22 | -129 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 386 | 0 | -73 | -19 | -294 | 0 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 74 | 0 | -5 | -18 | -51 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 127 | 0 | -9 | -19 | -99 | 0 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 1 | 0 | 0 | -1 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 5 | 0 | 0 | -4 | -1 | 0 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 321 | 0 | -59 | -50 | -212 |  | 1079 | 313 | 977 | 361 | 316 |  | 645 | 0 | -110 | -47 | -488 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 8 | -10 | 0 | 0 | 0 | -2 | 644 | 18 | 2 | 5 | 0 | 669 | 19 | -18 | -1 | 0 | -3 | -3 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 893 | -125 | -27 | 0 | -913 | -172 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 1806 | -107 | -185 | -43 | -1819 | -348 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 202 | -11 | 0 | 0 | -230 | -39 | 82 | 398 | 360 | 235 | 356 | 1431 | 404 | 0 | -17 | -6 | -458 | -77 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 1 | 25 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 1123 | -146 | -27 | 0 | -1167 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 2249 | -125 | -203 | -49 | -2304 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 151 | 0 | -1 | -18 | -132 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 275 | 0 | -1 | 0 | -274 | 0 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 536 | 0 | -4 | -121 | -411 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 1057 | 0 | -2 | -172 | -883 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 75 | 0 | 0 | -26 | -49 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 195 | 0 | 0 | -74 | -121 | 0 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 764 | 0 | -5 | -165 | -594 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 1529 | 0 | -3 | -246 | -1280 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 15253 | 0 | -2442 | -3355 | -9456 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 31473 | 0 | -5037 | -6922 | -19514 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 165 | 0 | -25 | -37 | -103 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 341 | 0 | -54 | -76 | -211 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 15418 | 0 | -2467 | -3392 | -9559 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 31814 | 0 | -5091 | -6998 | -19725 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 16 | 0 | -2 | 0 | -14 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 30 | -2 | -2 | -1 | -25 | 0 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 52 | 0 | -2 | -13 | -37 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 85 | -1 | 0 | -3 | -81 | 0 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 11 | 0 | 0 | -1 | -10 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 41 | 0 | 0 | -6 | -35 | 0 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 7 | 0 | -1 | -3 | -3 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 14 | 0 | 0 | -4 | -10 | 0 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 86 | 0 | -5 | -17 | -64 |  | 495 | 159 | 146 | 143 | 83 |  | 170 | -3 | -2 | -14 | -151 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 16 | 0 | 0 | -1 | -15 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 34 | 0 | 0 | 0 | -34 | 0 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 19 | 0 | 0 | -1 | -18 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 38 | 0 | 0 | 0 | -38 | 0 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 9 | 0 | 0 | 0 | -9 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 19 | 0 | 0 | 0 | -19 | 0 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 3 | 0 | 0 | -2 | -1 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 47 | 0 | 0 | -4 | -43 |  | 204 | 74 | 168 | 66 | 85 |  | 94 | 0 | 0 | 0 | -94 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | -17 | -17 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | -34 | -34 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | -17 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | -34 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | -7.2 | 0 | -7.2 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | -14.4 | -14.4 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | -7.2 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | -14.4 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 2 | 0 | 0 | 0 | -2 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 4 | 0 | 0 | 0 | -4 | 0 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 4 | 0 | 0 | 0 | -4 | 0 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 1 | 0 | 0 | 0 | -1 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 1 | 0 | 0 | 0 | -1 | 0 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 3 | 0 | 0 | 0 | -3 |  | 112 | 270 | 87 | 17 | 3 |  | 9 | 0 | 0 | 0 | -9 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 362 | 0 | -50 | -72 | -240 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 739 | 0 | -104 | -147 | -488 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 1685 | 0 | -237 | -337 | -1111 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 3440 | 0 | -482 | -687 | -2271 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 143 | 0 | -20 | -29 | -94 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 293 | 0 | -41 | -59 | -193 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 2190 | 0 | -307 | -438 | -1445 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 4472 | 0 | -627 | -893 | -2952 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 17 | 0 | 0 | -12 | -5 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 137 | 0 | 0 | 0 | -137 | 0 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 34 | 0 | 0 | 0 | -34 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 56 | 0 | 0 | 0 | -56 | 0 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 277 | 0 | 0 | -12 | -265 |  | 117 | 489 | 10 | 144 | 265 |  | 419 | 0 | 0 | 0 | -419 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 4 | 0 | 0 | 0 | -4 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 7 | 0 | 0 | -1 | -6 | 0 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 1 | 0 | 0 | 0 | -1 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 6 | 0 | 0 | -1 | -5 | 0 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 5 | 0 | 0 | -2 | -3 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 9 | 0 | 0 | 0 | -9 | 0 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 10 | 0 | 0 | -2 | -8 |  | 107 | 23 | 15 | 8 | 13 |  | 22 | 0 | 0 | -2 | -20 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 1 | 0 | 0 | -1 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 6 | 0 | 0 | -3 | -3 | 0 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 1 | 0 | 0 | -1 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 3 | 0 | 0 | -1 | -2 | 0 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 2 | 0 | 0 | -1 | -1 | 0 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 4 | 0 | -1 | -2 | -1 |  | 37 | 12 | 33 | 10 | 2 |  | 12 | 0 | 0 | -5 | -7 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0.2 | 0 | 0 | 0 | -0.2 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0.4 | 0 | 0 | 0 | -0.4 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0.2 | 0 | 0 | 0 | -0.2 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0.4 | 0 | 0 | 0 | -0.4 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 1 | 0 | 0 | 0 | -1 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 3 | 0 | 0 | 0 | -3 | 0 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 4 | 0 | 0 | 0 | -4 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 12 | 0 | 0 | 0 | -12 | 0 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 2 | 0 | 0 | 0 | -2 | 0 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 5 | 0 | 0 | 0 | -5 |  | 698 | 1901 | 354 | 130 | 5 |  | 17 | 0 | 0 | 0 | -17 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 258 | 0 | 0 | -256 | -2 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 459 | 0 | 0 | 0 | -459 | 0 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 146 | 0 | 0 | -146 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 264 | 0 | 0 | 0 | -264 | 0 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 68 | 0 | 0 | -68 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 175 | 0 | 0 | 0 | -175 | 0 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 4 | 0 | 0 | -4 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 26 | 0 | 0 | 0 | -26 | 0 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 476 | 0 | 0 | -474 | -2 |  | 2521 | 348 | 1063 | 794 | 38 |  | 924 | 0 | 0 | 0 | -924 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 40.805 | 0 | 0 | -32.346 | -8.459 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 66.899 | 0 | 0 | 0 | -66.899 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 1.495 | 0 | 0 | -1.495 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 27.981 | 0 | 0 | 0 | -27.981 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 3.72 | 0 | 0 | -2.99 | -0.731 | -0.001 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 42.3 | 0 | 0 | -33.841 | -8.459 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 98.6 | 0 | 0 | -2.99 | -95.611 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 35787.5 | -171 | -5197 | -7920.041 | -22740.659 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 73030 | -184 | -10734 | -14727.99 | -47864.411 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW4 - Refurbishment - SWEST
HI4: Secondary deliverables RIIO-ED1 - refurbishment
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV | 1.102 | 2.182 | 4.075
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV | 2.246 | 4.657 | 8.831
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV | 0.39 | 1.841 | 3.569
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV | 1.736 | 4.186 | 8.271
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 5.474 | 12.866 | 24.746
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 0 | 0 | 0 | 0 | 0 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 0 | 0 | 0 | 0 | 0 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 0 | 0 | 0 | 0 | 0 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 0 | 0 | 0 | 0 | 0 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 18 | 2 | 5 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 0 | 0 | 0 | 0 | 0 | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 0 | 0 | 0 | 0 | 0 | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 1 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 0 | 0 | 0 | 0 | 0 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 0 | 0 | 0 | 0 | 0 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 0 | 0 | 0 | 0 | 0 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 0 | 0 | 0 | 0 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 0 | 0 | 0 | 0 | 0 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 0 | 0 | 0 | 0 | 0 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 0 | 0 | 0 | 0 | 0 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 0 | 0 | 0 | 0 | 0 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 0 | 0 | 0 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 7 | 0 | -7 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 9 | 0 | -9 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 10 | 0 | -10 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 2 | 0 | -2 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 3 | 0 | -3 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 11 | 0 | -11 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 20 | 0 | -20 | 0 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 0 | 0 | 0 | 0 | 0 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 0 | 0 | 0 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 0 | 0 | 0 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 17 | 0 | -17 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 43 | 0 | -43 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 37 | 0 | -37 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 69 | 0 | -69 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 9 | 0 | -9 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 12 | 0 | -12 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 63 | 0 | -63 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 124 | 0 | -124 | 0 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 0 | 74 | 0 | -74 | 0 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 0 | 144 | 0 | -144 | 0 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW5 - General Reinf - SWEST
HI5: Secondary deliverables RIIO-ED1 - General reinforcement
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on General Reinforcement associated with HI Categories | LV
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on General Reinforcement associated with HI Categories | HV
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | EHV | 0.939 | 1.7656 | 4.9161
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | 132kV | 1.6644 | 5.0657 | 9.5264
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on General Reinforcement associated with HI Categories | Total | 2.6034 | 6.8313 | 14.4425
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | [5 empty] | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | [5 empty] | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | [5 empty] | 0 | 630 | 142 | 61 | 9 | 15 | 857 | [5 empty] | 0 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | [5 empty] | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | [5 empty] | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | [5 empty] | 0 | 18 | 15 | 53 | 6 | 15 | 107 | [5 empty] | 0 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | [5 empty] | 0 | 179 | 0 | 0 | 1 | 0 | 180 | [5 empty] | 0 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | [5 empty] | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | [5 empty] | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | [5 empty] | 0 | 15 | 16 | 125 | 7 | 16 | 179 | [5 empty] | 0 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | [5 empty] | 0 | 289 | 61 | 217 | 68 | 65 | 700 | [5 empty] | 0 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | [5 empty] | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | [5 empty] | 0 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | [5 empty] | 0 | 122 | 51 | 162 | 60 | 60 | 455 | [5 empty] | 0 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | [5 empty] | 0 | 7 | 3 | 12 | 1 | 0 | 23 | [5 empty] | 0 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | [5 empty] | 0 | 644 | 18 | 2 | 5 | 0 | 669 | [5 empty] | 0 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | [5 empty] | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | [5 empty] | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | [5 empty] | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | [5 empty] | 0 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | [5 empty] | 0 | 15 | 9 | 0 | 1 | 25 | 50 | [5 empty] | 0 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 0 | 0 | 0 | 0 | 0 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 0 | 0 | 0 | 0 | 0 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | [5 empty] | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | [5 empty] | 0 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | [5 empty] | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | [5 empty] | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | [5 empty] | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | [5 empty] | 0 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | [5 empty] | 0 | 3 | 6 | 3 | 0 | 2 | 14 | [5 empty] | 0 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 0 | 0 | 0 | 0 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 0 | 0 | 0 | 0 | 0 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | [5 empty] | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | [5 empty] | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | [5 empty] | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | [5 empty] | 0 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 1 | -1 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 4 | -1 | -2 | 0 | -1 | 0 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 2 | 0 | -6 | 0 | 0 | -4 | 184 | 76 | 83 | 86 | 46 | 475 | 12 | -1 | -6 | -1 | -3 | 1 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 3 | -1 | -6 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 16 | -2 | -8 | -1 | -4 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 1 | 0 | 0 | -1 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 2 | -2 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 7 | -4 | -2 | -1 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 2 | 0 | -2 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 4 | 0 | 0 | -4 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 4 | -2 | -2 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 12 | -4 | -2 | -6 | 0 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 142 | 0 | -52 | 0 | 0 | 90 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 170 | 0 | -80 | 0 | 0 | 90 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 142 | 0 | -52 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 170 | 0 | -80 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 9 | -9 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 12 | -10 | 0 | -2 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 2 | -2 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 3 | -2 | 0 | 0 | 0 | 1 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 3 | -3 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 3 | -2 | -1 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 1 | -1 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 1 | -1 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 15 | -15 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 19 | -15 | -1 | -2 | 0 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 1 | 0 | -1 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 3 | 0 | -2 | 0 | 0 | 1 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 1 | 0 | -1 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 3 | 0 | -2 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 165 | -18 | -61 | 0 | 0 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 220 | -21 | -93 | -9 | -4 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW6 - Faults - SWEST
HI6: Secondary deliverables RIIO-ED1 - Faults
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Faults associated with HI Categories | LV | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Faults associated with HI Categories | HV | 0.68289 | 1.3658 | 2.7316
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | EHV | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | 132kV | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Faults associated with HI Categories | Total | 0.68289 | 1.3658 | 2.7316
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 0 | 0 | 0 | 0 | 0 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 0 | 0 | 0 | 0 | 0 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 0 | 0 | 0 | 0 | 0 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 0 | 0 | 0 | 0 | 0 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 18 | 2 | 5 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 65 | -32 | -24 | -7 | -2 | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 131 | -61 | -44 | -18 | -8 | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 7 | -3 | -3 | -1 | 0 | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | 13 | -5 | -5 | -2 | -1 | 0 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 1 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 72 | -35 | -27 | -8 | -2 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 144 | -66 | -49 | -20 | -9 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 12 | -4 | -8 | 0 | 0 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 23 | -7 | -14 | -2 | 0 | 0 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 51 | -18 | -32 | -1 | 0 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 102 | -33 | -62 | -6 | -1 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 9 | -4 | -5 | 0 | 0 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 19 | -7 | -11 | -1 | 0 | 0 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 72 | -26 | -45 | -1 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 144 | -47 | -87 | -9 | -1 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 0 | 0 | 0 | 0 | 0 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 0 | 0 | 0 | 0 | 0 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 0 | 0 | 0 | 0 | 0 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 0 | 0 | 0 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 0 | 0 | 0 | 0 | 0 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 0 | 0 | 0 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 0 | 0 | 0 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 144 | -61 | -72 | -9 | -2 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 288 | -113 | -136 | -29 | -10 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW7 - HVP - SWEST
HI7: Secondary deliverables RIIO-ED1 - HVP
SWEST
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV |  | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV |  | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV |  | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV |  | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 0 | 0 | 0
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 0 | 0 | 0 | 0 | 0 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 198539 | 205889 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790
| LV Switchgear (at s/s) |  |  |  | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 148 | 93 | 10 | 20 | 857
[5 empty] | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 0 | 0 | 0 | 0 | 0 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 0 | 0 | 0 | 0 | 0 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264
[5 empty] | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 35 | 16 | 24 | 107
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12228 | 13276 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1 | 180
[5 empty] | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 0 | 0 | 0 | 0 | 0 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974
[5 empty] | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 114 | 18 | 24 | 179
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 12333 | 12711 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 98 | 163 | 72 | 120 | 700
[5 empty] | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 255 | 417 | 253 | 369 | 1868
[5 empty] | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 57 | 103 | 74 | 112 | 455
[5 empty] | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 6 | 6 | 1 | 23
|  | Yes | 3046 | 3093 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 18 | 2 | 5 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 36 | 2 | 0 | 5 | 669
[5 empty] | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 0 | 0 | 0 | 0 | 0 | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 0 | 0 | 0 | 0 | 0 | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652
[5 empty] | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 335 | 354 | 164 | 513 | 1431
[5 empty] | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 1 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 26 | 50
|  | Yes | 16802 | 16532.0018 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 0 | 0 | 0 | 0 | 0 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 0 | 0 | 0 | 0 | 0 |  | 4840 | 4406 | 3318 | 1336 | 2902
| HV Transformer (GM) |  |  |  | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 319 | 682 | 114 | 283 | 2220
[5 empty] | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 0 | 0 | 0 | 0 | 0 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983
[5 empty] | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 360 | 525 | 111 | 126 | 1848
[5 empty] | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 4 | 0 | 2 | 14
|  | Yes | 13065 | 13337 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 0 | 0 | 0 | 0 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 0 | 0 | 0 | 0 | 0 |  | 4522 | 2268 | 4202 | 708 | 1365
| HV UG Cable |  |  |  | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 0 | 0 | 0 | 0 | 0 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 0 | 0 | 0 | 0 | 0 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011
[5 empty] | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 213302 | 215615 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 80 | 31 | 12 | 36 | 369
[5 empty] | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 91 | 69 | 36 | 122 | 475
[5 empty] | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127
[5 empty] | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55
|  | Yes | 1026 | 1092 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 0 | 0 | 0 | 0 | 0 |  | 409 | 208 | 117 | 81 | 211
| EHV Transformer |  |  |  | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246
[5 empty] | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248
[5 empty] | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73
[5 empty] | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30
|  | Yes | 597 | 605 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 0 | 0 | 0 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 179 | 88 | 123 | 66 | 141
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34
| EHV UG Cable (Oil) |  |  |  | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926
[5 empty] | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901
[5 empty] | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 60.2782 | 45.8782 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125
[5 empty] | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299
[5 empty] | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 99 | 278 | 83 | 20 | 9
| EHV OHL Support - Poles |  |  |  | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894
[5 empty] | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 0 | 0 | 0 | 0 | 0 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777
[5 empty] | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 29607 | 29684 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 0 | 0 | 0 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 0 | 0 | 0 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427
[5 empty] | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456
[5 empty] | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55
[5 empty] | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87
|  | Yes | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481
[5 empty] | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696
[5 empty] | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374
[5 empty] | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199
|  | Yes | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72
[5 empty] | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 2 | 3 | 5 | 61
[5 empty] | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26
[5 empty] | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7
|  | Yes | 166 | 167 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 45 | 12 | 7 | 20
| 132kV Transformer |  |  |  | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27
[5 empty] | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 14 | 9 | 4 | 48
[5 empty] | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13
[5 empty] | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6
|  | Yes | 94 | 95 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  |  |  | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121
[5 empty] | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91
[5 empty] | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 61.6699 | 61.6699 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148
[5 empty] | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252
[5 empty] | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501
[5 empty] | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187
|  | Yes | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 656 | 1891 | 391 | 133 | 17
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974
[5 empty] | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409
[5 empty] | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945
[5 empty] | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436
|  | Yes | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743
[5 empty] | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373
[5 empty] | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328
[5 empty] | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686
|  | Yes | 1369.13 | 1297.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 511803.8282 | 522974.4299 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 0 | 0 | 0 | 0 | 0 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 0 | 0 | 0 | 0 | 0 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW8 - Average Crit - SWEST
HI8: Secondary deliverables RIIO-ED1
SWEST
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 502 | 1405 | 278 | 2688 | 4873
| LV Switchgear (at s/s) | 763 | 641 | 488 | 3771 | 5663
| LV UGB and LV Pillar OD (not at s/s) | 933 | 781 | 487 | 2469 | 4670
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 48320 | 1213 | 1901 | 11522 | 62956
| HV Switchgear (GM) - Distribution | 6914 | 1622 | 2365 | 4254 | 15155
| HV Transformer (GM) | 6675 | 1241 | 3654 | 4722 | 16292
| HV UG Cable | 21246 | 142 | 1102 | 10500 | 32990
| HV OHL Support - Poles | 1985 | 1463 | 478 | 2920 | 6846
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 82205 | 737 | 3545 | 15027 | 101514
| EHV Transformer | 252538 | 961 | 18652 | 104435 | 376586
| EHV UG Cable (Gas) | 1976 | 7 | 423 | 6018 | 8424
| EHV UG Cable (Oil) | 47104 | 710 | 11901 | 12557 | 72272
| EHV UG Cable (Non Pressurised) | 36616 | 142 | 1600 | 12307 | 50665
| EHV OHL Support - Towers | 127939 | 25436 | 2956 | 63510 | 219841
| EHV OHL Support - Poles | 5955 | 1468 | 478 | 4580 | 12481
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 84836 | 12718 | 880 | 4000 | 102434
| EHV OHL Conductor (Tower Lines) | 86729 | 12718 | 880 | 4000 | 104327
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 217321 | 944 | 6684 | 26385 | 251334
| 132kV Transformer | 2030169 | 1261 | 55430 | 288198 | 2375058
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 127182 | 710 | 11901 | 25113 | 164906
| 132kV UG Cable (Non Pressurised) | 1382681 | 710 | 2501 | 225000 | 1610892
| 132kV OHL Support - Tower | 625094 | 25436 | 4249 | 137123 | 791902
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 415727 | 12718 | 880 | 4000 | 433325
| 132kV OHL Conductor (Tower Lines) | 416091 | 12718 | 880 | 4000 | 433689
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]

## NAW1 - DPCR5 View - WMID
HI1: Network Outputs DPCR5
WMID
Price base (2012/13)
| ASSET CATEGORIES | ASSET REGISTER |  | HEALTH INDEX - CURRENT (as at 31 March) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with no further DPCR5 intervention) |  |  |  |  | HEALTH INDEX - 31 March 2015 (with DPCR5 actual & forecast intervention) |  |  |  |  | DATA QUALITY - CURRENT (as at 31 March)
[19 empty] | Number of assets included for HI output measure | Primary form of measure | Number of assets actually observed | Average age of data used | Description of the form of measure used to assign a HI, the quality of data used, and any other relevant information | Degradation assumption adopted
|  | Current (as at 31 March) | Forecast (as at 31 March 2015) | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 | Assets | Health Condition Age Other | % | Years | Commentary | Description
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 150524 | 150496 | 26120 | 52654 | 40931 | 11828 | 18991 | 20120 | 52654 | 41231 | 12728 | 23791 | 26120 | 52654 | 40903 | 11828 | 18991 | 150524 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
| LV Switchgear (at s/s) | 15400 | 15602 | 4790 | 2870 | 7265 | 209 | 266 | 4570 | 2498 | 7672 | 278 | 382 | 5096 | 2432 | 7633 | 210 | 231 | 15400 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| LV UGB and LV Pillar OD (not at s/s) | 21629 | 21732 | 4870 | 5168 | 10785 | 314 | 492 | 4764 | 4024 | 11780 | 380 | 681 | 6086 | 4014 | 11632 | 0 | 0 | 21629 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV Network
| HV Switchgear (GM) - Primary | 3536 | 3626 | 1263 | 258 | 1904 | 31 | 80 | 1214 | 276 | 1723 | 232 | 91 | 1686 | 268 | 1608 | 64 | 0 | 3536 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Switchgear (GM) - Distribution | 26928 | 26112 | 11663 | 5740 | 7821 | 910 | 794 | 10349 | 6443 | 7814 | 1271 | 1051 | 11490 | 6235 | 7572 | 684 | 131 | 26928 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| HV Transformer (GM) | 15478 | 15631 | 5209 | 4509 | 5262 | 204 | 294 | 4983 | 3527 | 6245 | 332 | 391 | 5401 | 3487 | 6192 | 332 | 219 | 15478 | Health | 1 | 6 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
HV UG Cable
| HV OHL Support - Poles | 201532 | 201544 | 80334 | 55946 | 27302 | 17625 | 20325 | 72834 | 55946 | 27677 | 18751 | 26324 | 80346 | 55946 | 27302 | 17625 | 20325 | 201532 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition
EHV Network
| EHV Switchgear (GM) | 453 | 467 | 140 | 79 | 209 | 8 | 17 | 137 | 66 | 222 | 8 | 20 | 190 | 62 | 209 | 4 | 2 | 453 | Health | 1 | 5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV Transformer | 270 | 272 | 55 | 8 | 149 | 47 | 11 | 51 | 8 | 135 | 57 | 19 | 70 | 8 | 128 | 57 | 9 | 270 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Gas) | 6 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Oil) | 114.925 | 73.925 | 14.457 | 44.563 | 15.081 | 40.824 | 0 | 13.897 | 28.198 | 32.006 | 40.824 | 0 | 13.71 | 27.818 | 31.575 | 0.822 | 0 | 114.925 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV UG Cable (Non Pressurised) | [22 empty] | 0
| EHV OHL Support - Towers | 1150 | 1150 | 1 | 824 | 119 | 206 | 0 | 1 | 771 | 128 | 204 | 46 | 49 | 783 | 126 | 192 | 0 | 1150 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Support - Poles | 19818 | 20282 | 3124 | 1706 | 11612 | 2796 | 580 | 2190 | 1706 | 11659 | 2936 | 1327 | 3587 | 1706 | 11613 | 2796 | 580 | 19818 | Condition | 1 | 5 | 10 yearly inspection which establishes the 'as found' condition | 0
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 2600 | 2600 | 504 | 980 | 942 | 48 | 126 | 504 | 980 | 786 | 185 | 145 | 504 | 980 | 786 | 185 | 145 | 2600 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| EHV OHL Conductor (Tower Lines) | 187.7 | 191.7 | 28.486 | 0 | 139.711 | 15.658 | 3.845 | 28.486 | 0 | 135.773 | 3.92 | 19.521 | 56.486 | 0 | 135.214 | 0 | 0 | 187.7 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV Network
| 132kV CBs | 260 | 263 | 91 | 15 | 84 | 62 | 8 | 87 | 19 | 71 | 72 | 11 | 131 | 16 | 56 | 59 | 1 | 260 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV Transformer | 245 | 248 | 96 | 14 | 118 | 11 | 6 | 93 | 13 | 113 | 16 | 10 | 99 | 13 | 113 | 16 | 7 | 245 | Health | 1 | 1.5 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Gas) | 25.935 | 20.935 | 0.092 | 3.578 | 10.996 | 0 | 11.269 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 25.935 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Oil) | 248.815 | 242.515 | 23.336 | 125.021 | 71.017 | 29.441 | 0 | 21.933 | 104.177 | 93.265 | 29.44 | 0 | 21.903 | 104.034 | 93.138 | 23.44 | 0 | 248.815 | Health | 1 |  | The HI is determined by consideration of leak history, circuit fault history, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. `Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV UG Cable (Non Pressurised) | [22 empty] | 0
| 132kV OHL Support - Tower | 2708 | 2732 | 155 | 1888 | 356 | 308 | 1 | 155 | 1888 | 356 | 308 | 1 | 182 | 1916 | 356 | 278 | 0 | 2708 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 5096 | 5088 | 1200 | 1193 | 1289 | 802 | 612 | 1198 | 1125 | 968 | 839 | 966 | 1822 | 1122 | 967 | 839 | 338 | 5096 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
| 132kV OHL Conductor (Tower Lines) | 1360 | 1374 | 269.82 | 45.941 | 886.664 | 52.877 | 104.698 | 269.82 | 45.941 | 886.749 | 0 | 157.49 | 441.31 | 45.941 | 886.749 | 0 | 0 | 1360 | Health | 1 | 3 | The HI is determined by consideration of 'as found' condition, defects, location, environment, age etc., within WPD's CBRM asset health/ risk model. The source data is extracted from WPD's Asset Management systems (including WPD’s CROWN database and EMU geographic mapping system ) | Forecast degradation based upon 'bath tub' type curve with asset health model. Rate of degradation dependant upon the existing observed asset health (relative to asset age)
Other
Submarine Cables
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required
Note on U7: Ofgem: Insert one of the following: Health; Condition; Age; or Other.

## NAW2 - Total - WMID
HI2: Secondary deliverables RIIO-ED1
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) with investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) with investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | Yes | Expenditure on Health Index asset categories | LV | 17.6235 | 40.428 | 78.663
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | No | Expenditure on Health Index asset categories | HV | 34.0891 | 65.6623 | 129.5415
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | EHV | 13.5873 | 25.2273 | 60.4753
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 |  | Expenditure on Health Index asset categories | 132kV | 18.8682 | 34.132 | 72.0073
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Health Index asset categories | Total | 84.1681 | 165.4495 | 340.6871
| LV UGB |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | 30525 | 52654 | 39581 | 10506 | 17230 | 150496 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | 34804 | 52654 | 38297 | 9222 | 15519 | 150496 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 30525 | 52654 | 39581 | 10506 | 17230 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 34804 | 52654 | 38297 | 9222 | 15519 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | 5117 | 1845 | 7150 | 341 | 33 | 14486 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | 5029 | 2060 | 5876 | 1445 | 76 | 14486 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | 286 | 77 | 674 | 60 | 19 | 1116 | 141 | 80 | 677 | 81 | 137 | 1116 | 372 | 85 | 431 | 220 | 8 | 1116 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 5403 | 1922 | 7824 | 401 | 52 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 5401 | 2145 | 6307 | 1665 | 84 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | 6863 | 3075 | 11612 | 182 | 0 | 21732 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | 7713 | 1808 | 9802 | 2397 | 12 | 21732 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 6863 | 3075 | 11612 | 182 | 0 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 7713 | 1808 | 9802 | 2397 | 12 |  | 5137 | 1824 | 9892 | 2658 | 2221
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | 265 | 57 | 267 | 68 | 6 | 663 | 186 | 65 | 271 | 78 | 63 | 663 | 287 | 83 | 120 | 146 | 27 | 663 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | 1334 | 199 | 824 | 108 | 0 | 2465 | 1107 | 210 | 873 | 273 | 2 | 2465 | 1453 | 254 | 429 | 314 | 15 | 2465 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | 262 | 47 | 111 | 0 | 0 | 420 | 217 | 55 | 133 | 15 | 0 | 420 | 279 | 75 | 64 | 2 | 0 | 420 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | 32 | 4 | 42 | 0 | 0 | 78 | 19 | 4 | 45 | 10 | 0 | 78 | 54 | 0 | 21 | 3 | 0 | 78 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 1893 | 307 | 1244 | 176 | 6 |  | 1529 | 334 | 1322 | 376 | 65 |  | 2073 | 412 | 634 | 465 | 42 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | 4210 | 2933 | 3543 | 407 | 22 | 11115 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | 3771 | 3183 | 2977 | 1124 | 16 | 11071 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | 4286 | 3422 | 2590 | 363 | 72 | 10733 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | 4141 | 3374 | 2361 | 755 | 51 | 10682 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | 1259 | 1103 | 1193 | 114 | 12 | 3681 | 925 | 1132 | 1211 | 409 | 36 | 3713 | 1372 | 946 | 1016 | 306 | 15 | 3655 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | 133 | 28 | 192 | 100 | 0 | 453 | 72 | 31 | 199 | 124 | 33 | 459 | 196 | 35 | 69 | 146 | 0 | 446 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 9888 | 7486 | 7518 | 984 | 106 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 9480 | 7538 | 6423 | 2331 | 82 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | 1164 | 839 | 1533 | 91 | 0 | 3627 | 952 | 844 | 1542 | 140 | 149 | 3627 | 1218 | 689 | 1586 | 134 | 0 | 3627 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | 3953 | 1489 | 4225 | 125 | 0 | 9792 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | 4064 | 1473 | 4036 | 219 | 0 | 9792 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | 788 | 136 | 1218 | 18 | 0 | 2160 | 576 | 137 | 1226 | 105 | 116 | 2160 | 931 | 182 | 1020 | 27 | 0 | 2160 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | 27 | 0 | 25 | 0 | 0 | 52 | 10 | 0 | 25 | 5 | 12 | 52 | 40 | 1 | 11 | 0 | 0 | 52 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 5932 | 2464 | 7001 | 234 | 0 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 6253 | 2345 | 6653 | 380 | 0 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | 197 | 137 | 67 | 43 | 50 | 494 | 151 | 137 | 69 | 50 | 87 | 494 | 197 | 137 | 67 | 43 | 50 | 494 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 41625 | 55946 | 29238 | 23433 | 51302
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 47 | 24 | 41 | 50 | 2 | 164 | 35 | 24 | 43 | 58 | 2 | 162 | 101 | 22 | 18 | 17 | 16 | 174 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 171 | 9 | 43 | 25 | 2 | 250 | 121 | 9 | 52 | 57 | 2 | 241 | 191 | 13 | 28 | 15 | 11 | 258 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 40 | 2 | 10 | 6 | 1 | 59 | 24 | 2 | 15 | 12 | 1 | 54 | 45 | 7 | 0 | 7 | 3 | 62 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 8 | 1 | 2 | 0 | 0 | 11 | 6 | 1 | 3 | 0 | 0 | 10 | 7 | 2 | 2 | 0 | 0 | 11 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 266 | 36 | 96 | 81 | 5 |  | 186 | 36 | 113 | 127 | 5 |  | 344 | 44 | 48 | 39 | 30 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 25 | 7 | 33 | 25 | 24 | 114 | 20 | 7 | 33 | 25 | 29 | 114 | 44 | 9 | 29 | 8 | 26 | 116 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 33 | 6 | 31 | 9 | 3 | 82 | 16 | 6 | 32 | 9 | 10 | 73 | 41 | 8 | 21 | 10 | 3 | 83 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 35 | 3 | 28 | 7 | 0 | 73 | 23 | 3 | 30 | 11 | 6 | 73 | 39 | 5 | 14 | 13 | 3 | 74 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 8 | 0 | 4 | 0 | 0 | 12 | 2 | 0 | 4 | 3 | 3 | 12 | 8 | 0 | 2 | 2 | 0 | 12 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 101 | 16 | 96 | 41 | 27 |  | 61 | 16 | 99 | 48 | 48 |  | 132 | 22 | 66 | 33 | 32 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 9.417 | 8.287 | 2.592 | 0 | 0.395 | 20.691 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 8.97 | 2.577 | 8.749 | 0 | 0 | 20.296 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.598 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 9.14 | 9.7 | 54.264 | 0 | 0.222 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 6 | 242 | 61 | 30 | 0 | 339 | 6 | 240 | 61 | 32 | 0 | 339 | 6 | 251 | 39 | 43 | 0 | 339 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 43 | 304 | 64 | 109 | 0 | 520 | 43 | 298 | 64 | 115 | 0 | 520 | 42 | 311 | 62 | 105 | 0 | 520 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 233 | 14 | 44 | 0 | 291 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 227 | 31 | 33 | 0 | 291 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 49 | 779 | 139 | 183 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 48 | 789 | 132 | 181 | 0 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 454 | 166 | 1100 | 226 | 31 | 1977 | 223 | 166 | 1143 | 284 | 160 | 1976 | 556 | 166 | 1069 | 180 | 5 | 1976 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 4181 | 1372 | 8737 | 1865 | 253 | 16408 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 5238 | 1372 | 8329 | 1486 | 43 | 16468 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 278 | 102 | 678 | 139 | 19 | 1216 | 138 | 102 | 702 | 176 | 98 | 1216 | 341 | 102 | 659 | 111 | 3 | 1216 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 179 | 66 | 433 | 89 | 12 | 779 | 89 | 66 | 451 | 110 | 63 | 779 | 219 | 66 | 421 | 71 | 2 | 779 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 5092 | 1706 | 10948 | 2319 | 315 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 6354 | 1706 | 10478 | 1848 | 53 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 63 | 187 | 102 | 142 | 0 | 494 | 0 | 187 | 102 | 142 | 63 | 494 | 205 | 6 | 238 | 45 | 0 | 494 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 795 | 397 | 590 | 54 | 0 | 1836 | 485 | 397 | 590 | 142 | 222 | 1836 | 1006 | 17 | 700 | 113 | 0 | 1836 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 179 | 0 | 91 | 0 | 0 | 270 | 19 | 0 | 91 | 115 | 45 | 270 | 240 | 0 | 30 | 0 | 0 | 270 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 1037 | 584 | 783 | 196 | 0 |  | 504 | 584 | 783 | 399 | 330 |  | 1451 | 23 | 968 | 158 | 0 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 20.478 | 24.117 | 84.327 | 12.775 | 0 | 141.697 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 27.109 | 28.486 | 84.326 | 1.776 | 0 | 141.697 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 40.369 | 24.117 | 114.439 | 12.775 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 47 | 28.486 | 114.438 | 1.776 | 0 |  | 28 | 28.486 | 114.438 | 1.776 | 19
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 56 | 18 | 12 | 19 | 24 | 129 | 31 | 18 | 16 | 19 | 41 | 125 | 88 | 20 | 3 | 6 | 20 | 137 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 73 | 3 | 7 | 3 | 0 | 86 | 53 | 4 | 9 | 3 | 15 | 84 | 82 | 5 | 5 | 2 | 0 | 94 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 29 | 4 | 2 | 4 | 0 | 39 | 22 | 5 | 3 | 5 | 4 | 39 | 32 | 5 | 0 | 2 | 0 | 39 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 1 | 0 | 15 | 15 | 0 | 0 | 0 | 0 | 15 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 173 | 25 | 21 | 26 | 24 |  | 120 | 27 | 28 | 28 | 60 |  | 217 | 30 | 8 | 10 | 20 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 34 | 10 | 37 | 6 | 0 | 87 | 33 | 10 | 37 | 6 | 1 | 87 | 32 | 15 | 29 | 8 | 3 | 87 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 51 | 2 | 52 | 8 | 2 | 115 | 38 | 2 | 52 | 8 | 8 | 108 | 65 | 5 | 43 | 7 | 0 | 120 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 23 | 5 | 11 | 3 | 0 | 42 | 16 | 5 | 11 | 4 | 6 | 42 | 24 | 8 | 9 | 1 | 0 | 42 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 6 | 1 | 2 | 2 | 0 | 11 | 2 | 1 | 2 | 4 | 2 | 11 | 8 | 0 | 3 | 0 | 0 | 11 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 114 | 18 | 102 | 19 | 2 |  | 89 | 18 | 102 | 22 | 17 |  | 129 | 28 | 84 | 16 | 3 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0.092 | 0 | 14.575 | 0 | 1.948 | 16.615 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0.092 | 0 | 12.202 | 0.001 | 0 | 12.295 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0.092 | 0 | 14.575 | 0 | 1.948 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0.092 | 0 | 12.202 | 0.001 | 0 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 16.26 | 48.6 | 85.423 | 0 | 11.72 | 162.003 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 12.36 | 49.921 | 82.297 | 5.705 | 0 | 150.283 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 21.517 | 70.48 | 127.078 | 0 | 11.72 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 13.026 | 67.637 | 132.708 | 5.705 | 0 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 37 | 862 | 156 | 63 | 0 | 1118 | 37 | 848 | 156 | 77 | 0 | 1118 | 37 | 850 | 182 | 49 | 0 | 1118 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 136 | 715 | 144 | 96 | 0 | 1091 | 136 | 695 | 144 | 116 | 0 | 1091 | 136 | 718 | 161 | 76 | 0 | 1091 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 9 | 335 | 77 | 41 | 0 | 462 | 9 | 321 | 77 | 55 | 0 | 462 | 9 | 338 | 88 | 27 | 0 | 462 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 39 | 0 | 22 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 47 | 0 | 14 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 182 | 1951 | 377 | 222 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 182 | 1953 | 431 | 166 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 1220 | 302 | 611 | 362 | 66 | 2561 | 782 | 302 | 611 | 362 | 504 | 2561 | 1648 | 69 | 732 | 112 | 0 | 2561 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 996 | 62 | 112 | 182 | 24 | 1376 | 664 | 62 | 112 | 182 | 356 | 1376 | 1204 | 20 | 122 | 32 | 0 | 1378 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 458 | 150 | 229 | 27 | 68 | 932 | 308 | 150 | 229 | 27 | 218 | 932 | 553 | 88 | 283 | 8 | 0 | 932 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 125 | 2 | 66 | 20 | 6 | 219 | 64 | 2 | 66 | 20 | 67 | 219 | 151 | 2 | 26 | 40 | 0 | 219 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 2799 | 516 | 1018 | 591 | 164 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 3556 | 179 | 1163 | 192 | 0 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 215.68 | 32.728 | 368.248 | 64.158 | 0 | 680.814 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 151.571 | 160.995 | 368.248 | 0 | 0 | 680.814 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 119.428 | 26.057 | 189.464 | 39.377 | 0 | 374.326 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 107.455 | 57.843 | 209.028 | 0 | 0 | 374.326 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 140.559 | 24.839 | 79.727 | 9.966 | 0 | 255.091 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 119.259 | 43.445 | 92.387 | 0 | 0 | 255.091 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 22.635 | 7.225 | 33.91 | -0.001 | 0 | 63.769 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 22.634 | 0 | 41.135 | 0 | 0 | 63.769 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 498.302 | 90.849 | 671.349 | 113.5 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 400.919 | 262.283 | 710.798 | 0 | 0 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C2 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C3 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[5 empty] | C4 | [5 empty] | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 151232.923 | 129689.332 | 116640.016 | 33912.299 | 38270.266 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 158953.177 | 127990.106 | 109826.41 | 36735.482 | 36202.222 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW3 - Asset Repl - WMID
HI3: Secondary deliverables RIIO-ED1 - Asset replacement
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Asset Replacement associated with HI Categories | LV | 16.722 | 38.42 | 74.571
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Asset Replacement associated with HI Categories | HV | 31.922 | 61.503 | 121.091
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | EHV | 12.336 | 19.685 | 39.359
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Asset Replacement associated with HI Categories | 132kV | 15.207 | 22.997 | 46.718
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Asset Replacement associated with HI Categories | Total | 76.187 | 142.605 | 281.739
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | 17621 | 0 | -2203 | -3084 | -12334 | 0 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | 34736 | 0 | -4343 | -6079 | -24314 | 0 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 17621 | 0 | -2203 | -3084 | -12334 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 34736 | 0 | -4343 | -6079 | -24314 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | 744 | -113 | -19 | -230 | -382 | 0 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | 1500 | -222 | -23 | -136 | -1119 | 0 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | 144 | -3 | -2 | -21 | -118 | 0 | 141 | 80 | 677 | 81 | 137 | 1116 | 272 | -9 | -1 | -17 | -245 | 0 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 888 | -116 | -21 | -251 | -500 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 1772 | -231 | -24 | -153 | -1364 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | 1224 | 0 | 0 | -1014 | -210 | 0 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | 2448 | 0 | 0 | -239 | -2209 | 0 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 1224 | 0 | 0 | -1014 | -210 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 2448 | 0 | 0 | -239 | -2209 |  | 5137 | 1824 | 9892 | 2658 | 2221
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | 79 | -8 | -4 | -10 | -57 | 0 | 186 | 65 | 271 | 78 | 63 | 663 | 140 | -11 | -14 | 0 | -115 | 0 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | 227 | -11 | -49 | -165 | -2 | 0 | 1107 | 210 | 873 | 273 | 2 | 2465 | 457 | -22 | -66 | -102 | -267 | 0 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | 45 | -8 | -22 | -15 | 0 | 0 | 217 | 55 | 133 | 15 | 0 | 420 | 98 | -13 | -13 | -55 | -17 | 0 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | 13 | 0 | -3 | -10 | 0 | 0 | 19 | 4 | 45 | 10 | 0 | 78 | 35 | 0 | 0 | -25 | -10 | 0 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 364 | -27 | -78 | -200 | -59 |  | 1529 | 334 | 1322 | 376 | 65 |  | 730 | -46 | -93 | -182 | -409 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | 413 | -51 | -56 | -239 | -108 | -41 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | 865 | -70 | -134 | -195 | -551 | -85 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | 511 | -53 | -30 | -327 | -152 | -51 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | 1035 | -68 | -105 | -262 | -702 | -102 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | 326 | -25 | -14 | -295 | -24 | -32 | 925 | 1132 | 1211 | 409 | 36 | 3713 | 587 | -36 | -45 | -229 | -335 | -58 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | 60 | -3 | -6 | -24 | -33 | -6 | 72 | 31 | 199 | 124 | 33 | 459 | 139 | -2 | -12 | -31 | -107 | -13 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 1310 | -132 | -106 | -885 | -317 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 2626 | -176 | -296 | -717 | -1695 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | 198 | 0 | 0 | -49 | -149 | 0 | 952 | 844 | 1542 | 140 | 149 | 3627 | 400 | 0 | 0 | -91 | -309 | 0 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | 585 | 0 | 0 | -231 | -354 | 0 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | 1155 | 0 | -1 | -377 | -777 | 0 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | 204 | 0 | -1 | -87 | -116 | 0 | 576 | 137 | 1226 | 105 | 116 | 2160 | 425 | 0 | -1 | -178 | -246 | 0 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | 17 | 0 | 0 | -5 | -12 | 0 | 10 | 0 | 25 | 5 | 12 | 52 | 31 | 0 | 0 | -13 | -18 | 0 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 1004 | 0 | -1 | -372 | -631 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 2011 | 0 | -2 | -659 | -1350 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | 17170 | 0 | -859 | -2576 | -13735 | 0 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | 34545 | 0 | -1727 | -5182 | -27636 | 0 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | 2030 | 0 | -101 | -304 | -1625 | 0 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | 4081 | 0 | -204 | -612 | -3265 | 0 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | 46 | 0 | -2 | -7 | -37 | 0 | 151 | 137 | 69 | 50 | 87 | 494 | 95 | 0 | -5 | -14 | -76 | 0 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 19246 | 0 | -962 | -2887 | -15397 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 38721 | 0 | -1936 | -5808 | -30977 |  | 41625 | 55946 | 29238 | 23433 | 51302
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 8 | 0 | 0 | -8 | 0 | 0 | 35 | 24 | 43 | 58 | 2 | 162 | 44 | 0 | 0 | 0 | -44 | 0 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 32 | 0 | 0 | -32 | 0 | 0 | 121 | 9 | 52 | 57 | 2 | 241 | 48 | 0 | 0 | 0 | -48 | 0 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 6 | 0 | 0 | -6 | 0 | 0 | 24 | 2 | 15 | 12 | 1 | 54 | 10 | 0 | 0 | 0 | -10 | 0 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1 | 3 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 46 | 0 | 0 | -46 | 0 |  | 186 | 36 | 113 | 127 | 5 |  | 102 | 0 | 0 | 0 | -102 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 5 | 0 | 0 | 0 | -5 | 0 | 20 | 7 | 33 | 25 | 29 | 114 | 22 | 0 | 0 | 0 | -22 | 0 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 7 | 0 | 0 | 0 | -7 | 0 | 16 | 6 | 32 | 9 | 10 | 73 | 15 | 0 | 0 | 0 | -15 | 0 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 9 | 0 | 0 | -3 | -6 | 0 | 23 | 3 | 30 | 11 | 6 | 73 | 12 | 0 | 0 | -2 | -10 | 0 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 6 | 0 | 0 | -3 | -3 | 0 | 2 | 0 | 4 | 3 | 3 | 12 | 6 | 0 | 0 | 0 | -6 | 0 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 27 | 0 | 0 | -6 | -21 |  | 61 | 16 | 99 | 48 | 48 |  | 55 | 0 | 0 | -2 | -53 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 0 | 0 | 0 | 0 | -0.2 | -0.2 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 0 | 0 | 0 | 0 | -0.6 | -0.6 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 0 | 0 | 0 | 0 | -0.2 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 0 | 0 | 0 | 0 | -0.6 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 240 | 61 | 32 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 298 | 64 | 115 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 0 | 0 | 0 | 0 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 231 | 0 | -43 | -58 | -129 | 1 | 223 | 166 | 1143 | 284 | 160 | 1976 | 458 | 0 | -86 | -115 | -257 | 0 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 1894 | 0 | -348 | -479 | -1066 | 1 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 3764 | 0 | -694 | -951 | -2119 | 0 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 140 | 0 | -24 | -37 | -79 | 0 | 138 | 102 | 702 | 176 | 98 | 1216 | 280 | 0 | -50 | -72 | -158 | 0 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 90 | 0 | -18 | -21 | -51 | 0 | 89 | 66 | 451 | 110 | 63 | 779 | 180 | 0 | -35 | -44 | -101 | 0 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 2355 | 0 | -433 | -595 | -1325 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 4682 | 0 | -865 | -1182 | -2635 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 63 | 0 | 0 | 0 | -63 | 0 | 0 | 187 | 102 | 142 | 63 | 494 | 205 | 0 | 0 | 0 | -205 | 0 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 310 | 0 | 0 | -88 | -222 | 0 | 485 | 397 | 590 | 142 | 222 | 1836 | 521 | 0 | 0 | 0 | -521 | 0 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 160 | 0 | 0 | -115 | -45 | 0 | 19 | 0 | 91 | 115 | 45 | 270 | 221 | 0 | 0 | 0 | -221 | 0 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 533 | 0 | 0 | -203 | -330 |  | 504 | 584 | 783 | 399 | 330 |  | 947 | 0 | 0 | 0 | -947 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 8 | 0 | 0 | -8 | 0 | 0 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 19 | 0 | 0 | 0 | -19 | 0 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 8 | 0 | 0 | -8 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 19 | 0 | 0 | 0 | -19 |  | 28 | 28.486 | 114.438 | 1.776 | 19
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 9 | 0 | 0 | 0 | -9 | 0 | 31 | 18 | 16 | 19 | 41 | 125 | 32 | 0 | 0 | 0 | -32 | 0 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 14 | 0 | 0 | 0 | -14 | 0 | 53 | 4 | 9 | 3 | 15 | 84 | 17 | 0 | 0 | 0 | -17 | 0 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 5 | 0 | 0 | -1 | -4 | 0 | 22 | 5 | 3 | 5 | 4 | 39 | 9 | 0 | 0 | 0 | -9 | 0 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 1 | 0 | 0 | -1 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 15 | 1 | 0 | 0 | 0 | -1 | 0 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 29 | 0 | 0 | -2 | -27 |  | 120 | 27 | 28 | 28 | 60 |  | 59 | 0 | 0 | 0 | -59 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 1 | 0 | 0 | 0 | -1 | 0 | 33 | 10 | 37 | 6 | 1 | 87 | 3 | 0 | 0 | 0 | -3 | 0 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 6 | 0 | 0 | 0 | -6 | 0 | 38 | 2 | 52 | 8 | 8 | 108 | 18 | 0 | 0 | -5 | -13 | 0 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 7 | 0 | 0 | -1 | -6 | 0 | 16 | 5 | 11 | 4 | 6 | 42 | 11 | 0 | 0 | -1 | -10 | 0 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 4 | 0 | 0 | -2 | -2 | 0 | 2 | 1 | 2 | 4 | 2 | 11 | 6 | 0 | 0 | 0 | -6 | 0 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 18 | 0 | 0 | -3 | -15 |  | 89 | 18 | 102 | 22 | 17 |  | 38 | 0 | 0 | -6 | -32 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0 | 0 | 0 | 0 | -4.32 | -4.32 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0 | 0 | -2.372 | 0 | -6.268 | -8.64 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0 | 0 | 0 | 0 | -4.32 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0 | 0 | -2.372 | 0 | -6.268 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 0 | 0 | 0 | 0 | -11.72 | -11.72 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 0 | 0 | 0 | 0 | -23.44 | -23.44 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 0 | 0 | 0 | 0 | 0 | 0 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 0 | 0 | 0 | 0 | -11.72 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 0 | 0 | 0 | 0 | -23.44 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 848 | 156 | 77 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 695 | 144 | 116 | 0 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 321 | 77 | 55 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 438 | 0 | 0 | 0 | -438 | 0 | 782 | 302 | 611 | 362 | 504 | 2561 | 866 | 0 | 0 | 0 | -866 | 0 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 332 | 0 | 0 | 0 | -332 | 0 | 664 | 62 | 112 | 182 | 356 | 1376 | 538 | 0 | 0 | 0 | -538 | 0 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 150 | 0 | 0 | 0 | -150 | 0 | 308 | 150 | 229 | 27 | 218 | 932 | 245 | 0 | 0 | 0 | -245 | 0 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 61 | 0 | 0 | 0 | -61 | 0 | 64 | 2 | 66 | 20 | 67 | 219 | 87 | 0 | 0 | 0 | -87 | 0 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 981 | 0 | 0 | 0 | -981 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 1736 | 0 | 0 | 0 | -1736 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 48.146 | 0 | 0 | -48.146 | 0 | 0 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 112.304 | 0 | 0 | 0 | -112.304 | 0 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 23.096 | 0 | 0 | -23.096 | 0 | 0 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 62.473 | 0 | 0 | 0 | -62.473 | 0 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 16.543 | 0 | 0 | -16.543 | 0 | 0 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 26.509 | 0 | 0 | 0 | -26.509 | 0 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 14.115 | 0 | 0 | -14.115 | 0 | 0 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 14.114 | 0 | 0 | 0 | -14.114 | 0 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 101.9 | 0 | 0 | -101.9 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 215.4 | 0 | 0 | 0 | -215.4 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 45755.9 | -275 | -3804 | -9657.9 | -32163.24 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 90897.4 | -453 | -7561.372 | -15027 | -68146.708 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW4 - Refurb - WMID
HI4: Secondary deliverables RIIO-ED1 - refurbishment
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV | 0.73 | 1.665 | 3.406
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV | 1.636 | 3.097 | 6.326
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV | 0.943 | 2.077 | 4.157
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV | 3.03 | 6.135 | 12.243
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 6.339 | 12.974 | 26.132
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 |  | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | 0 | 0 | 0 | 0 | 0 | 0 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 0 | 0 | 0 | 0 | 0 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | 0 | 0 | 0 | 0 | 0 | 0 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 80 | 677 | 81 | 137 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 0 | 0 | 0 | 0 | 0 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 0 | 0 | 0 | 0 | 0 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | 0 | 0 | 0 | 0 | 0 | 0 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | 0 | 0 | 0 | 0 | 0 | 0 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 0 | 0 | 0 | 0 | 0 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 0 | 0 | 0 | 0 | 0 |  | 5137 | 1824 | 9892 | 2658 | 2221
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 65 | 271 | 78 | 63 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 210 | 873 | 273 | 2 | 2465 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 55 | 133 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 45 | 10 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 0 | 0 | 0 | 0 | 0 |  | 1529 | 334 | 1322 | 376 | 65 |  | 0 | 0 | 0 | 0 | 0 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | 0 | 0 | 0 | 0 | 0 | 0 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | 0 | 0 | 0 | 0 | 0 | 0 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | 0 | 0 | 0 | 0 | 0 | 0 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | 0 | 0 | 0 | 0 | 0 | 0 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | 0 | 0 | 0 | 0 | 0 | 0 | 925 | 1132 | 1211 | 409 | 36 | 3713 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 31 | 199 | 124 | 33 | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 0 | 0 | 0 | 0 | 0 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 0 | 0 | 0 | 0 | 0 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 844 | 1542 | 140 | 149 | 3627 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | 0 | 0 | 0 | 0 | 0 | 0 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | 0 | 0 | 0 | 0 | 0 | 0 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 137 | 1226 | 105 | 116 | 2160 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 25 | 5 | 12 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 0 | 0 | 0 | 0 | 0 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 0 | 0 | 0 | 0 | 0 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | 0 | 0 | 0 | 0 | 0 | 0 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | 0 | 0 | 0 | 0 | 0 | 0 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 137 | 69 | 50 | 87 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 0 | 0 | 0 | 0 | 0 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 0 | 0 | 0 | 0 | 0 |  | 41625 | 55946 | 29238 | 23433 | 51302
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 24 | 43 | 58 | 2 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 9 | 52 | 57 | 2 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 15 | 12 | 1 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1 | 3 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 186 | 36 | 113 | 127 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 33 | 25 | 29 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 32 | 9 | 10 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 30 | 11 | 6 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 3 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 16 | 99 | 48 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 0 | 0 | 0 | 0 | 0 | 0 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 0 | 0 | 0 | 0 | 0 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 0 | 2 | 0 | -2 | 0 | 0 | 6 | 240 | 61 | 32 | 0 | 339 | 0 | 4 | 0 | -2 | -2 | 0 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 0 | 6 | 0 | -6 | 0 | 0 | 43 | 298 | 64 | 115 | 0 | 520 | 0 | 14 | 0 | -8 | -6 | 0 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 18 | 0 | -18 | 0 | 0 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 30 | 0 | -30 | 0 | 0 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 0 | 26 | 0 | -26 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 0 | 48 | 0 | -40 | -8 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 166 | 1143 | 284 | 160 | 1976 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 0 | 0 | 0 | 0 | 0 | 0 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 102 | 702 | 176 | 98 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 451 | 110 | 63 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 0 | 0 | 0 | 0 | 0 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 0 | 0 | 0 | 0 | 0 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 102 | 142 | 63 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 397 | 590 | 142 | 222 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 91 | 115 | 45 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 584 | 783 | 399 | 330 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 0 | 0 | 0 | 0 | 0 | 0 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 0 | 0 | 0 | 0 | 0 | 0 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 0 | 0 | 0 | 0 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 28 | 28.486 | 114.438 | 1.776 | 19
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 18 | 16 | 19 | 41 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 4 | 9 | 3 | 15 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 3 | 5 | 4 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 120 | 27 | 28 | 28 | 60 |  | 0 | 0 | 0 | 0 | 0 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 37 | 6 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 2 | 52 | 8 | 8 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 11 | 4 | 6 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 4 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 89 | 18 | 102 | 22 | 17 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 0 | 0 | 0 | 0 | 0 | 0 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 0 | 0 | 0 | 0 | 0 | 0 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 0 | 0 | 0 | 0 | 0 | 0 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 0 | 0 | 0 | 0 | 0 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 0 | 14 | 0 | -14 | 0 | 0 | 37 | 848 | 156 | 77 | 0 | 1118 | 0 | 28 | 0 | -28 | 0 | 0 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 0 | 20 | 0 | -20 | 0 | 0 | 136 | 695 | 144 | 116 | 0 | 1091 | 0 | 40 | 0 | -40 | 0 | 0 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 0 | 14 | 0 | -14 | 0 | 0 | 9 | 321 | 77 | 55 | 0 | 462 | 0 | 28 | 0 | -28 | 0 | 0 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 8 | 0 | -8 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 16 | 0 | -16 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 0 | 56 | 0 | -56 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 0 | 112 | 0 | -112 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 302 | 611 | 362 | 504 | 2561 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 62 | 112 | 182 | 356 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 150 | 229 | 27 | 218 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 66 | 20 | 67 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 0 | 0 | 0 | 0 | 0 | 0 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 0 | 0 | 0 | 0 | 0 | 0 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 0 | 0 | 0 | 0 | 0 | 0 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 0 | 0 | 0 | 0 | 0 | 0 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 0 | 0 | 0 | 0 | 0 | 0 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 0 | 0 | 0 | 0 | 0 | 0 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 0 | 0 | 0 | 0 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 0 | 82 | 0 | -82 | 0 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 0 | 160 | 0 | -152 | -8 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW5 - General Reinfor - WMID
HI5: Secondary deliverables RIIO-ED1 - General reinforcement
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on General Reinforcement associated with HI Categories | LV
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on General Reinforcement associated with HI Categories | HV
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | EHV | 0.30828 | 3.4653 | 16.9593
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on General Reinforcement associated with HI Categories | 132kV | 0.6312 | 5 | 13.0463
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on General Reinforcement associated with HI Categories | Total | 0.93948 | 8.4653 | 30.0056
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | [5 empty] | 0 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | [5 empty] | 0 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 0 | 0 | 0 | 0 | 0 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | [5 empty] | 0 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | [5 empty] | 0 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | [5 empty] | 0 | 141 | 80 | 677 | 81 | 137 | 1116 | [5 empty] | 0 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 0 | 0 | 0 | 0 | 0 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 0 | 0 | 0 | 0 | 0 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | [5 empty] | 0 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | [5 empty] | 0 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 0 | 0 | 0 | 0 | 0 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 0 | 0 | 0 | 0 | 0 |  | 5137 | 1824 | 9892 | 2658 | 2221
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | [5 empty] | 0 | 186 | 65 | 271 | 78 | 63 | 663 | [5 empty] | 0 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | [5 empty] | 0 | 1107 | 210 | 873 | 273 | 2 | 2465 | [5 empty] | 0 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | [5 empty] | 0 | 217 | 55 | 133 | 15 | 0 | 420 | [5 empty] | 0 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | [5 empty] | 0 | 19 | 4 | 45 | 10 | 0 | 78 | [5 empty] | 0 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 0 | 0 | 0 | 0 | 0 |  | 1529 | 334 | 1322 | 376 | 65 |  | 0 | 0 | 0 | 0 | 0 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | [5 empty] | 0 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | [5 empty] | 0 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | [5 empty] | 0 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | [5 empty] | 0 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | [5 empty] | 0 | 925 | 1132 | 1211 | 409 | 36 | 3713 | [5 empty] | 0 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | [5 empty] | 0 | 72 | 31 | 199 | 124 | 33 | 459 | [5 empty] | 0 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 0 | 0 | 0 | 0 | 0 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 0 | 0 | 0 | 0 | 0 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | [5 empty] | 0 | 952 | 844 | 1542 | 140 | 149 | 3627 | [5 empty] | 0 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | [5 empty] | 0 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | [5 empty] | 0 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | [5 empty] | 0 | 576 | 137 | 1226 | 105 | 116 | 2160 | [5 empty] | 0 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | [5 empty] | 0 | 10 | 0 | 25 | 5 | 12 | 52 | [5 empty] | 0 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 0 | 0 | 0 | 0 | 0 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 0 | 0 | 0 | 0 | 0 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | [5 empty] | 0 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | [5 empty] | 0 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | [5 empty] | 0 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | [5 empty] | 0 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | [5 empty] | 0 | 151 | 137 | 69 | 50 | 87 | 494 | [5 empty] | 0 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 0 | 0 | 0 | 0 | 0 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 0 | 0 | 0 | 0 | 0 |  | 41625 | 55946 | 29238 | 23433 | 51302
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 4 | 0 | -2 | 0 | 0 | 2 | 35 | 24 | 43 | 58 | 2 | 162 | 24 | 0 | -4 | -8 | 0 | 12 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 18 | 0 | -9 | 0 | 0 | 9 | 121 | 9 | 52 | 57 | 2 | 241 | 29 | 0 | -11 | -1 | 0 | 17 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 10 | 0 | -5 | 0 | 0 | 5 | 24 | 2 | 15 | 12 | 1 | 54 | 16 | 0 | -5 | -3 | 0 | 8 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 2 | 0 | -1 | 0 | 0 | 1 | 6 | 1 | 3 | 0 | 0 | 10 | 2 | 0 | -1 | 0 | 0 | 1 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 34 | 0 | -17 | 0 | 0 |  | 186 | 36 | 113 | 127 | 5 |  | 71 | 0 | -21 | -12 | 0 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 33 | 25 | 29 | 114 | 4 | 0 | 0 | -1 | -1 | 2 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 10 | 0 | -1 | 0 | 0 | 9 | 16 | 6 | 32 | 9 | 10 | 73 | 12 | 0 | -2 | 0 | 0 | 10 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 3 | 0 | -2 | -1 | 0 | 0 | 23 | 3 | 30 | 11 | 6 | 73 | 6 | 0 | -3 | -2 | 0 | 1 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 3 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 13 | 0 | -3 | -1 | 0 |  | 61 | 16 | 99 | 48 | 48 |  | 22 | 0 | -5 | -3 | -1 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 0 | 0 | 0 | 0 | 0 | 0 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 0 | 0 | 0 | 0 | 0 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 240 | 61 | 32 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 298 | 64 | 115 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 0 | 0 | 0 | 0 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 166 | 1143 | 284 | 160 | 1976 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 445 | 0 | -348 | 0 | 0 | 97 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 660 | 0 | -503 | 0 | 0 | 157 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 102 | 702 | 176 | 98 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 451 | 110 | 63 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 445 | 0 | -348 | 0 | 0 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 660 | 0 | -503 | 0 | 0 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 102 | 142 | 63 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 397 | 590 | 142 | 222 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 91 | 115 | 45 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 584 | 783 | 399 | 330 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 0 | 0 | 0 | 0 | 0 | 0 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 0 | 0 | 0 | 0 | 0 | 0 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 0 | 0 | 0 | 0 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 28 | 28.486 | 114.438 | 1.776 | 19
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 16 | 0 | -4 | 0 | -8 | 4 | 31 | 18 | 16 | 19 | 41 | 125 | 27 | 0 | -5 | -2 | -8 | 12 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 6 | -1 | -2 | 0 | -1 | 2 | 53 | 4 | 9 | 3 | 15 | 84 | 14 | -1 | -1 | -1 | -1 | 10 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 2 | -1 | -1 | 0 | 0 | 0 | 22 | 5 | 3 | 5 | 4 | 39 | 2 | -1 | -1 | 0 | 0 | 0 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 24 | -2 | -7 | 0 | -9 |  | 120 | 27 | 28 | 28 | 60 |  | 43 | -2 | -7 | -3 | -9 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 37 | 6 | 1 | 87 | 2 | -1 | -1 | 0 | 0 | 0 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 7 | 0 | 0 | 0 | 0 | 7 | 38 | 2 | 52 | 8 | 8 | 108 | 12 | 0 | 0 | 0 | 0 | 12 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 11 | 4 | 6 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 4 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 7 | 0 | 0 | 0 | 0 |  | 89 | 18 | 102 | 22 | 17 |  | 14 | -1 | -1 | 0 | 0 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 0 | 0 | 0 | 0 | 0 | 0 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 0 | 0 | 0 | 0 | 0 | 0 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 0 | 0 | 0 | 0 | 0 | 0 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 0 | 0 | 0 | 0 | 0 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 848 | 156 | 77 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 695 | 144 | 116 | 0 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 321 | 77 | 55 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 302 | 611 | 362 | 504 | 2561 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 62 | 112 | 182 | 356 | 1376 | 2 | 0 | 0 | 0 | 0 | 2 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 150 | 229 | 27 | 218 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 66 | 20 | 67 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 2 | 0 | 0 | 0 | 0 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 0 | 0 | 0 | 0 | 0 | 0 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 0 | 0 | 0 | 0 | 0 | 0 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 0 | 0 | 0 | 0 | 0 | 0 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 0 | 0 | 0 | 0 | 0 | 0 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 0 | 0 | 0 | 0 | 0 | 0 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 0 | 0 | 0 | 0 | 0 | 0 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 0 | 0 | 0 | 0 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 523 | -2 | -375 | -1 | -9 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 812 | -3 | -537 | -18 | -10 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW6 - Faults - WMID
HI6: Secondary deliverables RIIO-ED1 - Faults
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Faults associated with HI Categories | LV | 0.17149 | 0.34298 | 0.68596
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Faults associated with HI Categories | HV | 0.53114 | 1.0623 | 2.1245
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | EHV | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Faults associated with HI Categories | 132kV | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Faults associated with HI Categories | Total | 0.70263 | 1.4053 | 2.8105
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | 0 | 0 | 0 | 0 | 0 | 0 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 0 | 0 | 0 | 0 | 0 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | 7 | -2 | -5 | 0 | 0 | 0 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | 15 | -3 | -10 | -2 | 0 | 0 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | 1 | 0 | -1 | 0 | 0 | 0 | 141 | 80 | 677 | 81 | 137 | 1116 | 1 | 0 | -1 | 0 | 0 | 0 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 8 | -2 | -6 | 0 | 0 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 16 | -3 | -11 | -2 | 0 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | 64 | -14 | -50 | 0 | 0 | 0 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | 128 | -16 | -90 | -22 | 0 | 0 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 64 | -14 | -50 | 0 | 0 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 128 | -16 | -90 | -22 | 0 |  | 5137 | 1824 | 9892 | 2658 | 2221
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 65 | 271 | 78 | 63 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 210 | 873 | 273 | 2 | 2465 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 55 | 133 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 45 | 10 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 0 | 0 | 0 | 0 | 0 |  | 1529 | 334 | 1322 | 376 | 65 |  | 0 | 0 | 0 | 0 | 0 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | 24 | -11 | -13 | 0 | 0 | 0 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | 50 | -22 | -20 | -8 | 0 | 0 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | 23 | -14 | -9 | 0 | 0 | 0 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | 46 | -23 | -18 | -5 | 0 | 0 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | 8 | -4 | -4 | 0 | 0 | 0 | 925 | 1132 | 1211 | 409 | 36 | 3713 | 15 | -6 | -7 | -2 | 0 | 0 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | 1 | 0 | -1 | 0 | 0 | 0 | 72 | 31 | 199 | 124 | 33 | 459 | 1 | 0 | 0 | -1 | 0 | 0 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 56 | -29 | -27 | 0 | 0 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 112 | -51 | -45 | -16 | 0 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | 14 | -5 | -9 | 0 | 0 | 0 | 952 | 844 | 1542 | 140 | 149 | 3627 | 29 | -8 | -19 | -2 | 0 | 3.5527e-15 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | 34 | -10 | -24 | 0 | 0 | 0 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | 69 | -18 | -48 | -3 | 0 | 0 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | 8 | -1 | -7 | 0 | 0 | 0 | 576 | 137 | 1226 | 105 | 116 | 2160 | 14 | -2 | -12 | 0 | 0 | 0 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 25 | 5 | 12 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 56 | -16 | -40 | 0 | 0 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 112 | -28 | -79 | -5 | 0 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | 0 | 0 | 0 | 0 | 0 | 0 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | 0 | 0 | 0 | 0 | 0 | 0 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 137 | 69 | 50 | 87 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 0 | 0 | 0 | 0 | 0 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 0 | 0 | 0 | 0 | 0 |  | 41625 | 55946 | 29238 | 23433 | 51302
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 24 | 43 | 58 | 2 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 9 | 52 | 57 | 2 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 15 | 12 | 1 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1 | 3 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 186 | 36 | 113 | 127 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 33 | 25 | 29 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 32 | 9 | 10 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 30 | 11 | 6 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 3 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 16 | 99 | 48 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 0 | 0 | 0 | 0 | 0 | 0 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 0 | 0 | 0 | 0 | 0 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 240 | 61 | 32 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 298 | 64 | 115 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 0 | 0 | 0 | 0 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 166 | 1143 | 284 | 160 | 1976 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 0 | 0 | 0 | 0 | 0 | 0 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 102 | 702 | 176 | 98 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 451 | 110 | 63 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 0 | 0 | 0 | 0 | 0 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 0 | 0 | 0 | 0 | 0 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 102 | 142 | 63 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 397 | 590 | 142 | 222 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 91 | 115 | 45 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 584 | 783 | 399 | 330 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 0 | 0 | 0 | 0 | 0 | 0 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 0 | 0 | 0 | 0 | 0 | 0 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 0 | 0 | 0 | 0 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 28 | 28.486 | 114.438 | 1.776 | 19
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 18 | 16 | 19 | 41 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 4 | 9 | 3 | 15 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 3 | 5 | 4 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 120 | 27 | 28 | 28 | 60 |  | 0 | 0 | 0 | 0 | 0 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 37 | 6 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 2 | 52 | 8 | 8 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 11 | 4 | 6 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 4 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 89 | 18 | 102 | 22 | 17 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 0 | 0 | 0 | 0 | 0 | 0 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 0 | 0 | 0 | 0 | 0 | 0 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 0 | 0 | 0 | 0 | 0 | 0 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 0 | 0 | 0 | 0 | 0 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 848 | 156 | 77 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 695 | 144 | 116 | 0 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 321 | 77 | 55 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 302 | 611 | 362 | 504 | 2561 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 62 | 112 | 182 | 356 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 150 | 229 | 27 | 218 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 66 | 20 | 67 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 0 | 0 | 0 | 0 | 0 | 0 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 0 | 0 | 0 | 0 | 0 | 0 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 0 | 0 | 0 | 0 | 0 | 0 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 0 | 0 | 0 | 0 | 0 | 0 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 0 | 0 | 0 | 0 | 0 | 0 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 0 | 0 | 0 | 0 | 0 | 0 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 0 | 0 | 0 | 0 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
[5 empty] | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 184 | -61 | -123 | 0 | 0 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 368 | -98 | -225 | -45 | 0 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW7 - HVP - WMID
HI7: Secondary deliverables RIIO-ED1 - HVP
WMID
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [6 empty] | Expenditure on Health Index asset categories
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | End of DPCR5 (31 March 2015) with investment | Mid-Period Review (31 March 2019) planned investment | End of RIIO-ED1 (31 March 2023) planned investment
| LV Network | [43 empty] | £m | £m | £m
| LV Switchgear and Other |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes | Expenditure on Refurbishment associated with HI Categories | LV |  | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No | Expenditure on Refurbishment associated with HI Categories | HV |  | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | EHV |  | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | Expenditure on Refurbishment associated with HI Categories | 132kV |  | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Expenditure on Refurbishment associated with HI Categories | Total | 0 | 0 | 0
| LV UGB |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 26120 | 52654 | 40903 | 11828 | 18991 | 150496 | 20120 | 52654 | 41231 | 12728 | 23791 | 150524 | 0 | 0 | 0 | 0 | 0 | 0 | 12904 | 52654 | 41784 | 13590 | 29564 | 150496 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 52654 | 42640 | 15301 | 39833 | 150496
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 150496 | 156411 |  | 26120 | 52654 | 40903 | 11828 | 18991 |  | 20120 | 52654 | 41231 | 12728 | 23791 |  | 0 | 0 | 0 | 0 | 0 |  | 12904 | 52654 | 41784 | 13590 | 29564 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 52654 | 42640 | 15301 | 39833
| LV Switchgear (at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 4936 | 2329 | 6896 | 161 | 164 | 14486 | 4448 | 2392 | 6932 | 224 | 295 | 14291 | 0 | 0 | 0 | 0 | 0 | 0 | 4366 | 1960 | 7174 | 571 | 415 | 14486 | 0 | 0 | 0 | 0 | 0 | 0 | 3514 | 2285 | 5909 | 1583 | 1195 | 14486
[5 empty] | C3 | 160 | 103 | 737 | 49 | 67 | 1116 | 122 | 106 | 740 | 54 | 87 | 1109 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 80 | 677 | 81 | 137 | 1116 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 94 | 433 | 237 | 253 | 1116
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 15602 | 17290 |  | 5096 | 2432 | 7633 | 210 | 231 |  | 4570 | 2498 | 7672 | 278 | 382 |  | 0 | 0 | 0 | 0 | 0 |  | 4507 | 2040 | 7851 | 652 | 552 |  | 0 | 0 | 0 | 0 | 0 |  | 3613 | 2379 | 6342 | 1820 | 1448
| LV UGB and LV Pillar OD (not at s/s) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 6086 | 4014 | 11632 | 0 | 0 | 21732 | 4764 | 4024 | 11780 | 380 | 681 | 21629 | 0 | 0 | 0 | 0 | 0 | 0 | 5575 | 3089 | 11662 | 1196 | 210 | 21732 | 0 | 0 | 0 | 0 | 0 | 0 | 5137 | 1824 | 9892 | 2658 | 2221 | 21732
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 21732 | 22246 |  | 6086 | 4014 | 11632 | 0 | 0 |  | 4764 | 4024 | 11780 | 380 | 681 |  | 0 | 0 | 0 | 0 | 0 |  | 5575 | 3089 | 11662 | 1196 | 210 |  | 0 | 0 | 0 | 0 | 0 |  | 5137 | 1824 | 9892 | 2658 | 2221
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
HV Network
| HV Switchgear (GM) - Primary |  |  |  | C1 | 224 | 46 | 330 | 63 | 0 | 663 | 177 | 46 | 349 | 64 | 16 | 652 | 0 | 0 | 0 | 0 | 0 | 0 | 186 | 65 | 271 | 78 | 63 | 663 | 0 | 0 | 0 | 0 | 0 | 0 | 147 | 94 | 134 | 146 | 142 | 663
[5 empty] | C2 | 1195 | 177 | 1092 | 1 | 0 | 2465 | 867 | 185 | 1140 | 149 | 63 | 2404 | 0 | 0 | 0 | 0 | 0 | 0 | 1107 | 210 | 873 | 273 | 2 | 2465 | 0 | 0 | 0 | 0 | 0 | 0 | 996 | 276 | 495 | 416 | 282 | 2465
[5 empty] | C3 | 248 | 35 | 137 | 0 | 0 | 420 | 170 | 35 | 175 | 11 | 11 | 402 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 55 | 133 | 15 | 0 | 420 | 0 | 0 | 0 | 0 | 0 | 0 | 181 | 88 | 77 | 57 | 17 | 420
[5 empty] | C4 | 19 | 10 | 49 | 0 | 0 | 78 | 0 | 10 | 59 | 8 | 1 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 4 | 45 | 10 | 0 | 78 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 21 | 28 | 10 | 78
|  | Yes | 3626 | 3768 |  | 1686 | 268 | 1608 | 64 | 0 |  | 1214 | 276 | 1723 | 232 | 91 |  | 0 | 0 | 0 | 0 | 0 |  | 1529 | 334 | 1322 | 376 | 65 |  | 0 | 0 | 0 | 0 | 0 |  | 1343 | 458 | 727 | 647 | 451
| HV Switchgear (GM) - Distribution |  |  |  | C1 | 4920 | 2450 | 3514 | 253 | 19 | 11156 | 4512 | 2545 | 3655 | 344 | 272 | 11328 | 0 | 0 | 0 | 0 | 0 | 0 | 3773 | 2995 | 3612 | 646 | 130 | 11156 | 0 | 0 | 0 | 0 | 0 | 0 | 2856 | 3275 | 3131 | 1327 | 567 | 11156
[5 empty] | C2 | 5157 | 2756 | 2467 | 319 | 85 | 10784 | 4680 | 2831 | 2537 | 620 | 480 | 11148 | 0 | 0 | 0 | 0 | 0 | 0 | 3752 | 3489 | 2629 | 690 | 224 | 10784 | 0 | 0 | 0 | 0 | 0 | 0 | 3060 | 3465 | 2484 | 1022 | 753 | 10784
[5 empty] | C3 | 1330 | 997 | 1280 | 79 | 27 | 3713 | 1100 | 1023 | 1306 | 244 | 292 | 3965 | 0 | 0 | 0 | 0 | 0 | 0 | 925 | 1132 | 1211 | 409 | 36 | 3713 | 0 | 0 | 0 | 0 | 0 | 0 | 770 | 988 | 1068 | 537 | 350 | 3713
[5 empty] | C4 | 83 | 32 | 311 | 33 | 0 | 459 | 57 | 44 | 316 | 63 | 7 | 487 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 31 | 199 | 124 | 33 | 459 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 37 | 81 | 178 | 107 | 459
|  | Yes | 26112 | 27131 |  | 11490 | 6235 | 7572 | 684 | 131 |  | 10349 | 6443 | 7814 | 1271 | 1051 |  | 0 | 0 | 0 | 0 | 0 |  | 8522 | 7647 | 7651 | 1869 | 423 |  | 0 | 0 | 0 | 0 | 0 |  | 6742 | 7765 | 6764 | 3064 | 1777
| HV Transformer (GM) |  |  |  | C1 | 1103 | 1118 | 1268 | 79 | 59 | 3627 | 1008 | 1131 | 1279 | 79 | 94 | 3591 | 0 | 0 | 0 | 0 | 0 | 0 | 952 | 844 | 1542 | 140 | 149 | 3627 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 697 | 1605 | 227 | 309 | 3627
[5 empty] | C2 | 3666 | 2112 | 3712 | 183 | 119 | 9792 | 3422 | 2136 | 3744 | 183 | 210 | 9695 | 0 | 0 | 0 | 0 | 0 | 0 | 3334 | 1499 | 4249 | 356 | 354 | 9792 | 0 | 0 | 0 | 0 | 0 | 0 | 2840 | 1491 | 4085 | 599 | 777 | 9792
[5 empty] | C3 | 622 | 257 | 1182 | 64 | 35 | 2160 | 546 | 260 | 1192 | 64 | 78 | 2140 | 0 | 0 | 0 | 0 | 0 | 0 | 576 | 137 | 1226 | 105 | 116 | 2160 | 0 | 0 | 0 | 0 | 0 | 0 | 492 | 184 | 1033 | 205 | 246 | 2160
[5 empty] | C4 | 10 | 0 | 30 | 6 | 6 | 52 | 7 | 0 | 30 | 6 | 9 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 0 | 25 | 5 | 12 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 1 | 11 | 13 | 18 | 52
|  | Yes | 15631 | 16465 |  | 5401 | 3487 | 6192 | 332 | 219 |  | 4983 | 3527 | 6245 | 332 | 391 |  | 0 | 0 | 0 | 0 | 0 |  | 4872 | 2480 | 7042 | 606 | 631 |  | 0 | 0 | 0 | 0 | 0 |  | 4130 | 2373 | 6734 | 1044 | 1350
| HV UG Cable |  |  |  | C1 | 1093.64 | 827.705 | 176.287 | 4.299 | 3.252 | 2105.183 | 1066.273 | 832.287 | 177.219 | 4.312 | 6.1 | 2086.191 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 2622.669 | 2710.922 | 699.611 | 15.324 | 13.441 | 6061.967 | 2539.906 | 2725.93 | 703.34 | 15.369 | 22.798 | 6007.343 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 1780.594 | 2169.131 | 550.763 | 12.563 | 13.797 | 4526.848 | 1711.749 | 2181.139 | 553.7 | 17.187 | 22.344 | 4486.119 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 5496.903 | 5707.758 | 1426.661 | 32.186 | 30.49 |  | 5317.928 | 5739.356 | 1434.259 | 36.868 | 51.242 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 71680 | 49912 | 24357 | 15724 | 18133 | 179806 | 64978 | 49912 | 24692 | 16728 | 23484 | 179794 | 0 | 0 | 0 | 0 | 0 | 0 | 54510 | 49912 | 25216 | 18300 | 31868 | 179806 | 0 | 0 | 0 | 0 | 0 | 0 | 37135 | 49912 | 26084 | 20906 | 45769 | 179806
[5 empty] | C3 | 8469 | 5897 | 2878 | 1858 | 2142 | 21244 | 7678 | 5897 | 2917 | 1977 | 2775 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 6439 | 5897 | 2979 | 2162 | 3767 | 21244 | 0 | 0 | 0 | 0 | 0 | 0 | 4388 | 5897 | 3082 | 2470 | 5407 | 21244
[5 empty] | C4 | 197 | 137 | 67 | 43 | 50 | 494 | 178 | 137 | 68 | 46 | 65 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 151 | 137 | 69 | 50 | 87 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 137 | 72 | 57 | 126 | 494
|  | Yes | 201544 | 202756 |  | 80346 | 55946 | 27302 | 17625 | 20325 |  | 72834 | 55946 | 27677 | 18751 | 26324 |  | 0 | 0 | 0 | 0 | 0 |  | 61100 | 55946 | 28264 | 20512 | 35722 |  | 0 | 0 | 0 | 0 | 0 |  | 41625 | 55946 | 29238 | 23433 | 51302
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
EHV Network
| EHV Switchgear (GM) |  |  |  | C1 | 38 | 29 | 93 | 2 | 0 | 162 | 26 | 30 | 94 | 2 | 5 | 157 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 24 | 43 | 58 | 2 | 162 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 22 | 22 | 25 | 60 | 162
[5 empty] | C2 | 122 | 24 | 92 | 1 | 2 | 241 | 100 | 27 | 96 | 2 | 12 | 237 | 0 | 0 | 0 | 0 | 0 | 0 | 121 | 9 | 52 | 57 | 2 | 241 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 13 | 39 | 16 | 59 | 241
[5 empty] | C3 | 24 | 7 | 22 | 1 | 0 | 54 | 9 | 7 | 30 | 2 | 1 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 15 | 12 | 1 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 7 | 5 | 10 | 13 | 54
[5 empty] | C4 | 6 | 2 | 2 | 0 | 0 | 10 | 2 | 2 | 2 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 1 | 3 | 0 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 0 | 0 | 10
|  | Yes | 467 | 570 |  | 190 | 62 | 209 | 4 | 2 |  | 137 | 66 | 222 | 8 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 186 | 36 | 113 | 127 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 171 | 44 | 69 | 51 | 132
| EHV Transformer |  |  |  | C1 | 25 | 2 | 48 | 31 | 8 | 114 | 18 | 2 | 51 | 31 | 12 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 7 | 33 | 25 | 29 | 114 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 9 | 29 | 9 | 49 | 114
[5 empty] | C2 | 19 | 3 | 36 | 15 | 0 | 73 | 17 | 3 | 37 | 15 | 0 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 6 | 32 | 9 | 10 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 23 | 10 | 18 | 73
[5 empty] | C3 | 24 | 2 | 38 | 8 | 1 | 73 | 16 | 2 | 41 | 8 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 3 | 30 | 11 | 6 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 5 | 17 | 17 | 13 | 73
[5 empty] | C4 | 2 | 1 | 6 | 3 | 0 | 12 | 0 | 1 | 6 | 3 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 4 | 3 | 3 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 2 | 6 | 12
|  | Yes | 272 | 293 |  | 70 | 8 | 128 | 57 | 9 |  | 51 | 8 | 135 | 57 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 16 | 99 | 48 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 55 | 22 | 71 | 38 | 86
| EHV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 0 | 0 | 6
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 6 | 6 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 6 | 0 | 0
| EHV UG Cable (Oil) |  |  |  | C1 | 0.809 | 11.045 | 6.675 | 0.154 | 0 | 18.683 | 0.82 | 11.196 | 6.766 | 25.34 | 0 | 44.122 | 0 | 0 | 0 | 0 | 0 | 0 | 0.212 | 6.021 | 12.296 | 0 | 0.154 | 18.683 | 0 | 0 | 0 | 0 | 0 | 0 | 0.156 | 2.634 | 15.739 | 0 | 0.154 | 18.683
[5 empty] | C2 | 11.161 | 6.543 | 2.592 | 0.6 | 0 | 20.896 | 11.313 | 6.632 | 2.628 | 9.98 | 0 | 30.553 | 0 | 0 | 0 | 0 | 0 | 0 | 9.417 | 8.287 | 2.592 | 0 | 0.595 | 20.891 | 0 | 0 | 0 | 0 | 0 | 0 | 8.97 | 2.577 | 8.749 | 0 | 0.6 | 20.896
[5 empty] | C3 | 1.74 | 6.449 | 22.106 | 0.068 | 0 | 30.363 | 1.764 | 6.537 | 22.407 | 5.22 | 0 | 35.928 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.781 | 28.5 | 0.024 | 0.045 | 30.364 | 0 | 0 | 0 | 0 | 0 | 0 | 0.014 | 1.774 | 28.507 | 0 | 0.068 | 30.363
[5 empty] | C4 | 0 | 3.781 | 0.202 | 0 | 0 | 3.983 | 0 | 3.833 | 0.205 | 0.284 | 0 | 4.322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.797 | 1.187 | 0 | 0.004 | 3.988 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.715 | 1.269 | 0 | 0 | 3.984
|  | Yes | 73.925 | 73.325 |  | 13.71 | 27.818 | 31.575 | 0.822 | 0 |  | 13.897 | 28.198 | 32.006 | 40.824 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9.643 | 18.886 | 44.575 | 0.024 | 0.798 |  | 0 | 0 | 0 | 0 | 0 |  | 9.14 | 9.7 | 54.264 | 0 | 0.822
| EHV UG Cable (Non Pressurised) |  |  |  | C1 | 68.117 | 12.586 | 40.57 | 3.704 | 0 | 124.977 | 21.24 | 12.586 | 40.57 | 19.452 | 0 | 93.848 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 133.513 | 17.728 | 14.75 | 7.629 | 0 | 173.62 | 52.08 | 17.728 | 14.75 | 26.504 | 0 | 111.062 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 63.365 | 18.24 | 0.23 | 3.381 | 0 | 85.216 | 29.874 | 18.24 | 0.23 | 5.418 | 0 | 53.762 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 11.074 | 0.297 | 0 | 0.344 | 0 | 11.715 | 10.742 | 0.297 | 0 | 0.684 | 0 | 11.723 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 276.069 | 48.851 | 55.55 | 15.058 | 0 |  | 113.936 | 48.851 | 55.55 | 52.058 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  |  |  | C1 | 6 | 253 | 58 | 22 | 0 | 339 | 0 | 253 | 58 | 22 | 6 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 240 | 61 | 32 | 0 | 339 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 247 | 39 | 45 | 2 | 339
[5 empty] | C2 | 43 | 304 | 65 | 108 | 0 | 520 | 1 | 292 | 67 | 120 | 40 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 298 | 64 | 115 | 0 | 520 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 297 | 62 | 113 | 6 | 520
[5 empty] | C3 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 226 | 3 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 215 | 14 | 62 | 0 | 291 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 197 | 31 | 63 | 0 | 291
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 1150 | 1150 |  | 49 | 783 | 126 | 192 | 0 |  | 1 | 771 | 128 | 204 | 46 |  | 0 | 0 | 0 | 0 | 0 |  | 49 | 753 | 139 | 209 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 48 | 741 | 132 | 221 | 8
| EHV OHL Support - Poles |  |  |  | C1 | 350 | 166 | 1132 | 272 | 57 | 1977 | 214 | 166 | 1136 | 286 | 129 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 223 | 166 | 1143 | 284 | 160 | 1976 | 0 | 0 | 0 | 0 | 0 | 0 | 98 | 166 | 1155 | 295 | 262 | 1976
[5 empty] | C2 | 2884 | 1372 | 9339 | 2249 | 466 | 16310 | 1761 | 1372 | 9376 | 2361 | 1068 | 15938 | 0 | 0 | 0 | 0 | 0 | 0 | 1842 | 1372 | 9433 | 2344 | 1319 | 16310 | 0 | 0 | 0 | 0 | 0 | 0 | 814 | 1372 | 9526 | 2437 | 2162 | 16311
[5 empty] | C3 | 215 | 102 | 696 | 168 | 35 | 1216 | 131 | 102 | 699 | 176 | 80 | 1188 | 0 | 0 | 0 | 0 | 0 | 0 | 138 | 102 | 702 | 176 | 98 | 1216 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 102 | 709 | 183 | 161 | 1216
[5 empty] | C4 | 138 | 66 | 446 | 107 | 22 | 779 | 84 | 66 | 448 | 113 | 50 | 761 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 451 | 110 | 63 | 779 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 66 | 456 | 115 | 103 | 779
|  | Yes | 20282 | 20417 |  | 3587 | 1706 | 11613 | 2796 | 580 |  | 2190 | 1706 | 11659 | 2936 | 1327 |  | 0 | 0 | 0 | 0 | 0 |  | 2292 | 1706 | 11729 | 2914 | 1640 |  | 0 | 0 | 0 | 0 | 0 |  | 1012 | 1706 | 11846 | 3030 | 2688
| EHV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  |  |  | C1 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 239 | 192 | 58 | 5 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 102 | 142 | 63 | 494 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 238 | 45 | 205 | 494
[5 empty] | C2 | 485 | 711 | 418 | 104 | 118 | 1836 | 485 | 711 | 418 | 104 | 118 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 397 | 590 | 142 | 222 | 1836 | 0 | 0 | 0 | 0 | 0 | 0 | 485 | 17 | 700 | 113 | 521 | 1836
[5 empty] | C3 | 19 | 30 | 176 | 23 | 22 | 270 | 19 | 30 | 176 | 23 | 22 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 91 | 115 | 45 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 0 | 30 | 0 | 221 | 270
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 2600 | 2600 |  | 504 | 980 | 786 | 185 | 145 |  | 504 | 980 | 786 | 185 | 145 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 584 | 783 | 399 | 330 |  | 0 | 0 | 0 | 0 | 0 |  | 504 | 23 | 968 | 158 | 947
| EHV OHL Conductor (Tower Lines) |  |  |  | C1 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 28.029 | 0 | 0 | 28.029 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363 | 0 | 0 | 0 | 0 | 0 | 0 | 1.334 | 0 | 28.029 | 0 | 0 | 29.363
[5 empty] | C2 | 36.595 | 0 | 105.102 | 0 | 0 | 141.697 | 28.486 | 0 | 105.661 | 3.108 | 3.108 | 140.363 | 0 | 0 | 0 | 0 | 0 | 0 | 12.478 | 24.117 | 84.327 | 20.775 | 0 | 141.697 | 0 | 0 | 0 | 0 | 0 | 0 | 8.109 | 28.486 | 84.326 | 1.776 | 19 | 141.697
[5 empty] | C3 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 2.083 | 0.812 | 16.413 | 19.308 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64 | 0 | 0 | 0 | 0 | 0 | 0 | 18.557 | 0 | 2.083 | 0 | 0 | 20.64
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 191.7 | 191.7 |  | 56.486 | 0 | 135.214 | 0 | 0 |  | 28.486 | 0 | 135.773 | 3.92 | 19.521 |  | 0 | 0 | 0 | 0 | 0 |  | 32.369 | 24.117 | 114.439 | 20.775 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 28 | 28.486 | 114.438 | 1.776 | 19
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
132kV Network
| 132kV CBs |  |  |  | C1 | 38 | 11 | 35 | 40 | 1 | 125 | 22 | 11 | 44 | 40 | 8 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 18 | 16 | 19 | 41 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 20 | 8 | 8 | 60 | 125
[5 empty] | C2 | 56 | 1 | 12 | 15 | 0 | 84 | 45 | 4 | 15 | 15 | 2 | 81 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 4 | 9 | 3 | 15 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 6 | 6 | 3 | 18 | 84
[5 empty] | C3 | 23 | 4 | 8 | 4 | 0 | 39 | 11 | 4 | 11 | 12 | 1 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 5 | 3 | 5 | 4 | 39 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 6 | 1 | 2 | 9 | 39
[5 empty] | C4 | 14 | 0 | 1 | 0 | 0 | 15 | 9 | 0 | 1 | 5 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 0 | 0 | 0 | 1 | 15
|  | Yes | 263 | 285 |  | 131 | 16 | 56 | 59 | 1 |  | 87 | 19 | 71 | 72 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 120 | 27 | 28 | 28 | 60 |  | 0 | 0 | 0 | 0 | 0 |  | 115 | 32 | 15 | 13 | 88
| 132kV Transformer |  |  |  | C1 | 39 | 7 | 38 | 2 | 1 | 87 | 39 | 7 | 38 | 2 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 10 | 37 | 6 | 1 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 16 | 30 | 8 | 6 | 87
[5 empty] | C2 | 40 | 2 | 57 | 3 | 6 | 108 | 36 | 2 | 57 | 3 | 7 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 2 | 52 | 8 | 8 | 108 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 5 | 43 | 12 | 13 | 108
[5 empty] | C3 | 18 | 3 | 14 | 7 | 0 | 42 | 17 | 3 | 14 | 7 | 1 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 11 | 4 | 6 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 8 | 9 | 2 | 10 | 42
[5 empty] | C4 | 2 | 1 | 4 | 4 | 0 | 11 | 1 | 1 | 4 | 4 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 2 | 4 | 2 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 3 | 0 | 6 | 11
|  | Yes | 248 | 260 |  | 99 | 13 | 113 | 16 | 7 |  | 93 | 13 | 113 | 16 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 89 | 18 | 102 | 22 | 17 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 29 | 85 | 22 | 35
| 132kV UG Cable (Gas) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0.092 | 1.479 | 13.096 | 0 | 6.268 | 20.935 | 0.092 | 1.479 | 13.096 | 0 | 11.268 | 25.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.575 | 0 | 6.268 | 20.935 | 0 | 0 | 0 | 0 | 0 | 0 | 0.092 | 0 | 14.574 | 0.001 | 6.268 | 20.935
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Yes | 20.935 | 12.295 |  | 0.092 | 1.479 | 13.096 | 0 | 6.268 |  | 0.092 | 1.479 | 13.096 | 0 | 11.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.575 | 0 | 6.268 |  | 0 | 0 | 0 | 0 | 0 |  | 0.092 | 0 | 14.574 | 0.001 | 6.268
| 132kV UG Cable (Oil) |  |  |  | C1 | 0.666 | 22.879 | 10.446 | 0 | 0 | 33.991 | 0.667 | 22.91 | 10.46 | 0 | 0 | 34.037 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 14.253 | 19.072 | 0 | 0 | 33.991 | 0 | 0 | 0 | 0 | 0 | 0 | 0.666 | 6.613 | 26.713 | 0 | 0 | 33.992
[5 empty] | C2 | 16.646 | 67.615 | 66.022 | 23.44 | 0 | 173.723 | 16.669 | 67.708 | 66.112 | 29.44 | 0 | 179.929 | 0 | 0 | 0 | 0 | 0 | 0 | 16.26 | 48.6 | 85.423 | 0 | 23.44 | 173.723 | 0 | 0 | 0 | 0 | 0 | 0 | 12.36 | 49.921 | 82.297 | 5.705 | 23.44 | 173.723
[5 empty] | C3 | 4.591 | 13.54 | 7.139 | 0 | 0 | 25.27 | 4.597 | 13.559 | 7.149 | 0 | 0 | 25.305 | 0 | 0 | 0 | 0 | 0 | 0 | 4.591 | 7.627 | 13.052 | 0 | 0 | 25.27 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.103 | 14.167 | 0 | 0 | 25.27
[5 empty] | C4 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 9.544 | 0 | 0 | 9.544 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.531 | 0 | 0 | 9.531
|  | Yes | 242.515 | 219.075 |  | 21.903 | 104.034 | 93.138 | 23.44 | 0 |  | 21.933 | 104.177 | 93.265 | 29.44 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 21.517 | 70.48 | 127.078 | 0 | 23.44 |  | 0 | 0 | 0 | 0 | 0 |  | 13.026 | 67.637 | 132.708 | 5.705 | 23.44
| 132kV UG Cable (Non Pressurised) |  |  |  | C1 | 27.889 | 0 | 0 | 0 | 0 | 27.889 | 20.329 | 0 | 0 | 0 | 0 | 20.329 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 54.774 | 0 | 0 | 0 | 0 | 54.774 | 35.764 | 0 | 0 | 0 | 0 | 35.764 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 6.288 | 0 | 0 | 0 | 0 | 6.288 | 4.398 | 0 | 0 | 0 | 0 | 4.398 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | 4.459 | 0 | 0 | 0 | 0 | 4.459 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 93.41 | 0 | 0 | 0 | 0 |  | 64.95 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  |  |  | C1 | 37 | 860 | 144 | 77 | 0 | 1118 | 36 | 860 | 144 | 77 | 1 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 848 | 156 | 77 | 0 | 1118 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 822 | 182 | 77 | 0 | 1118
[5 empty] | C2 | 136 | 702 | 137 | 116 | 0 | 1091 | 110 | 694 | 137 | 126 | 0 | 1067 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 695 | 144 | 116 | 0 | 1091 | 0 | 0 | 0 | 0 | 0 | 0 | 136 | 678 | 161 | 116 | 0 | 1091
[5 empty] | C3 | 9 | 323 | 75 | 55 | 0 | 462 | 9 | 303 | 75 | 75 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 321 | 77 | 55 | 0 | 462 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 310 | 88 | 55 | 0 | 462
[5 empty] | C4 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 30 | 0 | 61
|  | Yes | 2732 | 2731.1 |  | 182 | 1916 | 356 | 278 | 0 |  | 155 | 1888 | 356 | 308 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1895 | 377 | 278 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 182 | 1841 | 431 | 278 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  |  |  | C1 | 786 | 660 | 577 | 406 | 132 | 2561 | 494 | 662 | 578 | 406 | 425 | 2565 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 302 | 611 | 362 | 504 | 2561 | 0 | 0 | 0 | 0 | 0 | 0 | 782 | 69 | 732 | 112 | 866 | 2561
[5 empty] | C2 | 664 | 124 | 224 | 192 | 172 | 1376 | 514 | 124 | 224 | 192 | 324 | 1378 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 62 | 112 | 182 | 356 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 664 | 20 | 122 | 32 | 538 | 1376
[5 empty] | C3 | 308 | 312 | 104 | 204 | 4 | 932 | 190 | 313 | 104 | 204 | 123 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 150 | 229 | 27 | 218 | 932 | 0 | 0 | 0 | 0 | 0 | 0 | 308 | 88 | 283 | 8 | 245 | 932
[5 empty] | C4 | 64 | 26 | 62 | 37 | 30 | 219 | 0 | 26 | 62 | 37 | 94 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 66 | 20 | 67 | 219 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 2 | 26 | 40 | 87 | 219
|  | Yes | 5088 | 5087 |  | 1822 | 1122 | 967 | 839 | 338 |  | 1198 | 1125 | 968 | 839 | 966 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 516 | 1018 | 591 | 1145 |  | 0 | 0 | 0 | 0 | 0 |  | 1818 | 179 | 1163 | 192 | 1736
| 132kV OHL Conductor (Tower Lines) |  |  |  | C1 | 200.262 | 0 | 480.552 | 0 | 0 | 680.814 | 160.995 | 0 | 480.552 | 0 | 34.601 | 676.148 | 0 | 0 | 0 | 0 | 0 | 0 | 167.534 | 32.728 | 368.248 | 112.304 | 0 | 680.814 | 0 | 0 | 0 | 0 | 0 | 0 | 39.267 | 160.995 | 368.248 | 0 | 112.304 | 680.814
[5 empty] | C2 | 96.332 | 26.057 | 251.937 | 0 | 0 | 374.326 | 51.35 | 26.057 | 251.937 | 0 | 40.314 | 369.658 | 0 | 0 | 0 | 0 | 0 | 0 | 96.332 | 26.057 | 189.464 | 62.473 | 0 | 374.326 | 0 | 0 | 0 | 0 | 0 | 0 | 44.982 | 57.843 | 209.028 | 0 | 62.473 | 374.326
[5 empty] | C3 | 136.196 | 12.659 | 106.236 | 0 | 0 | 255.091 | 57.475 | 12.659 | 106.236 | 0 | 74.055 | 250.425 | 0 | 0 | 0 | 0 | 0 | 0 | 124.016 | 24.839 | 79.727 | 26.509 | 0 | 255.091 | 0 | 0 | 0 | 0 | 0 | 0 | 92.75 | 43.445 | 92.387 | 0 | 26.509 | 255.091
[5 empty] | C4 | 8.52 | 7.225 | 48.024 | 0 | 0 | 63.769 | 0 | 7.225 | 48.024 | 0 | 8.52 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 7.225 | 33.91 | 14.114 | 0 | 63.769 | 0 | 0 | 0 | 0 | 0 | 0 | 8.52 | 0 | 41.135 | 0 | 14.114 | 63.769
|  | Yes | 1374 | 1374 |  | 441.31 | 45.941 | 886.749 | 0 | 0 |  | 269.82 | 45.941 | 886.749 | 0 | 157.49 |  | 0 | 0 | 0 | 0 | 0 |  | 396.402 | 90.849 | 671.349 | 215.4 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 185.519 | 262.283 | 710.798 | 0 | 215.4
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
Other
| Submarine Cables |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | No |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  |  |  | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[5 empty] | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [5 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0
[6 empty] | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 469754.075 | 481336.495 |  | 149258.883 | 137577.881 | 119843.983 | 35240.506 | 41015.758 |  | 129081.042 | 137912.002 | 121236.698 | 38760.11 | 55495.521 |  | 0 | 0 | 0 | 0 | 0 |  | 104770.023 | 129945.332 | 120942.016 | 43653.199 | 70442.506 |  | 0 | 0 | 0 | 0 | 0 |  | 66875.777 | 128384.106 | 118149.782 | 51977.482 | 104366.93
Health Index Definitions
|  |  | HI1 | New or as new
|  |  | HI2 | Good or seviceable condition
|  |  | HI3 | Deterioration requires assessment and monitoring
|  |  | HI4 | Material deterioration, intervention requires consideration
|  |  | HI5 | End of serviceable life, intervention required
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK6: Forecast without any investment in RIIO-ED1 period

## NAW8 - Average Crit - WMID
HI8: Secondary deliverables RIIO-ED1
WMID
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 625 | 1405 | 278 | 2688 | 4996
| LV Switchgear (at s/s) | 3455 | 870 | 488 | 3868 | 8681
| LV UGB and LV Pillar OD (not at s/s) | 3992 | 600 | 488 | 2445 | 7525
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 80547 | 1247 | 1983 | 12471 | 96248
| HV Switchgear (GM) - Distribution | 18409 | 1673 | 2453 | 4840 | 27375
| HV Transformer (GM) | 9185 | 1243 | 3654 | 4720 | 18802
| HV UG Cable | 40033 | 142 | 1102 | 10500 | 51777
| HV OHL Support - Poles | 3076 | 1670 | 478 | 2920 | 8144
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 87991 | 840 | 3277 | 11519 | 103627
| EHV Transformer | 279614 | 1083 | 23258 | 123580 | 427535
| EHV UG Cable (Gas) | 2355 | 10 | 238 | 8112 | 10715
| EHV UG Cable (Oil) | 24510 | 710 | 7277 | 7802 | 40299
| EHV UG Cable (Non Pressurised) | 54088 | 142 | 1602 | 15000 | 70832
| EHV OHL Support - Towers | 167196 | 25436 | 3086 | 84944 | 280662
| EHV OHL Support - Poles | 9269 | 1445 | 478 | 4100 | 15292
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 107483 | 12718 | 880 | 4000 | 125081
| EHV OHL Conductor (Tower Lines) | 106503 | 12718 | 880 | 4000 | 124101
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 272603 | 1128 | 7544 | 28367 | 309642
| 132kV Transformer | 1318287 | 1259 | 54819 | 279306 | 1653671
| 132kV UG Cable (Gas) | 2355 | 10 | 238 | 8112 | 10715
| 132kV UG Cable (Oil) | 37476 | 710 | 8005 | 14709 | 60900
| 132kV UG Cable (Non Pressurised) | 252967 | 710 | 2501 | 225000 | 481178
| 132kV OHL Support - Tower | 832373 | 25436 | 3097 | 137123 | 998029
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 454156 | 12718 | 880 | 4000 | 471754
| 132kV OHL Conductor (Tower Lines) | 458331 | 12718 | 880 | 4000 | 475929
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]

## HI Probs. of Failure - EMID
CM105: HI Ratings Probabilities of Failure
EMID
Price base (2012/13)
| ASSET CATEGORIES | HI Rating
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
EHV UG Cable (Gas)
| EHV UG Cable (Oil) | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.89173 | 0.89173 | 1.3378 | 1.3378 | 3.5244
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402
| EHV OHL Conductor (Tower Lines) | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 0.00018655 | 0.00018655 | 0.00027988 | 0.00027988 | 0.00073732
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.89173 | 0.89173 | 1.3378 | 1.3378 | 3.5244
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005
| 132kV OHL Conductor (Tower Lines) | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 0.00018655 | 0.00018655 | 0.00027988 | 0.00027988 | 0.00073732
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required

## HI Probs. of Failure - SWALES
CM105: HI Ratings Probabilities of Failure
SWALES
Price base (2012/13)
| ASSET CATEGORIES | HI Rating
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV UG Cable (Gas) | 0.13141 | 0.13141 | 0.13141 | 0.13141 | 0.13141 | 8.7749 | 8.7749 | 13.1646 | 13.1646 | 34.6807
| EHV UG Cable (Oil) | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.24174 | 0.24174 | 0.36267 | 0.36267 | 0.95542
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402
| EHV OHL Conductor (Tower Lines) | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 0.00022516 | 0.00022516 | 0.0003378 | 0.0003378 | 0.0008899
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.24174 | 0.24174 | 0.36267 | 0.36267 | 0.95542
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005
| 132kV OHL Conductor (Tower Lines) | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 0.00022516 | 0.00022516 | 0.0003378 | 0.0003378 | 0.0008899
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required

## HI Probs. of Failure - SWEST
CM105: HI Ratings Probabilities of Failure
SWEST
Price base (2012/13)
| ASSET CATEGORIES | HI Rating
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV UG Cable (Gas) | 0.093876 | 0.093876 | 0.093876 | 0.093876 | 0.093876 | 6.2683 | 6.2683 | 9.4042 | 9.4042 | 24.7742
| EHV UG Cable (Oil) | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.39821 | 0.39821 | 0.59743 | 0.59743 | 1.5738
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402
| EHV OHL Conductor (Tower Lines) | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 0.00022574 | 0.00022574 | 0.00033866 | 0.00033866 | 0.00089217
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.39821 | 0.39821 | 0.59743 | 0.59743 | 1.5738
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005
| 132kV OHL Conductor (Tower Lines) | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 0.00022574 | 0.00022574 | 0.00033866 | 0.00033866 | 0.00089217
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required

## HI Probs. of Failure - WMID
CM105: HI Ratings Probabilities of Failure
WMID
Price base (2012/13)
| ASSET CATEGORIES | HI Rating
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
LV Network
LV Switchgear and Other
LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984
HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| EHV UG Cable (Gas) | 0.069464 | 0.069464 | 0.069464 | 0.069464 | 0.069464 | 4.6383 | 4.6383 | 6.9586 | 6.9586 | 18.3317
| EHV UG Cable (Oil) | 0.013778 | 0.013778 | 0.013778 | 0.013778 | 0.013778 | 0.91999 | 0.91999 | 1.3802 | 1.3802 | 3.6361
EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
EHV OHL Fittings and Conductors (Tower Lines)
| EHV OHL Fittings | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402
| EHV OHL Conductor (Tower Lines) | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 0.00018942 | 0.00018942 | 0.00028419 | 0.00028419 | 0.00074866
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003
| 132kV UG Cable (Gas) | 0.069464 | 0.069464 | 0.069464 | 0.069464 | 0.069464 | 4.6383 | 4.6383 | 6.9586 | 6.9586 | 18.3317
| 132kV UG Cable (Oil) | 0.013778 | 0.013778 | 0.013778 | 0.013778 | 0.013778 | 0.91999 | 0.91999 | 1.3802 | 1.3802 | 3.6361
132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003
132kV OHL Fittings and Conductors (Tower Lines)
| 132kV OHL Fittings | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005
| 132kV OHL Conductor (Tower Lines) | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 6.8558e-05 | 0.00018942 | 0.00018942 | 0.00028419 | 0.00028419 | 0.00074866
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Other
Submarine Cables
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
[Please insert new asset category as required]
Health Index Definitions
|  | HI1 | New or as new
|  | HI2 | Good or seviceable condition
|  | HI3 | Deterioration requires assessment and monitoring
|  | HI4 | Material deterioration, intervention requires consideration
|  | HI5 | End of serviceable life, intervention required