## EPN - Total
Total Secondary Deliverables RIIO-ED1 - Asset Replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 64 | 64 | C1 | 8 | 25 | 31 | 0 | 0 | 64 | 8 | 25 | 31 | 0 | 0 | 64 | 1 | 0 | 0 | -1 | 0 | 0 | 4 | 25 | 33 | 2 | 0 | 64 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 24 | 33 | 6 | 1 | 64 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | C1 | 7.8518 | 17.9786 | 55.6367 | 90.6791 | 145.6343 | C1 | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 39.2589 | 449.4654 | 1836.0105 | 90.6791 | 0 | 2415.4139 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064 |  | 7.8518 | 431.4868 | 1836.0105 | 453.3957 | 145.6343 | 2874.3791
|  |  | 29908 | 29908 | C2 | 3760 | 11129 | 14935 | 84 | 0 | 29908 | 3531 | 10762 | 14935 | 265 | 48 | 29541 | 471 | 0 | -122 | -349 | 0 | 0 | 2069 | 11728 | 15262 | 789 | 60 | 29908 | 954 | 0 | -122 | -791 | -41 | 0 | 229 | 11673 | 15906 | 1851 | 249 | 29908 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10371 | 10371 | 10371 | 10371 | 10371 | C2 | 11.2168 | 25.6837 | 79.481 | 129.5416 | 208.049 | C2 | 39606.6007 | 276408.3808 | 1187048.316 | 34328.5337 | 9986.3537 | 1547378.1849 |  | 42175.2531 | 285834.3124 | 1187048.316 | 10881.4975 | 0 | 1525939.3789 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 28490.7295 | 301218.8711 | 1203341.9152 | 56998.3202 | 12482.9421 | 1602532.778 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369 |  | 13269.5012 | 299806.2655 | 1254527.6612 | 137314.135 | 43274.1992 | 1748191.762
|  |  | 63 | 63 | C3 | 8 | 25 | 30 | 0 | 0 | 63 | 7 | 25 | 30 | 1 | 0 | 63 | 14 | 0 | -13 | -1 | 0 | 0 | 5 | 24 | 33 | 1 | 0 | 63 | 18 | 0 | -13 | -5 | 0 | 0 | 1 | 23 | 33 | 5 | 1 | 63 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | C3 | 16.8252 | 38.5256 | 119.2215 | 194.3125 | 312.0736 | C3 | 117.7766 | 963.1401 | 3576.6437 | 194.3125 | 0 | 4851.873 |  | 134.6019 | 963.1401 | 3576.6437 | 0 | 0 | 4674.3858 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 319.6794 | 924.6145 | 2384.4292 | 0 | 0 | 3628.7231 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581 |  | 319.6794 | 886.0889 | 2384.4292 | 0 | 312.0736 | 3902.2711
|  |  | 5 | 5 | C4 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | C4 | 28.0421 | 64.2093 | 198.7024 | 323.8541 | 520.1226 | C4 | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656
|  |  | 30040 | 30040 |  | 3777 | 11181 | 14998 | 84 | 0 |  | 3547 | 10814 | 14998 | 266 | 48 |  | 487 | 0 | -136 | -351 | 0 |  | 2078 | 11779 | 15331 | 792 | 60 |  | 974 | 0 | -136 | -797 | -41 |  | 230 | 11722 | 15975 | 1862 | 251 | [22 empty] | 39815.2336 | 277949.4051 | 1192747.1017 | 34522.8462 | 9986.3537 | 1555020.9402 |  | 42400.7112 | 287375.3367 | 1192747.1017 | 10881.4975 | 0 | 1533404.647 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 28877.7098 | 302721.3697 | 1207959.7597 | 57088.9993 | 12482.9421 | 1609130.7806 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274 |  | 13625.0744 | 301252.2599 | 1259145.5056 | 137767.5307 | 43731.9071 | 1755522.2778
| LV UGB |  | 812 | 812 | C1 | 107 | 91 | 305 | 287 | 22 | 812 | 101 | 91 | 305 | 287 | 28 | 812 | 16 | 0 | 0 | 0 | -16 | 0 | 89 | 66 | 228 | 393 | 37 | 813 | 31 | 0 | 0 | 0 | -31 | 0 | 82 | 39 | 126 | 513 | 52 | 812 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | C1 | 11.222 | 16.833 | 56.11 | 123.4421 | 241.2731 | C1 | 1133.4225 | 1531.8036 | 17113.5572 | 35427.8689 | 6755.6468 | 61962.299 |  | 1200.7545 | 1531.8036 | 17113.5572 | 35427.8689 | 5308.0082 | 60581.9924 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 1178.3105 | 1110.9785 | 12793.0854 | 48512.7264 | 5066.7351 | 68661.8358 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285 |  | 1268.0865 | 656.4873 | 7069.863 | 63325.7726 | 5066.7351 | 77386.9445
|  |  | 25739 | 25739 | C2 | 3391 | 2894 | 9654 | 9102 | 698 | 25739 | 3189 | 2894 | 9654 | 9102 | 900 | 25739 | 2169 | 0 | 0 | -1648 | -521 | 0 | 2825 | 2088 | 7220 | 12437 | 1171 | 25741 | 2844 | 0 | 0 | -1857 | -987 | 0 | 2604 | 1240 | 4005 | 16258 | 1634 | 25741 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11183 | 11183 | 11183 | 11183 | 11183 | C2 | 16.0314 | 24.0472 | 80.1572 | 176.3458 | 344.6759 | C2 | 51124.2472 | 69592.4607 | 773837.3821 | 1605099.3654 | 310208.2731 | 2809861.7285 |  | 54362.5971 | 69592.4607 | 773837.3821 | 1605099.3654 | 240583.7496 | 2743475.5549 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 80060.9879 | 50210.4554 | 578734.8144 | 1902594.7103 | 224039.3084 | 2835640.2764 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995 |  | 87339.2595 | 29818.4697 | 321029.4919 | 2539555.6978 | 223005.2808 | 3200748.1997
|  |  | 5276 | 5276 | C3 | 695 | 593 | 1979 | 1866 | 143 | 5276 | 654 | 593 | 1979 | 1866 | 185 | 5277 | 590 | 0 | 0 | -483 | -107 | 0 | 579 | 428 | 1480 | 2549 | 240 | 5276 | 1180 | 0 | 0 | -978 | -202 | 0 | 534 | 254 | 821 | 3333 | 335 | 5277 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | C3 | 24.0472 | 36.0707 | 120.2358 | 264.5187 | 517.0138 | C3 | 15726.838 | 21389.9426 | 237946.5785 | 493591.8615 | 95647.5509 | 864302.7715 |  | 16712.7713 | 21389.9426 | 237946.5785 | 493591.8615 | 73932.9718 | 843574.1257 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 28111.1218 | 15438.2722 | 177948.9319 | 546495.598 | 68762.8339 | 836756.7578 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958 |  | 41216.8202 | 9161.9653 | 98713.5629 | 622941.4973 | 68762.8339 | 840796.6795
|  |  | 2285 | 2285 | C4 | 301 | 257 | 857 | 808 | 62 | 2285 | 283 | 257 | 857 | 808 | 80 | 2285 | 255 | 0 | 0 | -209 | -46 | 0 | 251 | 185 | 641 | 1104 | 104 | 2285 | 512 | 0 | 0 | -424 | -88 | 0 | 231 | 110 | 355 | 1443 | 145 | 2284 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | C4 | 40.0786 | 60.1179 | 200.3929 | 440.8645 | 861.6896 | C4 | 11342.2405 | 15450.2958 | 171736.7507 | 356218.4924 | 68935.1718 | 623682.9512 |  | 12063.6551 | 15450.2958 | 171736.7507 | 356218.4924 | 53424.7581 | 608893.9521 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 20279.7657 | 11121.8082 | 128451.8754 | 394573.7014 | 49977.9996 | 604405.1502 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454 |  | 29778.3911 | 6612.9671 | 71139.4942 | 449240.8958 | 49116.3099 | 605888.058
|  |  | 34112 | 34112 |  | 4494 | 3835 | 12795 | 12063 | 925 |  | 4227 | 3835 | 12795 | 12063 | 1193 |  | 3030 | 0 | 0 | -2340 | -690 |  | 3744 | 2767 | 9569 | 16483 | 1552 |  | 4567 | 0 | 0 | -3259 | -1308 |  | 3451 | 1643 | 5307 | 21547 | 2166 | [22 empty] | 79326.7482 | 107964.5026 | 1200634.2684 | 2490337.5883 | 481546.6426 | 4359809.7501 |  | 84339.778 | 107964.5026 | 1200634.2684 | 2490337.5883 | 373249.4877 | 4256525.6251 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 129630.1859 | 77881.5143 | 897928.707 | 2892176.7362 | 347846.8769 | 4345464.0203 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692 |  | 159602.5573 | 46249.8893 | 497952.412 | 3675063.8635 | 345951.1597 | 4724819.8817
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | C1 | 14.4557 | 14.4557 | 29.0421 | 79.9779 | 158.5738 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 246106 | 246106 | C2 | 44138 | 179341 | 6435 | 8501 | 7691 | 246106 | 40338 | 179599 | 6435 | 8501 | 11491 | 246364 | 6727 | 0 | 0 | 0 | -6727 | 0 | 26121 | 170027 | 31277 | 5151 | 13530 | 246106 | 13455 | 0 | 0 | 0 | -13455 | 0 | 23261 | 151153 | 47037 | 6192 | 18463 | 246106 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | C2 | 20.651 | 20.651 | 41.4888 | 114.2542 | 226.534 | C2 | 833019.9377 | 3708898.5026 | 266980.178 | 971274.7708 | 2603101.8733 | 8383275.2624 |  | 911493.7283 | 3703570.5452 | 266980.178 | 971274.7708 | 1742272.7793 | 7595592.0017 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 678343.9664 | 3511227.1544 | 1297643.9827 | 588523.2731 | 1541110.6121 | 7616848.9886 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384 |  | 758222.0247 | 3121460.2273 | 1951506.8585 | 707461.8728 | 1134482.1322 | 7673133.1156
|  |  | 1255 | 1255 | C3 | 115 | 1016 | 14 | 62 | 48 | 1255 | 115 | 1016 | 14 | 62 | 48 | 1255 | 42 | 0 | 0 | 0 | -42 | 0 | 114 | 868 | 159 | 26 | 88 | 1255 | 84 | 0 | 0 | 0 | -84 | 0 | 99 | 771 | 240 | 32 | 113 | 1255 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | C3 | 30.9765 | 30.9765 | 62.2331 | 171.3813 | 339.801 | C3 | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 4832.3334 | 26887.5988 | 9895.0695 | 4455.913 | 15630.8441 | 61701.7588 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146 |  | 5668.6988 | 23882.8786 | 14935.954 | 5484.2006 | 9854.2278 | 59825.9598
|  |  | 2 | 2 | C4 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | C4 | 51.6275 | 51.6275 | 103.7219 | 285.6354 | 566.3349 | C4 | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 51.6275 | 0 | 0 | 0 | 103.255 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 51.6275 | 0 | 0 | 0 | 103.255
|  |  | 247363 | 247363 |  | 44254 | 180357 | 6449 | 8563 | 7740 |  | 40454 | 180615 | 6449 | 8563 | 11540 |  | 6770 | 0 | 0 | 0 | -6770 |  | 26235 | 170896 | 31436 | 5177 | 13619 |  | 13540 | 0 | 0 | 0 | -13540 |  | 23360 | 151925 | 47277 | 6224 | 18577 | [22 empty] | 836633.8623 | 3740370.6228 | 267851.442 | 981900.4094 | 2619978.6542 | 8446734.9907 |  | 915107.6529 | 3735042.6654 | 267851.442 | 981900.4094 | 1759149.5602 | 7659051.73 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 683227.9273 | 3538166.3806 | 1307539.0522 | 592979.1861 | 1556741.4562 | 7678654.0023 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155 |  | 763942.351 | 3145394.7334 | 1966442.8125 | 712946.0734 | 1144336.36 | 7733062.3304
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 |  | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 841735.823 | 3918769.2646 | 3413427.519 | 3542244.9215 | 1917071.2752 | 13633248.8032 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 |  | 937169.9828 | 3492896.8826 | 3723540.7301 | 4525777.4676 | 1534019.4268 | 14213404.4898
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 3046 | 3052 | C1 | 1055 | 1042 | 885 | 52 | 12 | 3046 | 1044 | 1010 | 885 | 84 | 23 | 3046 | 155 | 4 | 0 | -55 | -99 | 5 | 967 | 904 | 830 | 246 | 99 | 3046 | 395 | 46 | 0 | -163 | -272 | 6 | 561 | 1107 | 785 | 300 | 293 | 3046 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33586 | 33586 | 33586 | 33586 | 33586 | C1 | 58.8156 | 58.8156 | 220.1504 | 404.4235 | 556.6962 | C1 | 61403.5232 | 59403.7916 | 194833.0619 | 33971.5713 | 12804.0121 | 362415.9602 |  | 62050.4952 | 61285.892 | 194833.0619 | 21030.0203 | 6680.3541 | 345879.8236 |  | 56874.7193 | 53169.3343 | 182724.7925 | 99488.1731 | 55112.9217 | 447369.9409 |  | 65991.1428 | 53404.5968 | 182724.7925 | 77244.8824 | 0 | 379365.4145 |  | 32995.5714 | 65108.9082 | 172818.0267 | 121327.0404 | 163111.9803 | 555361.527 |  | 56227.7473 | 67814.4275 | 172818.0267 | 55406.0151 | 11690.6197 | 363956.8363
|  |  | 1695 | 1698 | C2 | 261 | 967 | 397 | 50 | 20 | 1695 | 232 | 799 | 397 | 65 | 34 | 1527 | 118 | 2 | 0 | -41 | -78 | 1 | 253 | 702 | 545 | 115 | 80 | 1695 | 245 | 29 | 0 | -118 | -153 | 3 | 153 | 597 | 583 | 192 | 170 | 1695 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47980 | 47980 | 47980 | 47980 | 47980 | C2 | 84.0223 | 84.0223 | 314.5005 | 577.7478 | 795.2803 | C2 | 19493.182 | 67133.8465 | 124856.6999 | 37553.6077 | 27039.5287 | 276076.8648 |  | 21929.8297 | 81249.599 | 124856.6999 | 28887.3906 | 15905.6051 | 272829.1243 |  | 21257.651 | 58983.6799 | 171402.7744 | 66440.9983 | 63622.4204 | 381707.5241 |  | 31172.2867 | 59151.7246 | 171402.7744 | 42753.338 | 1590.5605 | 306070.6843 |  | 12855.4174 | 50161.3347 | 183353.7935 | 110927.5798 | 135197.6434 | 492495.7688 |  | 33440.8898 | 52597.9824 | 183353.7935 | 42753.338 | 13519.7643 | 325665.7681
|  |  | 618 | 620 | C3 | 127 | 359 | 113 | 17 | 2 | 618 | 122 | 359 | 113 | 19 | 5 | 618 | 49 | 1 | 0 | -15 | -34 | 1 | 113 | 256 | 178 | 34 | 37 | 618 | 89 | 10 | 0 | -42 | -55 | 2 | 64 | 179 | 266 | 54 | 55 | 618 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71970 | 71970 | 71970 | 71970 | 71970 | C3 | 126.0335 | 126.0335 | 471.7508 | 866.6217 | 1192.9204 | C3 | 15376.0875 | 45246.028 | 53307.8353 | 16465.8126 | 5964.6019 | 136360.3654 |  | 16006.255 | 45246.028 | 53307.8353 | 14732.5692 | 2385.8408 | 131678.5283 |  | 14241.786 | 32264.5771 | 83971.6344 | 29465.1384 | 44138.0542 | 204081.19 |  | 20417.4277 | 32390.6106 | 83971.6344 | 16465.8126 | 3578.7611 | 156824.2464 |  | 8066.1443 | 22559.9972 | 125485.7009 | 46797.5727 | 65610.621 | 268520.0362 |  | 19283.1261 | 23820.3323 | 125485.7009 | 10399.4606 | 0 | 178988.6199
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119950 | 119950 | 119950 | 119950 | 119950 | C4 | 210.0558 | 210.0558 | 786.2513 | 1444.3695 | 1988.2006 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5359 | 5370 |  | 1443 | 2368 | 1395 | 119 | 34 |  | 1398 | 2168 | 1395 | 168 | 62 |  | 322 | 7 | 0 | -111 | -211 |  | 1333 | 1862 | 1553 | 395 | 216 |  | 729 | 85 | 0 | -323 | -480 |  | 778 | 1883 | 1634 | 546 | 518 | [22 empty] | 96272.7927 | 171783.6662 | 372997.5972 | 87990.9917 | 45808.1427 | 774853.1904 |  | 99986.58 | 187781.5189 | 372997.5972 | 64649.9801 | 24971.8 | 750387.4762 |  | 92374.1563 | 144417.5913 | 438099.2014 | 195394.3098 | 162873.3962 | 1033158.655 |  | 117580.8571 | 144946.932 | 438099.2014 | 136464.0331 | 5169.3217 | 842260.3452 |  | 53917.1331 | 137830.2401 | 481657.5211 | 279052.1929 | 363920.2447 | 1316377.332 |  | 108951.7632 | 144232.7421 | 481657.5211 | 108558.8138 | 25210.3841 | 868611.2243
| HV Switchgear (GM) - Distribution |  | 16951 | 16951 | C1 | 7581 | 8348 | 596 | 426 | 0 | 16951 | 7566 | 8348 | 596 | 426 | 16 | 16952 | 0 | 0 | 0 | 0 | 0 | 0 | 3630 | 12149 | 623 | 533 | 16 | 16951 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 14318 | 1090 | 577 | 96 | 16951 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | C1 | 11.2991 | 11.2991 | 42.4721 | 77.873 | 133.2047 | C1 | 85488.9241 | 94324.8134 | 25313.3509 | 33173.9097 | 2131.2749 | 240432.273 |  | 85658.4105 | 94324.8134 | 25313.3509 | 33173.9097 | 0 | 238470.4845 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348
|  |  | 15770 | 15690 | C2 | 1149 | 9824 | 4343 | 454 | 0 | 15770 | 474 | 9350 | 4343 | 798 | 548 | 15513 | 1700 | 0 | 0 | -242 | -1498 | -40 | 1008 | 6422 | 4444 | 2126 | 1770 | 15770 | 3400 | 0 | 0 | -381 | -3099 | -80 | 917 | 4850 | 4656 | 1768 | 3579 | 15770 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 28897 | 28897 | 28897 | 28897 | 28897 | C2 | 16.1416 | 16.1416 | 60.6744 | 111.2472 | 190.2924 | C2 | 7651.0989 | 150923.5754 | 263508.8273 | 88775.2514 | 104280.2376 | 615138.9907 |  | 18546.6511 | 158574.6743 | 263508.8273 | 50506.2207 | 0 | 491136.3735 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 43711.3414 | 103661.0911 | 269636.9396 | 209589.6913 | 51759.534 | 678358.5974 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113 |  | 69683.1096 | 78286.5605 | 282499.9079 | 154299.8418 | 91340.3541 | 676109.7739
|  |  | 3 | 3 | C3 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | C3 | 24.2123 | 24.2123 | 91.0116 | 166.8708 | 285.4386 | C3 | 0 | 24.2123 | 0 | 333.7415 | 0 | 357.9539 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | C4 | 40.3539 | 40.3539 | 151.6859 | 278.118 | 475.731 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 32724 | 32644 |  | 8732 | 18173 | 4939 | 880 | 0 |  | 8040 | 17699 | 4939 | 1226 | 564 |  | 1700 | 0 | 0 | -242 | -1498 |  | 4640 | 18572 | 5067 | 2659 | 1786 |  | 3400 | 0 | 0 | -381 | -3099 |  | 1789 | 19169 | 5746 | 2345 | 3675 | [22 empty] | 93140.023 | 245272.6012 | 288822.1782 | 122282.9027 | 106411.5125 | 855929.2176 |  | 104253.4863 | 252923.7001 | 288822.1782 | 83680.1305 | 0 | 729679.495 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 84775.4672 | 240957.9625 | 296097.0362 | 251096.015 | 53890.8089 | 926817.2898 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831 |  | 79561.7437 | 240091.1608 | 328794.459 | 199232.5787 | 104128.0037 | 951807.9457
| HV Transformer (GM) |  | 15354 | 15354 | C1 | 2254 | 4991 | 8109 | 0 | 0 | 15354 | 2175 | 4991 | 8109 | 71 | 8 | 15354 | 197 | 0 | -125 | -72 | 0 | 0 | 1306 | 5562 | 8385 | 91 | 10 | 15354 | 403 | 0 | -125 | -265 | -13 | 0 | 79 | 6088 | 8844 | 291 | 52 | 15354 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | C1 | 33.5005 | 40.8282 | 115.1569 | 219.6408 | 370.4805 | C1 | 72863.5281 | 203773.5627 | 933807.1344 | 15594.4939 | 2963.844 | 1229002.5632 |  | 75510.0655 | 203773.5627 | 933807.1344 | 0 | 0 | 1213090.7626 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 50351.2105 | 227086.4668 | 951195.8232 | 4173.1744 | 3704.805 | 1236511.4799 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269 |  | 16147.2278 | 248562.1017 | 1004052.8308 | 5710.6598 | 14448.7395 | 1288921.5597
|  |  | 10916 | 10916 | C2 | 1472 | 4148 | 5296 | 0 | 0 | 10916 | 1285 | 3757 | 5432 | 46 | 5 | 10525 | 152 | 0 | -100 | -52 | 0 | 0 | 1028 | 4205 | 5611 | 65 | 7 | 10916 | 298 | 0 | -100 | -188 | -10 | 0 | 187 | 4563 | 5928 | 201 | 37 | 10916 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 54257 | 54257 | 54257 | 54257 | 54257 | C2 | 47.8578 | 58.326 | 164.5098 | 313.7725 | 529.2579 | C2 | 61497.2963 | 219130.7997 | 893617.3835 | 14433.5356 | 2646.2893 | 1191325.3045 |  | 70446.7083 | 241936.2676 | 871244.047 | 0 | 0 | 1183627.0229 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 56472.2254 | 245260.8499 | 906613.6599 | 4079.0427 | 3704.805 | 1216130.5829 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456 |  | 23211.0418 | 266141.5596 | 958763.2753 | 4079.0427 | 14289.9622 | 1266484.8815
|  |  | 4387 | 4387 | C3 | 644 | 1426 | 2317 | 0 | 0 | 4387 | 622 | 1426 | 2317 | 20 | 2 | 4387 | 63 | 0 | -42 | -21 | 0 | 0 | 373 | 1589 | 2396 | 26 | 3 | 4387 | 123 | 0 | -42 | -77 | -4 | 0 | 22 | 1740 | 2528 | 82 | 15 | 4387 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | C3 | 71.7867 | 87.489 | 246.7647 | 470.6588 | 793.8868 | C3 | 44651.3443 | 124759.3241 | 571753.9058 | 9413.1754 | 1587.7736 | 752165.5233 |  | 46230.6523 | 124759.3241 | 571753.9058 | 0 | 0 | 742743.8823 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 31299.0131 | 139020.0323 | 580884.2013 | 2353.2939 | 2381.6604 | 755938.2008 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676 |  | 10409.0754 | 152230.8723 | 613457.1471 | 2353.2939 | 8732.7547 | 787183.1434
|  |  | 1566 | 1566 | C4 | 230 | 509 | 827 | 0 | 0 | 1566 | 222 | 509 | 827 | 7 | 1 | 1566 | 23 | 0 | -15 | -8 | 0 | 0 | 133 | 567 | 855 | 10 | 1 | 1566 | 46 | 0 | -15 | -30 | -1 | 0 | 8 | 621 | 900 | 32 | 5 | 1566 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | C4 | 119.6445 | 145.815 | 411.2746 | 784.4313 | 1323.1446 | C4 | 26561.0891 | 74219.841 | 340124.0686 | 5491.019 | 1323.1446 | 447719.1623 |  | 27518.2454 | 74219.841 | 340124.0686 | 0 | 0 | 441862.155 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 18664.5491 | 82677.1117 | 345470.638 | 1568.8626 | 1323.1446 | 449704.306 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151 |  | 6460.8055 | 90551.1223 | 363977.9936 | 1568.8626 | 5292.5786 | 467851.3625
|  |  | 32223 | 32223 |  | 4600 | 11074 | 16549 | 0 | 0 |  | 4304 | 10683 | 16685 | 144 | 16 |  | 435 | 0 | -282 | -153 | 0 |  | 2840 | 11923 | 17247 | 192 | 21 |  | 870 | 0 | -282 | -560 | -28 |  | 296 | 13012 | 18200 | 606 | 109 | [22 empty] | 205573.2579 | 621883.5276 | 2739302.4923 | 44932.224 | 8521.0515 | 3620212.5533 |  | 219705.6716 | 644688.9954 | 2716929.1558 | 0 | 0 | 3581323.8228 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 156786.9981 | 694044.4606 | 2784164.3223 | 12174.3735 | 11114.415 | 3658284.5696 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553 |  | 56228.1506 | 757485.6559 | 2940251.2468 | 13711.8589 | 42764.035 | 3810440.9471
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 135 | 135 | C1 | 12 | 103 | 14 | 2 | 4 | 135 | 12 | 103 | 14 | 2 | 4 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 90 | 21 | 4 | 8 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 81 | 34 | 5 | 10 | 135 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | C1 | 17.6591 | 17.6591 | 66.4486 | 139.6696 | 215.3203 | C1 | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859
|  |  | 196526 | 196526 | C2 | 30344 | 147825 | 6695 | 6814 | 4848 | 196526 | 28983 | 147899 | 6695 | 6814 | 6209 | 196600 | 3484 | 0 | 0 | 0 | -3484 | 0 | 19315 | 130607 | 30746 | 5743 | 10115 | 196526 | 7082 | 0 | 0 | 0 | -7082 | 0 | 9135 | 117840 | 49495 | 7489 | 12567 | 196526 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | C2 | 25.2273 | 25.2273 | 94.9265 | 199.5279 | 307.6005 | C2 | 731162.86 | 3731092.5658 | 635533.0554 | 1359583.403 | 1909891.3827 | 8367263.2669 |  | 765497.2165 | 3729225.7455 | 635533.0554 | 1359583.403 | 1491247.1289 | 7981086.5493 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 575157.2317 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 2039698.7854 | 9974217.8754 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617 |  | 409111.1376 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 1687188.6349 | 11261737.8042
|  |  | 17623 | 17623 | C3 | 3370 | 13180 | 604 | 469 | 0 | 17623 | 2845 | 13180 | 604 | 469 | 525 | 17623 | 302 | 0 | 0 | 0 | -302 | 0 | 2134 | 11719 | 2763 | 508 | 499 | 17623 | 490 | 0 | 0 | 0 | -490 | 0 | 1222 | 10577 | 4441 | 664 | 719 | 17623 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | C3 | 37.841 | 37.841 | 142.3898 | 299.2919 | 461.4007 | C3 | 107657.5063 | 498743.7375 | 86003.4277 | 140367.9078 | 242235.3783 | 1075007.9576 |  | 127524.0057 | 498743.7375 | 86003.4277 | 140367.9078 | 0 | 852639.0787 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 92180.5572 | 443458.1077 | 393422.9646 | 152040.2925 | 90895.942 | 1171997.864 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35 |  | 64783.7085 | 400243.7414 | 632353.017 | 198729.8311 | 105660.765 | 1401771.063
|  |  | 59 | 59 | C4 | 14 | 38 | 1 | 6 | 0 | 59 | 6 | 38 | 1 | 6 | 8 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 2 | 9 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29 | 11 | 9 | 0 | 59 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | C4 | 63.0683 | 63.0683 | 237.3163 | 498.8199 | 769.0012 | C4 | 378.4095 | 2396.5936 | 237.3163 | 2992.9191 | 6152.0096 | 12157.2481 |  | 882.9555 | 2396.5936 | 237.3163 | 2992.9191 | 0 | 6509.7846 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199
|  |  | 214343 | 214343 |  | 33740 | 161146 | 7314 | 7291 | 4852 |  | 31846 | 161220 | 7314 | 7291 | 6746 |  | 3786 | 0 | 0 | 0 | -3786 |  | 21474 | 142451 | 33532 | 6264 | 10622 |  | 7572 | 0 | 0 | 0 | -7572 |  | 10372 | 128527 | 53981 | 8167 | 13296 | [22 empty] | 839410.6852 | 4234051.7852 | 722704.0793 | 1503223.5691 | 2159140.0519 | 9458530.1707 |  | 894116.087 | 4232184.9649 | 722704.0793 | 1503223.5691 | 1492108.4102 | 8844337.1106 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 668369.5855 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 2132317.2901 | 11159684.9169 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174 |  | 474613.8242 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 1795002.6033 | 12679697.8729
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 |  | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 |  | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 |  | 1027512.9079 | 4822066.2514 | 6832264.3794 | 1702711.7472 | 2202491.8357 | 16587047.1215 |  | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 |  | 719355.4816 | 4518097.7976 | 9086314.1115 | 2019685.5734 | 1967105.026 | 18310557.99
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 868 | 856 | C1 | 416 | 225 | 108 | 95 | 24 | 868 | 398 | 225 | 108 | 95 | 42 | 868 | 40 | 0 | 0 | -9 | -36 | -5 | 383 | 209 | 64 | 111 | 101 | 868 | 111 | 0 | 0 | -9 | -114 | -12 | 271 | 302 | 41 | 82 | 172 | 868 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | C1 | 165.9387 | 165.9387 | 626.127 | 1146.0231 | 1956.2345 | C1 | 66043.6106 | 37336.2121 | 67621.7214 | 108872.194 | 82161.8485 | 362035.5866 |  | 69030.5076 | 37336.2121 | 67621.7214 | 108872.194 | 46949.6277 | 329810.2627 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 70192.0787 | 34681.1925 | 40072.1312 | 116894.3556 | 127155.2418 | 388994.9998 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216 |  | 63388.5911 | 50113.4935 | 25671.209 | 83659.6859 | 113461.6004 | 336294.5799
|  |  | 437 | 458 | C2 | 139 | 148 | 49 | 84 | 17 | 437 | 102 | 101 | 49 | 90 | 48 | 390 | 52 | 0 | 0 | 0 | -33 | 19 | 97 | 140 | 23 | 66 | 111 | 437 | 111 | 0 | 0 | 0 | -90 | 21 | 81 | 130 | 42 | 26 | 158 | 437 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | C2 | 237.0553 | 237.0553 | 894.4672 | 1637.1758 | 2794.6207 | C2 | 24179.6421 | 23942.5868 | 43828.8935 | 147345.8264 | 134141.7935 | 373438.7423 |  | 32950.6887 | 35084.1866 | 43828.8935 | 137522.7713 | 47508.5519 | 296895.092 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 35321.2419 | 33187.744 | 20572.7459 | 108053.606 | 217980.4145 | 415115.7524 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369 |  | 45514.6204 | 30817.1909 | 37567.623 | 42566.5721 | 190034.2075 | 346500.2139
|  |  | 82 | 82 | C3 | 29 | 25 | 10 | 16 | 2 | 82 | 25 | 25 | 10 | 16 | 6 | 82 | 4 | 0 | 0 | -3 | -1 | 0 | 23 | 28 | 3 | 10 | 18 | 82 | 17 | 0 | 0 | -3 | -14 | 0 | 8 | 43 | 0 | 6 | 25 | 82 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | C3 | 355.583 | 355.583 | 1341.7008 | 2455.7638 | 4191.931 | C3 | 8889.5743 | 8889.5743 | 13417.0082 | 39292.2204 | 25151.5863 | 95639.9635 |  | 10311.9062 | 8889.5743 | 13417.0082 | 39292.2204 | 8383.8621 | 80294.5712 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 9600.7402 | 9956.3232 | 4025.1025 | 17190.3464 | 71262.8278 | 112035.3402 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904 |  | 8889.5743 | 15290.0678 | 0 | 7367.2913 | 46111.2415 | 77658.1749
|  |  | 88 | 88 | C4 | 28 | 33 | 12 | 14 | 1 | 88 | 18 | 33 | 12 | 14 | 11 | 88 | 9 | 0 | 0 | -1 | -8 | 0 | 25 | 27 | 10 | 14 | 12 | 88 | 22 | 0 | 0 | -2 | -20 | 0 | 21 | 27 | 9 | 10 | 21 | 88 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | C4 | 592.6383 | 592.6383 | 2236.168 | 4092.9396 | 6986.5517 | C4 | 10667.4892 | 19557.0635 | 26834.0164 | 57301.1547 | 76852.0692 | 191211.793 |  | 16593.872 | 19557.0635 | 26834.0164 | 57301.1547 | 6986.5517 | 127272.6584 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 20149.7017 | 16001.2337 | 22361.6803 | 53208.2151 | 27946.207 | 139667.0379 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133 |  | 25483.4463 | 16001.2337 | 20125.5123 | 32743.517 | 6986.5517 | 101340.2611
|  |  | 1475 | 1484 |  | 612 | 431 | 179 | 209 | 44 |  | 543 | 384 | 179 | 215 | 107 |  | 105 | 0 | 0 | -13 | -78 |  | 528 | 404 | 100 | 201 | 242 |  | 261 | 0 | 0 | -14 | -238 |  | 381 | 502 | 92 | 124 | 376 | [22 empty] | 109780.3162 | 89725.4366 | 151701.6395 | 352811.3955 | 318307.2976 | 1022326.0853 |  | 128886.9746 | 100867.0364 | 151701.6395 | 342988.3404 | 109828.5935 | 834272.5842 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 135263.7625 | 93826.4935 | 87031.6599 | 295346.5232 | 444344.6911 | 1055813.1302 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818 |  | 143276.2321 | 112221.9859 | 83364.3443 | 166337.0663 | 356593.6012 | 861793.2299
| EHV Transformer |  | 397 | 397 | C1 | 58 | 263 | 49 | 15 | 12 | 397 | 51 | 262 | 49 | 21 | 14 | 397 | 7 | 4 | 0 | 0 | -11 | 0 | 49 | 211 | 104 | 10 | 23 | 397 | 15 | 11 | 0 | -7 | -19 | 0 | 16 | 188 | 137 | 28 | 28 | 397 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | C1 | 914.8668 | 914.8668 | 3426.7195 | 7107.5305 | 14545.0524 | C1 | 46658.209 | 239695.1127 | 167909.2578 | 149258.1402 | 203630.7342 | 807151.454 |  | 53062.2769 | 240609.9796 | 167909.2578 | 106612.9573 | 174540.6294 | 742735.101 |  | 44828.4753 | 193036.9038 | 356378.833 | 71075.3049 | 334536.2063 | 999855.7232 |  | 51232.5432 | 196696.3711 | 356378.833 | 71075.3049 | 174540.6294 | 849923.6815 |  | 14637.8695 | 171994.9664 | 469460.5781 | 199010.8537 | 407261.4685 | 1262365.7361 |  | 28360.8721 | 182058.5017 | 469460.5781 | 149258.1402 | 130905.472 | 960043.5641
|  |  | 456 | 456 | C2 | 46 | 344 | 46 | 9 | 11 | 456 | 42 | 341 | 46 | 13 | 13 | 455 | 3 | 3 | 0 | -1 | -5 | 0 | 38 | 270 | 122 | 9 | 17 | 456 | 21 | 12 | 0 | -21 | -12 | 0 | 14 | 193 | 198 | 33 | 18 | 456 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | C2 | 1306.9526 | 1306.9526 | 4895.3136 | 10153.615 | 20778.6464 | C2 | 54892.0106 | 445670.8476 | 225184.4274 | 131996.9948 | 270122.4026 | 1127866.6829 |  | 60119.8211 | 449591.7055 | 225184.4274 | 91382.5348 | 228565.1099 | 1054843.5987 |  | 49664.2 | 352877.2107 | 597228.2641 | 91382.5348 | 353236.988 | 1444389.1976 |  | 53585.0579 | 356798.0686 | 597228.2641 | 81228.9199 | 249343.7562 | 1338184.0666 |  | 18297.3369 | 252241.858 | 969272.1007 | 335069.2944 | 374015.6343 | 1948896.2243 |  | 45743.3421 | 267925.2896 | 969272.1007 | 121843.3798 | 124671.8781 | 1529455.9903
|  |  | 28 | 28 | C3 | 13 | 11 | 3 | 0 | 1 | 28 | 12 | 9 | 3 | 2 | 2 | 28 | 3 | 0 | 0 | -1 | -2 | 0 | 10 | 11 | 4 | 1 | 2 | 28 | 4 | 0 | 0 | -2 | -2 | 0 | 5 | 16 | 3 | 2 | 2 | 28 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | C3 | 1960.4289 | 1960.4289 | 7342.9705 | 15230.4225 | 31167.9695 | C3 | 23525.1474 | 17643.8605 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 25485.5763 | 21564.7184 | 22028.9114 | 0 | 31167.9695 | 100247.1757 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 25485.5763 | 21564.7184 | 29371.8818 | 0 | 0 | 76422.1766 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 17643.8605 | 31366.8632 | 22028.9114 | 0 | 0 | 71039.6351
|  |  | 28 | 28 | C4 | 6 | 20 | 2 | 0 | 0 | 28 | 6 | 20 | 2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | 28 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | C4 | 3267.3816 | 3267.3816 | 12238.2841 | 25384.0375 | 51946.6159 | C4 | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069
|  |  | 909 | 909 |  | 123 | 638 | 100 | 24 | 24 |  | 111 | 632 | 100 | 36 | 29 |  | 13 | 7 | 0 | -2 | -18 |  | 102 | 509 | 236 | 20 | 42 |  | 40 | 23 | 0 | -30 | -33 |  | 35 | 416 | 347 | 63 | 48 | [22 empty] | 144679.6564 | 768357.4525 | 439599.1649 | 311715.98 | 536089.0759 | 2200441.3295 |  | 158271.9638 | 777114.0351 | 439599.1649 | 197995.4922 | 434273.7087 | 2007254.3646 |  | 130433.8727 | 623024.3198 | 1056408.6835 | 177688.2622 | 750109.1333 | 2737664.2714 |  | 146640.0853 | 630604.645 | 1056408.6835 | 152304.2247 | 423884.3856 | 2409842.0241 |  | 42737.3511 | 517683.9376 | 1570906.1471 | 564540.993 | 843613.0419 | 3539481.4706 |  | 91748.0748 | 543430.9045 | 1570906.1471 | 271101.52 | 255577.3501 | 2732763.9964
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 277 | 277 | C1 | 24 | 149 | 75 | 12 | 17 | 277 | 24 | 194 | 56 | 2 | 32 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 148 | 92 | 8 | 27 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 102 | 126 | 13 | 34 | 277 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | C1 | 119.927 | 119.927 | 449.5301 | 926.8824 | 1907.1654 | C1 | 2878.2491 | 23265.8473 | 25173.6858 | 1853.7648 | 61029.2928 | 114200.8398 |  | 2878.2491 | 17869.1301 | 33714.7578 | 11122.5886 | 32421.8118 | 98006.5374 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006
|  |  | 199 | 197 | C2 | 17 | 106 | 54 | 10 | 12 | 199 | 12 | 142 | 46 | 2 | 19 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 106 | 65 | 7 | 19 | 199 | 0 | 0 | 0 | 0 | -2 | -2 | 2 | 72 | 91 | 9 | 25 | 199 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 320532 | 320532 | 320532 | 320532 | 320532 | C2 | 171.3244 | 171.3244 | 642.1859 | 1324.1177 | 2724.522 | C2 | 2055.8922 | 24328.0583 | 29540.5497 | 2648.2354 | 51765.918 | 110338.6536 |  | 2912.514 | 18160.3815 | 34678.0365 | 13241.1769 | 32694.264 | 101686.373 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 62664.006 | 145697.9809
|  |  | 69 | 60.4 | C3 | 6 | 37 | 19 | 3 | 4 | 69 | 12 | 43 | 13 | 1 | 2 | 71 | 0 | 0 | -2.2 | 0 | -6.4 | -8.6 | 0 | 37 | 23 | 2 | 7 | 69 | 0 | 0 | -2.2 | 0 | -6.4 | -8.6 | 0 | 27 | 31 | 3 | 8 | 69 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 480798 | 480798 | 480798 | 480798 | 480798 | C3 | 256.9865 | 256.9865 | 963.2788 | 1986.1765 | 4086.783 | C3 | 3083.8384 | 11050.4208 | 12522.6243 | 1986.1765 | 8173.566 | 36816.6261 |  | 1541.9192 | 9508.5016 | 18302.2971 | 5958.5296 | 16347.132 | 51658.3795 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 9508.5016 | 20036.1989 | 3972.3531 | 2452.0698 | 35969.1234 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725 |  | 0 | 6938.6363 | 27742.4292 | 5958.5296 | 6538.8528 | 47178.448
|  |  | 11 | 10 | C4 | 1 | 6 | 3 | 0 | 1 | 11 | 0 | 9 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 6 | 4 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 4 | 5 | 1 | 1 | 11 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 801330 | 801330 | 801330 | 801330 | 801330 | C4 | 428.3109 | 428.3109 | 1605.4647 | 3310.2942 | 6811.305 | C4 | 0 | 3854.798 | 3210.9293 | 0 | 0 | 7065.7273 |  | 428.3109 | 2569.8653 | 4816.394 | 0 | 6811.305 | 14625.8752 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 2569.8653 | 6421.8586 | 0 | 0 | 8991.7239 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 0 | 13050.861
|  |  | 556 | 544.4 |  | 48 | 298 | 151 | 25 | 34 |  | 48 | 388 | 117 | 5 | 53 |  | 0 | 0 | -2.2 | 0 | -7.4 |  | 4 | 297 | 184 | 17 | 54 |  | 0 | 0 | -2.2 | 0 | -9.4 |  | 4 | 205 | 253 | 26 | 68 | [22 empty] | 8017.9798 | 62499.1243 | 70447.7891 | 6488.1767 | 120968.7768 | 268421.8467 |  | 7760.9932 | 48107.8786 | 91511.4853 | 30322.2951 | 88274.5128 | 265977.1651 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 47987.9516 | 109556.9081 | 20656.236 | 105711.4536 | 284495.052 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564 |  | 582.5028 | 33219.7922 | 150849.459 | 33235.3541 | 134046.4824 | 351933.5905
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 846 | 846 | C1 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 351 | 204 | 247 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 317 | 237 | 248 | 846 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 36.5855 | 85.2982 | C1 | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063
|  |  | 18 | 18 | C2 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 52.265 | 121.8546 | C2 | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662
|  |  | 2 | 2 | C3 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 78.3974 | 182.7819 | C3 | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819
|  |  | 287 | 287 | C4 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 119 | 69 | 84 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 80 | 84 | 287 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 130.6624 | 304.6366 | C4 | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215
|  |  | 1153 | 1153 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 478 | 278 | 337 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 432 | 323 | 338 | [22 empty] | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076
| EHV OHL Support - Poles |  | 7548 | 7548 | C1 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 120 | 0 | 0 | 0 | -120 | 0 | 877 | 5407 | 606 | 139 | 519 | 7548 | 240 | 0 | 0 | 0 | -240 | 0 | 725 | 4922 | 1093 | 176 | 632 | 7548 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | C1 | 12.5427 | 12.5427 | 47.1998 | 99.2168 | 152.9599 | C1 | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 12505.0428 | 67818.221 | 28603.0639 | 13791.1373 | 61031.0042 | 183748.4691 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392 |  | 12103.6773 | 61735.0257 | 51589.3545 | 17462.1594 | 59960.2848 | 202850.5017
|  |  | 27483 | 27483 | C2 | 4303 | 19734 | 1275 | 1189 | 982 | 27483 | 3986 | 19740 | 1275 | 1189 | 1299 | 27489 | 577 | 0 | 0 | 0 | -577 | 0 | 3193 | 19693 | 2205 | 504 | 1888 | 27483 | 1154 | 0 | 0 | 0 | -1154 | 0 | 2641 | 17922 | 3979 | 640 | 2301 | 27483 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 52273 | 52273 | 52273 | 52273 | 52273 | C2 | 17.9181 | 17.9181 | 67.4283 | 141.7383 | 218.5142 | C2 | 71421.5511 | 353703.3165 | 85971.0194 | 168526.8472 | 283849.8906 | 963472.6248 |  | 77101.5892 | 353595.8079 | 85971.0194 | 168526.8472 | 214580.9027 | 899776.1663 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 67551.2413 | 352861.1657 | 148679.2923 | 71436.1068 | 286472.0605 | 926999.8667 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155 |  | 67999.1938 | 321128.2086 | 268297.0087 | 90712.5166 | 250635.7387 | 998772.6664
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | C3 | 26.8772 | 26.8772 | 101.1424 | 212.6075 | 327.7712 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | C4 | 44.7953 | 44.7953 | 168.5706 | 354.3458 | 546.2854 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 35031 | 35031 |  | 5484 | 25155 | 1625 | 1515 | 1252 |  | 5167 | 25161 | 1625 | 1515 | 1569 |  | 697 | 0 | 0 | 0 | -697 |  | 4070 | 25100 | 2811 | 643 | 2407 |  | 1394 | 0 | 0 | 0 | -1394 |  | 3366 | 22844 | 5072 | 816 | 2933 | [22 empty] | 86234.4454 | 421697.1349 | 102490.9408 | 200871.5289 | 325149.0664 | 1136443.1163 |  | 91914.4834 | 421589.6263 | 102490.9408 | 200871.5289 | 255880.0785 | 1072746.6578 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 80056.2841 | 420679.3867 | 177282.3562 | 85227.2441 | 347503.0647 | 1110748.3358 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546 |  | 80102.8711 | 382863.2343 | 319886.3632 | 108174.676 | 310596.0235 | 1201623.1681
| EHV OHL Fittings and Conductors (Tower Lines) |  | 335 | 335 | C1 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 44 | 201 | 90 | 0 | 335 | 11.1551 | 0 | 0 | 0 | -11.1551 | 0 | 0 | 34 | 188 | 97 | 16 | 335 | 43.0603 | 0 | 0 | -13.9052 | -29.1551 | 0 | 0 | 29 | 102 | 154 | 50 | 335 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 34.3512 | 66.6554 | C1 | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1981.5835 | 3332.0668 | 322.9396 | 5636.5899 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708 |  | 0 | 0 | 1075.1145 | 4812.4244 | 1389.4263 | 7276.9652
|  |  | 17 | 17 | C2 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 5 | 0 | 17 | 4 | 0 | 0 | -3 | -1 | 0 | 0 | 1 | 5 | 8 | 3 | 17 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 49.0731 | 95.222 | C2 | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394 |  | 0 | 0 | 75.2881 | 245.3657 | 190.4441 | 511.0979
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 73.6097 | 142.833 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 163 | 163 | C4 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 92 | 47 | 8 | 163 | 34 | 0 | 0 | -18 | -16 | 0 | 0 | 14 | 50 | 75 | 24 | 163 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 122.6829 | 238.0551 | C4 | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401 |  | 0 | 0 | 1882.2032 | 6992.9237 | 1904.4405 | 10779.5674
|  |  | 515 | 515 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 68 | 308 | 139 | 0 |  | 11.1551 | 0 | 0 | 0 | -11.1551 |  | 0 | 52 | 290 | 149 | 24 |  | 81.0603 | 0 | 0 | -34.9052 | -46.1551 |  | 0 | 44 | 157 | 237 | 77 | [22 empty] | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2227.3801 | 17166.3212 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502 |  | 0 | 0 | 3032.6057 | 12050.7139 | 3484.3109 | 18567.6305
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 |  | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 |  | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 |  | 362542.6347 | 1193098.4768 | 1444174.7843 | 579618.2218 | 1371121.1654 | 4950555.2831 |  | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 |  | 315709.6809 | 1071735.9169 | 2135551.1686 | 610336.6685 | 1107833.2566 | 5241166.6914
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 188 | 232 | C1 | 70 | 62 | 25 | 18 | 13 | 188 | 39 | 62 | 25 | 18 | 44 | 188 | 36 | 0 | 0 | -8 | -14 | 14 | 48 | 63 | 27 | 14 | 36 | 188 | 66 | 0 | 0 | -8 | -14 | 44 | 42 | 58 | 26 | 12 | 50 | 188 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | C1 | 579.6435 | 579.6435 | 2212.3775 | 3916.6144 | 6007.2213 | C1 | 22606.0951 | 35937.8947 | 55309.4371 | 70499.0596 | 264317.7374 | 448670.2238 |  | 40575.0424 | 35937.8947 | 55309.4371 | 70499.0596 | 78093.877 | 280415.3107 |  | 27822.8862 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 395167.1853 |  | 48690.0509 | 36517.5382 | 59734.192 | 23499.6865 | 132158.8687 | 300600.3363 |  | 24345.0254 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 462846.5991 |  | 62601.494 | 33619.3209 | 57521.8145 | 15666.4577 | 216259.967 | 385669.0541
|  |  | 51 | 60 | C2 | 26 | 13 | 9 | 2 | 1 | 51 | 23 | 23 | 9 | 2 | 4 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 9 | 3 | 6 | 51 | 9 | 0 | 0 | 0 | 0 | 9 | 24 | 8 | 3 | 7 | 9 | 51 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | C2 | 828.0621 | 828.0621 | 3160.5393 | 5595.1635 | 8581.7447 | C2 | 19045.4281 | 19045.4281 | 28444.8533 | 11190.3269 | 34326.9789 | 112053.0153 |  | 21529.6143 | 10764.8072 | 28444.8533 | 11190.3269 | 8581.7447 | 80511.3465 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514 |  | 27326.049 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 159834.0102
|  |  | 54 | 56 | C3 | 47 | 5 | 2 | 0 | 0 | 54 | 47 | 5 | 2 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 3 | 3 | 0 | 2 | 54 | 2 | 0 | 0 | 0 | 0 | 2 | 22 | 27 | 1 | 2 | 2 | 54 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | C3 | 1242.0931 | 1242.0931 | 4740.8089 | 8392.7452 | 12872.6171 | C3 | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097 |  | 29810.2352 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 110618.2833
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | C4 | 2070.1552 | 2070.1552 | 7901.3482 | 13987.9086 | 21454.3618 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293 | 348 |  | 143 | 80 | 36 | 20 | 14 |  | 109 | 90 | 36 | 20 | 48 |  | 36 | 0 | 0 | -8 | -14 |  | 119 | 74 | 39 | 17 | 44 |  | 77 | 0 | 0 | -8 | -14 |  | 88 | 93 | 30 | 21 | 61 | [22 empty] | 100029.9005 | 61193.7885 | 93235.9082 | 81689.3865 | 298644.7163 | 634793.6999 |  | 120483.0341 | 52913.1676 | 93235.9082 | 81689.3865 | 86675.6217 | 434997.118 |  | 105660.7227 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 620044.2708 |  | 126527.8874 | 46868.3143 | 102401.472 | 40285.1769 | 209394.5712 | 525477.4218 |  | 71544.5646 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 723362.1475 |  | 119737.7782 | 73780.3322 | 71744.2412 | 71618.0922 | 319240.9037 | 656121.3475
| 132kV Transformer |  | 86 | 86 | C1 | 21 | 61 | 2 | 1 | 1 | 86 | 21 | 61 | 2 | 1 | 1 | 86 | 3 | 0 | 0 | -2 | -1 | 0 | 19 | 49 | 15 | 2 | 1 | 86 | 4 | 0 | 0 | -2 | -2 | 0 | 7 | 42 | 32 | 3 | 2 | 86 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | C1 | 2795.6945 | 2795.6945 | 10471.536 | 21719.5367 | 44447.4774 | C1 | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 61505.2793 | 136989.0312 | 157073.0394 | 0 | 0 | 355567.3498 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468 |  | 30752.6396 | 117419.1696 | 335089.1507 | 21719.5367 | 0 | 504980.4966
|  |  | 156 | 156 | C2 | 23 | 101 | 23 | 5 | 4 | 156 | 21 | 94 | 23 | 10 | 4 | 152 | 6 | 3 | 0 | -6 | -3 | 0 | 19 | 72 | 48 | 11 | 6 | 156 | 16 | 4 | 0 | -13 | -7 | 0 | 9 | 64 | 54 | 21 | 8 | 156 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469494 | 469494 | 469494 | 469494 | 469494 | C2 | 3993.8493 | 3993.8493 | 14959.3371 | 31027.9096 | 63496.3963 | C2 | 83870.8354 | 375421.8346 | 344064.7529 | 310279.0961 | 253985.5852 | 1367622.1043 |  | 91858.534 | 403378.7798 | 344064.7529 | 155139.5481 | 253985.5852 | 1248427.2 |  | 75883.1368 | 287557.1499 | 718048.18 | 341307.0057 | 380978.3778 | 1803773.8503 |  | 99846.2326 | 299538.6979 | 718048.18 | 155139.5481 | 190489.1889 | 1463061.8475 |  | 35944.6437 | 255606.3555 | 807804.2025 | 651586.1019 | 507971.1704 | 2258912.4741 |  | 99846.2326 | 271581.7527 | 807804.2025 | 248223.2769 | 63496.3963 | 1490951.8611
|  |  | 22 | 22 | C3 | 3 | 10 | 5 | 0 | 4 | 22 | 2 | 10 | 5 | 0 | 5 | 22 | 0 | 1 | 0 | -1 | 0 | 0 | 3 | 6 | 8 | 1 | 4 | 22 | 0 | 1 | 0 | -1 | 0 | 0 | 1 | 8 | 7 | 2 | 4 | 22 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 704241 | 704241 | 704241 | 704241 | 704241 | C3 | 5990.774 | 5990.774 | 22439.0056 | 46541.8644 | 95244.5945 | C3 | 11981.5479 | 59907.7396 | 112195.0281 | 0 | 476222.9723 | 660307.2879 |  | 17972.3219 | 59907.7396 | 112195.0281 | 0 | 380978.3778 | 571053.4674 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 17972.3219 | 41935.4177 | 179512.045 | 0 | 380978.3778 | 620398.1624 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117 |  | 5990.774 | 53916.9656 | 157073.0394 | 46541.8644 | 380978.3778 | 644501.0212
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1173735 | 1173735 | 1173735 | 1173735 | 1173735 | C4 | 9984.6233 | 9984.6233 | 37398.3427 | 77569.774 | 158740.9908 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 264 | 264 |  | 47 | 172 | 30 | 6 | 9 |  | 44 | 165 | 30 | 11 | 10 |  | 9 | 4 | 0 | -9 | -4 |  | 41 | 127 | 71 | 14 | 11 |  | 20 | 5 | 0 | -16 | -9 |  | 17 | 114 | 93 | 26 | 14 | [22 empty] | 154561.9681 | 605866.9395 | 477202.853 | 331998.6329 | 774656.0349 | 2344286.4284 |  | 168540.4407 | 633823.8847 | 477202.853 | 176859.0848 | 679411.4405 | 2135837.7036 |  | 146973.6544 | 460490.8248 | 1054633.2644 | 431287.9436 | 806404.2331 | 2899789.9204 |  | 179323.8338 | 478463.1467 | 1054633.2644 | 155139.5481 | 571467.5667 | 2439027.3597 |  | 61505.2793 | 420951.7167 | 1299966.3926 | 809828.4409 | 977844.5031 | 3570096.3326 |  | 136589.6462 | 442917.8879 | 1299966.3926 | 316484.678 | 444474.7741 | 2640433.3789
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 30 | 30 | C1 | 0 | 23 | 3 | 1 | 3 | 30 | 1 | 25 | 4 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 1 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 1 | 5 | 30 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | C1 | 286.0983 | 286.0983 | 1072.4002 | 2211.1731 | 4549.7389 | C1 | 286.0983 | 7152.4572 | 4289.6009 | 0 | 0 | 11728.1564 |  | 0 | 6580.2606 | 3217.2007 | 2211.1731 | 13649.2167 | 25657.8511 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642
|  |  | 68 | 65.1 | C2 | 1 | 49 | 8 | 2 | 8 | 68 | 2 | 57 | 9 | 1 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 12 | 2 | 10 | 68 | 0 | 0 | 0 | -2.9 | 0 | -2.9 | 1 | 34 | 18 | 3 | 12 | 68 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 764662 | 764662 | 764662 | 764662 | 764662 | C2 | 408.7118 | 408.7118 | 1532.0003 | 3158.8187 | 6499.627 | C2 | 817.4237 | 23296.5748 | 13788.0029 | 3158.8187 | 0 | 41060.8201 |  | 408.7118 | 20026.8801 | 12256.0025 | 6317.6374 | 51997.016 | 91006.2479 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002 |  | 408.7118 | 13896.2025 | 27576.0057 | 315.8819 | 77995.524 | 120192.3259
|  |  | 43 | 36.5 | C3 | 1 | 30 | 5 | 2 | 5 | 43 | 1 | 36 | 6 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | 8 | 2 | 7 | 43 | 0 | 0 | 0 | -2 | -4.5 | -6.5 | 1 | 20 | 12 | 2 | 8 | 43 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1146993 | 1146993 | 1146993 | 1146993 | 1146993 | C3 | 613.0678 | 613.0678 | 2298.0005 | 4738.2281 | 9749.4405 | C3 | 613.0678 | 22070.4393 | 13788.0029 | 0 | 0 | 36471.5099 |  | 613.0678 | 18392.0328 | 11490.0024 | 9476.4562 | 48747.2025 | 88718.7616 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088 |  | 613.0678 | 12261.3552 | 27576.0057 | 0 | 34123.0418 | 74573.4704
|  |  | 49 | 47 | C4 | 1 | 34 | 6 | 2 | 6 | 49 | 2 | 39 | 7 | 1 | 3 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 9 | 2 | 7 | 49 | 0 | 0 | 0 | -2 | 0 | -2 | 1 | 24 | 13 | 2 | 9 | 49 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1911655 | 1911655 | 1911655 | 1911655 | 1911655 | C4 | 1021.7796 | 1021.7796 | 3830.0008 | 7897.0468 | 16249.0675 | C4 | 2043.5592 | 39849.4043 | 26810.0055 | 7897.0468 | 48747.2025 | 125347.2184 |  | 1021.7796 | 34740.5063 | 22980.0048 | 15794.0936 | 97494.405 | 172030.7893 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013 |  | 1021.7796 | 24522.7103 | 49790.0103 | 0 | 146241.6075 | 221576.1077
|  |  | 190 | 178.6 |  | 3 | 136 | 22 | 7 | 22 |  | 6 | 157 | 26 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 117 | 34 | 7 | 29 |  | 0 | 0 | 0 | -6.9 | -4.5 |  | 3 | 94 | 51 | 8 | 34 | [22 empty] | 3760.1489 | 92368.8756 | 58675.6121 | 11055.8655 | 48747.2025 | 214607.7047 |  | 2043.5592 | 79739.6798 | 49943.2103 | 33799.3603 | 211887.8402 | 377413.6498 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524 |  | 2043.5592 | 55257.8406 | 113521.2235 | 2527.055 | 281108.8677 | 454458.546
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 51.9831 | 121.1975 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4405 | 4405 | C2 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 11 | 0 | 0 | 0 | -11 | 0 | 0 | 1073 | 2538 | 601 | 193 | 4405 | 22 | 0 | 0 | 0 | -22 | 0 | 0 | 1062 | 2518 | 627 | 198 | 4405 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 74.2616 | 173.1393 | C2 | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 54300.2328 | 44631.2111 | 31511.3483 | 130442.7922 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924 |  | 0 | 0 | 53872.335 | 46562.0122 | 30472.5126 | 130906.8599
|  |  | 342 | 342 | C3 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 83 | 198 | 46 | 15 | 342 | 3 | 0 | 0 | -3 | 0 | 0 | 0 | 83 | 197 | 47 | 15 | 342 | 3 | 0 | 0 | -3 | 0 | 0 | 0 | 83 | 195 | 49 | 15 | 342 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 111.3924 | 259.7089 | C3 | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6322.1902 | 4901.2644 | 3895.6337 | 15119.0884 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656 |  | 0 | 0 | 6258.0056 | 5124.0492 | 3895.6337 | 15277.6885
|  |  | 8 | 8 | C4 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 185.654 | 432.8482 | C4 | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901
|  |  | 4755 | 4755 |  | 0 | 1158 | 2749 | 642 | 206 |  | 0 | 1158 | 2749 | 642 | 206 |  | 14 | 0 | 0 | -3 | -11 |  | 0 | 1158 | 2740 | 649 | 208 |  | 25 | 0 | 0 | -3 | -22 |  | 0 | 1147 | 2718 | 677 | 213 | [22 empty] | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 60889.8592 | 50052.3066 | 37311.514 | 148253.6799 |  | 0 | 0 | 60889.8592 | 49718.1295 | 35406.982 | 146014.9707 |  | 0 | 0 | 60397.7767 | 52205.8925 | 38177.2104 | 150780.8796 |  | 0 | 0 | 60397.7767 | 51871.7154 | 34368.1463 | 146637.6384
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 48.8085 | 94.7085 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2361 | 2361 | C2 | 471 | 289 | 642 | 591 | 368 | 2361 | 413 | 252 | 642 | 591 | 426 | 2324 | 200.3547 | 0 | 0 | 0 | -200.3547 | 0 | 422 | 303 | 562 | 581 | 493 | 2361 | 431.5407 | 0 | 0 | 0 | -431.5407 | 0 | 58 | 649 | 257 | 698 | 699 | 2361 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 69.7264 | 135.2979 | C2 | 0 | 0 | 13735.5199 | 41208.3279 | 57636.898 | 112580.7458 |  | 0 | 0 | 13735.5199 | 41208.3279 | 49789.6208 | 104733.4686 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 12023.9286 | 40511.0635 | 39594.286 | 92129.2781 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643 |  | 0 | 0 | 5498.4869 | 48669.0573 | 36186.6748 | 90354.2191
|  |  | 196 | 196 | C3 | 43 | 21 | 54 | 50 | 28 | 196 | 38 | 21 | 54 | 50 | 33 | 196 | 27 | 0 | 0 | 0 | -27 | 0 | 36 | 22 | 48 | 49 | 41 | 196 | 55 | 0 | 0 | 0 | -55 | 0 | 5 | 51 | 22 | 59 | 59 | 196 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 104.5897 | 202.9468 | C3 | 0 | 0 | 1732.9862 | 5229.4832 | 6697.2452 | 13659.7146 |  | 0 | 0 | 1732.9862 | 5229.4832 | 5682.5111 | 12644.9805 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 1540.4321 | 5124.8936 | 2841.2555 | 9506.5812 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842 |  | 0 | 0 | 706.0314 | 6170.7902 | 811.7873 | 7688.6089
|  |  | 3 | 3 | C4 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 0 | 227.8033 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055 |  | 0 | 0 | 0 | 174.3161 | 0 | 174.3161
|  |  | 2560 | 2560 |  | 514 | 310 | 697 | 642 | 397 |  | 451 | 273 | 697 | 642 | 460 |  | 228.3547 | 0 | 0 | 0 | -228.3547 |  | 458 | 325 | 611 | 631 | 535 |  | 488.5407 | 0 | 0 | 0 | -488.5407 |  | 63 | 700 | 279 | 758 | 760 | [22 empty] | 0 | 0 | 15521.9933 | 46612.1272 | 64672.3879 | 126806.5085 |  | 0 | 0 | 15521.9933 | 46612.1272 | 55810.3766 | 117944.4971 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 13617.848 | 45810.2731 | 42435.5416 | 101863.6627 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254 |  | 0 | 0 | 6204.5183 | 55014.1636 | 36998.4621 | 98217.1441
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 |  | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 |  | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 |  | 307895.2803 | 594322.0194 | 1308142.4595 | 324752.4879 | 1128439.182 | 3663551.4292 |  | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 |  | 258370.9836 | 571956.0607 | 1551834.1523 | 497515.7043 | 1116191.154 | 3995868.055
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 643865 | 643837 |  | 108014 | 416640 | 71011 | 32459 | 15741 |  | 100295 | 415570 | 71117 | 33178 | 22842 |  | 17643.5098 | 18 | -420.2 | -3232 | -14023.9098 |  | 67669 | 388473 | 121329 | 34588 | 31809 |  | 34038.601 | 113 | -420.2 | -5432.8052 | -28326.5958 |  | 44233 | 354100 | 157644 | 44376 | 43514 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 |  | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 |  | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 |  | 2539686.6459 | 10528256.0122 | 12998009.1422 | 6149327.3785 | 6619123.4582 | 38834402.637 |  | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 |  | 2230606.1289 | 9654686.6578 | 16497240.1625 | 7653315.4137 | 5725148.8633 | 41760997.2263
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 | LV Network | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 841735.823 | 3918769.2646 | 3413427.519 | 3542244.9215 | 1917071.2752 | 13633248.8032 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 | LV Network | 937169.9828 | 3492896.8826 | 3723540.7301 | 4525777.4676 | 1534019.4268 | 14213404.4898
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 | HV Network | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 | HV Network | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 | HV Network | 1027512.9079 | 4822066.2514 | 6832264.3794 | 1702711.7472 | 2202491.8357 | 16587047.1215 | HV Network | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 | HV Network | 719355.4816 | 4518097.7976 | 9086314.1115 | 2019685.5734 | 1967105.026 | 18310557.99
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 | EHV Network | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 | EHV Network | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 | EHV Network | 362542.6347 | 1193098.4768 | 1444174.7843 | 579618.2218 | 1371121.1654 | 4950555.2831 | EHV Network | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 | EHV Network | 315709.6809 | 1071735.9169 | 2135551.1686 | 610336.6685 | 1107833.2566 | 5241166.6914
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 | 132kV Network | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 | 132kV Network | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 | 132kV Network | 307895.2803 | 594322.0194 | 1308142.4595 | 324752.4879 | 1128439.182 | 3663551.4292 | 132kV Network | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 | 132kV Network | 258370.9836 | 571956.0607 | 1551834.1523 | 497515.7043 | 1116191.154 | 3995868.055
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 | Total | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 | Total | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 | Total | 2539686.6459 | 10528256.0122 | 12998009.1422 | 6149327.3785 | 6619123.4582 | 38834402.637 | Total | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 | Total | 2230606.1289 | 9654686.6578 | 16497240.1625 | 7653315.4137 | 5725148.8633 | 41760997.2263
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EPN - Asset Rep
HI3: Secondary deliverables RIIO-ED1 - Asset replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 64 | 64 | C1 | 8 | 25 | 31 | 0 | 0 | 64 | 8 | 25 | 31 | 0 | 0 | 64 | 1 | 0 | 0 | -1 | 0 | 0 | 4 | 25 | 33 | 2 | 0 | 64 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 24 | 33 | 6 | 1 | 64 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | C1 | 7.8518 | 17.9786 | 55.6367 | 90.6791 | 145.6343 | C1 | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 39.2589 | 449.4654 | 1836.0105 | 90.6791 | 0 | 2415.4139 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064 |  | 7.8518 | 431.4868 | 1836.0105 | 453.3957 | 145.6343 | 2874.3791
|  |  | 29908 | 29908 | C2 | 3760 | 11129 | 14935 | 84 | 0 | 29908 | 3531 | 10762 | 14935 | 265 | 48 | 29541 | 471 | 0 | -122 | -349 | 0 | 0 | 2069 | 11728 | 15262 | 789 | 60 | 29908 | 954 | 0 | -122 | -791 | -41 | 0 | 229 | 11673 | 15906 | 1851 | 249 | 29908 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10371 | 10371 | 10371 | 10371 | 10371 | C2 | 11.2168 | 25.6837 | 79.481 | 129.5416 | 208.049 | C2 | 39606.6007 | 276408.3808 | 1187048.316 | 34328.5337 | 9986.3537 | 1547378.1849 |  | 42175.2531 | 285834.3124 | 1187048.316 | 10881.4975 | 0 | 1525939.3789 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 28490.7295 | 301218.8711 | 1203341.9152 | 56998.3202 | 12482.9421 | 1602532.778 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369 |  | 13269.5012 | 299806.2655 | 1254527.6612 | 137314.135 | 43274.1992 | 1748191.762
|  |  | 63 | 63 | C3 | 8 | 25 | 30 | 0 | 0 | 63 | 7 | 25 | 30 | 1 | 0 | 63 | 14 | 0 | -13 | -1 | 0 | 0 | 5 | 24 | 33 | 1 | 0 | 63 | 18 | 0 | -13 | -5 | 0 | 0 | 1 | 23 | 33 | 5 | 1 | 63 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | C3 | 16.8252 | 38.5256 | 119.2215 | 194.3125 | 312.0736 | C3 | 117.7766 | 963.1401 | 3576.6437 | 194.3125 | 0 | 4851.873 |  | 134.6019 | 963.1401 | 3576.6437 | 0 | 0 | 4674.3858 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 319.6794 | 924.6145 | 2384.4292 | 0 | 0 | 3628.7231 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581 |  | 319.6794 | 886.0889 | 2384.4292 | 0 | 312.0736 | 3902.2711
|  |  | 5 | 5 | C4 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | C4 | 28.0421 | 64.2093 | 198.7024 | 323.8541 | 520.1226 | C4 | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656
|  |  | 30040 | 30040 |  | 3777 | 11181 | 14998 | 84 | 0 |  | 3547 | 10814 | 14998 | 266 | 48 |  | 487 | 0 | -136 | -351 | 0 |  | 2078 | 11779 | 15331 | 792 | 60 |  | 974 | 0 | -136 | -797 | -41 |  | 230 | 11722 | 15975 | 1862 | 251 | [22 empty] | 39815.2336 | 277949.4051 | 1192747.1017 | 34522.8462 | 9986.3537 | 1555020.9402 |  | 42400.7112 | 287375.3367 | 1192747.1017 | 10881.4975 | 0 | 1533404.647 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 28877.7098 | 302721.3697 | 1207959.7597 | 57088.9993 | 12482.9421 | 1609130.7806 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274 |  | 13625.0744 | 301252.2599 | 1259145.5056 | 137767.5307 | 43731.9071 | 1755522.2778
| LV UGB |  | 812 | 812 | C1 | 107 | 91 | 305 | 287 | 22 | 812 | 101 | 91 | 305 | 287 | 28 | 812 | 16 | 0 | 0 | 0 | -16 | 0 | 89 | 66 | 228 | 393 | 37 | 813 | 31 | 0 | 0 | 0 | -31 | 0 | 82 | 39 | 126 | 513 | 52 | 812 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | C1 | 11.222 | 16.833 | 56.11 | 123.4421 | 241.2731 | C1 | 1133.4225 | 1531.8036 | 17113.5572 | 35427.8689 | 6755.6468 | 61962.299 |  | 1200.7545 | 1531.8036 | 17113.5572 | 35427.8689 | 5308.0082 | 60581.9924 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 1178.3105 | 1110.9785 | 12793.0854 | 48512.7264 | 5066.7351 | 68661.8358 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285 |  | 1268.0865 | 656.4873 | 7069.863 | 63325.7726 | 5066.7351 | 77386.9445
|  |  | 25739 | 25739 | C2 | 3391 | 2894 | 9654 | 9102 | 698 | 25739 | 3189 | 2894 | 9654 | 9102 | 900 | 25739 | 2169 | 0 | 0 | -1648 | -521 | 0 | 2825 | 2088 | 7220 | 12437 | 1171 | 25741 | 2844 | 0 | 0 | -1857 | -987 | 0 | 2604 | 1240 | 4005 | 16258 | 1634 | 25741 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11183 | 11183 | 11183 | 11183 | 11183 | C2 | 16.0314 | 24.0472 | 80.1572 | 176.3458 | 344.6759 | C2 | 51124.2472 | 69592.4607 | 773837.3821 | 1605099.3654 | 310208.2731 | 2809861.7285 |  | 54362.5971 | 69592.4607 | 773837.3821 | 1605099.3654 | 240583.7496 | 2743475.5549 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 80060.9879 | 50210.4554 | 578734.8144 | 1902594.7103 | 224039.3084 | 2835640.2764 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995 |  | 87339.2595 | 29818.4697 | 321029.4919 | 2539555.6978 | 223005.2808 | 3200748.1997
|  |  | 5276 | 5276 | C3 | 695 | 593 | 1979 | 1866 | 143 | 5276 | 654 | 593 | 1979 | 1866 | 185 | 5277 | 590 | 0 | 0 | -483 | -107 | 0 | 579 | 428 | 1480 | 2549 | 240 | 5276 | 1180 | 0 | 0 | -978 | -202 | 0 | 534 | 254 | 821 | 3333 | 335 | 5277 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | C3 | 24.0472 | 36.0707 | 120.2358 | 264.5187 | 517.0138 | C3 | 15726.838 | 21389.9426 | 237946.5785 | 493591.8615 | 95647.5509 | 864302.7715 |  | 16712.7713 | 21389.9426 | 237946.5785 | 493591.8615 | 73932.9718 | 843574.1257 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 28111.1218 | 15438.2722 | 177948.9319 | 546495.598 | 68762.8339 | 836756.7578 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958 |  | 41216.8202 | 9161.9653 | 98713.5629 | 622941.4973 | 68762.8339 | 840796.6795
|  |  | 2285 | 2285 | C4 | 301 | 257 | 857 | 808 | 62 | 2285 | 283 | 257 | 857 | 808 | 80 | 2285 | 255 | 0 | 0 | -209 | -46 | 0 | 251 | 185 | 641 | 1104 | 104 | 2285 | 512 | 0 | 0 | -424 | -88 | 0 | 231 | 110 | 355 | 1443 | 145 | 2284 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | C4 | 40.0786 | 60.1179 | 200.3929 | 440.8645 | 861.6896 | C4 | 11342.2405 | 15450.2958 | 171736.7507 | 356218.4924 | 68935.1718 | 623682.9512 |  | 12063.6551 | 15450.2958 | 171736.7507 | 356218.4924 | 53424.7581 | 608893.9521 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 20279.7657 | 11121.8082 | 128451.8754 | 394573.7014 | 49977.9996 | 604405.1502 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454 |  | 29778.3911 | 6612.9671 | 71139.4942 | 449240.8958 | 49116.3099 | 605888.058
|  |  | 34112 | 34112 |  | 4494 | 3835 | 12795 | 12063 | 925 |  | 4227 | 3835 | 12795 | 12063 | 1193 |  | 3030 | 0 | 0 | -2340 | -690 |  | 3744 | 2767 | 9569 | 16483 | 1552 |  | 4567 | 0 | 0 | -3259 | -1308 |  | 3451 | 1643 | 5307 | 21547 | 2166 | [22 empty] | 79326.7482 | 107964.5026 | 1200634.2684 | 2490337.5883 | 481546.6426 | 4359809.7501 |  | 84339.778 | 107964.5026 | 1200634.2684 | 2490337.5883 | 373249.4877 | 4256525.6251 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 129630.1859 | 77881.5143 | 897928.707 | 2892176.7362 | 347846.8769 | 4345464.0203 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692 |  | 159602.5573 | 46249.8893 | 497952.412 | 3675063.8635 | 345951.1597 | 4724819.8817
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | C1 | 14.4557 | 14.4557 | 29.0421 | 79.9779 | 158.5738 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 246106 | 246106 | C2 | 44138 | 179341 | 6435 | 8501 | 7691 | 246106 | 40338 | 179599 | 6435 | 8501 | 11491 | 246364 | 6727 | 0 | 0 | 0 | -6727 | 0 | 26121 | 170027 | 31277 | 5151 | 13530 | 246106 | 13455 | 0 | 0 | 0 | -13455 | 0 | 23261 | 151153 | 47037 | 6192 | 18463 | 246106 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | C2 | 20.651 | 20.651 | 41.4888 | 114.2542 | 226.534 | C2 | 833019.9377 | 3708898.5026 | 266980.178 | 971274.7708 | 2603101.8733 | 8383275.2624 |  | 911493.7283 | 3703570.5452 | 266980.178 | 971274.7708 | 1742272.7793 | 7595592.0017 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 678343.9664 | 3511227.1544 | 1297643.9827 | 588523.2731 | 1541110.6121 | 7616848.9886 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384 |  | 758222.0247 | 3121460.2273 | 1951506.8585 | 707461.8728 | 1134482.1322 | 7673133.1156
|  |  | 1255 | 1255 | C3 | 115 | 1016 | 14 | 62 | 48 | 1255 | 115 | 1016 | 14 | 62 | 48 | 1255 | 42 | 0 | 0 | 0 | -42 | 0 | 114 | 868 | 159 | 26 | 88 | 1255 | 84 | 0 | 0 | 0 | -84 | 0 | 99 | 771 | 240 | 32 | 113 | 1255 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | C3 | 30.9765 | 30.9765 | 62.2331 | 171.3813 | 339.801 | C3 | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 4832.3334 | 26887.5988 | 9895.0695 | 4455.913 | 15630.8441 | 61701.7588 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146 |  | 5668.6988 | 23882.8786 | 14935.954 | 5484.2006 | 9854.2278 | 59825.9598
|  |  | 2 | 2 | C4 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | C4 | 51.6275 | 51.6275 | 103.7219 | 285.6354 | 566.3349 | C4 | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 51.6275 | 0 | 0 | 0 | 103.255 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 51.6275 | 0 | 0 | 0 | 103.255
|  |  | 247363 | 247363 |  | 44254 | 180357 | 6449 | 8563 | 7740 |  | 40454 | 180615 | 6449 | 8563 | 11540 |  | 6770 | 0 | 0 | 0 | -6770 |  | 26235 | 170896 | 31436 | 5177 | 13619 |  | 13540 | 0 | 0 | 0 | -13540 |  | 23360 | 151925 | 47277 | 6224 | 18577 | [22 empty] | 836633.8623 | 3740370.6228 | 267851.442 | 981900.4094 | 2619978.6542 | 8446734.9907 |  | 915107.6529 | 3735042.6654 | 267851.442 | 981900.4094 | 1759149.5602 | 7659051.73 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 683227.9273 | 3538166.3806 | 1307539.0522 | 592979.1861 | 1556741.4562 | 7678654.0023 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155 |  | 763942.351 | 3145394.7334 | 1966442.8125 | 712946.0734 | 1144336.36 | 7733062.3304
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 |  | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 841735.823 | 3918769.2646 | 3413427.519 | 3542244.9215 | 1917071.2752 | 13633248.8032 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 |  | 937169.9828 | 3492896.8826 | 3723540.7301 | 4525777.4676 | 1534019.4268 | 14213404.4898
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 3046 | 3052 | C1 | 1055 | 1042 | 885 | 52 | 12 | 3046 | 1044 | 1010 | 885 | 84 | 23 | 3046 | 155 | 0 | 0 | -51 | -99 | 5 | 967 | 904 | 830 | 246 | 99 | 3046 | 395 | 0 | 0 | -117 | -272 | 6 | 561 | 1107 | 785 | 300 | 293 | 3046 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33586 | 33586 | 33586 | 33586 | 33586 | C1 | 58.8156 | 58.8156 | 220.1504 | 404.4235 | 556.6962 | C1 | 61403.5232 | 59403.7916 | 194833.0619 | 33971.5713 | 12804.0121 | 362415.9602 |  | 62050.4952 | 61285.892 | 194833.0619 | 21030.0203 | 6680.3541 | 345879.8236 |  | 56874.7193 | 53169.3343 | 182724.7925 | 99488.1731 | 55112.9217 | 447369.9409 |  | 65991.1428 | 53169.3343 | 182724.7925 | 78862.5763 | 0 | 380747.8458 |  | 32995.5714 | 65108.9082 | 172818.0267 | 121327.0404 | 163111.9803 | 555361.527 |  | 56227.7473 | 65108.9082 | 172818.0267 | 74009.4946 | 11690.6197 | 379854.7966
|  |  | 1695 | 1698 | C2 | 261 | 967 | 397 | 50 | 20 | 1695 | 232 | 799 | 397 | 65 | 34 | 1527 | 118 | 0 | 0 | -39 | -78 | 1 | 253 | 702 | 545 | 115 | 80 | 1695 | 245 | 0 | 0 | -89 | -153 | 3 | 153 | 597 | 583 | 192 | 170 | 1695 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47980 | 47980 | 47980 | 47980 | 47980 | C2 | 84.0223 | 84.0223 | 314.5005 | 577.7478 | 795.2803 | C2 | 19493.182 | 67133.8465 | 124856.6999 | 37553.6077 | 27039.5287 | 276076.8648 |  | 21929.8297 | 81249.599 | 124856.6999 | 28887.3906 | 15905.6051 | 272829.1243 |  | 21257.651 | 58983.6799 | 171402.7744 | 66440.9983 | 63622.4204 | 381707.5241 |  | 31172.2867 | 58983.6799 | 171402.7744 | 43908.8337 | 1590.5605 | 307058.1352 |  | 12855.4174 | 50161.3347 | 183353.7935 | 110927.5798 | 135197.6434 | 492495.7688 |  | 33440.8898 | 50161.3347 | 183353.7935 | 59508.0246 | 13519.7643 | 339983.8069
|  |  | 618 | 620 | C3 | 127 | 359 | 113 | 17 | 2 | 618 | 122 | 359 | 113 | 19 | 5 | 618 | 49 | 0 | 0 | -14 | -34 | 1 | 113 | 256 | 178 | 34 | 37 | 618 | 89 | 0 | 0 | -32 | -55 | 2 | 64 | 179 | 266 | 54 | 55 | 618 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71970 | 71970 | 71970 | 71970 | 71970 | C3 | 126.0335 | 126.0335 | 471.7508 | 866.6217 | 1192.9204 | C3 | 15376.0875 | 45246.028 | 53307.8353 | 16465.8126 | 5964.6019 | 136360.3654 |  | 16006.255 | 45246.028 | 53307.8353 | 14732.5692 | 2385.8408 | 131678.5283 |  | 14241.786 | 32264.5771 | 83971.6344 | 29465.1384 | 44138.0542 | 204081.19 |  | 20417.4277 | 32264.5771 | 83971.6344 | 17332.4343 | 3578.7611 | 157564.8347 |  | 8066.1443 | 22559.9972 | 125485.7009 | 46797.5727 | 65610.621 | 268520.0362 |  | 19283.1261 | 22559.9972 | 125485.7009 | 19065.6778 | 0 | 186394.5021
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119950 | 119950 | 119950 | 119950 | 119950 | C4 | 210.0558 | 210.0558 | 786.2513 | 1444.3695 | 1988.2006 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5359 | 5370 |  | 1443 | 2368 | 1395 | 119 | 34 |  | 1398 | 2168 | 1395 | 168 | 62 |  | 322 | 0 | 0 | -104 | -211 |  | 1333 | 1862 | 1553 | 395 | 216 |  | 729 | 0 | 0 | -238 | -480 |  | 778 | 1883 | 1634 | 546 | 518 | [22 empty] | 96272.7927 | 171783.6662 | 372997.5972 | 87990.9917 | 45808.1427 | 774853.1904 |  | 99986.58 | 187781.5189 | 372997.5972 | 64649.9801 | 24971.8 | 750387.4762 |  | 92374.1563 | 144417.5913 | 438099.2014 | 195394.3098 | 162873.3962 | 1033158.655 |  | 117580.8571 | 144417.5913 | 438099.2014 | 140103.8443 | 5169.3217 | 845370.8157 |  | 53917.1331 | 137830.2401 | 481657.5211 | 279052.1929 | 363920.2447 | 1316377.332 |  | 108951.7632 | 137830.2401 | 481657.5211 | 152583.197 | 25210.3841 | 906233.1055
| HV Switchgear (GM) - Distribution |  | 16951 | 16951 | C1 | 7581 | 8348 | 596 | 426 | 0 | 16951 | 7566 | 8348 | 596 | 426 | 16 | 16952 | 0 | 0 | 0 | 0 | 0 | 0 | 3630 | 12149 | 623 | 533 | 16 | 16951 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 14318 | 1090 | 577 | 96 | 16951 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | C1 | 11.2991 | 11.2991 | 42.4721 | 77.873 | 133.2047 | C1 | 85488.9241 | 94324.8134 | 25313.3509 | 33173.9097 | 2131.2749 | 240432.273 |  | 85658.4105 | 94324.8134 | 25313.3509 | 33173.9097 | 0 | 238470.4845 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348
|  |  | 15770 | 15690 | C2 | 1149 | 9824 | 4343 | 454 | 0 | 15770 | 474 | 9350 | 4343 | 798 | 548 | 15513 | 1700 | 0 | 0 | -242 | -1498 | -40 | 1008 | 6422 | 4444 | 2126 | 1770 | 15770 | 3400 | 0 | 0 | -381 | -3099 | -80 | 917 | 4850 | 4656 | 1768 | 3579 | 15770 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 28897 | 28897 | 28897 | 28897 | 28897 | C2 | 16.1416 | 16.1416 | 60.6744 | 111.2472 | 190.2924 | C2 | 7651.0989 | 150923.5754 | 263508.8273 | 88775.2514 | 104280.2376 | 615138.9907 |  | 18546.6511 | 158574.6743 | 263508.8273 | 50506.2207 | 0 | 491136.3735 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 43711.3414 | 103661.0911 | 269636.9396 | 209589.6913 | 51759.534 | 678358.5974 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113 |  | 69683.1096 | 78286.5605 | 282499.9079 | 154299.8418 | 91340.3541 | 676109.7739
|  |  | 3 | 3 | C3 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | C3 | 24.2123 | 24.2123 | 91.0116 | 166.8708 | 285.4386 | C3 | 0 | 24.2123 | 0 | 333.7415 | 0 | 357.9539 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | C4 | 40.3539 | 40.3539 | 151.6859 | 278.118 | 475.731 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 32724 | 32644 |  | 8732 | 18173 | 4939 | 880 | 0 |  | 8040 | 17699 | 4939 | 1226 | 564 |  | 1700 | 0 | 0 | -242 | -1498 |  | 4640 | 18572 | 5067 | 2659 | 1786 |  | 3400 | 0 | 0 | -381 | -3099 |  | 1789 | 19169 | 5746 | 2345 | 3675 | [22 empty] | 93140.023 | 245272.6012 | 288822.1782 | 122282.9027 | 106411.5125 | 855929.2176 |  | 104253.4863 | 252923.7001 | 288822.1782 | 83680.1305 | 0 | 729679.495 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 84775.4672 | 240957.9625 | 296097.0362 | 251096.015 | 53890.8089 | 926817.2898 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831 |  | 79561.7437 | 240091.1608 | 328794.459 | 199232.5787 | 104128.0037 | 951807.9457
| HV Transformer (GM) |  | 15354 | 15354 | C1 | 2254 | 4991 | 8109 | 0 | 0 | 15354 | 2175 | 4991 | 8109 | 71 | 8 | 15354 | 197 | 0 | -125 | -72 | 0 | 0 | 1306 | 5562 | 8385 | 91 | 10 | 15354 | 403 | 0 | -125 | -265 | -13 | 0 | 79 | 6088 | 8844 | 291 | 52 | 15354 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | C1 | 33.5005 | 40.8282 | 115.1569 | 219.6408 | 370.4805 | C1 | 72863.5281 | 203773.5627 | 933807.1344 | 15594.4939 | 2963.844 | 1229002.5632 |  | 75510.0655 | 203773.5627 | 933807.1344 | 0 | 0 | 1213090.7626 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 50351.2105 | 227086.4668 | 951195.8232 | 4173.1744 | 3704.805 | 1236511.4799 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269 |  | 16147.2278 | 248562.1017 | 1004052.8308 | 5710.6598 | 14448.7395 | 1288921.5597
|  |  | 10916 | 10916 | C2 | 1472 | 4148 | 5296 | 0 | 0 | 10916 | 1285 | 3757 | 5432 | 46 | 5 | 10525 | 152 | 0 | -100 | -52 | 0 | 0 | 1028 | 4205 | 5611 | 65 | 7 | 10916 | 298 | 0 | -100 | -188 | -10 | 0 | 187 | 4563 | 5928 | 201 | 37 | 10916 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 54257 | 54257 | 54257 | 54257 | 54257 | C2 | 47.8578 | 58.326 | 164.5098 | 313.7725 | 529.2579 | C2 | 61497.2963 | 219130.7997 | 893617.3835 | 14433.5356 | 2646.2893 | 1191325.3045 |  | 70446.7083 | 241936.2676 | 871244.047 | 0 | 0 | 1183627.0229 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 56472.2254 | 245260.8499 | 906613.6599 | 4079.0427 | 3704.805 | 1216130.5829 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456 |  | 23211.0418 | 266141.5596 | 958763.2753 | 4079.0427 | 14289.9622 | 1266484.8815
|  |  | 4387 | 4387 | C3 | 644 | 1426 | 2317 | 0 | 0 | 4387 | 622 | 1426 | 2317 | 20 | 2 | 4387 | 63 | 0 | -42 | -21 | 0 | 0 | 373 | 1589 | 2396 | 26 | 3 | 4387 | 123 | 0 | -42 | -77 | -4 | 0 | 22 | 1740 | 2528 | 82 | 15 | 4387 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | C3 | 71.7867 | 87.489 | 246.7647 | 470.6588 | 793.8868 | C3 | 44651.3443 | 124759.3241 | 571753.9058 | 9413.1754 | 1587.7736 | 752165.5233 |  | 46230.6523 | 124759.3241 | 571753.9058 | 0 | 0 | 742743.8823 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 31299.0131 | 139020.0323 | 580884.2013 | 2353.2939 | 2381.6604 | 755938.2008 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676 |  | 10409.0754 | 152230.8723 | 613457.1471 | 2353.2939 | 8732.7547 | 787183.1434
|  |  | 1566 | 1566 | C4 | 230 | 509 | 827 | 0 | 0 | 1566 | 222 | 509 | 827 | 7 | 1 | 1566 | 23 | 0 | -15 | -8 | 0 | 0 | 133 | 567 | 855 | 10 | 1 | 1566 | 46 | 0 | -15 | -30 | -1 | 0 | 8 | 621 | 900 | 32 | 5 | 1566 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | C4 | 119.6445 | 145.815 | 411.2746 | 784.4313 | 1323.1446 | C4 | 26561.0891 | 74219.841 | 340124.0686 | 5491.019 | 1323.1446 | 447719.1623 |  | 27518.2454 | 74219.841 | 340124.0686 | 0 | 0 | 441862.155 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 18664.5491 | 82677.1117 | 345470.638 | 1568.8626 | 1323.1446 | 449704.306 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151 |  | 6460.8055 | 90551.1223 | 363977.9936 | 1568.8626 | 5292.5786 | 467851.3625
|  |  | 32223 | 32223 |  | 4600 | 11074 | 16549 | 0 | 0 |  | 4304 | 10683 | 16685 | 144 | 16 |  | 435 | 0 | -282 | -153 | 0 |  | 2840 | 11923 | 17247 | 192 | 21 |  | 870 | 0 | -282 | -560 | -28 |  | 296 | 13012 | 18200 | 606 | 109 | [22 empty] | 205573.2579 | 621883.5276 | 2739302.4923 | 44932.224 | 8521.0515 | 3620212.5533 |  | 219705.6716 | 644688.9954 | 2716929.1558 | 0 | 0 | 3581323.8228 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 156786.9981 | 694044.4606 | 2784164.3223 | 12174.3735 | 11114.415 | 3658284.5696 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553 |  | 56228.1506 | 757485.6559 | 2940251.2468 | 13711.8589 | 42764.035 | 3810440.9471
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 135 | 135 | C1 | 12 | 103 | 14 | 2 | 4 | 135 | 12 | 103 | 14 | 2 | 4 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 90 | 21 | 4 | 8 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 81 | 34 | 5 | 10 | 135 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | C1 | 17.6591 | 17.6591 | 66.4486 | 139.6696 | 215.3203 | C1 | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859
|  |  | 196526 | 196526 | C2 | 30344 | 147825 | 6695 | 6814 | 4848 | 196526 | 28983 | 147899 | 6695 | 6814 | 6209 | 196600 | 3484 | 0 | 0 | 0 | -3484 | 0 | 19315 | 130607 | 30746 | 5743 | 10115 | 196526 | 7082 | 0 | 0 | 0 | -7082 | 0 | 9135 | 117840 | 49495 | 7489 | 12567 | 196526 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | C2 | 25.2273 | 25.2273 | 94.9265 | 199.5279 | 307.6005 | C2 | 731162.86 | 3731092.5658 | 635533.0554 | 1359583.403 | 1909891.3827 | 8367263.2669 |  | 765497.2165 | 3729225.7455 | 635533.0554 | 1359583.403 | 1491247.1289 | 7981086.5493 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 575157.2317 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 2039698.7854 | 9974217.8754 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617 |  | 409111.1376 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 1687188.6349 | 11261737.8042
|  |  | 17623 | 17623 | C3 | 3370 | 13180 | 604 | 469 | 0 | 17623 | 2845 | 13180 | 604 | 469 | 525 | 17623 | 302 | 0 | 0 | 0 | -302 | 0 | 2134 | 11719 | 2763 | 508 | 499 | 17623 | 490 | 0 | 0 | 0 | -490 | 0 | 1222 | 10577 | 4441 | 664 | 719 | 17623 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | C3 | 37.841 | 37.841 | 142.3898 | 299.2919 | 461.4007 | C3 | 107657.5063 | 498743.7375 | 86003.4277 | 140367.9078 | 242235.3783 | 1075007.9576 |  | 127524.0057 | 498743.7375 | 86003.4277 | 140367.9078 | 0 | 852639.0787 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 92180.5572 | 443458.1077 | 393422.9646 | 152040.2925 | 90895.942 | 1171997.864 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35 |  | 64783.7085 | 400243.7414 | 632353.017 | 198729.8311 | 105660.765 | 1401771.063
|  |  | 59 | 59 | C4 | 14 | 38 | 1 | 6 | 0 | 59 | 6 | 38 | 1 | 6 | 8 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 2 | 9 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29 | 11 | 9 | 0 | 59 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | C4 | 63.0683 | 63.0683 | 237.3163 | 498.8199 | 769.0012 | C4 | 378.4095 | 2396.5936 | 237.3163 | 2992.9191 | 6152.0096 | 12157.2481 |  | 882.9555 | 2396.5936 | 237.3163 | 2992.9191 | 0 | 6509.7846 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199
|  |  | 214343 | 214343 |  | 33740 | 161146 | 7314 | 7291 | 4852 |  | 31846 | 161220 | 7314 | 7291 | 6746 |  | 3786 | 0 | 0 | 0 | -3786 |  | 21474 | 142451 | 33532 | 6264 | 10622 |  | 7572 | 0 | 0 | 0 | -7572 |  | 10372 | 128527 | 53981 | 8167 | 13296 | [22 empty] | 839410.6852 | 4234051.7852 | 722704.0793 | 1503223.5691 | 2159140.0519 | 9458530.1707 |  | 894116.087 | 4232184.9649 | 722704.0793 | 1503223.5691 | 1492108.4102 | 8844337.1106 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 668369.5855 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 2132317.2901 | 11159684.9169 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174 |  | 474613.8242 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 1795002.6033 | 12679697.8729
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 |  | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 |  | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 |  | 1027512.9079 | 4821536.9106 | 6832264.3794 | 1706351.5584 | 2202491.8357 | 16590157.592 |  | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 |  | 719355.4816 | 4511695.2956 | 9086314.1115 | 2063709.9566 | 1967105.026 | 18348179.8713
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 868 | 856 | C1 | 416 | 225 | 108 | 95 | 24 | 868 | 398 | 225 | 108 | 95 | 42 | 868 | 40 | 0 | 0 | -9 | -36 | -5 | 383 | 209 | 64 | 111 | 101 | 868 | 111 | 0 | 0 | -9 | -114 | -12 | 271 | 302 | 41 | 82 | 172 | 868 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | C1 | 165.9387 | 165.9387 | 626.127 | 1146.0231 | 1956.2345 | C1 | 66043.6106 | 37336.2121 | 67621.7214 | 108872.194 | 82161.8485 | 362035.5866 |  | 69030.5076 | 37336.2121 | 67621.7214 | 108872.194 | 46949.6277 | 329810.2627 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 70192.0787 | 34681.1925 | 40072.1312 | 116894.3556 | 127155.2418 | 388994.9998 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216 |  | 63388.5911 | 50113.4935 | 25671.209 | 83659.6859 | 113461.6004 | 336294.5799
|  |  | 437 | 458 | C2 | 139 | 148 | 49 | 84 | 17 | 437 | 102 | 101 | 49 | 90 | 48 | 390 | 52 | 0 | 0 | 0 | -33 | 19 | 97 | 140 | 23 | 66 | 111 | 437 | 111 | 0 | 0 | 0 | -90 | 21 | 81 | 130 | 42 | 26 | 158 | 437 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | C2 | 237.0553 | 237.0553 | 894.4672 | 1637.1758 | 2794.6207 | C2 | 24179.6421 | 23942.5868 | 43828.8935 | 147345.8264 | 134141.7935 | 373438.7423 |  | 32950.6887 | 35084.1866 | 43828.8935 | 137522.7713 | 47508.5519 | 296895.092 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 35321.2419 | 33187.744 | 20572.7459 | 108053.606 | 217980.4145 | 415115.7524 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369 |  | 45514.6204 | 30817.1909 | 37567.623 | 42566.5721 | 190034.2075 | 346500.2139
|  |  | 82 | 82 | C3 | 29 | 25 | 10 | 16 | 2 | 82 | 25 | 25 | 10 | 16 | 6 | 82 | 4 | 0 | 0 | -3 | -1 | 0 | 23 | 28 | 3 | 10 | 18 | 82 | 17 | 0 | 0 | -3 | -14 | 0 | 8 | 43 | 0 | 6 | 25 | 82 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | C3 | 355.583 | 355.583 | 1341.7008 | 2455.7638 | 4191.931 | C3 | 8889.5743 | 8889.5743 | 13417.0082 | 39292.2204 | 25151.5863 | 95639.9635 |  | 10311.9062 | 8889.5743 | 13417.0082 | 39292.2204 | 8383.8621 | 80294.5712 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 9600.7402 | 9956.3232 | 4025.1025 | 17190.3464 | 71262.8278 | 112035.3402 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904 |  | 8889.5743 | 15290.0678 | 0 | 7367.2913 | 46111.2415 | 77658.1749
|  |  | 88 | 88 | C4 | 28 | 33 | 12 | 14 | 1 | 88 | 18 | 33 | 12 | 14 | 11 | 88 | 9 | 0 | 0 | -1 | -8 | 0 | 25 | 27 | 10 | 14 | 12 | 88 | 22 | 0 | 0 | -2 | -20 | 0 | 21 | 27 | 9 | 10 | 21 | 88 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | C4 | 592.6383 | 592.6383 | 2236.168 | 4092.9396 | 6986.5517 | C4 | 10667.4892 | 19557.0635 | 26834.0164 | 57301.1547 | 76852.0692 | 191211.793 |  | 16593.872 | 19557.0635 | 26834.0164 | 57301.1547 | 6986.5517 | 127272.6584 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 20149.7017 | 16001.2337 | 22361.6803 | 53208.2151 | 27946.207 | 139667.0379 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133 |  | 25483.4463 | 16001.2337 | 20125.5123 | 32743.517 | 6986.5517 | 101340.2611
|  |  | 1475 | 1484 |  | 612 | 431 | 179 | 209 | 44 |  | 543 | 384 | 179 | 215 | 107 |  | 105 | 0 | 0 | -13 | -78 |  | 528 | 404 | 100 | 201 | 242 |  | 261 | 0 | 0 | -14 | -238 |  | 381 | 502 | 92 | 124 | 376 | [22 empty] | 109780.3162 | 89725.4366 | 151701.6395 | 352811.3955 | 318307.2976 | 1022326.0853 |  | 128886.9746 | 100867.0364 | 151701.6395 | 342988.3404 | 109828.5935 | 834272.5842 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 135263.7625 | 93826.4935 | 87031.6599 | 295346.5232 | 444344.6911 | 1055813.1302 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818 |  | 143276.2321 | 112221.9859 | 83364.3443 | 166337.0663 | 356593.6012 | 861793.2299
| EHV Transformer |  | 397 | 397 | C1 | 58 | 263 | 49 | 15 | 12 | 397 | 51 | 262 | 49 | 21 | 14 | 397 | 7 | 0 | 0 | 0 | -7 | 0 | 49 | 211 | 104 | 10 | 23 | 397 | 15 | 0 | 0 | 0 | -15 | 0 | 16 | 188 | 137 | 28 | 28 | 397 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | C1 | 914.8668 | 914.8668 | 3426.7195 | 7107.5305 | 14545.0524 | C1 | 46658.209 | 239695.1127 | 167909.2578 | 149258.1402 | 203630.7342 | 807151.454 |  | 53062.2769 | 240609.9796 | 167909.2578 | 106612.9573 | 174540.6294 | 742735.101 |  | 44828.4753 | 193036.9038 | 356378.833 | 71075.3049 | 334536.2063 | 999855.7232 |  | 51232.5432 | 193036.9038 | 356378.833 | 71075.3049 | 232720.8391 | 904444.424 |  | 14637.8695 | 171994.9664 | 469460.5781 | 199010.8537 | 407261.4685 | 1262365.7361 |  | 28360.8721 | 171994.9664 | 469460.5781 | 199010.8537 | 189085.6818 | 1057912.952
|  |  | 456 | 456 | C2 | 46 | 344 | 46 | 9 | 11 | 456 | 42 | 341 | 46 | 13 | 13 | 455 | 3 | 0 | 0 | -1 | -2 | 0 | 38 | 270 | 122 | 9 | 17 | 456 | 21 | 0 | 0 | -13 | -8 | 0 | 14 | 193 | 198 | 33 | 18 | 456 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | C2 | 1306.9526 | 1306.9526 | 4895.3136 | 10153.615 | 20778.6464 | C2 | 54892.0106 | 445670.8476 | 225184.4274 | 131996.9948 | 270122.4026 | 1127866.6829 |  | 60119.8211 | 449591.7055 | 225184.4274 | 91382.5348 | 228565.1099 | 1054843.5987 |  | 49664.2 | 352877.2107 | 597228.2641 | 91382.5348 | 353236.988 | 1444389.1976 |  | 53585.0579 | 352877.2107 | 597228.2641 | 81228.9199 | 311679.6953 | 1396599.1478 |  | 18297.3369 | 252241.858 | 969272.1007 | 335069.2944 | 374015.6343 | 1948896.2243 |  | 45743.3421 | 252241.858 | 969272.1007 | 203072.2997 | 207786.4635 | 1678116.064
|  |  | 28 | 28 | C3 | 13 | 11 | 3 | 0 | 1 | 28 | 12 | 9 | 3 | 2 | 2 | 28 | 3 | 0 | 0 | -1 | -2 | 0 | 10 | 11 | 4 | 1 | 2 | 28 | 4 | 0 | 0 | -2 | -2 | 0 | 5 | 16 | 3 | 2 | 2 | 28 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | C3 | 1960.4289 | 1960.4289 | 7342.9705 | 15230.4225 | 31167.9695 | C3 | 23525.1474 | 17643.8605 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 25485.5763 | 21564.7184 | 22028.9114 | 0 | 31167.9695 | 100247.1757 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 25485.5763 | 21564.7184 | 29371.8818 | 0 | 0 | 76422.1766 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 17643.8605 | 31366.8632 | 22028.9114 | 0 | 0 | 71039.6351
|  |  | 28 | 28 | C4 | 6 | 20 | 2 | 0 | 0 | 28 | 6 | 20 | 2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | 28 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | C4 | 3267.3816 | 3267.3816 | 12238.2841 | 25384.0375 | 51946.6159 | C4 | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069
|  |  | 909 | 909 |  | 123 | 638 | 100 | 24 | 24 |  | 111 | 632 | 100 | 36 | 29 |  | 13 | 0 | 0 | -2 | -11 |  | 102 | 509 | 236 | 20 | 42 |  | 40 | 0 | 0 | -15 | -25 |  | 35 | 416 | 347 | 63 | 48 | [22 empty] | 144679.6564 | 768357.4525 | 439599.1649 | 311715.98 | 536089.0759 | 2200441.3295 |  | 158271.9638 | 777114.0351 | 439599.1649 | 197995.4922 | 434273.7087 | 2007254.3646 |  | 130433.8727 | 623024.3198 | 1056408.6835 | 177688.2622 | 750109.1333 | 2737664.2714 |  | 146640.0853 | 623024.3198 | 1056408.6835 | 152304.2247 | 544400.5344 | 2522777.8477 |  | 42737.3511 | 517683.9376 | 1570906.1471 | 564540.993 | 843613.0419 | 3539481.4706 |  | 91748.0748 | 517683.9376 | 1570906.1471 | 402083.1533 | 396872.1453 | 2979293.4581
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 277 | 277 | C1 | 24 | 149 | 75 | 12 | 17 | 277 | 24 | 194 | 56 | 2 | 32 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 148 | 92 | 8 | 27 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 102 | 126 | 13 | 34 | 277 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | C1 | 119.927 | 119.927 | 449.5301 | 926.8824 | 1907.1654 | C1 | 2878.2491 | 23265.8473 | 25173.6858 | 1853.7648 | 61029.2928 | 114200.8398 |  | 2878.2491 | 17869.1301 | 33714.7578 | 11122.5886 | 32421.8118 | 98006.5374 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006
|  |  | 199 | 197 | C2 | 17 | 106 | 54 | 10 | 12 | 199 | 12 | 142 | 46 | 2 | 19 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 106 | 65 | 7 | 19 | 199 | 0 | 0 | 0 | 0 | -2 | -2 | 2 | 72 | 91 | 9 | 25 | 199 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 320532 | 320532 | 320532 | 320532 | 320532 | C2 | 171.3244 | 171.3244 | 642.1859 | 1324.1177 | 2724.522 | C2 | 2055.8922 | 24328.0583 | 29540.5497 | 2648.2354 | 51765.918 | 110338.6536 |  | 2912.514 | 18160.3815 | 34678.0365 | 13241.1769 | 32694.264 | 101686.373 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 62664.006 | 145697.9809
|  |  | 69 | 60.4 | C3 | 6 | 37 | 19 | 3 | 4 | 69 | 12 | 43 | 13 | 1 | 2 | 71 | 0 | 0 | -2.2 | 0 | -6.4 | -8.6 | 0 | 37 | 23 | 2 | 7 | 69 | 0 | 0 | -2.2 | 0 | -6.4 | -8.6 | 0 | 27 | 31 | 3 | 8 | 69 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 480798 | 480798 | 480798 | 480798 | 480798 | C3 | 256.9865 | 256.9865 | 963.2788 | 1986.1765 | 4086.783 | C3 | 3083.8384 | 11050.4208 | 12522.6243 | 1986.1765 | 8173.566 | 36816.6261 |  | 1541.9192 | 9508.5016 | 18302.2971 | 5958.5296 | 16347.132 | 51658.3795 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 9508.5016 | 20036.1989 | 3972.3531 | 2452.0698 | 35969.1234 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725 |  | 0 | 6938.6363 | 27742.4292 | 5958.5296 | 6538.8528 | 47178.448
|  |  | 11 | 10 | C4 | 1 | 6 | 3 | 0 | 1 | 11 | 0 | 9 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 6 | 4 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | -1 | -1 | 0 | 4 | 5 | 1 | 1 | 11 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 801330 | 801330 | 801330 | 801330 | 801330 | C4 | 428.3109 | 428.3109 | 1605.4647 | 3310.2942 | 6811.305 | C4 | 0 | 3854.798 | 3210.9293 | 0 | 0 | 7065.7273 |  | 428.3109 | 2569.8653 | 4816.394 | 0 | 6811.305 | 14625.8752 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 2569.8653 | 6421.8586 | 0 | 0 | 8991.7239 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 0 | 13050.861
|  |  | 556 | 544.4 |  | 48 | 298 | 151 | 25 | 34 |  | 48 | 388 | 117 | 5 | 53 |  | 0 | 0 | -2.2 | 0 | -7.4 |  | 4 | 297 | 184 | 17 | 54 |  | 0 | 0 | -2.2 | 0 | -9.4 |  | 4 | 205 | 253 | 26 | 68 | [22 empty] | 8017.9798 | 62499.1243 | 70447.7891 | 6488.1767 | 120968.7768 | 268421.8467 |  | 7760.9932 | 48107.8786 | 91511.4853 | 30322.2951 | 88274.5128 | 265977.1651 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 47987.9516 | 109556.9081 | 20656.236 | 105711.4536 | 284495.052 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564 |  | 582.5028 | 33219.7922 | 150849.459 | 33235.3541 | 134046.4824 | 351933.5905
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 846 | 846 | C1 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 351 | 204 | 247 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 317 | 237 | 248 | 846 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 36.5855 | 85.2982 | C1 | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063
|  |  | 18 | 18 | C2 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 52.265 | 121.8546 | C2 | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662
|  |  | 2 | 2 | C3 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 78.3974 | 182.7819 | C3 | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819
|  |  | 287 | 287 | C4 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 119 | 69 | 84 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 80 | 84 | 287 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 130.6624 | 304.6366 | C4 | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215
|  |  | 1153 | 1153 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 478 | 278 | 337 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 432 | 323 | 338 | [22 empty] | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076
| EHV OHL Support - Poles |  | 7548 | 7548 | C1 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 120 | 0 | 0 | 0 | -120 | 0 | 877 | 5407 | 606 | 139 | 519 | 7548 | 240 | 0 | 0 | 0 | -240 | 0 | 725 | 4922 | 1093 | 176 | 632 | 7548 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | C1 | 12.5427 | 12.5427 | 47.1998 | 99.2168 | 152.9599 | C1 | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 12505.0428 | 67818.221 | 28603.0639 | 13791.1373 | 61031.0042 | 183748.4691 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392 |  | 12103.6773 | 61735.0257 | 51589.3545 | 17462.1594 | 59960.2848 | 202850.5017
|  |  | 27483 | 27483 | C2 | 4303 | 19734 | 1275 | 1189 | 982 | 27483 | 3986 | 19740 | 1275 | 1189 | 1299 | 27489 | 577 | 0 | 0 | 0 | -577 | 0 | 3193 | 19693 | 2205 | 504 | 1888 | 27483 | 1154 | 0 | 0 | 0 | -1154 | 0 | 2641 | 17922 | 3979 | 640 | 2301 | 27483 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 52273 | 52273 | 52273 | 52273 | 52273 | C2 | 17.9181 | 17.9181 | 67.4283 | 141.7383 | 218.5142 | C2 | 71421.5511 | 353703.3165 | 85971.0194 | 168526.8472 | 283849.8906 | 963472.6248 |  | 77101.5892 | 353595.8079 | 85971.0194 | 168526.8472 | 214580.9027 | 899776.1663 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 67551.2413 | 352861.1657 | 148679.2923 | 71436.1068 | 286472.0605 | 926999.8667 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155 |  | 67999.1938 | 321128.2086 | 268297.0087 | 90712.5166 | 250635.7387 | 998772.6664
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | C3 | 26.8772 | 26.8772 | 101.1424 | 212.6075 | 327.7712 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | C4 | 44.7953 | 44.7953 | 168.5706 | 354.3458 | 546.2854 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 35031 | 35031 |  | 5484 | 25155 | 1625 | 1515 | 1252 |  | 5167 | 25161 | 1625 | 1515 | 1569 |  | 697 | 0 | 0 | 0 | -697 |  | 4070 | 25100 | 2811 | 643 | 2407 |  | 1394 | 0 | 0 | 0 | -1394 |  | 3366 | 22844 | 5072 | 816 | 2933 | [22 empty] | 86234.4454 | 421697.1349 | 102490.9408 | 200871.5289 | 325149.0664 | 1136443.1163 |  | 91914.4834 | 421589.6263 | 102490.9408 | 200871.5289 | 255880.0785 | 1072746.6578 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 80056.2841 | 420679.3867 | 177282.3562 | 85227.2441 | 347503.0647 | 1110748.3358 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546 |  | 80102.8711 | 382863.2343 | 319886.3632 | 108174.676 | 310596.0235 | 1201623.1681
| EHV OHL Fittings and Conductors (Tower Lines) |  | 335 | 335 | C1 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 44 | 201 | 90 | 0 | 335 | 11.1551 | 0 | 0 | 0 | -11.1551 | 0 | 0 | 34 | 188 | 97 | 16 | 335 | 43.0603 | 0 | 0 | -13.9052 | -29.1551 | 0 | 0 | 29 | 102 | 154 | 50 | 335 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 34.3512 | 66.6554 | C1 | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1981.5835 | 3332.0668 | 322.9396 | 5636.5899 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708 |  | 0 | 0 | 1075.1145 | 4812.4244 | 1389.4263 | 7276.9652
|  |  | 17 | 17 | C2 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 5 | 0 | 17 | 4 | 0 | 0 | -3 | -1 | 0 | 0 | 1 | 5 | 8 | 3 | 17 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 49.0731 | 95.222 | C2 | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394 |  | 0 | 0 | 75.2881 | 245.3657 | 190.4441 | 511.0979
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 73.6097 | 142.833 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 163 | 163 | C4 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 92 | 47 | 8 | 163 | 34 | 0 | 0 | -18 | -16 | 0 | 0 | 14 | 50 | 75 | 24 | 163 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 122.6829 | 238.0551 | C4 | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401 |  | 0 | 0 | 1882.2032 | 6992.9237 | 1904.4405 | 10779.5674
|  |  | 515 | 515 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 68 | 308 | 139 | 0 |  | 11.1551 | 0 | 0 | 0 | -11.1551 |  | 0 | 52 | 290 | 149 | 24 |  | 81.0603 | 0 | 0 | -34.9052 | -46.1551 |  | 0 | 44 | 157 | 237 | 77 | [22 empty] | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2227.3801 | 17166.3212 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502 |  | 0 | 0 | 3032.6057 | 12050.7139 | 3484.3109 | 18567.6305
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 |  | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 |  | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 |  | 362542.6347 | 1185518.1516 | 1444174.7843 | 579618.2218 | 1491637.3142 | 5063491.1067 |  | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 |  | 315709.6809 | 1045988.9501 | 2135551.1686 | 741318.3017 | 1249128.0517 | 5487696.153
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 188 | 232 | C1 | 70 | 62 | 25 | 18 | 13 | 188 | 39 | 62 | 25 | 18 | 44 | 188 | 14 | 0 | 0 | 0 | 0 | 14 | 48 | 63 | 27 | 14 | 36 | 188 | 44 | 0 | 0 | 0 | 0 | 44 | 42 | 58 | 26 | 12 | 50 | 188 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | C1 | 579.6435 | 579.6435 | 2212.3775 | 3916.6144 | 6007.2213 | C1 | 22606.0951 | 35937.8947 | 55309.4371 | 70499.0596 | 264317.7374 | 448670.2238 |  | 40575.0424 | 35937.8947 | 55309.4371 | 70499.0596 | 78093.877 | 280415.3107 |  | 27822.8862 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 395167.1853 |  | 35937.8947 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 403282.1938 |  | 24345.0254 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 462846.5991 |  | 49849.3378 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 488350.9115
|  |  | 51 | 60 | C2 | 26 | 13 | 9 | 2 | 1 | 51 | 23 | 23 | 9 | 2 | 4 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 9 | 3 | 6 | 51 | 9 | 0 | 0 | 0 | 0 | 9 | 24 | 8 | 3 | 7 | 9 | 51 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | C2 | 828.0621 | 828.0621 | 3160.5393 | 5595.1635 | 8581.7447 | C2 | 19045.4281 | 19045.4281 | 28444.8533 | 11190.3269 | 34326.9789 | 112053.0153 |  | 21529.6143 | 10764.8072 | 28444.8533 | 11190.3269 | 8581.7447 | 80511.3465 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514 |  | 27326.049 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 159834.0102
|  |  | 54 | 56 | C3 | 47 | 5 | 2 | 0 | 0 | 54 | 47 | 5 | 2 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 3 | 3 | 0 | 2 | 54 | 2 | 0 | 0 | 0 | 0 | 2 | 22 | 27 | 1 | 2 | 2 | 54 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | C3 | 1242.0931 | 1242.0931 | 4740.8089 | 8392.7452 | 12872.6171 | C3 | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097 |  | 29810.2352 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 110618.2833
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | C4 | 2070.1552 | 2070.1552 | 7901.3482 | 13987.9086 | 21454.3618 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293 | 348 |  | 143 | 80 | 36 | 20 | 14 |  | 109 | 90 | 36 | 20 | 48 |  | 14 | 0 | 0 | 0 | 0 |  | 119 | 74 | 39 | 17 | 44 |  | 55 | 0 | 0 | 0 | 0 |  | 88 | 93 | 30 | 21 | 61 | [22 empty] | 100029.9005 | 61193.7885 | 93235.9082 | 81689.3865 | 298644.7163 | 634793.6999 |  | 120483.0341 | 52913.1676 | 93235.9082 | 81689.3865 | 86675.6217 | 434997.118 |  | 105660.7227 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 620044.2708 |  | 113775.7312 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 628159.2792 |  | 71544.5646 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 723362.1475 |  | 106985.622 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 758803.205
| 132kV Transformer |  | 86 | 86 | C1 | 21 | 61 | 2 | 1 | 1 | 86 | 21 | 61 | 2 | 1 | 1 | 86 | 3 | 0 | 0 | -2 | -1 | 0 | 19 | 49 | 15 | 2 | 1 | 86 | 4 | 0 | 0 | -2 | -2 | 0 | 7 | 42 | 32 | 3 | 2 | 86 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | C1 | 2795.6945 | 2795.6945 | 10471.536 | 21719.5367 | 44447.4774 | C1 | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 61505.2793 | 136989.0312 | 157073.0394 | 0 | 0 | 355567.3498 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468 |  | 30752.6396 | 117419.1696 | 335089.1507 | 21719.5367 | 0 | 504980.4966
|  |  | 156 | 156 | C2 | 23 | 101 | 23 | 5 | 4 | 156 | 21 | 94 | 23 | 10 | 4 | 152 | 6 | 0 | 0 | -5 | -1 | 0 | 19 | 72 | 48 | 11 | 6 | 156 | 16 | 0 | 0 | -11 | -5 | 0 | 9 | 64 | 54 | 21 | 8 | 156 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469494 | 469494 | 469494 | 469494 | 469494 | C2 | 3993.8493 | 3993.8493 | 14959.3371 | 31027.9096 | 63496.3963 | C2 | 83870.8354 | 375421.8346 | 344064.7529 | 310279.0961 | 253985.5852 | 1367622.1043 |  | 91858.534 | 403378.7798 | 344064.7529 | 155139.5481 | 253985.5852 | 1248427.2 |  | 75883.1368 | 287557.1499 | 718048.18 | 341307.0057 | 380978.3778 | 1803773.8503 |  | 99846.2326 | 287557.1499 | 718048.18 | 186167.4577 | 317481.9815 | 1609101.0018 |  | 35944.6437 | 255606.3555 | 807804.2025 | 651586.1019 | 507971.1704 | 2258912.4741 |  | 99846.2326 | 255606.3555 | 807804.2025 | 310279.0961 | 190489.1889 | 1664025.0757
|  |  | 22 | 22 | C3 | 3 | 10 | 5 | 0 | 4 | 22 | 2 | 10 | 5 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 8 | 1 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 7 | 2 | 4 | 22 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 704241 | 704241 | 704241 | 704241 | 704241 | C3 | 5990.774 | 5990.774 | 22439.0056 | 46541.8644 | 95244.5945 | C3 | 11981.5479 | 59907.7396 | 112195.0281 | 0 | 476222.9723 | 660307.2879 |  | 17972.3219 | 59907.7396 | 112195.0281 | 0 | 380978.3778 | 571053.4674 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1173735 | 1173735 | 1173735 | 1173735 | 1173735 | C4 | 9984.6233 | 9984.6233 | 37398.3427 | 77569.774 | 158740.9908 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 264 | 264 |  | 47 | 172 | 30 | 6 | 9 |  | 44 | 165 | 30 | 11 | 10 |  | 9 | 0 | 0 | -7 | -2 |  | 41 | 127 | 71 | 14 | 11 |  | 20 | 0 | 0 | -13 | -7 |  | 17 | 114 | 93 | 26 | 14 | [22 empty] | 154561.9681 | 605866.9395 | 477202.853 | 331998.6329 | 774656.0349 | 2344286.4284 |  | 168540.4407 | 633823.8847 | 477202.853 | 176859.0848 | 679411.4405 | 2135837.7036 |  | 146973.6544 | 460490.8248 | 1054633.2644 | 431287.9436 | 806404.2331 | 2899789.9204 |  | 179323.8338 | 460490.8248 | 1054633.2644 | 232709.3221 | 698460.3594 | 2625617.6045 |  | 61505.2793 | 420951.7167 | 1299966.3926 | 809828.4409 | 977844.5031 | 3570096.3326 |  | 136589.6462 | 420951.7167 | 1299966.3926 | 425082.3617 | 571467.5667 | 2854057.684
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 30 | 30 | C1 | 0 | 23 | 3 | 1 | 3 | 30 | 1 | 25 | 4 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 1 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 1 | 5 | 30 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | C1 | 286.0983 | 286.0983 | 1072.4002 | 2211.1731 | 4549.7389 | C1 | 286.0983 | 7152.4572 | 4289.6009 | 0 | 0 | 11728.1564 |  | 0 | 6580.2606 | 3217.2007 | 2211.1731 | 13649.2167 | 25657.8511 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642
|  |  | 68 | 65.1 | C2 | 1 | 49 | 8 | 2 | 8 | 68 | 2 | 57 | 9 | 1 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 12 | 2 | 10 | 68 | 0 | 0 | 0 | -2.9 | 0 | -2.9 | 1 | 34 | 18 | 3 | 12 | 68 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 764662 | 764662 | 764662 | 764662 | 764662 | C2 | 408.7118 | 408.7118 | 1532.0003 | 3158.8187 | 6499.627 | C2 | 817.4237 | 23296.5748 | 13788.0029 | 3158.8187 | 0 | 41060.8201 |  | 408.7118 | 20026.8801 | 12256.0025 | 6317.6374 | 51997.016 | 91006.2479 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002 |  | 408.7118 | 13896.2025 | 27576.0057 | 315.8819 | 77995.524 | 120192.3259
|  |  | 43 | 36.5 | C3 | 1 | 30 | 5 | 2 | 5 | 43 | 1 | 36 | 6 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | 8 | 2 | 7 | 43 | 0 | 0 | 0 | -2 | -4.5 | -6.5 | 1 | 20 | 12 | 2 | 8 | 43 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1146993 | 1146993 | 1146993 | 1146993 | 1146993 | C3 | 613.0678 | 613.0678 | 2298.0005 | 4738.2281 | 9749.4405 | C3 | 613.0678 | 22070.4393 | 13788.0029 | 0 | 0 | 36471.5099 |  | 613.0678 | 18392.0328 | 11490.0024 | 9476.4562 | 48747.2025 | 88718.7616 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088 |  | 613.0678 | 12261.3552 | 27576.0057 | 0 | 34123.0418 | 74573.4704
|  |  | 49 | 47 | C4 | 1 | 34 | 6 | 2 | 6 | 49 | 2 | 39 | 7 | 1 | 3 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 9 | 2 | 7 | 49 | 0 | 0 | 0 | -2 | 0 | -2 | 1 | 24 | 13 | 2 | 9 | 49 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1911655 | 1911655 | 1911655 | 1911655 | 1911655 | C4 | 1021.7796 | 1021.7796 | 3830.0008 | 7897.0468 | 16249.0675 | C4 | 2043.5592 | 39849.4043 | 26810.0055 | 7897.0468 | 48747.2025 | 125347.2184 |  | 1021.7796 | 34740.5063 | 22980.0048 | 15794.0936 | 97494.405 | 172030.7893 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013 |  | 1021.7796 | 24522.7103 | 49790.0103 | 0 | 146241.6075 | 221576.1077
|  |  | 190 | 178.6 |  | 3 | 136 | 22 | 7 | 22 |  | 6 | 157 | 26 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 117 | 34 | 7 | 29 |  | 0 | 0 | 0 | -6.9 | -4.5 |  | 3 | 94 | 51 | 8 | 34 | [22 empty] | 3760.1489 | 92368.8756 | 58675.6121 | 11055.8655 | 48747.2025 | 214607.7047 |  | 2043.5592 | 79739.6798 | 49943.2103 | 33799.3603 | 211887.8402 | 377413.6498 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524 |  | 2043.5592 | 55257.8406 | 113521.2235 | 2527.055 | 281108.8677 | 454458.546
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 51.9831 | 121.1975 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4405 | 4405 | C2 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 11 | 0 | 0 | 0 | -11 | 0 | 0 | 1073 | 2538 | 601 | 193 | 4405 | 22 | 0 | 0 | 0 | -22 | 0 | 0 | 1062 | 2518 | 627 | 198 | 4405 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 74.2616 | 173.1393 | C2 | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 54300.2328 | 44631.2111 | 31511.3483 | 130442.7922 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924 |  | 0 | 0 | 53872.335 | 46562.0122 | 30472.5126 | 130906.8599
|  |  | 342 | 342 | C3 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 197 | 47 | 15 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 195 | 49 | 15 | 342 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 111.3924 | 259.7089 | C3 | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656
|  |  | 8 | 8 | C4 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 185.654 | 432.8482 | C4 | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901
|  |  | 4755 | 4755 |  | 0 | 1158 | 2749 | 642 | 206 |  | 0 | 1158 | 2749 | 642 | 206 |  | 11 | 0 | 0 | 0 | -11 |  | 0 | 1158 | 2740 | 649 | 208 |  | 22 | 0 | 0 | 0 | -22 |  | 0 | 1147 | 2718 | 677 | 213 | [22 empty] | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 60889.8592 | 50052.3066 | 37311.514 | 148253.6799 |  | 0 | 0 | 60889.8592 | 50052.3066 | 35406.982 | 146349.1478 |  | 0 | 0 | 60397.7767 | 52205.8925 | 38177.2104 | 150780.8796 |  | 0 | 0 | 60397.7767 | 52205.8925 | 34368.1463 | 146971.8156
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 48.8085 | 94.7085 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2361 | 2361 | C2 | 471 | 289 | 642 | 591 | 368 | 2361 | 413 | 252 | 642 | 591 | 426 | 2324 | 200.3547 | 0 | 0 | 0 | -200.3547 | 0 | 422 | 303 | 562 | 581 | 493 | 2361 | 431.5407 | 0 | 0 | 0 | -431.5407 | 0 | 58 | 649 | 257 | 698 | 699 | 2361 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 69.7264 | 135.2979 | C2 | 0 | 0 | 13735.5199 | 41208.3279 | 57636.898 | 112580.7458 |  | 0 | 0 | 13735.5199 | 41208.3279 | 49789.6208 | 104733.4686 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 12023.9286 | 40511.0635 | 39594.286 | 92129.2781 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643 |  | 0 | 0 | 5498.4869 | 48669.0573 | 36186.6748 | 90354.2191
|  |  | 196 | 196 | C3 | 43 | 21 | 54 | 50 | 28 | 196 | 38 | 21 | 54 | 50 | 33 | 196 | 27 | 0 | 0 | 0 | -27 | 0 | 36 | 22 | 48 | 49 | 41 | 196 | 55 | 0 | 0 | 0 | -55 | 0 | 5 | 51 | 22 | 59 | 59 | 196 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 104.5897 | 202.9468 | C3 | 0 | 0 | 1732.9862 | 5229.4832 | 6697.2452 | 13659.7146 |  | 0 | 0 | 1732.9862 | 5229.4832 | 5682.5111 | 12644.9805 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 1540.4321 | 5124.8936 | 2841.2555 | 9506.5812 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842 |  | 0 | 0 | 706.0314 | 6170.7902 | 811.7873 | 7688.6089
|  |  | 3 | 3 | C4 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 3 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 0 | 227.8033 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055 |  | 0 | 0 | 0 | 174.3161 | 0 | 174.3161
|  |  | 2560 | 2560 |  | 514 | 310 | 697 | 642 | 397 |  | 451 | 273 | 697 | 642 | 460 |  | 228.3547 | 0 | 0 | 0 | -228.3547 |  | 458 | 325 | 611 | 631 | 535 |  | 488.5407 | 0 | 0 | 0 | -488.5407 |  | 63 | 700 | 279 | 758 | 760 | [22 empty] | 0 | 0 | 15521.9933 | 46612.1272 | 64672.3879 | 126806.5085 |  | 0 | 0 | 15521.9933 | 46612.1272 | 55810.3766 | 117944.4971 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 13617.848 | 45810.2731 | 42435.5416 | 101863.6627 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254 |  | 0 | 0 | 6204.5183 | 55014.1636 | 36998.4621 | 98217.1441
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 |  | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 |  | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 |  | 295143.1241 | 576349.6976 | 1308142.4595 | 433989.3544 | 1339533.0729 | 3953157.7085 |  | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 |  | 245618.8274 | 549989.8896 | 1551834.1523 | 637780.4804 | 1327285.0449 | 4312508.3947
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 643865 | 643837 |  | 108014 | 416640 | 71011 | 32459 | 15741 |  | 100295 | 415570 | 71117 | 33178 | 22842 |  | 17618.5098 | 0 | -420.2 | -3212 | -14000.9098 |  | 67669 | 388473 | 121329 | 34588 | 31809 |  | 34013.601 | 0 | -420.2 | -5318.8052 | -28302.5958 |  | 44233 | 354100 | 157644 | 44376 | 43514 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 |  | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 |  | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 |  | 2526934.4897 | 10502174.0244 | 12998009.1422 | 6262204.0562 | 6950733.498 | 39240055.2104 |  | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 |  | 2217853.9728 | 9600571.0178 | 16497240.1625 | 7968586.2063 | 6077537.5494 | 42361788.9088
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 | LV Network | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 841735.823 | 3918769.2646 | 3413427.519 | 3542244.9215 | 1917071.2752 | 13633248.8032 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 | LV Network | 937169.9828 | 3492896.8826 | 3723540.7301 | 4525777.4676 | 1534019.4268 | 14213404.4898
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 | HV Network | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 | HV Network | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 | HV Network | 1027512.9079 | 4821536.9106 | 6832264.3794 | 1706351.5584 | 2202491.8357 | 16590157.592 | HV Network | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 | HV Network | 719355.4816 | 4511695.2956 | 9086314.1115 | 2063709.9566 | 1967105.026 | 18348179.8713
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 | EHV Network | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 | EHV Network | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 | EHV Network | 362542.6347 | 1185518.1516 | 1444174.7843 | 579618.2218 | 1491637.3142 | 5063491.1067 | EHV Network | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 | EHV Network | 315709.6809 | 1045988.9501 | 2135551.1686 | 741318.3017 | 1249128.0517 | 5487696.153
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 | 132kV Network | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 | 132kV Network | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 | 132kV Network | 295143.1241 | 576349.6976 | 1308142.4595 | 433989.3544 | 1339533.0729 | 3953157.7085 | 132kV Network | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 | 132kV Network | 245618.8274 | 549989.8896 | 1551834.1523 | 637780.4804 | 1327285.0449 | 4312508.3947
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 | Total | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 | Total | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 | Total | 2526934.4897 | 10502174.0244 | 12998009.1422 | 6262204.0562 | 6950733.498 | 39240055.2104 | Total | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 | Total | 2217853.9728 | 9600571.0178 | 16497240.1625 | 7968586.2063 | 6077537.5494 | 42361788.9088
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EPN - Refurb
HI4: Secondary deliverables RIIO-ED1 - refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 64 | 64 | C1 | 8 | 25 | 31 | 0 | 0 | 64 | 8 | 25 | 31 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 33 | 2 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 33 | 6 | 1 | 64 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | C1 | 7.8518 | 17.9786 | 55.6367 | 90.6791 | 145.6343 | C1 | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064
|  |  | 29908 | 29908 | C2 | 3760 | 11129 | 14935 | 84 | 0 | 29908 | 3531 | 10762 | 14935 | 265 | 48 | 29541 | 0 | 0 | 0 | 0 | 0 | 0 | 2069 | 11728 | 15262 | 789 | 60 | 29908 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 11673 | 15906 | 1851 | 249 | 29908 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10371 | 10371 | 10371 | 10371 | 10371 | C2 | 11.2168 | 25.6837 | 79.481 | 129.5416 | 208.049 | C2 | 39606.6007 | 276408.3808 | 1187048.316 | 34328.5337 | 9986.3537 | 1547378.1849 |  | 42175.2531 | 285834.3124 | 1187048.316 | 10881.4975 | 0 | 1525939.3789 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369
|  |  | 63 | 63 | C3 | 8 | 25 | 30 | 0 | 0 | 63 | 7 | 25 | 30 | 1 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | 33 | 1 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 23 | 33 | 5 | 1 | 63 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | C3 | 16.8252 | 38.5256 | 119.2215 | 194.3125 | 312.0736 | C3 | 117.7766 | 963.1401 | 3576.6437 | 194.3125 | 0 | 4851.873 |  | 134.6019 | 963.1401 | 3576.6437 | 0 | 0 | 4674.3858 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581
|  |  | 5 | 5 | C4 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 2 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | C4 | 28.0421 | 64.2093 | 198.7024 | 323.8541 | 520.1226 | C4 | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526
|  |  | 30040 | 30040 |  | 3777 | 11181 | 14998 | 84 | 0 |  | 3547 | 10814 | 14998 | 266 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 2078 | 11779 | 15331 | 792 | 60 |  | 0 | 0 | 0 | 0 | 0 |  | 230 | 11722 | 15975 | 1862 | 251 | [22 empty] | 39815.2336 | 277949.4051 | 1192747.1017 | 34522.8462 | 9986.3537 | 1555020.9402 |  | 42400.7112 | 287375.3367 | 1192747.1017 | 10881.4975 | 0 | 1533404.647 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274
| LV UGB |  | 812 | 812 | C1 | 107 | 91 | 305 | 287 | 22 | 812 | 101 | 91 | 305 | 287 | 28 | 812 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 228 | 393 | 37 | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 39 | 126 | 513 | 52 | 812 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | C1 | 11.222 | 16.833 | 56.11 | 123.4421 | 241.2731 | C1 | 1133.4225 | 1531.8036 | 17113.5572 | 35427.8689 | 6755.6468 | 61962.299 |  | 1200.7545 | 1531.8036 | 17113.5572 | 35427.8689 | 5308.0082 | 60581.9924 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285
|  |  | 25739 | 25739 | C2 | 3391 | 2894 | 9654 | 9102 | 698 | 25739 | 3189 | 2894 | 9654 | 9102 | 900 | 25739 | 0 | 0 | 0 | 0 | 0 | 0 | 2825 | 2088 | 7220 | 12437 | 1171 | 25741 | 0 | 0 | 0 | 0 | 0 | 0 | 2604 | 1240 | 4005 | 16258 | 1634 | 25741 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11183 | 11183 | 11183 | 11183 | 11183 | C2 | 16.0314 | 24.0472 | 80.1572 | 176.3458 | 344.6759 | C2 | 51124.2472 | 69592.4607 | 773837.3821 | 1605099.3654 | 310208.2731 | 2809861.7285 |  | 54362.5971 | 69592.4607 | 773837.3821 | 1605099.3654 | 240583.7496 | 2743475.5549 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995
|  |  | 5276 | 5276 | C3 | 695 | 593 | 1979 | 1866 | 143 | 5276 | 654 | 593 | 1979 | 1866 | 185 | 5277 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 428 | 1480 | 2549 | 240 | 5276 | 0 | 0 | 0 | 0 | 0 | 0 | 534 | 254 | 821 | 3333 | 335 | 5277 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | C3 | 24.0472 | 36.0707 | 120.2358 | 264.5187 | 517.0138 | C3 | 15726.838 | 21389.9426 | 237946.5785 | 493591.8615 | 95647.5509 | 864302.7715 |  | 16712.7713 | 21389.9426 | 237946.5785 | 493591.8615 | 73932.9718 | 843574.1257 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958
|  |  | 2285 | 2285 | C4 | 301 | 257 | 857 | 808 | 62 | 2285 | 283 | 257 | 857 | 808 | 80 | 2285 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 185 | 641 | 1104 | 104 | 2285 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 110 | 355 | 1443 | 145 | 2284 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | C4 | 40.0786 | 60.1179 | 200.3929 | 440.8645 | 861.6896 | C4 | 11342.2405 | 15450.2958 | 171736.7507 | 356218.4924 | 68935.1718 | 623682.9512 |  | 12063.6551 | 15450.2958 | 171736.7507 | 356218.4924 | 53424.7581 | 608893.9521 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454
|  |  | 34112 | 34112 |  | 4494 | 3835 | 12795 | 12063 | 925 |  | 4227 | 3835 | 12795 | 12063 | 1193 |  | 0 | 0 | 0 | 0 | 0 |  | 3744 | 2767 | 9569 | 16483 | 1552 |  | 0 | 0 | 0 | 0 | 0 |  | 3451 | 1643 | 5307 | 21547 | 2166 | [22 empty] | 79326.7482 | 107964.5026 | 1200634.2684 | 2490337.5883 | 481546.6426 | 4359809.7501 |  | 84339.778 | 107964.5026 | 1200634.2684 | 2490337.5883 | 373249.4877 | 4256525.6251 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | C1 | 14.4557 | 14.4557 | 29.0421 | 79.9779 | 158.5738 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 246106 | 246106 | C2 | 44138 | 179341 | 6435 | 8501 | 7691 | 246106 | 40338 | 179599 | 6435 | 8501 | 11491 | 246364 | 0 | 0 | 0 | 0 | 0 | 0 | 26121 | 170027 | 31277 | 5151 | 13530 | 246106 | 0 | 0 | 0 | 0 | 0 | 0 | 23261 | 151153 | 47037 | 6192 | 18463 | 246106 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | C2 | 20.651 | 20.651 | 41.4888 | 114.2542 | 226.534 | C2 | 833019.9377 | 3708898.5026 | 266980.178 | 971274.7708 | 2603101.8733 | 8383275.2624 |  | 911493.7283 | 3703570.5452 | 266980.178 | 971274.7708 | 1742272.7793 | 7595592.0017 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384
|  |  | 1255 | 1255 | C3 | 115 | 1016 | 14 | 62 | 48 | 1255 | 115 | 1016 | 14 | 62 | 48 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 868 | 159 | 26 | 88 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 771 | 240 | 32 | 113 | 1255 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | C3 | 30.9765 | 30.9765 | 62.2331 | 171.3813 | 339.801 | C3 | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146
|  |  | 2 | 2 | C4 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | C4 | 51.6275 | 51.6275 | 103.7219 | 285.6354 | 566.3349 | C4 | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624
|  |  | 247363 | 247363 |  | 44254 | 180357 | 6449 | 8563 | 7740 |  | 40454 | 180615 | 6449 | 8563 | 11540 |  | 0 | 0 | 0 | 0 | 0 |  | 26235 | 170896 | 31436 | 5177 | 13619 |  | 0 | 0 | 0 | 0 | 0 |  | 23360 | 151925 | 47277 | 6224 | 18577 | [22 empty] | 836633.8623 | 3740370.6228 | 267851.442 | 981900.4094 | 2619978.6542 | 8446734.9907 |  | 915107.6529 | 3735042.6654 | 267851.442 | 981900.4094 | 1759149.5602 | 7659051.73 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 |  | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 3046 | 3046 | C1 | 1055 | 1042 | 885 | 52 | 12 | 3046 | 1044 | 1010 | 885 | 84 | 23 | 3046 | 0 | 4 | 0 | -4 | 0 | 0 | 967 | 904 | 830 | 246 | 99 | 3046 | 0 | 46 | 0 | -46 | 0 | 0 | 561 | 1107 | 785 | 300 | 293 | 3046 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33586 | 33586 | 33586 | 33586 | 33586 | C1 | 58.8156 | 58.8156 | 220.1504 | 404.4235 | 556.6962 | C1 | 61403.5232 | 59403.7916 | 194833.0619 | 33971.5713 | 12804.0121 | 362415.9602 |  | 62050.4952 | 61285.892 | 194833.0619 | 21030.0203 | 6680.3541 | 345879.8236 |  | 56874.7193 | 53169.3343 | 182724.7925 | 99488.1731 | 55112.9217 | 447369.9409 |  | 56874.7193 | 53404.5968 | 182724.7925 | 97870.4793 | 55112.9217 | 445987.5096 |  | 32995.5714 | 65108.9082 | 172818.0267 | 121327.0404 | 163111.9803 | 555361.527 |  | 32995.5714 | 67814.4275 | 172818.0267 | 102723.5609 | 163111.9803 | 539463.5667
|  |  | 1695 | 1695 | C2 | 261 | 967 | 397 | 50 | 20 | 1695 | 232 | 799 | 397 | 65 | 34 | 1527 | 0 | 2 | 0 | -2 | 0 | 0 | 253 | 702 | 545 | 115 | 80 | 1695 | 0 | 29 | 0 | -29 | 0 | 0 | 153 | 597 | 583 | 192 | 170 | 1695 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47980 | 47980 | 47980 | 47980 | 47980 | C2 | 84.0223 | 84.0223 | 314.5005 | 577.7478 | 795.2803 | C2 | 19493.182 | 67133.8465 | 124856.6999 | 37553.6077 | 27039.5287 | 276076.8648 |  | 21929.8297 | 81249.599 | 124856.6999 | 28887.3906 | 15905.6051 | 272829.1243 |  | 21257.651 | 58983.6799 | 171402.7744 | 66440.9983 | 63622.4204 | 381707.5241 |  | 21257.651 | 59151.7246 | 171402.7744 | 65285.5027 | 63622.4204 | 380720.0732 |  | 12855.4174 | 50161.3347 | 183353.7935 | 110927.5798 | 135197.6434 | 492495.7688 |  | 12855.4174 | 52597.9824 | 183353.7935 | 94172.8933 | 135197.6434 | 478177.73
|  |  | 618 | 618 | C3 | 127 | 359 | 113 | 17 | 2 | 618 | 122 | 359 | 113 | 19 | 5 | 618 | 0 | 1 | 0 | -1 | 0 | 0 | 113 | 256 | 178 | 34 | 37 | 618 | 0 | 10 | 0 | -10 | 0 | 0 | 64 | 179 | 266 | 54 | 55 | 618 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71970 | 71970 | 71970 | 71970 | 71970 | C3 | 126.0335 | 126.0335 | 471.7508 | 866.6217 | 1192.9204 | C3 | 15376.0875 | 45246.028 | 53307.8353 | 16465.8126 | 5964.6019 | 136360.3654 |  | 16006.255 | 45246.028 | 53307.8353 | 14732.5692 | 2385.8408 | 131678.5283 |  | 14241.786 | 32264.5771 | 83971.6344 | 29465.1384 | 44138.0542 | 204081.19 |  | 14241.786 | 32390.6106 | 83971.6344 | 28598.5167 | 44138.0542 | 203340.6018 |  | 8066.1443 | 22559.9972 | 125485.7009 | 46797.5727 | 65610.621 | 268520.0362 |  | 8066.1443 | 23820.3323 | 125485.7009 | 38131.3556 | 65610.621 | 261114.154
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119950 | 119950 | 119950 | 119950 | 119950 | C4 | 210.0558 | 210.0558 | 786.2513 | 1444.3695 | 1988.2006 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5359 | 5359 |  | 1443 | 2368 | 1395 | 119 | 34 |  | 1398 | 2168 | 1395 | 168 | 62 |  | 0 | 7 | 0 | -7 | 0 |  | 1333 | 1862 | 1553 | 395 | 216 |  | 0 | 85 | 0 | -85 | 0 |  | 778 | 1883 | 1634 | 546 | 518 | [22 empty] | 96272.7927 | 171783.6662 | 372997.5972 | 87990.9917 | 45808.1427 | 774853.1904 |  | 99986.58 | 187781.5189 | 372997.5972 | 64649.9801 | 24971.8 | 750387.4762 |  | 92374.1563 | 144417.5913 | 438099.2014 | 195394.3098 | 162873.3962 | 1033158.655 |  | 92374.1563 | 144946.932 | 438099.2014 | 191754.4986 | 162873.3962 | 1030048.1845 |  | 53917.1331 | 137830.2401 | 481657.5211 | 279052.1929 | 363920.2447 | 1316377.332 |  | 53917.1331 | 144232.7421 | 481657.5211 | 235027.8097 | 363920.2447 | 1278755.4507
| HV Switchgear (GM) - Distribution |  | 16951 | 16951 | C1 | 7581 | 8348 | 596 | 426 | 0 | 16951 | 7566 | 8348 | 596 | 426 | 16 | 16952 | 0 | 0 | 0 | 0 | 0 | 0 | 3630 | 12149 | 623 | 533 | 16 | 16951 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 14318 | 1090 | 577 | 96 | 16951 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | C1 | 11.2991 | 11.2991 | 42.4721 | 77.873 | 133.2047 | C1 | 85488.9241 | 94324.8134 | 25313.3509 | 33173.9097 | 2131.2749 | 240432.273 |  | 85658.4105 | 94324.8134 | 25313.3509 | 33173.9097 | 0 | 238470.4845 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348
|  |  | 15770 | 15770 | C2 | 1149 | 9824 | 4343 | 454 | 0 | 15770 | 474 | 9350 | 4343 | 798 | 548 | 15513 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 6422 | 4444 | 2126 | 1770 | 15770 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 4850 | 4656 | 1768 | 3579 | 15770 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 28897 | 28897 | 28897 | 28897 | 28897 | C2 | 16.1416 | 16.1416 | 60.6744 | 111.2472 | 190.2924 | C2 | 7651.0989 | 150923.5754 | 263508.8273 | 88775.2514 | 104280.2376 | 615138.9907 |  | 18546.6511 | 158574.6743 | 263508.8273 | 50506.2207 | 0 | 491136.3735 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113
|  |  | 3 | 3 | C3 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | C3 | 24.2123 | 24.2123 | 91.0116 | 166.8708 | 285.4386 | C3 | 0 | 24.2123 | 0 | 333.7415 | 0 | 357.9539 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | C4 | 40.3539 | 40.3539 | 151.6859 | 278.118 | 475.731 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 32724 | 32724 |  | 8732 | 18173 | 4939 | 880 | 0 |  | 8040 | 17699 | 4939 | 1226 | 564 |  | 0 | 0 | 0 | 0 | 0 |  | 4640 | 18572 | 5067 | 2659 | 1786 |  | 0 | 0 | 0 | 0 | 0 |  | 1789 | 19169 | 5746 | 2345 | 3675 | [22 empty] | 93140.023 | 245272.6012 | 288822.1782 | 122282.9027 | 106411.5125 | 855929.2176 |  | 104253.4863 | 252923.7001 | 288822.1782 | 83680.1305 | 0 | 729679.495 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831
| HV Transformer (GM) |  | 15354 | 15354 | C1 | 2254 | 4991 | 8109 | 0 | 0 | 15354 | 2175 | 4991 | 8109 | 71 | 8 | 15354 | 0 | 0 | 0 | 0 | 0 | 0 | 1306 | 5562 | 8385 | 91 | 10 | 15354 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6088 | 8844 | 291 | 52 | 15354 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | C1 | 33.5005 | 40.8282 | 115.1569 | 219.6408 | 370.4805 | C1 | 72863.5281 | 203773.5627 | 933807.1344 | 15594.4939 | 2963.844 | 1229002.5632 |  | 75510.0655 | 203773.5627 | 933807.1344 | 0 | 0 | 1213090.7626 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269
|  |  | 10916 | 10916 | C2 | 1472 | 4148 | 5296 | 0 | 0 | 10916 | 1285 | 3757 | 5432 | 46 | 5 | 10525 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 4205 | 5611 | 65 | 7 | 10916 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 4563 | 5928 | 201 | 37 | 10916 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 54257 | 54257 | 54257 | 54257 | 54257 | C2 | 47.8578 | 58.326 | 164.5098 | 313.7725 | 529.2579 | C2 | 61497.2963 | 219130.7997 | 893617.3835 | 14433.5356 | 2646.2893 | 1191325.3045 |  | 70446.7083 | 241936.2676 | 871244.047 | 0 | 0 | 1183627.0229 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456
|  |  | 4387 | 4387 | C3 | 644 | 1426 | 2317 | 0 | 0 | 4387 | 622 | 1426 | 2317 | 20 | 2 | 4387 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 1589 | 2396 | 26 | 3 | 4387 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1740 | 2528 | 82 | 15 | 4387 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | C3 | 71.7867 | 87.489 | 246.7647 | 470.6588 | 793.8868 | C3 | 44651.3443 | 124759.3241 | 571753.9058 | 9413.1754 | 1587.7736 | 752165.5233 |  | 46230.6523 | 124759.3241 | 571753.9058 | 0 | 0 | 742743.8823 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676
|  |  | 1566 | 1566 | C4 | 230 | 509 | 827 | 0 | 0 | 1566 | 222 | 509 | 827 | 7 | 1 | 1566 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 567 | 855 | 10 | 1 | 1566 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 621 | 900 | 32 | 5 | 1566 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | C4 | 119.6445 | 145.815 | 411.2746 | 784.4313 | 1323.1446 | C4 | 26561.0891 | 74219.841 | 340124.0686 | 5491.019 | 1323.1446 | 447719.1623 |  | 27518.2454 | 74219.841 | 340124.0686 | 0 | 0 | 441862.155 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151
|  |  | 32223 | 32223 |  | 4600 | 11074 | 16549 | 0 | 0 |  | 4304 | 10683 | 16685 | 144 | 16 |  | 0 | 0 | 0 | 0 | 0 |  | 2840 | 11923 | 17247 | 192 | 21 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 13012 | 18200 | 606 | 109 | [22 empty] | 205573.2579 | 621883.5276 | 2739302.4923 | 44932.224 | 8521.0515 | 3620212.5533 |  | 219705.6716 | 644688.9954 | 2716929.1558 | 0 | 0 | 3581323.8228 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 135 | 135 | C1 | 12 | 103 | 14 | 2 | 4 | 135 | 12 | 103 | 14 | 2 | 4 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 90 | 21 | 4 | 8 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 81 | 34 | 5 | 10 | 135 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | C1 | 17.6591 | 17.6591 | 66.4486 | 139.6696 | 215.3203 | C1 | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859
|  |  | 196526 | 196526 | C2 | 30344 | 147825 | 6695 | 6814 | 4848 | 196526 | 28983 | 147899 | 6695 | 6814 | 6209 | 196600 | 0 | 0 | 0 | 0 | 0 | 0 | 19315 | 130607 | 30746 | 5743 | 10115 | 196526 | 0 | 0 | 0 | 0 | 0 | 0 | 9135 | 117840 | 49495 | 7489 | 12567 | 196526 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | C2 | 25.2273 | 25.2273 | 94.9265 | 199.5279 | 307.6005 | C2 | 731162.86 | 3731092.5658 | 635533.0554 | 1359583.403 | 1909891.3827 | 8367263.2669 |  | 765497.2165 | 3729225.7455 | 635533.0554 | 1359583.403 | 1491247.1289 | 7981086.5493 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617
|  |  | 17623 | 17623 | C3 | 3370 | 13180 | 604 | 469 | 0 | 17623 | 2845 | 13180 | 604 | 469 | 525 | 17623 | 0 | 0 | 0 | 0 | 0 | 0 | 2134 | 11719 | 2763 | 508 | 499 | 17623 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 10577 | 4441 | 664 | 719 | 17623 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | C3 | 37.841 | 37.841 | 142.3898 | 299.2919 | 461.4007 | C3 | 107657.5063 | 498743.7375 | 86003.4277 | 140367.9078 | 242235.3783 | 1075007.9576 |  | 127524.0057 | 498743.7375 | 86003.4277 | 140367.9078 | 0 | 852639.0787 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35
|  |  | 59 | 59 | C4 | 14 | 38 | 1 | 6 | 0 | 59 | 6 | 38 | 1 | 6 | 8 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 2 | 9 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29 | 11 | 9 | 0 | 59 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | C4 | 63.0683 | 63.0683 | 237.3163 | 498.8199 | 769.0012 | C4 | 378.4095 | 2396.5936 | 237.3163 | 2992.9191 | 6152.0096 | 12157.2481 |  | 882.9555 | 2396.5936 | 237.3163 | 2992.9191 | 0 | 6509.7846 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199
|  |  | 214343 | 214343 |  | 33740 | 161146 | 7314 | 7291 | 4852 |  | 31846 | 161220 | 7314 | 7291 | 6746 |  | 0 | 0 | 0 | 0 | 0 |  | 21474 | 142451 | 33532 | 6264 | 10622 |  | 0 | 0 | 0 | 0 | 0 |  | 10372 | 128527 | 53981 | 8167 | 13296 | [22 empty] | 839410.6852 | 4234051.7852 | 722704.0793 | 1503223.5691 | 2159140.0519 | 9458530.1707 |  | 894116.087 | 4232184.9649 | 722704.0793 | 1503223.5691 | 1492108.4102 | 8844337.1106 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 |  | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 |  | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 |  | 854397.3038 | 4822066.2514 | 6879643.2097 | 1833213.6207 | 3856277.0233 | 18245597.4088 |  | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 |  | 370142.0039 | 4518097.7976 | 9133692.9418 | 2365507.4436 | 5314651.5198 | 21702091.7066
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 868 | 868 | C1 | 416 | 225 | 108 | 95 | 24 | 868 | 398 | 225 | 108 | 95 | 42 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 209 | 64 | 111 | 101 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 302 | 41 | 82 | 172 | 868 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | C1 | 165.9387 | 165.9387 | 626.127 | 1146.0231 | 1956.2345 | C1 | 66043.6106 | 37336.2121 | 67621.7214 | 108872.194 | 82161.8485 | 362035.5866 |  | 69030.5076 | 37336.2121 | 67621.7214 | 108872.194 | 46949.6277 | 329810.2627 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216
|  |  | 437 | 437 | C2 | 139 | 148 | 49 | 84 | 17 | 437 | 102 | 101 | 49 | 90 | 48 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 140 | 23 | 66 | 111 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 130 | 42 | 26 | 158 | 437 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | C2 | 237.0553 | 237.0553 | 894.4672 | 1637.1758 | 2794.6207 | C2 | 24179.6421 | 23942.5868 | 43828.8935 | 147345.8264 | 134141.7935 | 373438.7423 |  | 32950.6887 | 35084.1866 | 43828.8935 | 137522.7713 | 47508.5519 | 296895.092 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369
|  |  | 82 | 82 | C3 | 29 | 25 | 10 | 16 | 2 | 82 | 25 | 25 | 10 | 16 | 6 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 28 | 3 | 10 | 18 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | 0 | 6 | 25 | 82 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | C3 | 355.583 | 355.583 | 1341.7008 | 2455.7638 | 4191.931 | C3 | 8889.5743 | 8889.5743 | 13417.0082 | 39292.2204 | 25151.5863 | 95639.9635 |  | 10311.9062 | 8889.5743 | 13417.0082 | 39292.2204 | 8383.8621 | 80294.5712 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904
|  |  | 88 | 88 | C4 | 28 | 33 | 12 | 14 | 1 | 88 | 18 | 33 | 12 | 14 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 10 | 14 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 27 | 9 | 10 | 21 | 88 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | C4 | 592.6383 | 592.6383 | 2236.168 | 4092.9396 | 6986.5517 | C4 | 10667.4892 | 19557.0635 | 26834.0164 | 57301.1547 | 76852.0692 | 191211.793 |  | 16593.872 | 19557.0635 | 26834.0164 | 57301.1547 | 6986.5517 | 127272.6584 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133
|  |  | 1475 | 1475 |  | 612 | 431 | 179 | 209 | 44 |  | 543 | 384 | 179 | 215 | 107 |  | 0 | 0 | 0 | 0 | 0 |  | 528 | 404 | 100 | 201 | 242 |  | 0 | 0 | 0 | 0 | 0 |  | 381 | 502 | 92 | 124 | 376 | [22 empty] | 109780.3162 | 89725.4366 | 151701.6395 | 352811.3955 | 318307.2976 | 1022326.0853 |  | 128886.9746 | 100867.0364 | 151701.6395 | 342988.3404 | 109828.5935 | 834272.5842 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818
| EHV Transformer |  | 397 | 397 | C1 | 58 | 263 | 49 | 15 | 12 | 397 | 51 | 262 | 49 | 21 | 14 | 397 | 0 | 4 | 0 | 0 | -4 | 0 | 49 | 211 | 104 | 10 | 23 | 397 | 0 | 11 | 0 | -7 | -4 | 0 | 16 | 188 | 137 | 28 | 28 | 397 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | C1 | 914.8668 | 914.8668 | 3426.7195 | 7107.5305 | 14545.0524 | C1 | 46658.209 | 239695.1127 | 167909.2578 | 149258.1402 | 203630.7342 | 807151.454 |  | 53062.2769 | 240609.9796 | 167909.2578 | 106612.9573 | 174540.6294 | 742735.101 |  | 44828.4753 | 193036.9038 | 356378.833 | 71075.3049 | 334536.2063 | 999855.7232 |  | 44828.4753 | 196696.3711 | 356378.833 | 71075.3049 | 276355.9965 | 945334.9808 |  | 14637.8695 | 171994.9664 | 469460.5781 | 199010.8537 | 407261.4685 | 1262365.7361 |  | 14637.8695 | 182058.5017 | 469460.5781 | 149258.1402 | 349081.2587 | 1164496.3482
|  |  | 456 | 456 | C2 | 46 | 344 | 46 | 9 | 11 | 456 | 42 | 341 | 46 | 13 | 13 | 455 | 0 | 3 | 0 | 0 | -3 | 0 | 38 | 270 | 122 | 9 | 17 | 456 | 0 | 12 | 0 | -8 | -4 | 0 | 14 | 193 | 198 | 33 | 18 | 456 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | C2 | 1306.9526 | 1306.9526 | 4895.3136 | 10153.615 | 20778.6464 | C2 | 54892.0106 | 445670.8476 | 225184.4274 | 131996.9948 | 270122.4026 | 1127866.6829 |  | 60119.8211 | 449591.7055 | 225184.4274 | 91382.5348 | 228565.1099 | 1054843.5987 |  | 49664.2 | 352877.2107 | 597228.2641 | 91382.5348 | 353236.988 | 1444389.1976 |  | 49664.2 | 356798.0686 | 597228.2641 | 91382.5348 | 290901.0489 | 1385974.1164 |  | 18297.3369 | 252241.858 | 969272.1007 | 335069.2944 | 374015.6343 | 1948896.2243 |  | 18297.3369 | 267925.2896 | 969272.1007 | 253840.3746 | 290901.0489 | 1800236.1506
|  |  | 28 | 28 | C3 | 13 | 11 | 3 | 0 | 1 | 28 | 12 | 9 | 3 | 2 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 4 | 1 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 3 | 2 | 2 | 28 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | C3 | 1960.4289 | 1960.4289 | 7342.9705 | 15230.4225 | 31167.9695 | C3 | 23525.1474 | 17643.8605 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 25485.5763 | 21564.7184 | 22028.9114 | 0 | 31167.9695 | 100247.1757 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033
|  |  | 28 | 28 | C4 | 6 | 20 | 2 | 0 | 0 | 28 | 6 | 20 | 2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | 28 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | C4 | 3267.3816 | 3267.3816 | 12238.2841 | 25384.0375 | 51946.6159 | C4 | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069
|  |  | 909 | 909 |  | 123 | 638 | 100 | 24 | 24 |  | 111 | 632 | 100 | 36 | 29 |  | 0 | 7 | 0 | 0 | -7 |  | 102 | 509 | 236 | 20 | 42 |  | 0 | 23 | 0 | -15 | -8 |  | 35 | 416 | 347 | 63 | 48 | [22 empty] | 144679.6564 | 768357.4525 | 439599.1649 | 311715.98 | 536089.0759 | 2200441.3295 |  | 158271.9638 | 777114.0351 | 439599.1649 | 197995.4922 | 434273.7087 | 2007254.3646 |  | 130433.8727 | 623024.3198 | 1056408.6835 | 177688.2622 | 750109.1333 | 2737664.2714 |  | 130433.8727 | 630604.645 | 1056408.6835 | 177688.2622 | 629592.9844 | 2624728.4478 |  | 42737.3511 | 517683.9376 | 1570906.1471 | 564540.993 | 843613.0419 | 3539481.4706 |  | 42737.3511 | 543430.9045 | 1570906.1471 | 433559.3598 | 702318.2467 | 3292952.009
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 277 | 277 | C1 | 24 | 149 | 75 | 12 | 17 | 277 | 24 | 194 | 56 | 2 | 32 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 148 | 92 | 8 | 27 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 102 | 126 | 13 | 34 | 277 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | C1 | 119.927 | 119.927 | 449.5301 | 926.8824 | 1907.1654 | C1 | 2878.2491 | 23265.8473 | 25173.6858 | 1853.7648 | 61029.2928 | 114200.8398 |  | 2878.2491 | 17869.1301 | 33714.7578 | 11122.5886 | 32421.8118 | 98006.5374 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006
|  |  | 199 | 199 | C2 | 17 | 106 | 54 | 10 | 12 | 199 | 12 | 142 | 46 | 2 | 19 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 106 | 65 | 7 | 19 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 72 | 91 | 9 | 25 | 199 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 320532 | 320532 | 320532 | 320532 | 320532 | C2 | 171.3244 | 171.3244 | 642.1859 | 1324.1177 | 2724.522 | C2 | 2055.8922 | 24328.0583 | 29540.5497 | 2648.2354 | 51765.918 | 110338.6536 |  | 2912.514 | 18160.3815 | 34678.0365 | 13241.1769 | 32694.264 | 101686.373 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249
|  |  | 69 | 69 | C3 | 6 | 37 | 19 | 3 | 4 | 69 | 12 | 43 | 13 | 1 | 2 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 23 | 2 | 7 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 31 | 3 | 8 | 69 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 480798 | 480798 | 480798 | 480798 | 480798 | C3 | 256.9865 | 256.9865 | 963.2788 | 1986.1765 | 4086.783 | C3 | 3083.8384 | 11050.4208 | 12522.6243 | 1986.1765 | 8173.566 | 36816.6261 |  | 1541.9192 | 9508.5016 | 18302.2971 | 5958.5296 | 16347.132 | 51658.3795 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725
|  |  | 11 | 11 | C4 | 1 | 6 | 3 | 0 | 1 | 11 | 0 | 9 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 1 | 1 | 11 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 801330 | 801330 | 801330 | 801330 | 801330 | C4 | 428.3109 | 428.3109 | 1605.4647 | 3310.2942 | 6811.305 | C4 | 0 | 3854.798 | 3210.9293 | 0 | 0 | 7065.7273 |  | 428.3109 | 2569.8653 | 4816.394 | 0 | 6811.305 | 14625.8752 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166
|  |  | 556 | 556 |  | 48 | 298 | 151 | 25 | 34 |  | 48 | 388 | 117 | 5 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 4 | 297 | 184 | 17 | 54 |  | 0 | 0 | 0 | 0 | 0 |  | 4 | 205 | 253 | 26 | 68 | [22 empty] | 8017.9798 | 62499.1243 | 70447.7891 | 6488.1767 | 120968.7768 | 268421.8467 |  | 7760.9932 | 48107.8786 | 91511.4853 | 30322.2951 | 88274.5128 | 265977.1651 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 846 | 846 | C1 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 351 | 204 | 247 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 317 | 237 | 248 | 846 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 36.5855 | 85.2982 | C1 | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063
|  |  | 18 | 18 | C2 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 52.265 | 121.8546 | C2 | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662
|  |  | 2 | 2 | C3 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 78.3974 | 182.7819 | C3 | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819
|  |  | 287 | 287 | C4 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 119 | 69 | 84 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 80 | 84 | 287 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 130.6624 | 304.6366 | C4 | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215
|  |  | 1153 | 1153 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 478 | 278 | 337 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 432 | 323 | 338 | [22 empty] | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076
| EHV OHL Support - Poles |  | 7548 | 7548 | C1 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 0 | 0 | 0 | 0 | 0 | 0 | 877 | 5407 | 606 | 139 | 519 | 7548 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 4922 | 1093 | 176 | 632 | 7548 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | C1 | 12.5427 | 12.5427 | 47.1998 | 99.2168 | 152.9599 | C1 | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392
|  |  | 27483 | 27483 | C2 | 4303 | 19734 | 1275 | 1189 | 982 | 27483 | 3986 | 19740 | 1275 | 1189 | 1299 | 27489 | 0 | 0 | 0 | 0 | 0 | 0 | 3193 | 19693 | 2205 | 504 | 1888 | 27483 | 0 | 0 | 0 | 0 | 0 | 0 | 2641 | 17922 | 3979 | 640 | 2301 | 27483 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 52273 | 52273 | 52273 | 52273 | 52273 | C2 | 17.9181 | 17.9181 | 67.4283 | 141.7383 | 218.5142 | C2 | 71421.5511 | 353703.3165 | 85971.0194 | 168526.8472 | 283849.8906 | 963472.6248 |  | 77101.5892 | 353595.8079 | 85971.0194 | 168526.8472 | 214580.9027 | 899776.1663 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | C3 | 26.8772 | 26.8772 | 101.1424 | 212.6075 | 327.7712 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | C4 | 44.7953 | 44.7953 | 168.5706 | 354.3458 | 546.2854 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 35031 | 35031 |  | 5484 | 25155 | 1625 | 1515 | 1252 |  | 5167 | 25161 | 1625 | 1515 | 1569 |  | 0 | 0 | 0 | 0 | 0 |  | 4070 | 25100 | 2811 | 643 | 2407 |  | 0 | 0 | 0 | 0 | 0 |  | 3366 | 22844 | 5072 | 816 | 2933 | [22 empty] | 86234.4454 | 421697.1349 | 102490.9408 | 200871.5289 | 325149.0664 | 1136443.1163 |  | 91914.4834 | 421589.6263 | 102490.9408 | 200871.5289 | 255880.0785 | 1072746.6578 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546
| EHV OHL Fittings and Conductors (Tower Lines) |  | 335 | 335 | C1 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 188 | 97 | 16 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 102 | 154 | 50 | 335 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 34.3512 | 66.6554 | C1 | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708
|  |  | 17 | 17 | C2 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 8 | 3 | 17 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 49.0731 | 95.222 | C2 | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 73.6097 | 142.833 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 163 | 163 | C4 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 92 | 47 | 8 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 75 | 24 | 163 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 122.6829 | 238.0551 | C4 | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401
|  |  | 515 | 515 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 52 | 290 | 149 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 44 | 157 | 237 | 77 | [22 empty] | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 |  | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 |  | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 |  | 308772.0556 | 1193098.4768 | 1446293.9977 | 626776.6981 | 1977709.1553 | 5552650.3835 |  | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 |  | 179195.9368 | 1071735.9169 | 2137670.3819 | 801495.0587 | 2560657.7414 | 6750755.0358
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 188 | 188 | C1 | 70 | 62 | 25 | 18 | 13 | 188 | 39 | 62 | 25 | 18 | 44 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 63 | 27 | 14 | 36 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 58 | 26 | 12 | 50 | 188 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | C1 | 579.6435 | 579.6435 | 2212.3775 | 3916.6144 | 6007.2213 | C1 | 22606.0951 | 35937.8947 | 55309.4371 | 70499.0596 | 264317.7374 | 448670.2238 |  | 40575.0424 | 35937.8947 | 55309.4371 | 70499.0596 | 78093.877 | 280415.3107 |  | 27822.8862 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 395167.1853 |  | 27822.8862 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 395167.1853 |  | 24345.0254 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 462846.5991 |  | 24345.0254 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 462846.5991
|  |  | 51 | 51 | C2 | 26 | 13 | 9 | 2 | 1 | 51 | 23 | 23 | 9 | 2 | 4 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 9 | 3 | 6 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 8 | 3 | 7 | 9 | 51 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | C2 | 828.0621 | 828.0621 | 3160.5393 | 5595.1635 | 8581.7447 | C2 | 19045.4281 | 19045.4281 | 28444.8533 | 11190.3269 | 34326.9789 | 112053.0153 |  | 21529.6143 | 10764.8072 | 28444.8533 | 11190.3269 | 8581.7447 | 80511.3465 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514
|  |  | 54 | 54 | C3 | 47 | 5 | 2 | 0 | 0 | 54 | 47 | 5 | 2 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 3 | 3 | 0 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 1 | 2 | 2 | 54 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | C3 | 1242.0931 | 1242.0931 | 4740.8089 | 8392.7452 | 12872.6171 | C3 | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | C4 | 2070.1552 | 2070.1552 | 7901.3482 | 13987.9086 | 21454.3618 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293 | 293 |  | 143 | 80 | 36 | 20 | 14 |  | 109 | 90 | 36 | 20 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 119 | 74 | 39 | 17 | 44 |  | 0 | 0 | 0 | 0 | 0 |  | 88 | 93 | 30 | 21 | 61 | [22 empty] | 100029.9005 | 61193.7885 | 93235.9082 | 81689.3865 | 298644.7163 | 634793.6999 |  | 120483.0341 | 52913.1676 | 93235.9082 | 81689.3865 | 86675.6217 | 434997.118 |  | 105660.7227 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 620044.2708 |  | 105660.7227 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 620044.2708 |  | 71544.5646 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 723362.1475 |  | 71544.5646 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 723362.1475
| 132kV Transformer |  | 86 | 86 | C1 | 21 | 61 | 2 | 1 | 1 | 86 | 21 | 61 | 2 | 1 | 1 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 49 | 15 | 2 | 1 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 42 | 32 | 3 | 2 | 86 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | C1 | 2795.6945 | 2795.6945 | 10471.536 | 21719.5367 | 44447.4774 | C1 | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468
|  |  | 156 | 156 | C2 | 23 | 101 | 23 | 5 | 4 | 156 | 21 | 94 | 23 | 10 | 4 | 152 | 0 | 3 | 0 | -1 | -2 | 0 | 19 | 72 | 48 | 11 | 6 | 156 | 0 | 4 | 0 | -2 | -2 | 0 | 9 | 64 | 54 | 21 | 8 | 156 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469494 | 469494 | 469494 | 469494 | 469494 | C2 | 3993.8493 | 3993.8493 | 14959.3371 | 31027.9096 | 63496.3963 | C2 | 83870.8354 | 375421.8346 | 344064.7529 | 310279.0961 | 253985.5852 | 1367622.1043 |  | 91858.534 | 403378.7798 | 344064.7529 | 155139.5481 | 253985.5852 | 1248427.2 |  | 75883.1368 | 287557.1499 | 718048.18 | 341307.0057 | 380978.3778 | 1803773.8503 |  | 75883.1368 | 299538.6979 | 718048.18 | 310279.0961 | 253985.5852 | 1657734.696 |  | 35944.6437 | 255606.3555 | 807804.2025 | 651586.1019 | 507971.1704 | 2258912.4741 |  | 35944.6437 | 271581.7527 | 807804.2025 | 589530.2826 | 380978.3778 | 2085839.2595
|  |  | 22 | 22 | C3 | 3 | 10 | 5 | 0 | 4 | 22 | 2 | 10 | 5 | 0 | 5 | 22 | 0 | 1 | 0 | -1 | 0 | 0 | 3 | 6 | 8 | 1 | 4 | 22 | 0 | 1 | 0 | -1 | 0 | 0 | 1 | 8 | 7 | 2 | 4 | 22 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 704241 | 704241 | 704241 | 704241 | 704241 | C3 | 5990.774 | 5990.774 | 22439.0056 | 46541.8644 | 95244.5945 | C3 | 11981.5479 | 59907.7396 | 112195.0281 | 0 | 476222.9723 | 660307.2879 |  | 17972.3219 | 59907.7396 | 112195.0281 | 0 | 380978.3778 | 571053.4674 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 17972.3219 | 41935.4177 | 179512.045 | 0 | 380978.3778 | 620398.1624 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117 |  | 5990.774 | 53916.9656 | 157073.0394 | 46541.8644 | 380978.3778 | 644501.0212
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1173735 | 1173735 | 1173735 | 1173735 | 1173735 | C4 | 9984.6233 | 9984.6233 | 37398.3427 | 77569.774 | 158740.9908 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 264 | 264 |  | 47 | 172 | 30 | 6 | 9 |  | 44 | 165 | 30 | 11 | 10 |  | 0 | 4 | 0 | -2 | -2 |  | 41 | 127 | 71 | 14 | 11 |  | 0 | 5 | 0 | -3 | -2 |  | 17 | 114 | 93 | 26 | 14 | [22 empty] | 154561.9681 | 605866.9395 | 477202.853 | 331998.6329 | 774656.0349 | 2344286.4284 |  | 168540.4407 | 633823.8847 | 477202.853 | 176859.0848 | 679411.4405 | 2135837.7036 |  | 146973.6544 | 460490.8248 | 1054633.2644 | 431287.9436 | 806404.2331 | 2899789.9204 |  | 146973.6544 | 478463.1467 | 1054633.2644 | 353718.1696 | 679411.4405 | 2713199.6756 |  | 61505.2793 | 420951.7167 | 1299966.3926 | 809828.4409 | 977844.5031 | 3570096.3326 |  | 61505.2793 | 442917.8879 | 1299966.3926 | 701230.7572 | 850851.7105 | 3356472.0275
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 30 | 30 | C1 | 0 | 23 | 3 | 1 | 3 | 30 | 1 | 25 | 4 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 1 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 1 | 5 | 30 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | C1 | 286.0983 | 286.0983 | 1072.4002 | 2211.1731 | 4549.7389 | C1 | 286.0983 | 7152.4572 | 4289.6009 | 0 | 0 | 11728.1564 |  | 0 | 6580.2606 | 3217.2007 | 2211.1731 | 13649.2167 | 25657.8511 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642
|  |  | 68 | 68 | C2 | 1 | 49 | 8 | 2 | 8 | 68 | 2 | 57 | 9 | 1 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 12 | 2 | 10 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 34 | 18 | 3 | 12 | 68 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 764662 | 764662 | 764662 | 764662 | 764662 | C2 | 408.7118 | 408.7118 | 1532.0003 | 3158.8187 | 6499.627 | C2 | 817.4237 | 23296.5748 | 13788.0029 | 3158.8187 | 0 | 41060.8201 |  | 408.7118 | 20026.8801 | 12256.0025 | 6317.6374 | 51997.016 | 91006.2479 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002
|  |  | 43 | 43 | C3 | 1 | 30 | 5 | 2 | 5 | 43 | 1 | 36 | 6 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | 8 | 2 | 7 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 12 | 2 | 8 | 43 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1146993 | 1146993 | 1146993 | 1146993 | 1146993 | C3 | 613.0678 | 613.0678 | 2298.0005 | 4738.2281 | 9749.4405 | C3 | 613.0678 | 22070.4393 | 13788.0029 | 0 | 0 | 36471.5099 |  | 613.0678 | 18392.0328 | 11490.0024 | 9476.4562 | 48747.2025 | 88718.7616 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088
|  |  | 49 | 49 | C4 | 1 | 34 | 6 | 2 | 6 | 49 | 2 | 39 | 7 | 1 | 3 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 9 | 2 | 7 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | 13 | 2 | 9 | 49 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1911655 | 1911655 | 1911655 | 1911655 | 1911655 | C4 | 1021.7796 | 1021.7796 | 3830.0008 | 7897.0468 | 16249.0675 | C4 | 2043.5592 | 39849.4043 | 26810.0055 | 7897.0468 | 48747.2025 | 125347.2184 |  | 1021.7796 | 34740.5063 | 22980.0048 | 15794.0936 | 97494.405 | 172030.7893 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013
|  |  | 190 | 190 |  | 3 | 136 | 22 | 7 | 22 |  | 6 | 157 | 26 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 117 | 34 | 7 | 29 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 94 | 51 | 8 | 34 | [22 empty] | 3760.1489 | 92368.8756 | 58675.6121 | 11055.8655 | 48747.2025 | 214607.7047 |  | 2043.5592 | 79739.6798 | 49943.2103 | 33799.3603 | 211887.8402 | 377413.6498 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 51.9831 | 121.1975 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4405 | 4405 | C2 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1073 | 2538 | 601 | 193 | 4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062 | 2518 | 627 | 198 | 4405 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 74.2616 | 173.1393 | C2 | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924
|  |  | 342 | 342 | C3 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 197 | 47 | 15 | 342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 83 | 195 | 49 | 15 | 342 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 111.3924 | 259.7089 | C3 | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656
|  |  | 8 | 8 | C4 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 185.654 | 432.8482 | C4 | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901
|  |  | 4755 | 4755 |  | 0 | 1158 | 2749 | 642 | 206 |  | 0 | 1158 | 2749 | 642 | 206 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 1158 | 2740 | 649 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 1147 | 2718 | 677 | 213 | [22 empty] | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 60889.8592 | 50052.3066 | 37311.514 | 148253.6799 |  | 0 | 0 | 60889.8592 | 50052.3066 | 37311.514 | 148253.6799 |  | 0 | 0 | 60397.7767 | 52205.8925 | 38177.2104 | 150780.8796 |  | 0 | 0 | 60397.7767 | 52205.8925 | 38177.2104 | 150780.8796
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 48.8085 | 94.7085 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2361 | 2361 | C2 | 471 | 289 | 642 | 591 | 368 | 2361 | 413 | 252 | 642 | 591 | 426 | 2324 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 303 | 562 | 581 | 493 | 2361 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 649 | 257 | 698 | 699 | 2361 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 69.7264 | 135.2979 | C2 | 0 | 0 | 13735.5199 | 41208.3279 | 57636.898 | 112580.7458 |  | 0 | 0 | 13735.5199 | 41208.3279 | 49789.6208 | 104733.4686 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643
|  |  | 196 | 196 | C3 | 43 | 21 | 54 | 50 | 28 | 196 | 38 | 21 | 54 | 50 | 33 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 48 | 49 | 41 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51 | 22 | 59 | 59 | 196 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 104.5897 | 202.9468 | C3 | 0 | 0 | 1732.9862 | 5229.4832 | 6697.2452 | 13659.7146 |  | 0 | 0 | 1732.9862 | 5229.4832 | 5682.5111 | 12644.9805 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842
|  |  | 3 | 3 | C4 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055
|  |  | 2560 | 2560 |  | 514 | 310 | 697 | 642 | 397 |  | 451 | 273 | 697 | 642 | 460 |  | 0 | 0 | 0 | 0 | 0 |  | 458 | 325 | 611 | 631 | 535 |  | 0 | 0 | 0 | 0 | 0 |  | 63 | 700 | 279 | 758 | 760 | [22 empty] | 0 | 0 | 15521.9933 | 46612.1272 | 64672.3879 | 126806.5085 |  | 0 | 0 | 15521.9933 | 46612.1272 | 55810.3766 | 117944.4971 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 |  | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 |  | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 |  | 254677.9363 | 594322.0194 | 1308142.4595 | 554998.2019 | 1355314.0652 | 4067454.6823 |  | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 |  | 135093.4031 | 571956.0607 | 1551834.1523 | 948360 | 1724575.8449 | 4931819.4611
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 643865 | 643865 |  | 108014 | 416640 | 71011 | 32459 | 15741 |  | 100295 | 415570 | 71117 | 33178 | 22842 |  | 0 | 18 | 0 | -9 | -9 |  | 67669 | 388473 | 121329 | 34588 | 31809 |  | 0 | 113 | 0 | -103 | -10 |  | 44233 | 354100 | 157644 | 44376 | 43514 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 |  | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 |  | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 |  | 2054397.052 | 10528256.0122 | 13058952.4458 | 7113249.5223 | 10923498.2157 | 43678353.248 |  | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 |  | 1235211.7431 | 9654686.6578 | 16558183.4661 | 9517769.5821 | 14747498.7664 | 51713350.2156
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 | LV Network | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 | HV Network | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 | HV Network | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 | HV Network | 854397.3038 | 4822066.2514 | 6879643.2097 | 1833213.6207 | 3856277.0233 | 18245597.4088 | HV Network | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 | HV Network | 370142.0039 | 4518097.7976 | 9133692.9418 | 2365507.4436 | 5314651.5198 | 21702091.7066
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 | EHV Network | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 | EHV Network | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 | EHV Network | 308772.0556 | 1193098.4768 | 1446293.9977 | 626776.6981 | 1977709.1553 | 5552650.3835 | EHV Network | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 | EHV Network | 179195.9368 | 1071735.9169 | 2137670.3819 | 801495.0587 | 2560657.7414 | 6750755.0358
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 | 132kV Network | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 | 132kV Network | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 | 132kV Network | 254677.9363 | 594322.0194 | 1308142.4595 | 554998.2019 | 1355314.0652 | 4067454.6823 | 132kV Network | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 | 132kV Network | 135093.4031 | 571956.0607 | 1551834.1523 | 948360 | 1724575.8449 | 4931819.4611
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 | Total | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 | Total | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 | Total | 2054397.052 | 10528256.0122 | 13058952.4458 | 7113249.5223 | 10923498.2157 | 43678353.248 | Total | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 | Total | 1235211.7431 | 9654686.6578 | 16558183.4661 | 9517769.5821 | 14747498.7664 | 51713350.2156
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EPN - HVP
HI7: Secondary deliverables RIIO-ED1 - HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 64 | 64 | C1 | 8 | 25 | 31 | 0 | 0 | 64 | 8 | 25 | 31 | 0 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 25 | 33 | 2 | 0 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 33 | 6 | 1 | 64 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | 7259.7 | C1 | 7.8518 | 17.9786 | 55.6367 | 90.6791 | 145.6343 | C1 | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 62.8142 | 449.4654 | 1724.7371 | 0 | 0 | 2237.0167 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 31.4071 | 449.4654 | 1836.0105 | 181.3583 | 0 | 2498.2412 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064 |  | 0 | 431.4868 | 1836.0105 | 544.0749 | 145.6343 | 2957.2064
|  |  | 29908 | 29908 | C2 | 3760 | 11129 | 14935 | 84 | 0 | 29908 | 3531 | 10762 | 14935 | 265 | 48 | 29541 | 0 | 0 | 0 | 0 | 0 | 0 | 2069 | 11728 | 15262 | 789 | 60 | 29908 | 0 | 0 | 0 | 0 | 0 | 0 | 229 | 11673 | 15906 | 1851 | 249 | 29908 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10371 | 10371 | 10371 | 10371 | 10371 | C2 | 11.2168 | 25.6837 | 79.481 | 129.5416 | 208.049 | C2 | 39606.6007 | 276408.3808 | 1187048.316 | 34328.5337 | 9986.3537 | 1547378.1849 |  | 42175.2531 | 285834.3124 | 1187048.316 | 10881.4975 | 0 | 1525939.3789 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 23207.606 | 301218.8711 | 1213038.5938 | 102208.3514 | 12482.9421 | 1652156.3644 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369 |  | 2568.6524 | 299806.2655 | 1264224.3397 | 239781.5697 | 51804.2096 | 1858185.0369
|  |  | 63 | 63 | C3 | 8 | 25 | 30 | 0 | 0 | 63 | 7 | 25 | 30 | 1 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 24 | 33 | 1 | 0 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 23 | 33 | 5 | 1 | 63 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | 15556.5 | C3 | 16.8252 | 38.5256 | 119.2215 | 194.3125 | 312.0736 | C3 | 117.7766 | 963.1401 | 3576.6437 | 194.3125 | 0 | 4851.873 |  | 134.6019 | 963.1401 | 3576.6437 | 0 | 0 | 4674.3858 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 84.1262 | 924.6145 | 3934.3081 | 194.3125 | 0 | 5137.3613 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581 |  | 16.8252 | 886.0889 | 3934.3081 | 971.5623 | 312.0736 | 6120.8581
|  |  | 5 | 5 | C4 | 1 | 2 | 2 | 0 | 0 | 5 | 1 | 2 | 2 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 0 | 0 | 5 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | 25927.5 | C4 | 28.0421 | 64.2093 | 198.7024 | 323.8541 | 520.1226 | C4 | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 28.0421 | 128.4187 | 397.4049 | 0 | 0 | 553.8656 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526 |  | 0 | 128.4187 | 596.1073 | 0 | 0 | 724.526
|  |  | 30040 | 30040 |  | 3777 | 11181 | 14998 | 84 | 0 |  | 3547 | 10814 | 14998 | 266 | 48 |  | 0 | 0 | 0 | 0 | 0 |  | 2078 | 11779 | 15331 | 792 | 60 |  | 0 | 0 | 0 | 0 | 0 |  | 230 | 11722 | 15975 | 1862 | 251 | [22 empty] | 39815.2336 | 277949.4051 | 1192747.1017 | 34522.8462 | 9986.3537 | 1555020.9402 |  | 42400.7112 | 287375.3367 | 1192747.1017 | 10881.4975 | 0 | 1533404.647 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 23323.1393 | 302721.3697 | 1219405.0197 | 102584.0222 | 12482.9421 | 1660516.4929 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274 |  | 2585.4776 | 301252.2599 | 1270590.7656 | 241297.2068 | 52261.9175 | 1867987.6274
| LV UGB |  | 812 | 812 | C1 | 107 | 91 | 305 | 287 | 22 | 812 | 101 | 91 | 305 | 287 | 28 | 812 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 66 | 228 | 393 | 37 | 813 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 39 | 126 | 513 | 52 | 812 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | 7828.1 | C1 | 11.222 | 16.833 | 56.11 | 123.4421 | 241.2731 | C1 | 1133.4225 | 1531.8036 | 17113.5572 | 35427.8689 | 6755.6468 | 61962.299 |  | 1200.7545 | 1531.8036 | 17113.5572 | 35427.8689 | 5308.0082 | 60581.9924 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 998.7584 | 1110.9785 | 12793.0854 | 48512.7264 | 8927.1047 | 72342.6534 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285 |  | 920.2044 | 656.4873 | 7069.863 | 63325.7726 | 12546.2013 | 84518.5285
|  |  | 25739 | 25739 | C2 | 3391 | 2894 | 9654 | 9102 | 698 | 25739 | 3189 | 2894 | 9654 | 9102 | 900 | 25739 | 0 | 0 | 0 | 0 | 0 | 0 | 2825 | 2088 | 7220 | 12437 | 1171 | 25741 | 0 | 0 | 0 | 0 | 0 | 0 | 2604 | 1240 | 4005 | 16258 | 1634 | 25741 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11183 | 11183 | 11183 | 11183 | 11183 | C2 | 16.0314 | 24.0472 | 80.1572 | 176.3458 | 344.6759 | C2 | 51124.2472 | 69592.4607 | 773837.3821 | 1605099.3654 | 310208.2731 | 2809861.7285 |  | 54362.5971 | 69592.4607 | 773837.3821 | 1605099.3654 | 240583.7496 | 2743475.5549 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 45288.8047 | 50210.4554 | 578734.8144 | 2193212.5695 | 403615.4309 | 3271062.075 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995 |  | 41745.8575 | 29818.4697 | 321029.4919 | 2867029.8267 | 563200.3536 | 3822823.9995
|  |  | 5276 | 5276 | C3 | 695 | 593 | 1979 | 1866 | 143 | 5276 | 654 | 593 | 1979 | 1866 | 185 | 5277 | 0 | 0 | 0 | 0 | 0 | 0 | 579 | 428 | 1480 | 2549 | 240 | 5276 | 0 | 0 | 0 | 0 | 0 | 0 | 534 | 254 | 821 | 3333 | 335 | 5277 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | 16774.5 | C3 | 24.0472 | 36.0707 | 120.2358 | 264.5187 | 517.0138 | C3 | 15726.838 | 21389.9426 | 237946.5785 | 493591.8615 | 95647.5509 | 864302.7715 |  | 16712.7713 | 21389.9426 | 237946.5785 | 493591.8615 | 73932.9718 | 843574.1257 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 13923.3016 | 15438.2722 | 177948.9319 | 674258.1217 | 124083.3092 | 1005651.9366 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958 |  | 12841.1797 | 9161.9653 | 98713.5629 | 881640.7688 | 173199.6192 | 1175557.0958
|  |  | 2285 | 2285 | C4 | 301 | 257 | 857 | 808 | 62 | 2285 | 283 | 257 | 857 | 808 | 80 | 2285 | 0 | 0 | 0 | 0 | 0 | 0 | 251 | 185 | 641 | 1104 | 104 | 2285 | 0 | 0 | 0 | 0 | 0 | 0 | 231 | 110 | 355 | 1443 | 145 | 2284 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | 27957.5 | C4 | 40.0786 | 60.1179 | 200.3929 | 440.8645 | 861.6896 | C4 | 11342.2405 | 15450.2958 | 171736.7507 | 356218.4924 | 68935.1718 | 623682.9512 |  | 12063.6551 | 15450.2958 | 171736.7507 | 356218.4924 | 53424.7581 | 608893.9521 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 10059.7257 | 11121.8082 | 128451.8754 | 486714.3758 | 89615.7233 | 725963.5084 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454 |  | 9258.1539 | 6612.9671 | 71139.4942 | 636167.4314 | 124944.9989 | 848123.0454
|  |  | 34112 | 34112 |  | 4494 | 3835 | 12795 | 12063 | 925 |  | 4227 | 3835 | 12795 | 12063 | 1193 |  | 0 | 0 | 0 | 0 | 0 |  | 3744 | 2767 | 9569 | 16483 | 1552 |  | 0 | 0 | 0 | 0 | 0 |  | 3451 | 1643 | 5307 | 21547 | 2166 | [22 empty] | 79326.7482 | 107964.5026 | 1200634.2684 | 2490337.5883 | 481546.6426 | 4359809.7501 |  | 84339.778 | 107964.5026 | 1200634.2684 | 2490337.5883 | 373249.4877 | 4256525.6251 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 70270.5904 | 77881.5143 | 897928.707 | 3402697.7934 | 626241.5682 | 5075020.1733 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692 |  | 64765.3955 | 46249.8893 | 497952.412 | 4448163.7995 | 873891.173 | 5931022.6692
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | 9509.0552 | C1 | 14.4557 | 14.4557 | 29.0421 | 79.9779 | 158.5738 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 246106 | 246106 | C2 | 44138 | 179341 | 6435 | 8501 | 7691 | 246106 | 40338 | 179599 | 6435 | 8501 | 11491 | 246364 | 0 | 0 | 0 | 0 | 0 | 0 | 26121 | 170027 | 31277 | 5151 | 13530 | 246106 | 0 | 0 | 0 | 0 | 0 | 0 | 23261 | 151153 | 47037 | 6192 | 18463 | 246106 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | 13584.3646 | C2 | 20.651 | 20.651 | 41.4888 | 114.2542 | 226.534 | C2 | 833019.9377 | 3708898.5026 | 266980.178 | 971274.7708 | 2603101.8733 | 8383275.2624 |  | 911493.7283 | 3703570.5452 | 266980.178 | 971274.7708 | 1742272.7793 | 7595592.0017 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 539424.7061 | 3511227.1544 | 1297643.9827 | 588523.2731 | 3065004.6423 | 9001823.7586 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384 |  | 480362.8532 | 3121460.2273 | 1951506.8585 | 707461.8728 | 4182496.7266 | 10443288.5384
|  |  | 1255 | 1255 | C3 | 115 | 1016 | 14 | 62 | 48 | 1255 | 115 | 1016 | 14 | 62 | 48 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 114 | 868 | 159 | 26 | 88 | 1255 | 0 | 0 | 0 | 0 | 0 | 0 | 99 | 771 | 240 | 32 | 113 | 1255 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | 20376.547 | C3 | 30.9765 | 30.9765 | 62.2331 | 171.3813 | 339.801 | C3 | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3562.2971 | 31472.1202 | 871.264 | 10625.6386 | 16310.446 | 62841.7659 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 3531.3206 | 26887.5988 | 9895.0695 | 4455.913 | 29902.4843 | 74672.3861 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146 |  | 3066.6731 | 23882.8786 | 14935.954 | 5484.2006 | 38397.5083 | 85767.2146
|  |  | 2 | 2 | C4 | 1 | 0 | 0 | 0 | 1 | 2 | 1 | 0 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | 33960.9116 | C4 | 51.6275 | 51.6275 | 103.7219 | 285.6354 | 566.3349 | C4 | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 51.6275 | 0 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624 |  | 0 | 51.6275 | 0 | 0 | 566.3349 | 617.9624
|  |  | 247363 | 247363 |  | 44254 | 180357 | 6449 | 8563 | 7740 |  | 40454 | 180615 | 6449 | 8563 | 11540 |  | 0 | 0 | 0 | 0 | 0 |  | 26235 | 170896 | 31436 | 5177 | 13619 |  | 0 | 0 | 0 | 0 | 0 |  | 23360 | 151925 | 47277 | 6224 | 18577 | [22 empty] | 836633.8623 | 3740370.6228 | 267851.442 | 981900.4094 | 2619978.6542 | 8446734.9907 |  | 915107.6529 | 3735042.6654 | 267851.442 | 981900.4094 | 1759149.5602 | 7659051.73 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 542956.0266 | 3538166.3806 | 1307539.0522 | 592979.1861 | 3095473.4616 | 9077114.1071 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155 |  | 483429.5263 | 3145394.7334 | 1966442.8125 | 712946.0734 | 4221460.5698 | 10529673.7155
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 |  | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 |  | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 3046 | 3046 | C1 | 1055 | 1042 | 885 | 52 | 12 | 3046 | 1044 | 1010 | 885 | 84 | 23 | 3046 | 0 | 0 | 0 | 0 | 0 | 0 | 967 | 904 | 830 | 246 | 99 | 3046 | 0 | 0 | 0 | 0 | 0 | 0 | 561 | 1107 | 785 | 300 | 293 | 3046 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33586 | 33586 | 33586 | 33586 | 33586 | C1 | 58.8156 | 58.8156 | 220.1504 | 404.4235 | 556.6962 | C1 | 61403.5232 | 59403.7916 | 194833.0619 | 33971.5713 | 12804.0121 | 362415.9602 |  | 62050.4952 | 61285.892 | 194833.0619 | 21030.0203 | 6680.3541 | 345879.8236 |  | 56874.7193 | 53169.3343 | 182724.7925 | 99488.1731 | 55112.9217 | 447369.9409 |  | 56874.7193 | 53169.3343 | 182724.7925 | 99488.1731 | 55112.9217 | 447369.9409 |  | 32995.5714 | 65108.9082 | 172818.0267 | 121327.0404 | 163111.9803 | 555361.527 |  | 32995.5714 | 65108.9082 | 172818.0267 | 121327.0404 | 163111.9803 | 555361.527
|  |  | 1695 | 1695 | C2 | 261 | 967 | 397 | 50 | 20 | 1695 | 232 | 799 | 397 | 65 | 34 | 1527 | 0 | 0 | 0 | 0 | 0 | 0 | 253 | 702 | 545 | 115 | 80 | 1695 | 0 | 0 | 0 | 0 | 0 | 0 | 153 | 597 | 583 | 192 | 170 | 1695 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47980 | 47980 | 47980 | 47980 | 47980 | C2 | 84.0223 | 84.0223 | 314.5005 | 577.7478 | 795.2803 | C2 | 19493.182 | 67133.8465 | 124856.6999 | 37553.6077 | 27039.5287 | 276076.8648 |  | 21929.8297 | 81249.599 | 124856.6999 | 28887.3906 | 15905.6051 | 272829.1243 |  | 21257.651 | 58983.6799 | 171402.7744 | 66440.9983 | 63622.4204 | 381707.5241 |  | 21257.651 | 58983.6799 | 171402.7744 | 66440.9983 | 63622.4204 | 381707.5241 |  | 12855.4174 | 50161.3347 | 183353.7935 | 110927.5798 | 135197.6434 | 492495.7688 |  | 12855.4174 | 50161.3347 | 183353.7935 | 110927.5798 | 135197.6434 | 492495.7688
|  |  | 618 | 618 | C3 | 127 | 359 | 113 | 17 | 2 | 618 | 122 | 359 | 113 | 19 | 5 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 256 | 178 | 34 | 37 | 618 | 0 | 0 | 0 | 0 | 0 | 0 | 64 | 179 | 266 | 54 | 55 | 618 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71970 | 71970 | 71970 | 71970 | 71970 | C3 | 126.0335 | 126.0335 | 471.7508 | 866.6217 | 1192.9204 | C3 | 15376.0875 | 45246.028 | 53307.8353 | 16465.8126 | 5964.6019 | 136360.3654 |  | 16006.255 | 45246.028 | 53307.8353 | 14732.5692 | 2385.8408 | 131678.5283 |  | 14241.786 | 32264.5771 | 83971.6344 | 29465.1384 | 44138.0542 | 204081.19 |  | 14241.786 | 32264.5771 | 83971.6344 | 29465.1384 | 44138.0542 | 204081.19 |  | 8066.1443 | 22559.9972 | 125485.7009 | 46797.5727 | 65610.621 | 268520.0362 |  | 8066.1443 | 22559.9972 | 125485.7009 | 46797.5727 | 65610.621 | 268520.0362
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119950 | 119950 | 119950 | 119950 | 119950 | C4 | 210.0558 | 210.0558 | 786.2513 | 1444.3695 | 1988.2006 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5359 | 5359 |  | 1443 | 2368 | 1395 | 119 | 34 |  | 1398 | 2168 | 1395 | 168 | 62 |  | 0 | 0 | 0 | 0 | 0 |  | 1333 | 1862 | 1553 | 395 | 216 |  | 0 | 0 | 0 | 0 | 0 |  | 778 | 1883 | 1634 | 546 | 518 | [22 empty] | 96272.7927 | 171783.6662 | 372997.5972 | 87990.9917 | 45808.1427 | 774853.1904 |  | 99986.58 | 187781.5189 | 372997.5972 | 64649.9801 | 24971.8 | 750387.4762 |  | 92374.1563 | 144417.5913 | 438099.2014 | 195394.3098 | 162873.3962 | 1033158.655 |  | 92374.1563 | 144417.5913 | 438099.2014 | 195394.3098 | 162873.3962 | 1033158.655 |  | 53917.1331 | 137830.2401 | 481657.5211 | 279052.1929 | 363920.2447 | 1316377.332 |  | 53917.1331 | 137830.2401 | 481657.5211 | 279052.1929 | 363920.2447 | 1316377.332
| HV Switchgear (GM) - Distribution |  | 16951 | 16951 | C1 | 7581 | 8348 | 596 | 426 | 0 | 16951 | 7566 | 8348 | 596 | 426 | 16 | 16952 | 0 | 0 | 0 | 0 | 0 | 0 | 3630 | 12149 | 623 | 533 | 16 | 16951 | 0 | 0 | 0 | 0 | 0 | 0 | 870 | 14318 | 1090 | 577 | 96 | 16951 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | 20227.9 | C1 | 11.2991 | 11.2991 | 42.4721 | 77.873 | 133.2047 | C1 | 85488.9241 | 94324.8134 | 25313.3509 | 33173.9097 | 2131.2749 | 240432.273 |  | 85658.4105 | 94324.8134 | 25313.3509 | 33173.9097 | 0 | 238470.4845 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 41015.7011 | 137272.6591 | 26460.0966 | 41506.3237 | 2131.2749 | 248386.0554 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348 |  | 9830.2094 | 161780.3879 | 46294.5511 | 44932.7369 | 12787.6496 | 275625.5348
|  |  | 15770 | 15770 | C2 | 1149 | 9824 | 4343 | 454 | 0 | 15770 | 474 | 9350 | 4343 | 798 | 548 | 15513 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 6422 | 4444 | 2126 | 1770 | 15770 | 0 | 0 | 0 | 0 | 0 | 0 | 917 | 4850 | 4656 | 1768 | 3579 | 15770 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 28897 | 28897 | 28897 | 28897 | 28897 | C2 | 16.1416 | 16.1416 | 60.6744 | 111.2472 | 190.2924 | C2 | 7651.0989 | 150923.5754 | 263508.8273 | 88775.2514 | 104280.2376 | 615138.9907 |  | 18546.6511 | 158574.6743 | 263508.8273 | 50506.2207 | 0 | 491136.3735 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 16270.6913 | 103661.0911 | 269636.9396 | 236511.5094 | 336817.5557 | 962897.7871 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113 |  | 14801.8095 | 78286.5605 | 282499.9079 | 196685.0182 | 681056.5152 | 1253329.8113
|  |  | 3 | 3 | C3 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 1 | 0 | 2 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 1 | 0 | 0 | 0 | 3 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | 43345.5 | C3 | 24.2123 | 24.2123 | 91.0116 | 166.8708 | 285.4386 | C3 | 0 | 24.2123 | 0 | 333.7415 | 0 | 357.9539 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637 |  | 48.4247 | 24.2123 | 0 | 0 | 0 | 72.637
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | 72242.5 | C4 | 40.3539 | 40.3539 | 151.6859 | 278.118 | 475.731 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 32724 | 32724 |  | 8732 | 18173 | 4939 | 880 | 0 |  | 8040 | 17699 | 4939 | 1226 | 564 |  | 0 | 0 | 0 | 0 | 0 |  | 4640 | 18572 | 5067 | 2659 | 1786 |  | 0 | 0 | 0 | 0 | 0 |  | 1789 | 19169 | 5746 | 2345 | 3675 | [22 empty] | 93140.023 | 245272.6012 | 288822.1782 | 122282.9027 | 106411.5125 | 855929.2176 |  | 104253.4863 | 252923.7001 | 288822.1782 | 83680.1305 | 0 | 729679.495 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 57334.8171 | 240957.9625 | 296097.0362 | 278017.8331 | 338948.8307 | 1211356.4796 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831 |  | 24680.4435 | 240091.1608 | 328794.459 | 241617.7551 | 693844.1648 | 1529027.9831
| HV Transformer (GM) |  | 15354 | 15354 | C1 | 2254 | 4991 | 8109 | 0 | 0 | 15354 | 2175 | 4991 | 8109 | 71 | 8 | 15354 | 0 | 0 | 0 | 0 | 0 | 0 | 1306 | 5562 | 8385 | 91 | 10 | 15354 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 6088 | 8844 | 291 | 52 | 15354 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | 37979.9 | C1 | 33.5005 | 40.8282 | 115.1569 | 219.6408 | 370.4805 | C1 | 72863.5281 | 203773.5627 | 933807.1344 | 15594.4939 | 2963.844 | 1229002.5632 |  | 75510.0655 | 203773.5627 | 933807.1344 | 0 | 0 | 1213090.7626 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 43751.6174 | 227086.4668 | 965590.4331 | 19987.3091 | 3704.805 | 1260120.6314 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269 |  | 2646.5373 | 248562.1017 | 1018447.4407 | 63915.4611 | 19264.9861 | 1352836.5269
|  |  | 10916 | 10916 | C2 | 1472 | 4148 | 5296 | 0 | 0 | 10916 | 1285 | 3757 | 5432 | 46 | 5 | 10525 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 4205 | 5611 | 65 | 7 | 10916 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 4563 | 5928 | 201 | 37 | 10916 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 54257 | 54257 | 54257 | 54257 | 54257 | C2 | 47.8578 | 58.326 | 164.5098 | 313.7725 | 529.2579 | C2 | 61497.2963 | 219130.7997 | 893617.3835 | 14433.5356 | 2646.2893 | 1191325.3045 |  | 70446.7083 | 241936.2676 | 871244.047 | 0 | 0 | 1183627.0229 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 49197.8371 | 245260.8499 | 923064.6427 | 20395.2134 | 3704.805 | 1241623.348 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456 |  | 8949.412 | 266141.5596 | 975214.258 | 63068.2753 | 19582.5408 | 1332956.0456
|  |  | 4387 | 4387 | C3 | 644 | 1426 | 2317 | 0 | 0 | 4387 | 622 | 1426 | 2317 | 20 | 2 | 4387 | 0 | 0 | 0 | 0 | 0 | 0 | 373 | 1589 | 2396 | 26 | 3 | 4387 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 1740 | 2528 | 82 | 15 | 4387 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | 81385.5 | C3 | 71.7867 | 87.489 | 246.7647 | 470.6588 | 793.8868 | C3 | 44651.3443 | 124759.3241 | 571753.9058 | 9413.1754 | 1587.7736 | 752165.5233 |  | 46230.6523 | 124759.3241 | 571753.9058 | 0 | 0 | 742743.8823 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 26776.4493 | 139020.0323 | 591248.3204 | 12237.128 | 2381.6604 | 771663.5903 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676 |  | 1579.308 | 152230.8723 | 623821.2663 | 38594.0192 | 11908.3018 | 828133.7676
|  |  | 1566 | 1566 | C4 | 230 | 509 | 827 | 0 | 0 | 1566 | 222 | 509 | 827 | 7 | 1 | 1566 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 567 | 855 | 10 | 1 | 1566 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 621 | 900 | 32 | 5 | 1566 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | 135642.5 | C4 | 119.6445 | 145.815 | 411.2746 | 784.4313 | 1323.1446 | C4 | 26561.0891 | 74219.841 | 340124.0686 | 5491.019 | 1323.1446 | 447719.1623 |  | 27518.2454 | 74219.841 | 340124.0686 | 0 | 0 | 441862.155 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 15912.7245 | 82677.1117 | 351639.7565 | 7844.3128 | 1323.1446 | 459397.0502 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151 |  | 957.1564 | 90551.1223 | 370147.1121 | 25101.8011 | 6615.7232 | 493372.9151
|  |  | 32223 | 32223 |  | 4600 | 11074 | 16549 | 0 | 0 |  | 4304 | 10683 | 16685 | 144 | 16 |  | 0 | 0 | 0 | 0 | 0 |  | 2840 | 11923 | 17247 | 192 | 21 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 13012 | 18200 | 606 | 109 | [22 empty] | 205573.2579 | 621883.5276 | 2739302.4923 | 44932.224 | 8521.0515 | 3620212.5533 |  | 219705.6716 | 644688.9954 | 2716929.1558 | 0 | 0 | 3581323.8228 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 135638.6282 | 694044.4606 | 2831543.1527 | 60463.9634 | 11114.415 | 3732804.62 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553 |  | 14132.4137 | 757485.6559 | 2987630.0771 | 190679.5567 | 57371.5519 | 4007299.2553
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 135 | 135 | C1 | 12 | 103 | 14 | 2 | 4 | 135 | 12 | 103 | 14 | 2 | 4 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 90 | 21 | 4 | 8 | 135 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 81 | 34 | 5 | 10 | 135 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | 17138.8622 | C1 | 17.6591 | 17.6591 | 66.4486 | 139.6696 | 215.3203 | C1 | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1818.8884 | 930.2799 | 279.3391 | 861.2813 | 4101.6981 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 211.9093 | 1589.32 | 1395.4199 | 558.6782 | 1722.5627 | 5477.8901 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859 |  | 88.2956 | 1430.388 | 2259.2512 | 698.3478 | 2153.2034 | 6629.4859
|  |  | 196526 | 196526 | C2 | 30344 | 147825 | 6695 | 6814 | 4848 | 196526 | 28983 | 147899 | 6695 | 6814 | 6209 | 196600 | 0 | 0 | 0 | 0 | 0 | 0 | 19315 | 130607 | 30746 | 5743 | 10115 | 196526 | 0 | 0 | 0 | 0 | 0 | 0 | 9135 | 117840 | 49495 | 7489 | 12567 | 196526 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | 24484.0888 | C2 | 25.2273 | 25.2273 | 94.9265 | 199.5279 | 307.6005 | C2 | 731162.86 | 3731092.5658 | 635533.0554 | 1359583.403 | 1909891.3827 | 8367263.2669 |  | 765497.2165 | 3729225.7455 | 635533.0554 | 1359583.403 | 1491247.1289 | 7981086.5493 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 487265.3156 | 3294862.0798 | 2918610.8024 | 1145888.9761 | 3111378.8591 | 10958006.033 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617 |  | 230451.3931 | 2972785.1301 | 4698388.1371 | 1494264.7644 | 3865615.237 | 13261504.6617
|  |  | 17623 | 17623 | C3 | 3370 | 13180 | 604 | 469 | 0 | 17623 | 2845 | 13180 | 604 | 469 | 525 | 17623 | 0 | 0 | 0 | 0 | 0 | 0 | 2134 | 11719 | 2763 | 508 | 499 | 17623 | 0 | 0 | 0 | 0 | 0 | 0 | 1222 | 10577 | 4441 | 664 | 719 | 17623 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | 36726.1333 | C3 | 37.841 | 37.841 | 142.3898 | 299.2919 | 461.4007 | C3 | 107657.5063 | 498743.7375 | 86003.4277 | 140367.9078 | 242235.3783 | 1075007.9576 |  | 127524.0057 | 498743.7375 | 86003.4277 | 140367.9078 | 0 | 852639.0787 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 80752.59 | 443458.1077 | 393422.9646 | 152040.2925 | 230238.9596 | 1299912.9143 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35 |  | 46241.6424 | 400243.7414 | 632353.017 | 198729.8311 | 331747.1181 | 1609315.35
|  |  | 59 | 59 | C4 | 14 | 38 | 1 | 6 | 0 | 59 | 6 | 38 | 1 | 6 | 8 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 35 | 2 | 9 | 0 | 59 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 29 | 11 | 9 | 0 | 59 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | 61210.2221 | C4 | 63.0683 | 63.0683 | 237.3163 | 498.8199 | 769.0012 | C4 | 378.4095 | 2396.5936 | 237.3163 | 2992.9191 | 6152.0096 | 12157.2481 |  | 882.9555 | 2396.5936 | 237.3163 | 2992.9191 | 0 | 6509.7846 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 819.8873 | 2207.3888 | 474.6326 | 4489.3787 | 0 | 7991.2874 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199 |  | 630.6825 | 1828.9793 | 2610.4793 | 4489.3787 | 0 | 9559.5199
|  |  | 214343 | 214343 |  | 33740 | 161146 | 7314 | 7291 | 4852 |  | 31846 | 161220 | 7314 | 7291 | 6746 |  | 0 | 0 | 0 | 0 | 0 |  | 21474 | 142451 | 33532 | 6264 | 10622 |  | 0 | 0 | 0 | 0 | 0 |  | 10372 | 128527 | 53981 | 8167 | 13296 | [22 empty] | 839410.6852 | 4234051.7852 | 722704.0793 | 1503223.5691 | 2159140.0519 | 9458530.1707 |  | 894116.087 | 4232184.9649 | 722704.0793 | 1503223.5691 | 1492108.4102 | 8844337.1106 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 569049.7021 | 3742116.8963 | 3313903.8195 | 1302977.3256 | 3343340.3813 | 12271388.1248 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174 |  | 277412.0136 | 3376288.2387 | 5335610.8846 | 1698182.3221 | 4199515.5584 | 14887009.0174
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 |  | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 |  | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 |  | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 |  | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 |  | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 868 | 868 | C1 | 416 | 225 | 108 | 95 | 24 | 868 | 398 | 225 | 108 | 95 | 42 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 383 | 209 | 64 | 111 | 101 | 868 | 0 | 0 | 0 | 0 | 0 | 0 | 271 | 302 | 41 | 82 | 172 | 868 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | 37554.9745 | C1 | 165.9387 | 165.9387 | 626.127 | 1146.0231 | 1956.2345 | C1 | 66043.6106 | 37336.2121 | 67621.7214 | 108872.194 | 82161.8485 | 362035.5866 |  | 69030.5076 | 37336.2121 | 67621.7214 | 108872.194 | 46949.6277 | 329810.2627 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 63554.5298 | 34681.1925 | 40072.1312 | 127208.5635 | 197579.6834 | 463096.1004 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216 |  | 44969.3932 | 50113.4935 | 25671.209 | 93973.8937 | 336472.3321 | 551200.3216
|  |  | 437 | 437 | C2 | 139 | 148 | 49 | 84 | 17 | 437 | 102 | 101 | 49 | 90 | 48 | 390 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 140 | 23 | 66 | 111 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 81 | 130 | 42 | 26 | 158 | 437 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | 53649.9635 | C2 | 237.0553 | 237.0553 | 894.4672 | 1637.1758 | 2794.6207 | C2 | 24179.6421 | 23942.5868 | 43828.8935 | 147345.8264 | 134141.7935 | 373438.7423 |  | 32950.6887 | 35084.1866 | 43828.8935 | 137522.7713 | 47508.5519 | 296895.092 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 22994.3655 | 33187.744 | 20572.7459 | 108053.606 | 310202.8976 | 495011.3591 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369 |  | 19201.4805 | 30817.1909 | 37567.623 | 42566.5721 | 441550.0704 | 571702.9369
|  |  | 82 | 82 | C3 | 29 | 25 | 10 | 16 | 2 | 82 | 25 | 25 | 10 | 16 | 6 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 28 | 3 | 10 | 18 | 82 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 43 | 0 | 6 | 25 | 82 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | 80474.9453 | C3 | 355.583 | 355.583 | 1341.7008 | 2455.7638 | 4191.931 | C3 | 8889.5743 | 8889.5743 | 13417.0082 | 39292.2204 | 25151.5863 | 95639.9635 |  | 10311.9062 | 8889.5743 | 13417.0082 | 39292.2204 | 8383.8621 | 80294.5712 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 8178.4084 | 9956.3232 | 4025.1025 | 24557.6377 | 75454.7589 | 122172.2306 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904 |  | 2844.6638 | 15290.0678 | 0 | 14734.5826 | 104798.2762 | 137667.5904
|  |  | 88 | 88 | C4 | 28 | 33 | 12 | 14 | 1 | 88 | 18 | 33 | 12 | 14 | 11 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 27 | 10 | 14 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 27 | 9 | 10 | 21 | 88 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | 134124.9088 | C4 | 592.6383 | 592.6383 | 2236.168 | 4092.9396 | 6986.5517 | C4 | 10667.4892 | 19557.0635 | 26834.0164 | 57301.1547 | 76852.0692 | 191211.793 |  | 16593.872 | 19557.0635 | 26834.0164 | 57301.1547 | 6986.5517 | 127272.6584 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 14815.9572 | 16001.2337 | 22361.6803 | 57301.1547 | 83838.621 | 194318.6469 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133 |  | 12445.404 | 16001.2337 | 20125.5123 | 40929.3962 | 146717.5867 | 236219.133
|  |  | 1475 | 1475 |  | 612 | 431 | 179 | 209 | 44 |  | 543 | 384 | 179 | 215 | 107 |  | 0 | 0 | 0 | 0 | 0 |  | 528 | 404 | 100 | 201 | 242 |  | 0 | 0 | 0 | 0 | 0 |  | 381 | 502 | 92 | 124 | 376 | [22 empty] | 109780.3162 | 89725.4366 | 151701.6395 | 352811.3955 | 318307.2976 | 1022326.0853 |  | 128886.9746 | 100867.0364 | 151701.6395 | 342988.3404 | 109828.5935 | 834272.5842 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 109543.2609 | 93826.4935 | 87031.6599 | 317120.962 | 667075.9608 | 1274598.3371 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818 |  | 79460.9415 | 112221.9859 | 83364.3443 | 192204.4447 | 1029538.2654 | 1496789.9818
| EHV Transformer |  | 397 | 397 | C1 | 58 | 263 | 49 | 15 | 12 | 397 | 51 | 262 | 49 | 21 | 14 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 211 | 104 | 10 | 23 | 397 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 188 | 137 | 28 | 28 | 397 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | 107546.4948 | C1 | 914.8668 | 914.8668 | 3426.7195 | 7107.5305 | 14545.0524 | C1 | 46658.209 | 239695.1127 | 167909.2578 | 149258.1402 | 203630.7342 | 807151.454 |  | 53062.2769 | 240609.9796 | 167909.2578 | 106612.9573 | 174540.6294 | 742735.101 |  | 44828.4753 | 193036.9038 | 356378.833 | 71075.3049 | 334536.2063 | 999855.7232 |  | 44828.4753 | 193036.9038 | 356378.833 | 71075.3049 | 334536.2063 | 999855.7232 |  | 14637.8695 | 171994.9664 | 469460.5781 | 199010.8537 | 407261.4685 | 1262365.7361 |  | 14637.8695 | 171994.9664 | 469460.5781 | 199010.8537 | 407261.4685 | 1262365.7361
|  |  | 456 | 456 | C2 | 46 | 344 | 46 | 9 | 11 | 456 | 42 | 341 | 46 | 13 | 13 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 270 | 122 | 9 | 17 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 193 | 198 | 33 | 18 | 456 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | 153637.8497 | C2 | 1306.9526 | 1306.9526 | 4895.3136 | 10153.615 | 20778.6464 | C2 | 54892.0106 | 445670.8476 | 225184.4274 | 131996.9948 | 270122.4026 | 1127866.6829 |  | 60119.8211 | 449591.7055 | 225184.4274 | 91382.5348 | 228565.1099 | 1054843.5987 |  | 49664.2 | 352877.2107 | 597228.2641 | 91382.5348 | 353236.988 | 1444389.1976 |  | 49664.2 | 352877.2107 | 597228.2641 | 91382.5348 | 353236.988 | 1444389.1976 |  | 18297.3369 | 252241.858 | 969272.1007 | 335069.2944 | 374015.6343 | 1948896.2243 |  | 18297.3369 | 252241.858 | 969272.1007 | 335069.2944 | 374015.6343 | 1948896.2243
|  |  | 28 | 28 | C3 | 13 | 11 | 3 | 0 | 1 | 28 | 12 | 9 | 3 | 2 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 4 | 1 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 16 | 3 | 2 | 2 | 28 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | 230456.7745 | C3 | 1960.4289 | 1960.4289 | 7342.9705 | 15230.4225 | 31167.9695 | C3 | 23525.1474 | 17643.8605 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 25485.5763 | 21564.7184 | 22028.9114 | 0 | 31167.9695 | 100247.1757 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 19604.2895 | 21564.7184 | 29371.8818 | 15230.4225 | 62335.9391 | 148107.2513 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033 |  | 9802.1447 | 31366.8632 | 22028.9114 | 30460.8449 | 62335.9391 | 155994.7033
|  |  | 28 | 28 | C4 | 6 | 20 | 2 | 0 | 0 | 28 | 6 | 20 | 2 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 17 | 6 | 0 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 9 | 0 | 0 | 28 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | 384094.6242 | C4 | 3267.3816 | 3267.3816 | 12238.2841 | 25384.0375 | 51946.6159 | C4 | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 19604.2895 | 65347.6316 | 24476.5682 | 0 | 0 | 109428.4893 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 16336.9079 | 55545.4869 | 73429.7046 | 0 | 0 | 145312.0994 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069 |  | 0 | 62080.25 | 110144.5569 | 0 | 0 | 172224.8069
|  |  | 909 | 909 |  | 123 | 638 | 100 | 24 | 24 |  | 111 | 632 | 100 | 36 | 29 |  | 0 | 0 | 0 | 0 | 0 |  | 102 | 509 | 236 | 20 | 42 |  | 0 | 0 | 0 | 0 | 0 |  | 35 | 416 | 347 | 63 | 48 | [22 empty] | 144679.6564 | 768357.4525 | 439599.1649 | 311715.98 | 536089.0759 | 2200441.3295 |  | 158271.9638 | 777114.0351 | 439599.1649 | 197995.4922 | 434273.7087 | 2007254.3646 |  | 130433.8727 | 623024.3198 | 1056408.6835 | 177688.2622 | 750109.1333 | 2737664.2714 |  | 130433.8727 | 623024.3198 | 1056408.6835 | 177688.2622 | 750109.1333 | 2737664.2714 |  | 42737.3511 | 517683.9376 | 1570906.1471 | 564540.993 | 843613.0419 | 3539481.4706 |  | 42737.3511 | 517683.9376 | 1570906.1471 | 564540.993 | 843613.0419 | 3539481.4706
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 277 | 277 | C1 | 24 | 149 | 75 | 12 | 17 | 277 | 24 | 194 | 56 | 2 | 32 | 308 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 148 | 92 | 8 | 27 | 277 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 102 | 126 | 13 | 34 | 277 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | 224372.4 | C1 | 119.927 | 119.927 | 449.5301 | 926.8824 | 1907.1654 | C1 | 2878.2491 | 23265.8473 | 25173.6858 | 1853.7648 | 61029.2928 | 114200.8398 |  | 2878.2491 | 17869.1301 | 33714.7578 | 11122.5886 | 32421.8118 | 98006.5374 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 17749.2031 | 41356.7695 | 7415.0591 | 51493.4658 | 118254.3516 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006 |  | 239.8541 | 12232.5589 | 56640.793 | 12049.471 | 64843.6236 | 146006.3006
|  |  | 199 | 199 | C2 | 17 | 106 | 54 | 10 | 12 | 199 | 12 | 142 | 46 | 2 | 19 | 221 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 106 | 65 | 7 | 19 | 199 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 72 | 91 | 9 | 25 | 199 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 320532 | 320532 | 320532 | 320532 | 320532 | C2 | 171.3244 | 171.3244 | 642.1859 | 1324.1177 | 2724.522 | C2 | 2055.8922 | 24328.0583 | 29540.5497 | 2648.2354 | 51765.918 | 110338.6536 |  | 2912.514 | 18160.3815 | 34678.0365 | 13241.1769 | 32694.264 | 101686.373 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 18160.3815 | 41742.081 | 9268.8238 | 51765.918 | 121279.8531 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249 |  | 342.6487 | 12335.3535 | 58438.9134 | 11917.0592 | 68113.05 | 151147.0249
|  |  | 69 | 69 | C3 | 6 | 37 | 19 | 3 | 4 | 69 | 12 | 43 | 13 | 1 | 2 | 71 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 23 | 2 | 7 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 31 | 3 | 8 | 69 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 480798 | 480798 | 480798 | 480798 | 480798 | C3 | 256.9865 | 256.9865 | 963.2788 | 1986.1765 | 4086.783 | C3 | 3083.8384 | 11050.4208 | 12522.6243 | 1986.1765 | 8173.566 | 36816.6261 |  | 1541.9192 | 9508.5016 | 18302.2971 | 5958.5296 | 16347.132 | 51658.3795 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 9508.5016 | 22155.4122 | 3972.3531 | 28607.481 | 64243.748 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725 |  | 0 | 6938.6363 | 29861.6426 | 5958.5296 | 32694.264 | 75453.0725
|  |  | 11 | 11 | C4 | 1 | 6 | 3 | 0 | 1 | 11 | 0 | 9 | 2 | 0 | 0 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 0 | 1 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 1 | 1 | 11 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 801330 | 801330 | 801330 | 801330 | 801330 | C4 | 428.3109 | 428.3109 | 1605.4647 | 3310.2942 | 6811.305 | C4 | 0 | 3854.798 | 3210.9293 | 0 | 0 | 7065.7273 |  | 428.3109 | 2569.8653 | 4816.394 | 0 | 6811.305 | 14625.8752 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 2569.8653 | 6421.8586 | 0 | 6811.305 | 15803.0289 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166 |  | 0 | 1713.2435 | 8027.3233 | 3310.2942 | 6811.305 | 19862.166
|  |  | 556 | 556 |  | 48 | 298 | 151 | 25 | 34 |  | 48 | 388 | 117 | 5 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 4 | 297 | 184 | 17 | 54 |  | 0 | 0 | 0 | 0 | 0 |  | 4 | 205 | 253 | 26 | 68 | [22 empty] | 8017.9798 | 62499.1243 | 70447.7891 | 6488.1767 | 120968.7768 | 268421.8467 |  | 7760.9932 | 48107.8786 | 91511.4853 | 30322.2951 | 88274.5128 | 265977.1651 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 47987.9516 | 111676.1214 | 20656.236 | 138678.1698 | 319580.9816 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564 |  | 582.5028 | 33219.7922 | 152968.6723 | 33235.3541 | 172462.2426 | 392468.564
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 846 | 846 | C1 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 44 | 495 | 169 | 138 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 351 | 204 | 247 | 846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 317 | 237 | 248 | 846 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 36.5855 | 85.2982 | C1 | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 5217.4672 | 6182.9446 | 11771.1566 | 23171.5684 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3699.6585 | 7463.4361 | 21068.6644 | 32231.759 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063 |  | 0 | 0 | 3341.2871 | 8670.7567 | 21153.9626 | 33166.0063
|  |  | 18 | 18 | C2 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 11 | 4 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 5 | 5 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 6 | 5 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 52.265 | 121.8546 | C2 | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 165.6339 | 209.0598 | 365.5639 | 740.2576 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 120.461 | 261.3248 | 609.2731 | 991.0589 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662 |  | 0 | 0 | 105.4034 | 313.5898 | 609.2731 | 1028.2662
|  |  | 2 | 2 | C3 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 2 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 78.3974 | 182.7819 | C3 | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 22.5864 | 0 | 0 | 22.5864 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819 |  | 0 | 0 | 0 | 0 | 182.7819 | 182.7819
|  |  | 287 | 287 | C4 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 15 | 168 | 57 | 47 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 119 | 69 | 84 | 287 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 108 | 80 | 84 | 287 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 130.6624 | 304.6366 | C4 | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 6324.2026 | 7447.7566 | 14317.9182 | 28089.8775 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4479.6435 | 9015.7054 | 25589.4709 | 39084.8198 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215 |  | 0 | 0 | 4065.5588 | 10452.9918 | 25589.4709 | 40108.0215
|  |  | 1153 | 1153 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 60 | 675 | 230 | 188 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 478 | 278 | 337 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 60 | 432 | 323 | 338 | [22 empty] | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 11729.8901 | 13839.7611 | 26454.6387 | 52024.29 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 8299.7631 | 16740.4663 | 47450.1903 | 72490.4197 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076 |  | 0 | 0 | 7512.2493 | 19437.3382 | 47535.4885 | 74485.076
| EHV OHL Support - Poles |  | 7548 | 7548 | C1 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 1181 | 5421 | 350 | 326 | 270 | 7548 | 0 | 0 | 0 | 0 | 0 | 0 | 877 | 5407 | 606 | 139 | 519 | 7548 | 0 | 0 | 0 | 0 | 0 | 0 | 725 | 4922 | 1093 | 176 | 632 | 7548 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | 36591.1 | C1 | 12.5427 | 12.5427 | 47.1998 | 99.2168 | 152.9599 | C1 | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 14812.8942 | 67993.8184 | 16519.9214 | 32344.6817 | 41299.1758 | 172970.4914 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 10999.9223 | 67818.221 | 28603.0639 | 13791.1373 | 79386.1934 | 200598.5379 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392 |  | 9093.4363 | 61735.0257 | 51589.3545 | 17462.1594 | 96670.6633 | 236550.6392
|  |  | 27483 | 27483 | C2 | 4303 | 19734 | 1275 | 1189 | 982 | 27483 | 3986 | 19740 | 1275 | 1189 | 1299 | 27489 | 0 | 0 | 0 | 0 | 0 | 0 | 3193 | 19693 | 2205 | 504 | 1888 | 27483 | 0 | 0 | 0 | 0 | 0 | 0 | 2641 | 17922 | 3979 | 640 | 2301 | 27483 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 52273 | 52273 | 52273 | 52273 | 52273 | C2 | 17.9181 | 17.9181 | 67.4283 | 141.7383 | 218.5142 | C2 | 71421.5511 | 353703.3165 | 85971.0194 | 168526.8472 | 283849.8906 | 963472.6248 |  | 77101.5892 | 353595.8079 | 85971.0194 | 168526.8472 | 214580.9027 | 899776.1663 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 57212.4969 | 352861.1657 | 148679.2923 | 71436.1068 | 412554.7294 | 1042743.7912 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155 |  | 47321.7051 | 321128.2086 | 268297.0087 | 90712.5166 | 502801.0764 | 1230260.5155
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | 78409.5 | C3 | 26.8772 | 26.8772 | 101.1424 | 212.6075 | 327.7712 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | 130682.5 | C4 | 44.7953 | 44.7953 | 168.5706 | 354.3458 | 546.2854 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 35031 | 35031 |  | 5484 | 25155 | 1625 | 1515 | 1252 |  | 5167 | 25161 | 1625 | 1515 | 1569 |  | 0 | 0 | 0 | 0 | 0 |  | 4070 | 25100 | 2811 | 643 | 2407 |  | 0 | 0 | 0 | 0 | 0 |  | 3366 | 22844 | 5072 | 816 | 2933 | [22 empty] | 86234.4454 | 421697.1349 | 102490.9408 | 200871.5289 | 325149.0664 | 1136443.1163 |  | 91914.4834 | 421589.6263 | 102490.9408 | 200871.5289 | 255880.0785 | 1072746.6578 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 68212.4192 | 420679.3867 | 177282.3562 | 85227.2441 | 491940.9228 | 1243342.3291 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546 |  | 56415.1414 | 382863.2343 | 319886.3632 | 108174.676 | 599471.7397 | 1466811.1546
| EHV OHL Fittings and Conductors (Tower Lines) |  | 335 | 335 | C1 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 44 | 201 | 90 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 188 | 97 | 16 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 102 | 154 | 50 | 335 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | 130506.2558 | C1 | 0 | 0 | 10.5403 | 34.3512 | 66.6554 | C1 | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 2118.6079 | 3091.6084 | 0 | 5210.2163 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1981.5835 | 3332.0668 | 1066.4867 | 6380.137 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708 |  | 0 | 0 | 1075.1145 | 5290.0854 | 3332.7709 | 9697.9708
|  |  | 17 | 17 | C2 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 10 | 5 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 8 | 3 | 17 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | 186437.5082 | C2 | 0 | 0 | 15.0576 | 49.0731 | 95.222 | C2 | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 150.5763 | 245.3657 | 0 | 395.942 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394 |  | 0 | 0 | 75.2881 | 392.5852 | 285.6661 | 753.5394
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | 279656.2624 | C3 | 0 | 0 | 22.5864 | 73.6097 | 142.833 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 163 | 163 | C4 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 22 | 97 | 44 | 0 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 92 | 47 | 8 | 163 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 50 | 75 | 24 | 163 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | 466093.7706 | C4 | 0 | 0 | 37.6441 | 122.6829 | 238.0551 | C4 | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3651.4741 | 5398.0464 | 0 | 9049.5205 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 3463.2538 | 5766.095 | 1904.4405 | 11133.7893 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401 |  | 0 | 0 | 1882.2032 | 9201.2154 | 5713.3215 | 16796.7401
|  |  | 515 | 515 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 68 | 308 | 139 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 52 | 290 | 149 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 44 | 157 | 237 | 77 | [22 empty] | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5920.6583 | 8735.0205 | 0 | 14655.6788 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 5595.4136 | 9343.5275 | 2970.9272 | 17909.8683 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502 |  | 0 | 0 | 3032.6057 | 14883.886 | 9331.7585 | 27248.2502
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 |  | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 |  | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 |  | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 |  | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 |  | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 188 | 188 | C1 | 70 | 62 | 25 | 18 | 13 | 188 | 39 | 62 | 25 | 18 | 44 | 188 | 22 | 0 | 0 | -8 | -14 | 0 | 48 | 63 | 27 | 14 | 36 | 188 | 22 | 0 | 0 | -8 | -14 | 0 | 42 | 58 | 26 | 12 | 50 | 188 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | 112077.0526 | C1 | 579.6435 | 579.6435 | 2212.3775 | 3916.6144 | 6007.2213 | C1 | 22606.0951 | 35937.8947 | 55309.4371 | 70499.0596 | 264317.7374 | 448670.2238 |  | 40575.0424 | 35937.8947 | 55309.4371 | 70499.0596 | 78093.877 | 280415.3107 |  | 27822.8862 | 36517.5382 | 59734.192 | 54832.6019 | 216259.967 | 395167.1853 |  | 40575.0424 | 36517.5382 | 59734.192 | 23499.6865 | 132158.8687 | 292485.3278 |  | 24345.0254 | 33619.3209 | 57521.8145 | 46999.373 | 300361.0653 | 462846.5991 |  | 37097.1816 | 33619.3209 | 57521.8145 | 15666.4577 | 216259.967 | 360164.7417
|  |  | 51 | 51 | C2 | 26 | 13 | 9 | 2 | 1 | 51 | 23 | 23 | 9 | 2 | 4 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 8 | 9 | 3 | 6 | 51 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 8 | 3 | 7 | 9 | 51 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | 160110.0752 | C2 | 828.0621 | 828.0621 | 3160.5393 | 5595.1635 | 8581.7447 | C2 | 19045.4281 | 19045.4281 | 28444.8533 | 11190.3269 | 34326.9789 | 112053.0153 |  | 21529.6143 | 10764.8072 | 28444.8533 | 11190.3269 | 8581.7447 | 80511.3465 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 20701.5523 | 6624.4967 | 28444.8533 | 16785.4904 | 51490.4683 | 124046.861 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514 |  | 19873.4902 | 6624.4967 | 9481.6178 | 39166.1442 | 77235.7025 | 152381.4514
|  |  | 54 | 54 | C3 | 47 | 5 | 2 | 0 | 0 | 54 | 47 | 5 | 2 | 0 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 3 | 3 | 0 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 27 | 1 | 2 | 2 | 54 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | 240165.1127 | C3 | 1242.0931 | 1242.0931 | 4740.8089 | 8392.7452 | 12872.6171 | C3 | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 58378.3773 | 6210.4657 | 9481.6178 | 0 | 0 | 74070.4608 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 57136.2842 | 3726.2794 | 14222.4267 | 0 | 25745.2342 | 100830.2245 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097 |  | 27326.049 | 33536.5146 | 4740.8089 | 16785.4904 | 25745.2342 | 108134.097
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | 400275.1879 | C4 | 2070.1552 | 2070.1552 | 7901.3482 | 13987.9086 | 21454.3618 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293 | 293 |  | 143 | 80 | 36 | 20 | 14 |  | 109 | 90 | 36 | 20 | 48 |  | 22 | 0 | 0 | -8 | -14 |  | 119 | 74 | 39 | 17 | 44 |  | 22 | 0 | 0 | -8 | -14 |  | 88 | 93 | 30 | 21 | 61 | [22 empty] | 100029.9005 | 61193.7885 | 93235.9082 | 81689.3865 | 298644.7163 | 634793.6999 |  | 120483.0341 | 52913.1676 | 93235.9082 | 81689.3865 | 86675.6217 | 434997.118 |  | 105660.7227 | 46868.3143 | 102401.472 | 71618.0922 | 293495.6695 | 620044.2708 |  | 118412.8789 | 46868.3143 | 102401.472 | 40285.1769 | 209394.5712 | 517362.4133 |  | 71544.5646 | 73780.3322 | 71744.2412 | 102951.0076 | 403342.0019 | 723362.1475 |  | 84296.7208 | 73780.3322 | 71744.2412 | 71618.0922 | 319240.9037 | 620680.2901
| 132kV Transformer |  | 86 | 86 | C1 | 21 | 61 | 2 | 1 | 1 | 86 | 21 | 61 | 2 | 1 | 1 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 49 | 15 | 2 | 1 | 86 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 42 | 32 | 3 | 2 | 86 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | 328645.8 | C1 | 2795.6945 | 2795.6945 | 10471.536 | 21719.5367 | 44447.4774 | C1 | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 58709.5848 | 170537.3653 | 20943.0719 | 21719.5367 | 44447.4774 | 316357.0362 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 53118.1958 | 136989.0312 | 157073.0394 | 43439.0735 | 44447.4774 | 435066.8172 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468 |  | 19569.8616 | 117419.1696 | 335089.1507 | 65158.6102 | 88894.9548 | 626131.7468
|  |  | 156 | 156 | C2 | 23 | 101 | 23 | 5 | 4 | 156 | 21 | 94 | 23 | 10 | 4 | 152 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 72 | 48 | 11 | 6 | 156 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 64 | 54 | 21 | 8 | 156 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469494 | 469494 | 469494 | 469494 | 469494 | C2 | 3993.8493 | 3993.8493 | 14959.3371 | 31027.9096 | 63496.3963 | C2 | 83870.8354 | 375421.8346 | 344064.7529 | 310279.0961 | 253985.5852 | 1367622.1043 |  | 91858.534 | 403378.7798 | 344064.7529 | 155139.5481 | 253985.5852 | 1248427.2 |  | 75883.1368 | 287557.1499 | 718048.18 | 341307.0057 | 380978.3778 | 1803773.8503 |  | 75883.1368 | 287557.1499 | 718048.18 | 341307.0057 | 380978.3778 | 1803773.8503 |  | 35944.6437 | 255606.3555 | 807804.2025 | 651586.1019 | 507971.1704 | 2258912.4741 |  | 35944.6437 | 255606.3555 | 807804.2025 | 651586.1019 | 507971.1704 | 2258912.4741
|  |  | 22 | 22 | C3 | 3 | 10 | 5 | 0 | 4 | 22 | 2 | 10 | 5 | 0 | 5 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 8 | 1 | 4 | 22 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 8 | 7 | 2 | 4 | 22 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 704241 | 704241 | 704241 | 704241 | 704241 | C3 | 5990.774 | 5990.774 | 22439.0056 | 46541.8644 | 95244.5945 | C3 | 11981.5479 | 59907.7396 | 112195.0281 | 0 | 476222.9723 | 660307.2879 |  | 17972.3219 | 59907.7396 | 112195.0281 | 0 | 380978.3778 | 571053.4674 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 17972.3219 | 35944.6437 | 179512.045 | 46541.8644 | 380978.3778 | 660949.2529 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117 |  | 5990.774 | 47926.1917 | 157073.0394 | 93083.7288 | 380978.3778 | 685052.1117
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1173735 | 1173735 | 1173735 | 1173735 | 1173735 | C4 | 9984.6233 | 9984.6233 | 37398.3427 | 77569.774 | 158740.9908 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 264 | 264 |  | 47 | 172 | 30 | 6 | 9 |  | 44 | 165 | 30 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 127 | 71 | 14 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 17 | 114 | 93 | 26 | 14 | [22 empty] | 154561.9681 | 605866.9395 | 477202.853 | 331998.6329 | 774656.0349 | 2344286.4284 |  | 168540.4407 | 633823.8847 | 477202.853 | 176859.0848 | 679411.4405 | 2135837.7036 |  | 146973.6544 | 460490.8248 | 1054633.2644 | 431287.9436 | 806404.2331 | 2899789.9204 |  | 146973.6544 | 460490.8248 | 1054633.2644 | 431287.9436 | 806404.2331 | 2899789.9204 |  | 61505.2793 | 420951.7167 | 1299966.3926 | 809828.4409 | 977844.5031 | 3570096.3326 |  | 61505.2793 | 420951.7167 | 1299966.3926 | 809828.4409 | 977844.5031 | 3570096.3326
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 30 | 30 | C1 | 0 | 23 | 3 | 1 | 3 | 30 | 1 | 25 | 4 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 1 | 5 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 8 | 1 | 5 | 30 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | 535263.4 | C1 | 286.0983 | 286.0983 | 1072.4002 | 2211.1731 | 4549.7389 | C1 | 286.0983 | 7152.4572 | 4289.6009 | 0 | 0 | 11728.1564 |  | 0 | 6580.2606 | 3217.2007 | 2211.1731 | 13649.2167 | 25657.8511 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 5435.8675 | 5362.0011 | 2211.1731 | 22748.6945 | 35757.7362 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642 |  | 0 | 4577.5726 | 8579.2018 | 2211.1731 | 22748.6945 | 38116.642
|  |  | 68 | 68 | C2 | 1 | 49 | 8 | 2 | 8 | 68 | 2 | 57 | 9 | 1 | 0 | 69 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 43 | 12 | 2 | 10 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 34 | 18 | 3 | 12 | 68 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 764662 | 764662 | 764662 | 764662 | 764662 | C2 | 408.7118 | 408.7118 | 1532.0003 | 3158.8187 | 6499.627 | C2 | 817.4237 | 23296.5748 | 13788.0029 | 3158.8187 | 0 | 41060.8201 |  | 408.7118 | 20026.8801 | 12256.0025 | 6317.6374 | 51997.016 | 91006.2479 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 17574.6091 | 18384.0038 | 6317.6374 | 64996.27 | 107681.2322 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002 |  | 408.7118 | 13896.2025 | 27576.0057 | 9476.4562 | 77995.524 | 129352.9002
|  |  | 43 | 43 | C3 | 1 | 30 | 5 | 2 | 5 | 43 | 1 | 36 | 6 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 25 | 8 | 2 | 7 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 20 | 12 | 2 | 8 | 43 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1146993 | 1146993 | 1146993 | 1146993 | 1146993 | C3 | 613.0678 | 613.0678 | 2298.0005 | 4738.2281 | 9749.4405 | C3 | 613.0678 | 22070.4393 | 13788.0029 | 0 | 0 | 36471.5099 |  | 613.0678 | 18392.0328 | 11490.0024 | 9476.4562 | 48747.2025 | 88718.7616 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 15326.694 | 18384.0038 | 9476.4562 | 68246.0835 | 112046.3052 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088 |  | 613.0678 | 12261.3552 | 27576.0057 | 9476.4562 | 77995.524 | 127922.4088
|  |  | 49 | 49 | C4 | 1 | 34 | 6 | 2 | 6 | 49 | 2 | 39 | 7 | 1 | 3 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 30 | 9 | 2 | 7 | 49 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 24 | 13 | 2 | 9 | 49 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1911655 | 1911655 | 1911655 | 1911655 | 1911655 | C4 | 1021.7796 | 1021.7796 | 3830.0008 | 7897.0468 | 16249.0675 | C4 | 2043.5592 | 39849.4043 | 26810.0055 | 7897.0468 | 48747.2025 | 125347.2184 |  | 1021.7796 | 34740.5063 | 22980.0048 | 15794.0936 | 97494.405 | 172030.7893 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 30653.3879 | 34470.0071 | 15794.0936 | 113743.4725 | 195682.7408 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013 |  | 1021.7796 | 24522.7103 | 49790.0103 | 15794.0936 | 146241.6075 | 237370.2013
|  |  | 190 | 190 |  | 3 | 136 | 22 | 7 | 22 |  | 6 | 157 | 26 | 2 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 117 | 34 | 7 | 29 |  | 0 | 0 | 0 | 0 | 0 |  | 3 | 94 | 51 | 8 | 34 | [22 empty] | 3760.1489 | 92368.8756 | 58675.6121 | 11055.8655 | 48747.2025 | 214607.7047 |  | 2043.5592 | 79739.6798 | 49943.2103 | 33799.3603 | 211887.8402 | 377413.6498 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 68990.5584 | 76600.0158 | 33799.3603 | 269734.5205 | 451168.0143 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524 |  | 2043.5592 | 55257.8406 | 113521.2235 | 36958.179 | 324981.35 | 532762.1524
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 51.9831 | 121.1975 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4405 | 4405 | C2 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 1073 | 2546 | 595 | 191 | 4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1073 | 2538 | 601 | 193 | 4405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1062 | 2518 | 627 | 198 | 4405 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 74.2616 | 173.1393 | C2 | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54471.392 | 44185.6416 | 33069.6018 | 131726.6353 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 54300.2328 | 44631.2111 | 33415.8803 | 132347.3242 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924 |  | 0 | 0 | 53872.335 | 46562.0122 | 34281.5767 | 134715.924
|  |  | 342 | 342 | C3 | 0 | 83 | 198 | 46 | 15 | 342 | 0 | 83 | 198 | 46 | 15 | 342 | 3 | 0 | 0 | -3 | 0 | 0 | 0 | 83 | 197 | 47 | 15 | 342 | 3 | 0 | 0 | -3 | 0 | 0 | 0 | 83 | 195 | 49 | 15 | 342 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 111.3924 | 259.7089 | C3 | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6354.2826 | 5124.0492 | 3895.6337 | 15373.9655 |  | 0 | 0 | 6322.1902 | 5235.4416 | 3895.6337 | 15453.2655 |  | 0 | 0 | 6322.1902 | 4901.2644 | 3895.6337 | 15119.0884 |  | 0 | 0 | 6258.0056 | 5458.2263 | 3895.6337 | 15611.8656 |  | 0 | 0 | 6258.0056 | 5124.0492 | 3895.6337 | 15277.6885
|  |  | 8 | 8 | C4 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 1 | 0 | 8 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 185.654 | 432.8482 | C4 | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901 |  | 0 | 0 | 267.4361 | 185.654 | 0 | 453.0901
|  |  | 4755 | 4755 |  | 0 | 1158 | 2749 | 642 | 206 |  | 0 | 1158 | 2749 | 642 | 206 |  | 3 | 0 | 0 | -3 | 0 |  | 0 | 1158 | 2740 | 649 | 208 |  | 3 | 0 | 0 | -3 | 0 |  | 0 | 1147 | 2718 | 677 | 213 | [22 empty] | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 61093.1107 | 49495.3447 | 36965.2355 | 147553.6909 |  | 0 | 0 | 60889.8592 | 50052.3066 | 37311.514 | 148253.6799 |  | 0 | 0 | 60889.8592 | 49718.1295 | 37311.514 | 147919.5027 |  | 0 | 0 | 60397.7767 | 52205.8925 | 38177.2104 | 150780.8796 |  | 0 | 0 | 60397.7767 | 51871.7154 | 38177.2104 | 150446.7025
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | 185432.1 | C1 | 0 | 0 | 14.9764 | 48.8085 | 94.7085 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2361 | 2361 | C2 | 471 | 289 | 642 | 591 | 368 | 2361 | 413 | 252 | 642 | 591 | 426 | 2324 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 303 | 562 | 581 | 493 | 2361 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 649 | 257 | 698 | 699 | 2361 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 264903 | 264903 | 264903 | 264903 | 264903 | C2 | 0 | 0 | 21.3949 | 69.7264 | 135.2979 | C2 | 0 | 0 | 13735.5199 | 41208.3279 | 57636.898 | 112580.7458 |  | 0 | 0 | 13735.5199 | 41208.3279 | 49789.6208 | 104733.4686 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 12023.9286 | 40511.0635 | 66701.8562 | 119236.8483 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643 |  | 0 | 0 | 5498.4869 | 48669.0573 | 94573.22 | 148740.7643
|  |  | 196 | 196 | C3 | 43 | 21 | 54 | 50 | 28 | 196 | 38 | 21 | 54 | 50 | 33 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 22 | 48 | 49 | 41 | 196 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 51 | 22 | 59 | 59 | 196 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | 397354.5 | C3 | 0 | 0 | 32.0923 | 104.5897 | 202.9468 | C3 | 0 | 0 | 1732.9862 | 5229.4832 | 6697.2452 | 13659.7146 |  | 0 | 0 | 1732.9862 | 5229.4832 | 5682.5111 | 12644.9805 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 1540.4321 | 5124.8936 | 8320.8198 | 14986.1455 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842 |  | 0 | 0 | 706.0314 | 6170.7902 | 11973.8626 | 18850.6842
|  |  | 3 | 3 | C4 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 3 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | 662257.5 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | C4 | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 53.4872 | 174.3161 | 338.2447 | 566.048 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055 |  | 0 | 0 | 0 | 174.3161 | 676.4894 | 850.8055
|  |  | 2560 | 2560 |  | 514 | 310 | 697 | 642 | 397 |  | 451 | 273 | 697 | 642 | 460 |  | 0 | 0 | 0 | 0 | 0 |  | 458 | 325 | 611 | 631 | 535 |  | 0 | 0 | 0 | 0 | 0 |  | 63 | 700 | 279 | 758 | 760 | [22 empty] | 0 | 0 | 15521.9933 | 46612.1272 | 64672.3879 | 126806.5085 |  | 0 | 0 | 15521.9933 | 46612.1272 | 55810.3766 | 117944.4971 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 13617.848 | 45810.2731 | 75360.9207 | 134789.0418 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254 |  | 0 | 0 | 6204.5183 | 55014.1636 | 107223.5721 | 168442.254
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 |  | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 |  | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 |  | 267430.0925 | 576349.6976 | 1308142.4595 | 600900.8835 | 1398205.7595 | 4151028.8925 |  | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 |  | 147845.5593 | 549989.8896 | 1551834.1523 | 1025290.5912 | 1767467.5392 | 5042427.7316
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 643865 | 643865 |  | 108014 | 416640 | 71011 | 32459 | 15741 |  | 100295 | 415570 | 71117 | 33178 | 22842 |  | 25 | 0 | 0 | -11 | -14 |  | 67669 | 388473 | 121329 | 34588 | 31809 |  | 25 | 0 | 0 | -11 | -14 |  | 44233 | 354100 | 157644 | 44376 | 43514 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 |  | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 |  | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 |  | 2067149.2081 | 10502174.0244 | 13058952.4458 | 7162792.0151 | 11086906.0588 | 43877973.7523 |  | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 |  | 1247963.8993 | 9600571.0178 | 16558183.4661 | 9769706.1897 | 14931685.256 | 52108109.8289
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 955775.844 | 4126284.5305 | 2661232.8121 | 3506760.8439 | 3111511.6505 | 14361565.681 | LV Network | 1041848.142 | 4130382.5047 | 2661232.8121 | 3483119.4952 | 2132399.048 | 13448982.0021 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 636549.7563 | 3918769.2646 | 3424872.7789 | 4098261.0016 | 3734197.9719 | 15812650.7733 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121 | LV Network | 550780.3994 | 3492896.8826 | 3734985.9901 | 5402407.0797 | 5147613.6603 | 18328684.0121
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 1234396.7587 | 5272991.5801 | 4123826.347 | 1758429.6875 | 2319880.7587 | 14709525.1319 | HV Network | 1318061.8248 | 5317579.1794 | 4101453.0104 | 1651553.6796 | 1517080.2102 | 13905727.9045 | HV Network | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 | HV Network | 854397.3038 | 4821536.9106 | 6879643.2097 | 1836853.4319 | 3856277.0233 | 18248707.8793 | HV Network | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879 | HV Network | 370142.0039 | 4511695.2956 | 9133692.9418 | 2409531.8268 | 5314651.5198 | 21739713.5879
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 348712.3977 | 1342279.1483 | 781890.0826 | 894461.8626 | 1326968.8553 | 4694312.3465 | EHV Network | 386834.415 | 1347678.5763 | 802953.7789 | 794752.4382 | 914711.5322 | 4246930.7405 | EHV Network | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 | EHV Network | 308772.0556 | 1185518.1516 | 1446293.9977 | 626776.6981 | 2098225.3042 | 5665586.2071 | EHV Network | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974 | EHV Network | 179195.9368 | 1045988.9501 | 2137670.3819 | 932476.692 | 2701952.5366 | 6997284.4974
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 258352.0175 | 759429.6036 | 705729.4772 | 520851.3568 | 1223685.5772 | 3468048.0323 | 132kV Network | 291067.034 | 766476.732 | 696997.0754 | 388455.3036 | 1070750.5145 | 3213746.6594 | 132kV Network | 254677.9363 | 576349.6976 | 1308142.4595 | 632567.9759 | 1482306.8578 | 4254044.9271 | 132kV Network | 267430.0925 | 576349.6976 | 1308142.4595 | 600900.8835 | 1398205.7595 | 4151028.8925 | 132kV Network | 135093.4031 | 549989.8896 | 1551834.1523 | 1056957.6837 | 1851568.6375 | 5145443.7662 | 132kV Network | 147845.5593 | 549989.8896 | 1551834.1523 | 1025290.5912 | 1767467.5392 | 5042427.7316
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 2797237.018 | 11500984.8624 | 8272678.7189 | 6680503.7508 | 7982046.8417 | 37233451.1918 | Total | 3037811.4158 | 11562116.9924 | 8262636.6768 | 6317880.9166 | 5634941.3048 | 34815387.3065 | Total | 2054397.052 | 10502174.0244 | 13058952.4458 | 7194459.1076 | 11171007.1571 | 43980989.7868 | Total | 2067149.2081 | 10502174.0244 | 13058952.4458 | 7162792.0151 | 11086906.0588 | 43877973.7523 | Total | 1235211.7431 | 9600571.0178 | 16558183.4661 | 9801373.2822 | 15015786.3542 | 52211125.8635 | Total | 1247963.8993 | 9600571.0178 | 16558183.4661 | 9769706.1897 | 14931685.256 | 52108109.8289
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EPN - Ave Crit
HI8: Secondary deliverables RIIO-ED1 - Average Criticality | [6 empty] | HI8: Secondary deliverables RIIO-ED1
EPN | [6 empty] | EPN
Price base (2012/13) | [6 empty] | Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period | [5 empty] | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure |  |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
| LV Network | [6 empty] | LV Network
| LV Switchgear and Other | 487 | 8406 | 1000 | 478 | 10371 |  | LV Switchgear and Other | 487 | 8406 | 1000 | 478 | 10371
| LV UGB | 704 | 8504 | 1500 | 475 | 11183 |  | LV UGB | 704 | 8504 | 1500 | 475 | 11183
| LV OHL Support | 878 | 7464 | 4620 | 622.3646 | 13584.3646 |  | LV OHL Support | 878 | 7464 | 4620 | 622.3646 | 13584.3646
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| HV Network | 0 | 0 | 0 | 0 | 0 |  | HV Network
| HV Switchgear (GM) - Primary | 30211 | 6786 | 4013 | 6970 | 47980 |  | HV Switchgear (GM) - Primary | 30211 | 6786 | 4013 | 6970 | 47980
| HV Switchgear (GM) - Distribution | 13635 | 7877 | 4689 | 2696 | 28897 |  | HV Switchgear (GM) - Distribution | 13635 | 7877 | 4689 | 2696 | 28897
| HV Transformer (GM) | 31531 | 6242 | 5330 | 11154 | 54257 |  | HV Transformer (GM) | 31531 | 6242 | 5330 | 11154 | 54257
| HV UG Cable | N/A | N/A | N/A | N/A | N/A |  | HV UG Cable | N/A | N/A | N/A | N/A | 0
| HV OHL Support - Poles | 11767 | 6562 | 4604 | 1551.0888 | 24484.0888 |  | HV OHL Support - Poles | 11767 | 6562 | 4604 | 1551.0888 | 24484.0888
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| EHV Network | 0 | 0 | 0 | 0 | 0 |  | EHV Network
| EHV Switchgear (GM) | 31346 | 3517 | 5565 | 13221.9635 | 53649.9635 |  | EHV Switchgear (GM) | 31346 | 3517 | 5565 | 13221.9635 | 53649.9635
| EHV Transformer | 88284 | 886 | 28993 | 35474.8497 | 153637.8497 |  | EHV Transformer | 88284 | 886 | 28993 | 35474.8497 | 153637.8497
| EHV UG Cable (Gas) | N/A | N/A | N/A | N/A | N/A |  | EHV UG Cable (Gas) | N/A | N/A | N/A | N/A | 0
| EHV UG Cable (Oil) | 143797 | 301 | 85968 | 90466 | 320532 |  | EHV UG Cable (Oil) | 143797 | 301 | 85968 | 90466 | 320532
| EHV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | N/A |  | EHV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | 0
| EHV OHL Support - Towers | 124765 | 15238.5082 | 14770 | 31664 | 186437.5082 |  | EHV OHL Support - Towers | 124765 | 15238.5082 | 14770 | 31664 | 186437.5082
| EHV OHL Support - Poles | 41122 | 4947 | 4620 | 1584 | 52273 |  | EHV OHL Support - Poles | 41122 | 4947 | 4620 | 1584 | 52273
| EHV OHL Fittings and Conductors (Tower Lines) | 124765 | 15238.5082 | 14770 | 31664 | 186437.5082 |  | EHV OHL Fittings and Conductors (Tower Lines) | 124765 | 15238.5082 | 14770 | 31664 | 186437.5082
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| 132kV Network | 0 | 0 | 0 | 0 | 0 |  | 132kV Network
| 132kV CBs | 106278 | 3957 | 19360 | 30515.0752 | 160110.0752 |  | 132kV CBs | 106278 | 3957 | 19360 | 30515.0752 | 160110.0752
| 132kV Transformer | 231927 | 889 | 63794 | 172884 | 469494 |  | 132kV Transformer | 231927 | 889 | 63794 | 172884 | 469494
| 132kV UG Cable (Gas) | N/A | N/A | N/A | N/A | N/A |  | 132kV UG Cable (Gas) | N/A | N/A | N/A | N/A | 0
| 132kV UG Cable (Oil) | 594233 | 301 | 79788 | 90340 | 764662 |  | 132kV UG Cable (Oil) | 594233 | 301 | 79788 | 90340 | 764662
| 132kV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | N/A |  | 132kV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | 0
| 132kV OHL Support - Tower | 191695 | 16219 | 14770 | 42219 | 264903 |  | 132kV OHL Support - Tower | 191695 | 16219 | 14770 | 42219 | 264903
| 132kV OHL Fittings and Conductors (Tower Lines) | 191695 | 16219 | 14770 | 42219 | 264903 |  | 132kV OHL Fittings and Conductors (Tower Lines) | 191695 | 16219 | 14770 | 42219 | 264903
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 |  | Other
| Submarine Cables | N/A | N/A | N/A | N/A | N/A |  | Submarine Cables | N/A | N/A | N/A | N/A | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]

## EPN - HI Probs. of Failure
CM105: HI Ratings Probabilities of Failure
EPN
Price base (2012/13)
Average Probabilities of Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0.0021631 | 0 | 0.004953 | 0.004953 | 0.010375 | 0.010375 | 0.014607 | 0.014607 | 0.025514 | LV Switchgear and Other | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061
| LV UGB | 0 | 0.0028671 | 0 | 0.0043007 | 0.0043007 | 0.010035 | 0.010035 | 0.021503 | 0.021503 | 0.04014 | LV UGB | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821
| LV OHL Support | 0 | 0.0030404 | 0 | 0.0030404 | 0.0030404 | 0.0030679 | 0.0030679 | 0.013754 | 0.013754 | 0.019599 | LV OHL Support | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear (at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB and LV Pillar OD (not at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV Network
| HV Switchgear (GM) - Primary | 0 | 0.0035024 | 0 | 0.0035024 | 0.0035024 | 0.0096073 | 0.0096073 | 0.014476 | 0.014476 | 0.018675 | HV Switchgear (GM) - Primary | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575
| HV Switchgear (GM) - Distribution | 0 | 0.0011172 | 0 | 0.0011172 | 0.0011172 | 0.0030822 | 0.0030822 | 0.0046174 | 0.0046174 | 0.008553 | HV Switchgear (GM) - Distribution | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852
| HV Transformer (GM) | 0 | 0.0017641 | 0 | 0.00215 | 0.00215 | 0.0039141 | 0.0039141 | 0.0076521 | 0.0076521 | 0.011857 | HV Transformer (GM) | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546
| HV UG Cable | 0 | 0.0017641 | 0 | 0.00215 | 0.00215 | 0.0039141 | 0.0039141 | 0.0076521 | 0.0076521 | 0.011857 | HV UG Cable | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546
| HV OHL Support - Poles | 0 | 0.0020607 | 0 | 0.0020607 | 0.0020607 | 0.0056934 | 0.0056934 | 0.010605 | 0.010605 | 0.014521 | HV OHL Support - Poles | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV Network
| EHV Switchgear (GM) | 0 | 0.0088371 | 0 | 0.0088371 | 0.0088371 | 0.024507 | 0.024507 | 0.036524 | 0.036524 | 0.067655 | EHV Switchgear (GM) | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209
| EHV Transformer | 0 | 0.017013 | 0 | 0.017013 | 0.017013 | 0.046712 | 0.046712 | 0.085464 | 0.085464 | 0.18502 | EHV Transformer | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524
| EHV UG Cable (Gas) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | EHV UG Cable (Gas) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| EHV UG Cable (Oil) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | EHV UG Cable (Oil) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.00039914 | 0.00039914 | 0.00090805 | EHV OHL Support - Towers | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359
| EHV OHL Support - Poles | 0 | 0.00068556 | 0 | 0.00068556 | 0.00068556 | 0.0018943 | 0.0018943 | 0.0035287 | 0.0035287 | 0.0048318 | EHV OHL Support - Poles | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.0003649 | 0.0003649 | 0.00065659 | EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV Network
| 132kV CBs | 0 | 0.010344 | 0 | 0.010344 | 0.010344 | 0.029136 | 0.029136 | 0.040756 | 0.040756 | 0.066443 | 132kV CBs | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599
| 132kV Transformer | 0 | 0.017013 | 0 | 0.017013 | 0.017013 | 0.046712 | 0.046712 | 0.085464 | 0.085464 | 0.18502 | 132kV Transformer | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524
| 132kV UG Cable (Gas) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | 132kV UG Cable (Gas) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| 132kV UG Cable (Oil) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | 132kV UG Cable (Oil) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.00039914 | 0.00039914 | 0.00090805 | 132kV OHL Support - Tower | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.0003649 | 0.0003649 | 0.00065659 | 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 13448982.0021 | 15812650.7733 | 13633248.8032 | 18328684.0121 | 14213404.4898
HV Network | 13905727.9045 | 18248707.8793 | 16587047.1215 | 21739713.5879 | 18310557.99
EHV Network | 4246930.7405 | 5665586.2071 | 4950555.2831 | 6997284.4974 | 5241166.6914
132kV Network | 3213746.6594 | 4254044.9271 | 3663551.4292 | 5145443.7662 | 3995868.055
Other | 0 | 0 | 0 | 0 | 0
Total | 34815387.3065 | 43980989.7868 | 38834402.637 | 52211125.8635 | 41760997.2263
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary Deliverables target)
LV Network |  | 2363668.7713 | -2179401.9701 | 4879702.0101 | -4115279.5223
HV Network |  | 4342979.9748 | -1661660.7578 | 7833985.6833 | -3429155.5978
EHV Network |  | 1418655.4666 | -715030.924 | 2750353.7569 | -1756117.806
132kV Network |  | 1040298.2676 | -590493.4979 | 1931697.1067 | -1149575.7111
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 9165602.4804 | -5146587.1498 | 17395738.557 | -10450128.6372