## NPgN - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
NPGN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 32035 | 32630 | C1 | 9664 | 7276 | 12171 | 1565 | 1359 | 32035 | 8728 | 7327 | 12342 | 1906 | 1617 | 31920 | 1661 | -39 | -244 | -480 | -670 | 228 | 8443 | 1599 | 8642 | 10620 | 2211 | 31515 | 3901 | -87 | -560 | -1110 | -1549 | 595 | 7452 | 1226 | 6986 | 10535 | 5206 | 31405 |  |  | C1 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C1 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | C1 | 0.12877 | 0.55385 | 1.5985 | 3.5782 | 6.808 | C1 | 1123.9253 | 4058.0377 | 19729.2174 | 6819.9924 | 11008.5989 | 42739.7717 |  | 1244.4562 | 4029.7915 | 19455.8666 | 5599.8363 | 9252.1249 | 39582.0755 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 1301.1161 | 864.0015 | 13424.5639 | 36282.6457 | 10491.1879 | 62363.5151 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723 |  | 1461.9528 | 630.8318 | 10272.2372 | 33724.254 | 24896.9983 | 70986.2741
|  |  | 23767 | 22983 | C2 | 6593 | 5704 | 9745 | 886 | 839 | 23767 | 5948 | 5742 | 9876 | 1268 | 1127 | 23961 | 1145 | -23 | -190 | -538 | -750 | -356 | 5770 | 1274 | 6931 | 7777 | 1467 | 23219 | 2684 | -55 | -434 | -1242 | -1737 | -784 | 5104 | 992 | 5617 | 7720 | 3656 | 23089 |  |  | C2 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C2 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | C2 | 0.18396 | 0.79121 | 2.2836 | 5.1117 | 9.7258 | C2 | 1094.1973 | 4543.1286 | 22553.1578 | 6481.5997 | 10960.9426 | 45633.026 |  | 1212.8518 | 4513.0626 | 22254.0019 | 4528.9411 | 8159.9209 | 40668.7784 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 1272.0871 | 989.8039 | 15393.9689 | 37003.3914 | 6973.377 | 61632.6283 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007 |  | 1432.6847 | 741.3639 | 11836.0689 | 33113.4092 | 18663.7524 | 65787.2791
|  |  | 6362 | 6508 | C3 | 761 | 1889 | 2641 | 666 | 405 | 6362 | 689 | 1903 | 2679 | 666 | 405 | 6342 | 128 | -13 | -54 | 0 | 0 | 61 | 662 | 410 | 1873 | 3143 | 598 | 6686 | 301 | -29 | -126 | 0 | 0 | 146 | 582 | 312 | 1512 | 3118 | 1282 | 6806 |  |  | C3 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C3 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | C3 | 0.27594 | 1.1868 | 3.4254 | 7.6675 | 14.5887 | C3 | 190.1232 | 2258.5093 | 9176.7785 | 5106.56 | 5908.4052 | 22640.3763 |  | 209.991 | 2241.8939 | 9046.6114 | 5106.56 | 5908.4052 | 22513.4615 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 217.9932 | 471.1656 | 6230.8922 | 24098.9762 | 8724.0156 | 39743.0428 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071 |  | 243.6557 | 335.8687 | 4747.6726 | 23907.2885 | 18702.6554 | 47937.141
|  |  | 9964 | 9207 | C4 | 1217 | 3352 | 4087 | 861 | 447 | 9964 | 1100 | 3376 | 4145 | 989 | 545 | 10155 | 206 | -21 | -84 | -182 | -252 | -333 | 1061 | 733 | 2900 | 5277 | 737 | 10708 | 484 | -45 | -192 | -421 | -583 | -757 | 934 | 560 | 2341 | 5234 | 1759 | 10828 |  |  | C4 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C4 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | C4 | 0.4599 | 1.978 | 5.7091 | 12.7792 | 24.3144 | C4 | 505.8915 | 6677.8136 | 23664.1451 | 12638.6083 | 13251.3614 | 56737.8199 |  | 559.6999 | 6630.341 | 23333.0184 | 11002.8733 | 10868.5478 | 52394.4804 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 582.695 | 1408.354 | 16076.7751 | 65109.9182 | 11792.496 | 94970.2383 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003 |  | 652.1401 | 1018.6831 | 12268.8173 | 61506.1897 | 28593.7634 | 104039.5936
|  |  | 72128 | 71328 |  | 18235 | 18221 | 28644 | 3978 | 3050 |  | 16465 | 18348 | 29042 | 4829 | 3694 |  | 3140 | -96 | -572 | -1200 | -1672 |  | 15936 | 4016 | 20346 | 26817 | 5013 |  | 7370 | -216 | -1312 | -2773 | -3869 |  | 14072 | 3090 | 16456 | 26607 | 11903 | [22 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1598 | 1589 | C1 | 200 | 510 | 480 | 286 | 122 | 1598 | 168 | 514 | 493 | 307 | 134 | 1616 | 58 | -1 | -4 | -21 | -37 | -5 | 168 | 430 | 357 | 375 | 286 | 1616 | 181 | -1 | -6 | -34 | -149 | -9 | 145 | 299 | 379 | 303 | 490 | 1616 |  |  | C1 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C1 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | C1 | 7.6091 | 32.7266 | 94.4572 | 211.4325 | 402.2841 | C1 | 1278.3294 | 16821.4644 | 46567.4046 | 64909.7843 | 53906.0643 | 183483.0471 |  | 1521.8208 | 16690.5581 | 45339.4609 | 60469.7014 | 49078.6555 | 173100.1966 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1719.6575 | 14039.7047 | 33343.3952 | 74847.1129 | 100168.7314 | 224118.6017 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096 |  | 2480.5678 | 9752.5222 | 35232.5394 | 56875.3485 | 137178.8651 | 241519.843
|  |  | 565 | 562 | C2 | 93 | 126 | 180 | 125 | 41 | 565 | 81 | 126 | 181 | 135 | 42 | 565 | 43 | -3 | -7 | -22 | -12 | -1 | 80 | 82 | 150 | 160 | 93 | 565 | 93 | -3 | -8 | -42 | -43 | -3 | 67 | 81 | 104 | 134 | 179 | 565 |  |  | C2 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C2 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | C2 | 10.8701 | 46.7523 | 134.9389 | 302.0465 | 574.6915 | C2 | 880.482 | 5890.7852 | 24423.9358 | 40776.2721 | 24137.0437 | 96108.5189 |  | 1010.9238 | 5890.7852 | 24288.9969 | 37755.8075 | 23562.3522 | 92508.8656 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 1337.0282 | 3693.4288 | 19296.2587 | 41682.4115 | 46550.0129 | 112559.1401 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831 |  | 1739.2237 | 3646.6766 | 12954.1317 | 27788.2744 | 78158.0463 | 124286.3526
|  |  | 111 | 111 | C3 | 4 | 64 | 41 | 2 | 0 | 111 | 4 | 64 | 41 | 2 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 58 | 39 | 10 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 32 | 20 | 4 | 111 |  |  | C3 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C3 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | C3 | 16.3052 | 70.1284 | 202.4083 | 453.0697 | 862.0373 | C3 | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473
|  |  | 267 | 255 | C4 | 47 | 50 | 66 | 74 | 30 | 267 | 36 | 50 | 70 | 80 | 34 | 270 | 23 | 0 | -2 | -13 | -14 | -6 | 36 | 42 | 28 | 97 | 67 | 270 | 42 | 0 | -2 | -24 | -28 | -12 | 35 | 36 | 23 | 38 | 138 | 270 |  |  | C4 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C4 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | C4 | 27.1754 | 116.8807 | 337.3472 | 755.1162 | 1436.7288 | C4 | 978.3133 | 5844.0329 | 23614.3026 | 60409.2921 | 48848.7789 | 139694.7198 |  | 1277.2424 | 5844.0329 | 22264.9138 | 55878.5952 | 43101.8638 | 128366.6481 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 1603.3469 | 4908.9877 | 8771.0267 | 63429.7567 | 76146.626 | 154859.7439 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139 |  | 2092.5035 | 4207.7037 | 7084.2908 | 10571.6261 | 158040.1671 | 181996.2913
|  |  | 2541 | 2517 |  | 344 | 750 | 767 | 487 | 193 |  | 289 | 754 | 785 | 524 | 210 |  | 124 | -4 | -13 | -56 | -63 |  | 288 | 612 | 574 | 642 | 446 |  | 316 | -4 | -16 | -100 | -220 |  | 248 | 470 | 538 | 495 | 811 | [22 empty] | 3202.3457 | 33044.4999 | 102904.3836 | 167001.4879 | 126891.8869 | 433044.604 |  | 3875.2078 | 32913.5935 | 100192.1123 | 155010.2435 | 115742.8715 | 407734.0286 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 4725.2534 | 26709.5682 | 69304.6045 | 184489.978 | 222865.3702 | 508094.7744 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404 |  | 6328.6003 | 21393.8358 | 61748.0277 | 104296.6428 | 376825.2276 | 570592.3342
| HV Switchgear (GM) - Distribution |  | 5352 | 5310 | C1 | 3986 | 1248 | 108 | 9 | 1 | 5352 | 3792 | 1272 | 172 | 49 | 123 | 5408 | 147 | -20 | -80 | -42 | -18 | -13 | 3745 | 1052 | 480 | 48 | 27 | 5352 | 291 | -41 | -147 | -83 | -62 | -42 | 3399 | 1205 | 588 | 96 | 64 | 5352 |  |  | C1 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C1 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | C1 | 10.5841 | 45.5219 | 131.3876 | 294.0973 | 559.567 | C1 | 40134.7977 | 57903.7962 | 22598.6661 | 14410.7676 | 68826.7371 | 203874.7647 |  | 42188.1075 | 56811.2717 | 14189.8601 | 2646.8757 | 559.567 | 116395.682 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 41193.2049 | 46978.5516 | 52555.0374 | 1764.5838 | 5036.1027 | 147527.4804 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214 |  | 39055.2225 | 52987.4361 | 57941.9287 | 3823.2649 | 1119.1339 | 154926.9861
|  |  | 6308 | 5809 | C2 | 3108 | 2682 | 458 | 22 | 38 | 6308 | 2935 | 2728 | 670 | 89 | 195 | 6617 | 137 | -34 | -275 | -64 | -16 | -252 | 2775 | 2151 | 1032 | 266 | 84 | 6308 | 273 | -70 | -507 | -132 | -63 | -499 | 2438 | 2053 | 1198 | 417 | 202 | 6308 |  |  | C2 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C2 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | C2 | 15.1201 | 65.0312 | 187.6966 | 420.139 | 799.3814 | C2 | 44377.4983 | 177405.1617 | 125756.6966 | 37392.3707 | 155879.3698 | 540811.0971 |  | 46993.2758 | 174413.7257 | 85965.0254 | 9243.0579 | 30376.4926 | 346991.5775 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 44029.7359 | 137671.0878 | 142086.2975 | 84868.0774 | 54357.9341 | 463013.1326 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801 |  | 40990.5955 | 128956.9046 | 129698.3244 | 119739.6141 | 111114.0123 | 530499.4509
|  |  | 2231 | 1899 | C3 | 924 | 1031 | 228 | 0 | 48 | 2231 | 880 | 1054 | 339 | 40 | 86 | 2399 | 33 | -18 | -139 | -42 | -8 | -174 | 789 | 765 | 488 | 111 | 78 | 2231 | 65 | -36 | -255 | -83 | -23 | -332 | 682 | 745 | 483 | 198 | 123 | 2231 |  |  | C3 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C3 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | C3 | 22.6802 | 97.5468 | 281.5448 | 630.2085 | 1199.0721 | C3 | 19958.5341 | 102814.3551 | 95443.7018 | 25208.3398 | 103120.1985 | 346545.1293 |  | 20956.4608 | 100570.7781 | 64192.2242 | 0 | 57555.4596 | 243274.9228 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 18643.0853 | 72867.4794 | 98259.1503 | 43484.3862 | 83935.0453 | 317189.1464 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562 |  | 16942.0739 | 69160.7 | 64192.2242 | 72473.9769 | 119907.2075 | 342676.1825
|  |  | 895 | 670 | C4 | 304 | 445 | 105 | 23 | 18 | 895 | 290 | 456 | 166 | 54 | 50 | 1016 | 9 | -8 | -76 | -34 | -6 | -115 | 233 | 358 | 194 | 55 | 55 | 895 | 17 | -16 | -140 | -69 | -17 | -225 | 199 | 292 | 226 | 90 | 88 | 895 |  |  | C4 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C4 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | C4 | 37.8003 | 162.578 | 469.2414 | 1050.3475 | 1998.4535 | C4 | 10962.0737 | 74135.5881 | 77894.0733 | 56718.7646 | 99922.6729 | 319633.1726 |  | 11491.2772 | 72347.2296 | 49270.3476 | 24157.9923 | 35972.1623 | 193239.009 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 9147.6615 | 56902.3154 | 55370.4858 | 22057.2973 | 97924.2195 | 241401.9796 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757 |  | 8164.8549 | 44871.5402 | 40354.7609 | 22057.2973 | 141890.1956 | 257338.6488
|  |  | 14786 | 13688 |  | 8322 | 5406 | 899 | 54 | 105 |  | 7897 | 5510 | 1347 | 232 | 454 |  | 326 | -80 | -570 | -182 | -48 |  | 7542 | 4326 | 2194 | 480 | 244 |  | 646 | -163 | -1049 | -367 | -165 |  | 6718 | 4295 | 2495 | 801 | 477 | [22 empty] | 115432.9038 | 412258.9011 | 321693.1378 | 133730.2427 | 427748.9783 | 1410864.1637 |  | 121629.1215 | 404143.0052 | 213617.4573 | 36047.9259 | 124463.6814 | 899901.1913 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 113013.6875 | 314419.4342 | 348270.971 | 152174.3446 | 241253.3016 | 1169131.7389 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334 |  | 105152.7467 | 295976.5809 | 292187.2382 | 218094.1532 | 374030.5494 | 1285441.2684
| HV Transformer (GM) |  | 3258 | 3451 | C1 | 2494 | 563 | 122 | 64 | 15 | 3258 | 2396 | 571 | 126 | 72 | 39 | 3204 | 144 | -1 | 0 | -12 | -38 | 93 | 2368 | 492 | 250 | 78 | 70 | 3258 | 296 | -1 | 0 | -24 | -78 | 193 | 2251 | 422 | 376 | 88 | 121 | 3258 |  |  | C1 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C1 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | C1 | 7.0107 | 30.1527 | 87.0284 | 194.8038 | 370.6454 | C1 | 16797.5544 | 17217.2001 | 10965.5746 | 14025.8769 | 14455.1688 | 73461.3748 |  | 17484.5996 | 16975.9783 | 10617.4612 | 12467.4461 | 5559.6803 | 63105.1655 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 17610.7916 | 14804.9829 | 21757.0925 | 12857.0538 | 11860.6514 | 78890.5722 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947 |  | 17856.1649 | 12694.2929 | 32722.6672 | 12467.4461 | 15937.7503 | 91678.3213
|  |  | 5365 | 5253 | C2 | 2652 | 1750 | 484 | 405 | 74 | 5365 | 2536 | 1753 | 478 | 446 | 166 | 5379 | 163 | 2 | 0 | -70 | -147 | -52 | 2335 | 1610 | 674 | 315 | 431 | 5365 | 335 | 2 | 0 | -146 | -303 | -112 | 2105 | 1538 | 788 | 263 | 671 | 5365 |  |  | C2 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C2 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | C2 | 10.0152 | 43.0753 | 124.3262 | 278.2912 | 529.4934 | C2 | 25398.6393 | 75511.0125 | 59427.9442 | 124117.8788 | 87895.8985 | 372351.3733 |  | 26560.4068 | 75381.7866 | 60173.9016 | 112707.9393 | 39182.509 | 314006.5432 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 25018.0604 | 69437.3943 | 83795.8878 | 68181.346 | 150376.1155 | 396808.8039 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088 |  | 24437.1767 | 66335.9722 | 97969.0795 | 32560.0713 | 194853.5581 | 416155.8578
|  |  | 914 | 889 | C3 | 498 | 275 | 75 | 57 | 9 | 914 | 480 | 281 | 79 | 65 | 25 | 930 | 27 | -1 | 0 | -12 | -27 | -13 | 460 | 202 | 145 | 48 | 59 | 914 | 55 | -1 | 0 | -24 | -55 | -25 | 428 | 159 | 190 | 43 | 94 | 914 |  |  | C3 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C3 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | C3 | 15.0229 | 64.613 | 186.4894 | 417.4368 | 794.24 | C3 | 7210.9702 | 18156.2417 | 14732.6598 | 27133.3928 | 19856.0012 | 87089.2657 |  | 7481.3815 | 17768.564 | 13986.7023 | 23793.8983 | 7148.1604 | 70178.7066 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 7316.1301 | 12987.205 | 27040.9579 | 15027.7252 | 25415.6815 | 87787.6997 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689 |  | 7256.0387 | 10208.8477 | 35432.9793 | 7931.2994 | 30975.3618 | 91804.5269
|  |  | 423 | 367 | C4 | 180 | 130 | 64 | 42 | 7 | 423 | 174 | 136 | 68 | 48 | 23 | 449 | 8 | -1 | 0 | -8 | -27 | -28 | 163 | 106 | 75 | 35 | 44 | 423 | 16 | -1 | 0 | -16 | -55 | -56 | 141 | 104 | 60 | 45 | 73 | 423 |  |  | C4 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C4 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | C4 | 25.0381 | 107.6883 | 310.8156 | 695.728 | 1323.7334 | C4 | 4356.6278 | 14645.6043 | 21135.4613 | 33394.945 | 30445.8685 | 103978.5068 |  | 4506.8563 | 13999.4747 | 19892.1989 | 29220.5768 | 9266.1339 | 76885.2406 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 4281.5135 | 11307.268 | 23311.1706 | 18784.6565 | 22503.468 | 80188.0766 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869 |  | 3930.9803 | 11091.8915 | 18648.9365 | 20176.1126 | 23827.2014 | 77675.1222
|  |  | 9960 | 9960 |  | 5824 | 2718 | 745 | 568 | 105 |  | 5586 | 2741 | 751 | 631 | 253 |  | 342 | -1 | 0 | -102 | -239 |  | 5326 | 2410 | 1144 | 476 | 604 |  | 702 | -1 | 0 | -210 | -491 |  | 4925 | 2223 | 1414 | 439 | 959 | [22 empty] | 53763.7917 | 125530.0586 | 106261.6399 | 198672.0934 | 152652.9369 | 636880.5206 |  | 56033.2442 | 124125.8036 | 104670.264 | 178189.8605 | 61156.4836 | 524175.6559 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 54226.4956 | 108536.8501 | 155905.1087 | 114850.7816 | 210155.9163 | 643675.1523 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116 |  | 53480.3605 | 100331.0042 | 184773.6624 | 73134.9295 | 265593.8716 | 677313.8281
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 42673 | 42754 | C1 | 14496 | 9898 | 9947 | 7197 | 1135 | 42673 | 13237 | 9960 | 10135 | 7612 | 1702 | 42646 | 1476 | -40 | -218 | -423 | -770 | 25 | 12621 | 5451 | 14288 | 8600 | 1822 | 42782 | 4196 | -80 | -558 | -1107 | -2370 | 81 | 10834 | 5196 | 12471 | 9058 | 5121 | 42680 |  |  | C1 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C1 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | C1 | 0.053585 | 0.23047 | 0.66519 | 1.489 | 2.833 | C1 | 709.303 | 2295.4547 | 6741.6714 | 11333.8975 | 4821.7101 | 25902.0367 |  | 776.7663 | 2281.1658 | 6616.6162 | 10715.9827 | 3215.4177 | 23605.9487 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 755.386 | 1247.0588 | 9359.1827 | 12175.155 | 2980.2814 | 26517.0639 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412 |  | 805.3807 | 1179.0709 | 7924.3741 | 11838.652 | 7793.4926 | 29540.9703
|  |  | 56579 | 56824 | C2 | 19086 | 13113 | 12487 | 10437 | 1456 | 56579 | 17419 | 13191 | 12717 | 11032 | 2157 | 56516 | 1966 | -44 | -261 | -603 | -961 | 97 | 16628 | 7242 | 17935 | 12476 | 2327 | 56608 | 5558 | -88 | -681 | -1583 | -2961 | 245 | 14288 | 6915 | 15666 | 13149 | 6479 | 56497 |  |  | C2 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C2 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | C2 | 0.07655 | 0.32924 | 0.95027 | 2.1271 | 4.0471 | C2 | 1333.4213 | 4342.9924 | 12084.5493 | 23465.873 | 8729.5859 | 49956.4219 |  | 1461.0299 | 4317.3118 | 11865.9878 | 22200.2643 | 5892.5717 | 45737.1655 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1423.3674 | 2369.8628 | 16795.0243 | 25254.7416 | 5528.333 | 51371.3291 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412 |  | 1519.2077 | 2247.7151 | 14239.7555 | 24601.7301 | 14237.6835 | 56846.0919
|  |  | 23551 | 23321 | C3 | 7796 | 5437 | 5297 | 4320 | 701 | 23551 | 7119 | 5471 | 5397 | 4570 | 1053 | 23610 | 792 | -24 | -116 | -257 | -477 | -82 | 6787 | 2993 | 7607 | 5162 | 1125 | 23674 | 2252 | -48 | -300 | -669 | -1465 | -230 | 5824 | 2852 | 6638 | 5437 | 3165 | 23916 |  |  | C3 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C3 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | C3 | 0.11482 | 0.49386 | 1.4254 | 3.1906 | 6.0706 | C3 | 817.4373 | 2701.9004 | 7692.8889 | 14581.0877 | 6392.388 | 32185.7022 |  | 895.1736 | 2685.1092 | 7550.3489 | 13783.4352 | 4255.5214 | 29169.5882 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 870.2566 | 1466.2662 | 10677.6785 | 15649.942 | 3933.7772 | 32597.9206 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699 |  | 927.3245 | 1384.7795 | 9034.1912 | 15212.8284 | 10320.0946 | 36879.2183
|  |  | 3346 | 3250 | C4 | 705 | 1366 | 725 | 486 | 64 | 3346 | 645 | 1375 | 740 | 516 | 101 | 3377 | 66 | -8 | -17 | -31 | -50 | -40 | 611 | 749 | 1041 | 580 | 104 | 3085 | 194 | -16 | -45 | -79 | -150 | -96 | 521 | 713 | 906 | 610 | 306 | 3056 |  |  | C4 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C4 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | C4 | 0.19137 | 0.8231 | 2.3757 | 5.3177 | 10.1177 | C4 | 123.4366 | 1131.7593 | 1757.9945 | 2743.9246 | 1021.8917 | 6779.0067 |  | 134.9191 | 1124.3514 | 1722.3595 | 2584.3941 | 647.5353 | 6213.5594 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 129.5606 | 609.9154 | 2432.6843 | 2919.4081 | 546.3579 | 6637.9263 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454 |  | 136.8328 | 573.6991 | 2045.4504 | 2823.6898 | 1578.3674 | 7158.0395
|  |  | 126149 | 126149 |  | 42083 | 29814 | 28456 | 22440 | 3356 |  | 38420 | 29997 | 28989 | 23730 | 5013 |  | 4300 | -116 | -612 | -1314 | -2258 |  | 36647 | 16435 | 40871 | 26818 | 5378 |  | 12200 | -232 | -1584 | -3438 | -6946 |  | 31467 | 15676 | 35681 | 28254 | 15071 | [22 empty] | 2983.5982 | 10472.1068 | 28277.1041 | 52124.7828 | 20965.5757 | 114823.1676 |  | 3267.8889 | 10407.9381 | 27755.3123 | 49284.0763 | 14011.0461 | 104726.2617 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 3178.5706 | 5693.1031 | 39264.5698 | 55999.2468 | 12988.7497 | 117124.2399 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977 |  | 3388.7457 | 5385.2645 | 33243.7712 | 54476.9004 | 33929.6381 | 130424.32
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 |  | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 175144.0071 | 455358.9556 | 612745.254 | 507514.351 | 687263.3378 | 2438025.9055 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 |  | 168350.4533 | 423086.6854 | 571952.6995 | 450002.6259 | 1050379.2866 | 2663771.7507
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 267 | 267 | C1 | 134 | 87 | 42 | 4 | 0 | 267 | 126 | 87 | 50 | 4 | 0 | 267 | 1 | 0 | 0 | 0 | -1 | 0 | 119 | 62 | 43 | 42 | 1 | 267 | 12 | 0 | 0 | -8 | -4 | 0 | 113 | 46 | 64 | 40 | 4 | 267 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 239 | 238 | C2 | 79 | 57 | 72 | 23 | 8 | 239 | 45 | 57 | 81 | 30 | 26 | 239 | 14 | 0 | -1 | -3 | -10 | 0 | 45 | 23 | 34 | 86 | 51 | 239 | 38 | 0 | -1 | -16 | -22 | -1 | 39 | 18 | 45 | 81 | 56 | 239 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 109 | 109 | C3 | 1 | 51 | 51 | 6 | 0 | 109 | 1 | 51 | 51 | 6 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | 46 | 23 | 3 | 109 | 8 | 0 | 0 | -2 | -6 | 0 | 0 | 19 | 35 | 49 | 6 | 109 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44 | 47 | C4 | 2 | 0 | 42 | 0 | 0 | 44 | 2 | 0 | 42 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 | 18 | 0 | 0 | -15 | 0 | 3 | 2 | 0 | 0 | 42 | 0 | 44 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 659 | 661 |  | 216 | 195 | 207 | 33 | 8 |  | 174 | 195 | 224 | 40 | 26 |  | 15 | 0 | -1 | -3 | -11 |  | 167 | 121 | 123 | 193 | 55 |  | 76 | 0 | -1 | -41 | -32 |  | 154 | 83 | 144 | 212 | 66 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV Transformer |  | 103 | 103 | C1 | 37 | 47 | 14 | 5 | 0 | 103 | 37 | 47 | 14 | 5 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 24 | 11 | 0 | 103 | 2 | 0 | 1 | 0 | -3 | 0 | 34 | 17 | 35 | 12 | 5 | 103 |  |  | C1 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C1 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | C1 | 130.7046 | 562.1576 | 1622.5291 | 3631.8605 | 6910.1933 | C1 | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 9556.6785 | 56788.5173 | 43582.3262 | 34550.9666 | 148922.445 |  | 4705.3657 | 9556.6785 | 58411.0463 | 43582.3262 | 13820.3866 | 130075.8033
|  |  | 194 | 194 | C2 | 53 | 54 | 65 | 22 | 0 | 194 | 46 | 54 | 70 | 24 | 0 | 194 | 14 | 1 | 0 | -10 | -5 | 0 | 39 | 40 | 65 | 43 | 7 | 194 | 20 | 2 | 3 | -15 | -10 | 0 | 34 | 29 | 61 | 42 | 28 | 194 |  |  | C2 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C2 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | C2 | 186.7209 | 803.0822 | 2317.8987 | 5188.3722 | 9871.7047 | C2 | 8589.1595 | 43366.4401 | 162252.9065 | 124520.9321 | 0 | 338729.4383 |  | 9896.2055 | 43366.4401 | 150663.4132 | 114144.1878 | 0 | 318070.2466 |  | 7282.1135 | 32123.289 | 150663.4132 | 223100.0034 | 69101.9332 | 482270.7522 |  | 9896.2055 | 32926.3712 | 150663.4132 | 171216.2817 | 19743.4095 | 384445.6811 |  | 6348.5092 | 23289.3845 | 141391.8185 | 217911.6312 | 276407.7327 | 665349.0761 |  | 10082.9264 | 24895.5489 | 148345.5145 | 140086.0486 | 177690.6853 | 501100.7238
|  |  | 16 | 16 | C3 | 9 | 2 | 2 | 3 | 0 | 16 | 8 | 2 | 3 | 3 | 0 | 16 | 4 | 0 | 0 | -2 | -2 | 0 | 8 | 2 | 2 | 2 | 2 | 16 | 4 | 0 | 0 | -2 | -2 | 0 | 8 | 2 | 0 | 3 | 3 | 16 |  |  | C3 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C3 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | C3 | 280.0813 | 1204.6233 | 3476.848 | 7782.5583 | 14807.5571 | C3 | 2240.6503 | 2409.2467 | 10430.544 | 23347.6748 | 0 | 38428.1157 |  | 2520.7316 | 2409.2467 | 6953.696 | 23347.6748 | 0 | 35231.349 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 3360.9755 | 2409.2467 | 6953.696 | 0 | 0 | 12723.9181 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431 |  | 3360.9755 | 2409.2467 | 0 | 7782.5583 | 14807.5571 | 28360.3375
|  |  | 28 | 28 | C4 | 10 | 7 | 9 | 2 | 0 | 28 | 6 | 7 | 11 | 4 | 0 | 28 | 2 | 0 | 0 | -2 | 0 | 0 | 4 | 7 | 10 | 6 | 1 | 28 | 2 | 0 | 0 | -1 | -1 | 0 | 4 | 4 | 7 | 9 | 4 | 28 |  |  | C4 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C4 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | C4 | 466.8021 | 2007.7056 | 5794.7467 | 12970.9304 | 24679.2618 | C4 | 2800.8129 | 14053.9389 | 63742.2133 | 51883.7217 | 0 | 132480.6868 |  | 4668.0215 | 14053.9389 | 52152.72 | 25941.8609 | 0 | 96816.5412 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 2800.8129 | 14053.9389 | 57947.4666 | 51883.7217 | 24679.2618 | 151365.202 |  | 1867.2086 | 8030.8222 | 40563.2266 | 116738.3739 | 98717.0474 | 265916.6787 |  | 2800.8129 | 8030.8222 | 40563.2266 | 103767.4434 | 74037.7855 | 229200.0907
|  |  | 341 | 341 |  | 109 | 110 | 90 | 32 | 0 |  | 97 | 110 | 98 | 36 | 0 |  | 20 | 1 | 0 | -14 | -7 |  | 85 | 83 | 101 | 62 | 10 |  | 28 | 2 | 4 | -18 | -16 |  | 80 | 52 | 103 | 66 | 40 | [22 empty] | 18466.693 | 86251.0309 | 259141.0707 | 217911.6312 | 0 | 581770.4258 |  | 21921.0289 | 86251.0309 | 232485.2361 | 181593.026 | 0 | 522250.3218 |  | 15833.9289 | 67699.8315 | 254505.2734 | 356441.1682 | 123396.3092 | 817876.5111 |  | 20501.9503 | 68502.9137 | 254505.2734 | 263050.4691 | 44422.6713 | 650983.2779 |  | 14900.3246 | 43286.1319 | 238743.5624 | 401580.0061 | 454098.4179 | 1152608.4429 |  | 20950.0804 | 44892.2963 | 247319.7875 | 295218.3766 | 280356.4146 | 888736.9554
| EHV UG Cable (Gas) |  | 6.4128 | 6.0584 | C1 | 0 | 4.5123 | 0.72891 | 0 | 1.1715 | 6.4128 | 0 | 4.5123 | 0.98216 | 0 | 2.3941 | 7.8886 | 0 | 0 | -0.03329 | 0 | -0.32106 | -0.35435 | 0 | 2.4022 | 3.4025 | 0 | 1.1715 | 6.9762 | 0 | 0 | -0.03329 | 0 | -0.32106 | -0.35435 | 0 | 0.0013324 | 7.0872 | 0 | 1.5485 | 8.6371 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 22.4586 | 21.4054 | C2 | 0.097004 | 16.0222 | 2.797 | 1.9898 | 1.5526 | 22.4586 | 0.097004 | 16.0222 | 3.7687 | 2.9407 | 3.1729 | 26.0015 | 0 | 0 | -0.12774 | -0.5 | -0.42551 | -1.0533 | 0.097004 | 8.5295 | 13.056 | 6.2328 | 1.5526 | 29.4679 | 0 | 0 | -0.12774 | -0.5 | -0.42551 | -1.0533 | 0.097004 | 0.004731 | 27.1948 | 4.1778 | 2.0523 | 33.5266 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 37.0822 | 35.9898 | C3 | 0 | 31.4728 | 1.9481 | 0 | 3.6613 | 37.0822 | 0 | 31.4728 | 2.6249 | 0 | 7.4822 | 41.5799 | 0 | 0 | -0.08897 | 0 | -1.0034 | -1.0924 | 0 | 16.7547 | 9.0934 | 0 | 3.6613 | 29.5095 | 0 | 0 | -0.08897 | 0 | -1.0034 | -1.0924 | 0 | 0.0092933 | 18.941 | 0 | 4.8396 | 23.7899 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 65.9536 | 63.4536 |  | 0.097004 | 52.0074 | 5.474 | 1.9898 | 6.3855 |  | 0.097004 | 52.0074 | 7.3758 | 2.9407 | 13.0492 |  | 0 | 0 | -0.25 | -0.5 | -1.75 |  | 0.097004 | 27.6864 | 25.552 | 6.2328 | 6.3855 |  | 0 | 0 | -0.25 | -0.5 | -1.75 |  | 0.097004 | 0.015357 | 53.223 | 4.1778 | 8.4405 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 76.0126 | 70.4969 | C1 | 9.9431 | 39.0737 | 14.5585 | 1.188 | 11.2492 | 76.0126 | 9.9388 | 39.0737 | 15.2955 | 2.2227 | 17.0115 | 83.5423 | 0 | 0 | -0.32942 | -0.4625 | -2.5725 | -3.3644 | 6.9676 | 31.7613 | 18.3957 | 4.3897 | 12.4727 | 73.987 | 0 | 0 | -0.54006 | -0.75824 | -4.2174 | -5.5157 | 6.9676 | 21.5006 | 25.67 | 4.2208 | 16.4892 | 74.8482 |  |  | C1 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C1 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | C1 | 22.4315 | 96.4774 | 278.4582 | 623.2993 | 1185.9263 | C1 | 222.9432 | 3769.7333 | 4259.1647 | 1385.4153 | 20174.4041 | 29811.6606 |  | 223.0388 | 3769.7333 | 4053.9411 | 740.4654 | 13340.7556 | 22127.9343 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 3064.2429 | 5030.7142 | 2447.812 | 11740.9925 | 22440.055 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826 |  | 156.2934 | 2074.3195 | 6997.6362 | 2158.2394 | 14553.5165 | 25940.0049
|  |  | 136.6281 | 124.5747 | C2 | 5.0986 | 76.2932 | 29.9538 | 5.5582 | 19.7242 | 136.6281 | 5.0965 | 76.2932 | 31.4701 | 10.3995 | 29.8278 | 153.087 | 0 | 0 | -0.67777 | -2.1639 | -4.5105 | -7.3522 | 3.5729 | 62.0152 | 37.8487 | 20.5382 | 21.8695 | 145.8445 | 0 | 0 | -1.1112 | -3.5476 | -7.3947 | -12.0534 | 3.5729 | 41.9808 | 52.8153 | 19.7482 | 28.912 | 147.0291 |  |  | C2 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C2 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | C2 | 32.045 | 137.8248 | 397.7974 | 890.4276 | 1694.1804 | C2 | 163.3161 | 10515.0973 | 12518.7377 | 9259.9833 | 50533.6075 | 82990.7419 |  | 163.3862 | 10515.0973 | 11915.5351 | 4949.2 | 33416.4272 | 60959.6459 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 8547.2391 | 14786.5126 | 16360.9414 | 29409.2802 | 69218.4654 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254 |  | 114.4921 | 5785.9984 | 20567.7824 | 14425.466 | 36454.1963 | 77347.9352
|  |  | 182.0691 | 169.9895 | C3 | 5.2629 | 106.478 | 45.3634 | 3.9391 | 21.0257 | 182.0691 | 5.2606 | 106.478 | 47.6598 | 7.3702 | 31.7959 | 198.5645 | 0 | 0 | -1.0265 | -1.5336 | -4.8082 | -7.3682 | 3.6879 | 86.5511 | 57.3199 | 14.5555 | 23.3126 | 185.4269 | 0 | 0 | -1.6828 | -2.5142 | -7.8826 | -12.0796 | 3.6879 | 58.5902 | 79.986 | 13.9956 | 30.8197 | 187.0794 |  |  | C3 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C3 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | C3 | 48.0675 | 206.7373 | 596.6961 | 1335.6414 | 2541.2706 | C3 | 252.8657 | 22012.9658 | 28438.4362 | 9843.8816 | 80801.9857 | 141350.1351 |  | 252.9741 | 22012.9658 | 27068.1591 | 5261.2773 | 53432.0388 | 108027.4152 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 17893.3278 | 33590.0715 | 17392.5985 | 47024.7101 | 116077.9782 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677 |  | 177.2704 | 12112.7728 | 46723.2065 | 15335.0795 | 58289.3563 | 132637.6856
|  |  | 67.6959 | 63.2445 | C4 | 20.1271 | 33.8496 | 2.0485 | 0 | 11.6707 | 67.6959 | 20.1185 | 33.8496 | 2.1522 | 0 | 17.6488 | 73.7691 | 0 | 0 | -0.046353 | 0 | -2.6688 | -2.7152 | 14.104 | 27.5148 | 2.5885 | 0 | 12.94 | 57.1472 | 0 | 0 | -0.075992 | 0 | -4.3754 | -4.4514 | 14.104 | 18.626 | 3.612 | 0 | 17.107 | 53.4489 |  |  | C4 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C4 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | C4 | 80.1125 | 344.5621 | 994.4935 | 2226.069 | 4235.451 | C4 | 1611.7417 | 11663.2874 | 2140.3925 | 0 | 74750.6707 | 90166.0923 |  | 1612.4329 | 11663.2874 | 2037.2599 | 0 | 49430.4775 | 64743.4578 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 9480.5501 | 2528.1256 | 0 | 43502.9979 | 56641.578 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041 |  | 1129.9045 | 6417.7972 | 3516.5788 | 0 | 53924.0273 | 64988.3078
|  |  | 462.4057 | 428.3057 |  | 40.4318 | 255.6945 | 91.9242 | 10.6853 | 63.6698 |  | 40.4144 | 255.6945 | 96.5777 | 19.9923 | 96.284 |  | 0 | 0 | -2.08 | -4.16 | -14.56 |  | 28.3324 | 207.8423 | 116.1528 | 39.4833 | 70.5948 |  | 0 | 0 | -3.41 | -6.82 | -23.87 |  | 28.3324 | 140.6975 | 162.0833 | 37.9646 | 93.3278 | [22 empty] | 2250.8667 | 47961.0839 | 47356.7311 | 20489.2802 | 226260.668 | 344318.6299 |  | 2251.8321 | 47961.0839 | 45074.8952 | 10950.9427 | 149619.6993 | 255858.4532 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 38985.3599 | 55935.4239 | 36201.3519 | 131677.9806 | 264378.0767 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798 |  | 1577.9603 | 26390.8878 | 77805.204 | 31918.785 | 163221.0964 | 300913.9335
| EHV UG Cable (Non Pressurised) |  | 55.8648 | 60.7939 | C1 | 20.28 | 31.8691 | 0.49426 | 3.1782 | 0.043172 | 55.8648 | 15.4973 | 31.8691 | 0.52291 | 3.2075 | 0.050667 | 51.1475 | 5.0876 | 0 | -0.23393 | -1.0753 | 0 | 3.7783 | 19.8549 | 31.5642 | 1.0578 | 3.4079 | 0.043172 | 55.928 | 6.3115 | 0 | -0.26598 | -1.1081 | -0.0083129 | 4.9291 | 19.6892 | 26.0768 | 2.3638 | 2.9471 | 0.14836 | 51.2253 |  |  | C1 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C1 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | C1 | 38.0736 | 163.7538 | 472.6349 | 1057.9435 | 2012.9061 | C1 | 590.0392 | 5218.6824 | 247.147 | 3393.3298 | 101.9869 | 9551.1853 |  | 772.1344 | 5218.6824 | 233.6066 | 3362.3692 | 86.9003 | 9673.6929 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 949.65 | 5168.7648 | 389.3817 | 2467.7516 | 86.9003 | 9062.4484 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524 |  | 989.9409 | 4270.1698 | 991.5227 | 1945.5783 | 281.8949 | 8479.1065
|  |  | 65.5759 | 73.4791 | C2 | 31.9175 | 27.5701 | 0.87467 | 3.5588 | 1.6548 | 65.5759 | 24.3903 | 27.5701 | 0.92537 | 3.5916 | 1.942 | 58.4194 | 8.0071 | 0 | -0.41398 | -1.2041 | 0 | 6.389 | 31.2484 | 27.3064 | 1.8719 | 3.8161 | 1.6548 | 65.8975 | 9.9333 | 0 | -0.47069 | -1.2408 | -0.31863 | 7.9032 | 30.9877 | 22.5591 | 4.1831 | 3.3 | 5.6865 | 66.7165 |  |  | C2 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C2 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | C2 | 54.3909 | 233.934 | 675.1927 | 1511.3479 | 2875.5801 | C2 | 1326.6111 | 6449.5749 | 624.8015 | 5428.1624 | 5584.5139 | 19413.6637 |  | 1736.0237 | 6449.5749 | 590.5706 | 5378.6361 | 4758.4114 | 18913.2167 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 2135.1397 | 6387.8836 | 984.3788 | 3947.5552 | 4758.4114 | 18213.3687 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267 |  | 2225.7274 | 5277.3436 | 2506.6251 | 3112.2571 | 15435.7586 | 28557.7118
|  |  | 77.7419 | 91.3793 | C3 | 51.2718 | 20.023 | 0.37769 | 6.0695 | 0 | 77.7419 | 39.1802 | 20.023 | 0.39959 | 6.1254 | 0 | 65.7281 | 12.8624 | 0 | -0.17876 | -2.0536 | 0 | 10.6301 | 50.1969 | 19.8314 | 0.80831 | 6.5082 | 0 | 77.3448 | 15.9567 | 0 | -0.20325 | -2.1161 | 0 | 13.6373 | 49.7781 | 16.3837 | 1.8063 | 5.6281 | 0 | 73.5962 |  |  | C3 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C3 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | C3 | 81.5863 | 350.901 | 1012.7891 | 2267.0218 | 4313.3702 | C3 | 3196.5691 | 7026.074 | 404.6965 | 13886.3435 | 0 | 24513.6831 |  | 4183.0795 | 7026.074 | 382.5244 | 13759.6454 | 0 | 25351.3233 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 5144.7794 | 6958.8685 | 637.6019 | 10098.6492 | 0 | 22839.899 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393 |  | 5363.0573 | 5749.0621 | 1623.5914 | 7961.7868 | 0 | 20697.4976
|  |  | 209.0164 | 244.8468 | C4 | 150.0512 | 26.0249 | 1.3381 | 26.0295 | 5.5727 | 209.0164 | 114.6641 | 26.0249 | 1.4157 | 26.2691 | 6.5402 | 174.914 | 37.6429 | 0 | -0.63333 | -8.807 | 0 | 28.2026 | 146.9054 | 25.7759 | 2.8638 | 27.9108 | 5.5727 | 209.0287 | 46.6985 | 0 | -0.72009 | -9.0751 | -1.0731 | 35.8303 | 145.6797 | 21.2948 | 6.3997 | 24.1366 | 19.1504 | 216.6611 |  |  | C4 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C4 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | C4 | 135.9772 | 584.835 | 1687.9818 | 3778.3697 | 7188.9503 | C4 | 15591.7087 | 15220.2533 | 2389.6645 | 99254.5314 | 47017.1975 | 179473.3554 |  | 20403.55 | 15220.2533 | 2258.7424 | 98348.939 | 40062.0667 | 176293.5514 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 25094.3749 | 15074.6691 | 3764.9319 | 72181.4706 | 40062.0667 | 156177.5132 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899 |  | 26159.0557 | 12453.9225 | 9587.034 | 56907.9552 | 129956.8984 | 235064.8659
|  |  | 408.199 | 470.499 |  | 253.5206 | 105.487 | 3.0848 | 38.836 | 7.2707 |  | 193.732 | 105.487 | 3.2636 | 39.1936 | 8.5329 |  | 63.6 | 0 | -1.46 | -13.14 | 0 |  | 248.2056 | 104.478 | 6.6018 | 41.643 | 7.2707 |  | 78.9 | 0 | -1.66 | -13.54 | -1.4 |  | 246.1346 | 86.3144 | 14.753 | 36.0118 | 24.9852 | [22 empty] | 20704.9281 | 33914.5845 | 3666.3094 | 121962.3671 | 52703.6984 | 232951.8875 |  | 27094.7876 | 33914.5845 | 3465.444 | 120849.5897 | 44907.3784 | 230231.7843 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 33323.944 | 33590.186 | 5776.2942 | 88695.4267 | 44907.3784 | 206293.2294 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799 |  | 34737.7814 | 27750.498 | 14708.7732 | 69927.5773 | 145674.5519 | 292799.1818
| EHV OHL Support - Towers |  | 637 | 637 | C1 | 103 | 280 | 61 | 33 | 160 | 637 | 61 | 85 | 118 | 81 | 292 | 637 | 95 | 134 | -63 | -13 | -153 | 0 | 56 | 266 | 96 | 24 | 195 | 637 | 95 | 145 | -63 | -13 | -164 | 0 | 5 | 96 | 221 | 96 | 219 | 637 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 561 | 561 | C2 | 77 | 171 | 92 | 96 | 125 | 561 | 35 | 97 | 106 | 109 | 214 | 561 | 140 | 194 | -91 | -42 | -201 | 0 | 60 | 116 | 104 | 42 | 239 | 561 | 159 | 221 | -106 | -53 | -221 | 0 | 3 | 67 | 106 | 104 | 281 | 561 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18 | 18 | C3 | 4 | 5 | 1 | 7 | 1 | 18 | 3 | 2 | 2 | 7 | 4 | 18 | 2 | 4 | -3 | 0 | -3 | 0 | 1 | 6 | 3 | 0 | 8 | 18 | 2 | 5 | -3 | 0 | -4 | 0 | 0 | 4 | 3 | 3 | 8 | 18 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 212 | 75 | C4 | 10 | 27 | 1 | 2 | 172 | 212 | 10 | 27 | 1 | 2 | 172 | 212 | 7 | 32 | -4 | 0 | -172 | -137 | 5 | 6 | 27 | 0 | 174 | 212 | 25 | 33 | -6 | -17 | -172 | -137 | 2 | 3 | 6 | 27 | 174 | 212 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1428 | 1291 |  | 194 | 483 | 155 | 138 | 458 |  | 109 | 211 | 227 | 199 | 682 |  | 244 | 364 | -161 | -55 | -529 |  | 122 | 394 | 230 | 66 | 616 |  | 281 | 404 | -178 | -83 | -561 |  | 10 | 170 | 336 | 230 | 682 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Poles |  | 4038 | 3943 | C1 | 1046 | 1806 | 1095 | 69 | 22 | 4038 | 925 | 1817 | 1103 | 151 | 75 | 4071 | 117 | 106 | -171 | -68 | -63 | -79 | 936 | 1591 | 1154 | 219 | 163 | 4063 | 121 | 209 | -171 | -105 | -149 | -95 | 861 | 1220 | 1485 | 243 | 334 | 4143 |  |  | C1 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C1 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | C1 | 0.58127 | 2.5 | 7.2157 | 16.1517 | 30.7311 | C1 | 537.6765 | 4542.5678 | 7958.962 | 2438.9031 | 2304.8353 | 17782.9447 |  | 608.0104 | 4515.0674 | 7901.2361 | 1114.4657 | 676.085 | 14814.8646 |  | 544.0705 | 3977.5594 | 8326.9648 | 3537.2171 | 5009.1754 | 21394.9871 |  | 612.0793 | 4242.5633 | 7093.0732 | 2438.9031 | 3073.1137 | 17459.7326 |  | 500.4751 | 3050.0455 | 10715.375 | 3924.8573 | 10264.1999 | 28454.9528 |  | 570.809 | 3572.5533 | 9481.4833 | 2228.9313 | 5685.2604 | 21539.0374
|  |  | 4370 | 4473 | C2 | 1624 | 1865 | 758 | 111 | 12 | 4370 | 1433 | 1874 | 762 | 214 | 58 | 4341 | 191 | 121 | -104 | -78 | -45 | 85 | 1463 | 1655 | 804 | 312 | 141 | 4375 | 207 | 233 | -104 | -118 | -115 | 103 | 1357 | 1287 | 1033 | 349 | 298 | 4324 |  |  | C2 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C2 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | C2 | 0.83039 | 3.5715 | 10.3082 | 23.0738 | 43.9016 | C2 | 1189.9466 | 6692.957 | 7854.8492 | 4937.7981 | 2546.2942 | 23221.8452 |  | 1348.5508 | 6660.8137 | 7813.6164 | 2561.1944 | 526.8195 | 18910.9947 |  | 1214.8582 | 5910.8025 | 8287.7937 | 7199.0328 | 6190.1291 | 28802.6163 |  | 1373.4624 | 6342.9518 | 7215.7408 | 5399.2746 | 4214.556 | 24545.9855 |  | 1126.8371 | 4596.4972 | 10648.3717 | 8052.7642 | 13082.6842 | 37507.1543 |  | 1298.7275 | 5428.6524 | 9576.3188 | 5330.0531 | 8033.9973 | 29667.7491
|  |  | 123 | 123 | C3 | 57 | 55 | 9 | 0 | 2 | 123 | 51 | 56 | 10 | 0 | 2 | 119 | 3 | 1 | -6 | 0 | 0 | -2 | 49 | 46 | 9 | 0 | 2 | 106 | 3 | 3 | -6 | 0 | 0 | 0 | 42 | 31 | 12 | 0 | 2 | 87 |  |  | C3 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C3 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | C3 | 1.2456 | 5.3572 | 15.4623 | 34.6107 | 65.8524 | C3 | 63.5247 | 300.0045 | 154.623 | 0 | 131.7049 | 649.8571 |  | 70.9982 | 294.6473 | 139.1607 | 0 | 131.7049 | 636.5111 |  | 61.0335 | 246.4322 | 139.1607 | 0 | 131.7049 | 578.3314 |  | 64.7703 | 251.7895 | 46.3869 | 0 | 131.7049 | 494.6515 |  | 52.3145 | 166.0739 | 185.5476 | 0 | 131.7049 | 535.6409 |  | 56.0512 | 182.1456 | 92.7738 | 0 | 131.7049 | 462.6755
|  |  | 1365 | 1335 | C4 | 451 | 525 | 357 | 28 | 4 | 1365 | 399 | 528 | 360 | 67 | 11 | 1365 | 48 | 30 | -59 | -33 | -12 | -26 | 402 | 461 | 376 | 96 | 17 | 1352 | 48 | 58 | -59 | -53 | -24 | -30 | 368 | 351 | 484 | 107 | 32 | 1342 |  |  | C4 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C4 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | C4 | 2.076 | 8.9287 | 25.7705 | 57.6846 | 109.7541 | C4 | 828.3124 | 4714.3561 | 9277.381 | 3864.8654 | 1207.2947 | 19892.2095 |  | 936.2629 | 4687.5699 | 9200.0695 | 1615.1676 | 439.0162 | 16878.0862 |  | 834.5403 | 4116.1328 | 9689.709 | 5537.7175 | 1865.8191 | 22043.9188 |  | 934.1869 | 4383.994 | 8169.2494 | 3634.1271 | 548.7703 | 17670.3277 |  | 763.9573 | 3133.9753 | 12472.9233 | 6172.2477 | 3512.13 | 26055.2336 |  | 863.6039 | 3651.8402 | 10952.4636 | 3114.9661 | 878.0325 | 19460.9064
|  |  | 9896 | 9874 |  | 3178 | 4251 | 2219 | 208 | 40 |  | 2808 | 4275 | 2235 | 432 | 146 |  | 359 | 258 | -340 | -179 | -120 |  | 2850 | 3753 | 2343 | 627 | 323 |  | 379 | 503 | -340 | -276 | -288 |  | 2628 | 2889 | 3014 | 699 | 666 | [22 empty] | 2619.4602 | 16249.8853 | 25245.8153 | 11241.5666 | 6190.1291 | 61546.8565 |  | 2963.8223 | 16158.0983 | 25054.0827 | 5290.8276 | 1773.6256 | 51240.4565 |  | 2654.5026 | 14250.9269 | 26443.6282 | 16273.9674 | 13196.8284 | 72819.8535 |  | 2984.4989 | 15221.2986 | 22524.4502 | 11472.3048 | 7968.1449 | 60170.6974 |  | 2443.5839 | 10946.5919 | 34022.2176 | 18149.8692 | 26990.7189 | 92552.9816 |  | 2789.1916 | 12835.1915 | 30103.0396 | 10673.9505 | 14728.9951 | 71130.3684
| EHV OHL Fittings and Conductors (Tower Lines) |  | 591.3506 | 536.1351 | C1 | 2.2333 | 172.982 | 97.1676 | 158.0498 | 160.9179 | 591.3506 | 2.2333 | 90.3849 | 47.0231 | 230.8255 | 220.8837 | 591.3506 | 102.8067 | 32.543 | 45.7931 | -41.532 | -194.8261 | -55.2155 | 1.9354 | 41.9414 | 191.087 | 41.7973 | 314.5894 | 591.3506 | 118.5467 | 32.543 | 55.6663 | -43.3214 | -218.65 | -55.2155 | 1.0705 | 4.1592 | 181.3945 | 85.7587 | 318.9677 | 591.3506 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.4348 | 6.4348 | C3 | 0 | 0.83798 | 0.69576 | 1.2627 | 3.6383 | 6.4348 | 0 | 0.29214 | 0.69576 | 1.2627 | 4.1841 | 6.4348 | 0.72651 | 0 | 2.6888 | 0 | -3.4154 | 0 | 0 | 0.29214 | 0.91871 | 0.32289 | 4.901 | 6.4348 | 0.98982 | 0 | 2.6888 | 0 | -3.6787 | 0 | 0 | 0 | 0.83798 | 0.69576 | 4.901 | 6.4348 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.5628 | 4.5628 | C4 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0.36325 | 0 | 1.9374 | 0 | -2.3006 | 0 | 0 | 0.73612 | 0.59389 | 0.29022 | 2.9425 | 4.5628 | 0.65347 | 0 | 1.9374 | 0 | -2.5908 | 0 | 0 | 0.29791 | 0.43821 | 0.59389 | 3.2328 | 4.5628 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 602.3481 | 547.1327 |  | 2.2333 | 174.5561 | 98.4572 | 161.171 | 165.9304 |  | 2.2333 | 91.4132 | 48.3128 | 233.9468 | 226.442 |  | 103.8964 | 32.543 | 50.4193 | -41.532 | -200.5421 |  | 1.9354 | 42.9697 | 192.5996 | 42.4104 | 322.433 |  | 120.19 | 32.543 | 60.2925 | -43.3214 | -224.9195 |  | 1.0705 | 4.4571 | 182.6707 | 87.0484 | 327.1015 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 |  | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 |  | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 |  | 58388.3536 | 156299.7581 | 338741.4417 | 399419.5526 | 228976.1753 | 1181825.2813 |  | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 |  | 60055.0137 | 111868.8737 | 369936.8043 | 407738.6894 | 603981.058 | 1553580.439
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 32 | 32 | C1 | 30 | 0 | 2 | 0 | 0 | 32 | 30 | 0 | 2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 2 | 0 | 2 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 3 | 0 | 2 | 0 | 32 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23 | 23 | C2 | 23 | 0 | 0 | 0 | 0 | 23 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 8 | 23 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26 | 27 | C3 | 18 | 0 | 0 | 8 | 0 | 26 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 0 | 26 | 9 | 0 | 0 | 0 | -8 | 1 | 18 | 0 | 0 | 0 | 8 | 26 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 83 | 84 |  | 73 | 0 | 2 | 8 | 0 |  | 63 | 0 | 4 | 8 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 2 | 0 | 12 | 8 |  | 9 | 0 | 0 | 0 | -8 |  | 55 | 8 | 0 | 4 | 16 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Transformer |  | 30 | 30 | C1 | 18 | 9 | 3 | 0 | 0 | 30 | 16 | 9 | 3 | 1 | 1 | 30 | 2 | -2 | 0 | 0 | 0 | 0 | 15 | 9 | 1 | 3 | 2 | 30 | 2 | -2 | 0 | 0 | 0 | 0 | 15 | 6 | 4 | 3 | 2 | 30 |  |  | C1 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C1 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | C1 | 273.0427 | 1174.3506 | 3389.4731 | 7586.9787 | 14435.4359 | C1 | 4368.6833 | 10569.155 | 10168.4193 | 7586.9787 | 14435.4359 | 47128.6721 |  | 4914.7687 | 10569.155 | 10168.4193 | 0 | 0 | 25652.343 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4641.726 | 8220.4539 | 3389.4731 | 22760.9361 | 28870.8717 | 67883.4609 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441 |  | 4641.726 | 4697.4022 | 13557.8923 | 22760.9361 | 28870.8717 | 74528.8284
|  |  | 34 | 34 | C2 | 12 | 10 | 8 | 4 | 0 | 34 | 12 | 10 | 8 | 4 | 0 | 34 | 2 | 2 | -2 | 0 | -2 | 0 | 10 | 11 | 8 | 2 | 3 | 34 | 2 | 2 | -2 | 1 | -3 | 0 | 8 | 11 | 8 | 3 | 4 | 34 |  |  | C2 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C2 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | C2 | 390.061 | 1677.6436 | 4842.1044 | 10838.541 | 20622.0512 | C2 | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 3900.6101 | 18454.0801 | 38736.8352 | 21677.082 | 61866.1537 | 144634.7612 |  | 4680.7321 | 21809.3674 | 29052.6264 | 21677.082 | 20622.0512 | 97841.8593 |  | 3120.4881 | 18454.0801 | 38736.8352 | 32515.6231 | 82488.2049 | 175315.2315 |  | 3900.6101 | 21809.3674 | 29052.6264 | 43354.1641 | 20622.0512 | 118738.8193
|  |  | 13 | 13 | C3 | 7 | 4 | 2 | 0 | 0 | 13 | 5 | 4 | 2 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 |  |  | C3 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C3 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | C3 | 585.0915 | 2516.4655 | 7263.1566 | 16257.8115 | 30933.0768 | C3 | 2925.4576 | 10065.8619 | 14526.3132 | 32515.6231 | 0 | 60033.2558 |  | 4095.6406 | 10065.8619 | 14526.3132 | 0 | 0 | 28687.8157 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 |  |  | C4 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C4 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | C4 | 975.1525 | 4194.1091 | 12105.261 | 27096.3525 | 51555.1281 | C4 | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051
|  |  | 79 | 79 |  | 39 | 23 | 13 | 4 | 0 |  | 35 | 23 | 13 | 7 | 1 |  | 4 | 0 | -2 | 0 | -2 |  | 32 | 24 | 11 | 5 | 7 |  | 4 | 0 | -2 | 1 | -3 |  | 30 | 21 | 14 | 6 | 8 | [22 empty] | 13925.1781 | 37411.4534 | 63431.5677 | 83456.7658 | 14435.4359 | 212660.4009 |  | 15641.4465 | 37411.4534 | 63431.5677 | 43354.1641 | 0 | 159838.6317 |  | 12872.0133 | 39089.097 | 56652.6215 | 44438.0182 | 152603.1791 | 305654.9292 |  | 14198.2208 | 40095.6832 | 46968.4127 | 44438.0182 | 111359.0766 | 257059.4116 |  | 12091.8913 | 35566.0454 | 66821.0408 | 55276.5592 | 173225.2303 | 342980.767 |  | 13418.0988 | 36572.6316 | 57136.832 | 66115.1002 | 111359.0766 | 284601.7392
| 132kV UG Cable (Gas) |  | 0.0030333 | 0.0030333 | C1 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0.67969 | 0.67969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0011431 | 0.0011431 | C2 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0.25615 | 0.25615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.016356 | 0.016356 | C3 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 3.6651 | 3.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0054672 | 0.0054672 | C4 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 1.2251 | 1.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.026 | 0.026 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 5.826 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 6.9437 | 3.5895 | C1 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 0 | -0.048089 | -0.23887 | -1.264 | -1.5509 | 0 | 2.7908 | 0.70587 | 1.9907 | 1.6982 | 7.1857 | 0 | 0 | -0.12567 | -1.0489 | -2.1796 | -3.3542 | 0 | 0.64753 | 1.6511 | 1.1276 | 4.3905 | 7.8167 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23.6291 | 13.5056 | C2 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 0 | 0 | -0.29466 | -1.4717 | -1.6764 | -3.4428 | 1.3281 | 3.2115 | 4.3252 | 12.2653 | 2.2523 | 23.3825 | 0 | 0 | -0.77005 | -6.4626 | -2.8908 | -10.1235 | 1.3281 | 0.74514 | 10.1171 | 6.9474 | 5.823 | 24.9608 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26.675 | 20.5527 | C3 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 0 | -0.40725 | -0.53938 | -1.5597 | -2.5063 | 0 | 14.1616 | 5.9778 | 4.4951 | 2.0955 | 26.73 | 0 | 0 | -1.0643 | -2.3685 | -2.6895 | -6.1223 | 0 | 3.2858 | 13.9829 | 2.5462 | 5.4176 | 25.2324 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.97712 | 0.97712 | C4 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21505 | 0 | 0 | 0 | 0.21505 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 58.225 | 38.625 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 0 | 0 | -0.75 | -2.25 | -4.5 |  | 1.3281 | 21.0908 | 11.0088 | 18.7512 | 6.0461 |  | 0 | 0 | -1.96 | -9.88 | -7.76 |  | 1.3281 | 4.8935 | 25.7511 | 10.6212 | 15.6311 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  | 32.1946 | 51.7946 | C1 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 24.6703 | 1.6243 | 0 | 0 | 0 | 26.2946 | 7.5 | 0 | 0 | 0 | 0 | 7.5 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 19.6 | 0 | 0 | 0 | 0 | 19.6 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 |  |  | C1 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C1 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | C1 | 2149.4357 | 9244.6748 | 26682.4726 | 59725.9062 | 94592.4846 | C1 | 53027.1783 | 15016.3613 | 0 | 0 | 0 | 68043.5396 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 81829.6171 | 15016.3613 | 0 | 0 | 0 | 96845.9784 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 107837.7894 | 15016.3613 | 0 | 0 | 0 | 122854.1507
|  |  | 0.61927 | 0.61927 | C2 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 |  |  | C2 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C2 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | C2 | 3070.6225 | 13206.6783 | 38117.818 | 85322.7231 | 135132.1208 | C2 | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C3 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | C3 | 4605.9337 | 19810.0175 | 57176.727 | 127984.0847 | 202698.1813 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.0781 | 6.0781 | C4 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 |  |  | C4 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C4 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | C4 | 7676.5562 | 33016.6958 | 95294.5449 | 213306.8078 | 337830.3021 | C4 | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825
|  |  | 38.892 | 58.492 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 24.6703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 7.5 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 19.6 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 | [22 empty] | 53027.1783 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 283805.6892 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 81829.6171 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 312608.1279 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 107837.7894 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 338616.3003
| 132kV OHL Support - Tower |  | 572 | 572 | C1 | 145 | 227 | 58 | 28 | 114 | 572 | 52 | 139 | 94 | 35 | 252 | 572 | 116 | 0 | 0 | 0 | -116 | 0 | 88 | 237 | 56 | 46 | 145 | 572 | 119 | 34 | 0 | -21 | -132 | 0 | 34 | 111 | 180 | 56 | 191 | 572 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 363 | 363 | C2 | 184 | 73 | 9 | 41 | 56 | 363 | 17 | 67 | 23 | 48 | 208 | 363 | 18 | 0 | 0 | 0 | -18 | 0 | 115 | 88 | 56 | 7 | 97 | 363 | 96 | 36 | 0 | -34 | -98 | 0 | 4 | 171 | 28 | 56 | 104 | 363 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 122 | 122 | C3 | 28 | 66 | 0 | 23 | 5 | 122 | 4 | 8 | 13 | 26 | 71 | 122 | 2 | 0 | 0 | 0 | -2 | 0 | 10 | 82 | 2 | 0 | 28 | 122 | 5 | 1 | 0 | 0 | -6 | 0 | 2 | 26 | 64 | 2 | 28 | 122 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 112 | 112 | C4 | 97 | 7 | 0 | 0 | 8 | 112 | 1 | 2 | 4 | 22 | 83 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 7 | 1 | 0 | 8 | 112 | 9 | 0 | 0 | -1 | -8 | 0 | 0 | 97 | 6 | 1 | 8 | 112 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1169 | 1169 |  | 454 | 373 | 67 | 92 | 183 |  | 74 | 216 | 134 | 131 | 614 |  | 136 | 0 | 0 | 0 | -136 |  | 309 | 414 | 115 | 53 | 278 |  | 229 | 71 | 0 | -56 | -244 |  | 40 | 405 | 278 | 115 | 331 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 535.0969 | 535.0969 | C1 | 59.426 | 153.5999 | 184.0823 | 56.0422 | 81.9465 | 535.0969 | 58.4481 | 35.9218 | 99.5766 | 159.0191 | 182.1313 | 535.0969 | 0 | 7.2837 | 70.9715 | -9.4694 | -68.7858 | 0 | 55.9704 | 21.8938 | 243.6033 | 80.0159 | 133.6134 | 535.0969 | 0 | 11.7094 | 73.1077 | -11.7764 | -73.0407 | 0 | 55.9704 | 13.4634 | 234.4327 | 94.4155 | 136.8148 | 535.0969 |  | 307.5404 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 40.1377 | 40.1377 | C2 | 0.52193 | 3.2945 | 27.6214 | 2.1808 | 6.5189 | 40.1377 | 0.52193 | 0 | 26.7231 | 3.2693 | 9.6234 | 40.1377 | 0 | 0 | 4.449 | -0.76252 | -3.6865 | 0 | 0.52193 | 0 | 29.3017 | 1.6143 | 8.6998 | 40.1377 | 0 | 0 | 28.5993 | -24.6916 | -3.9077 | 0 | 0.52193 | 0 | 5.3726 | 25.5434 | 8.6998 | 40.1377 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.9077 | 3.9077 | C3 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 0.74894 | -0.74894 | 0 | 0 | 0 | 0 | 0.49864 | 2.6601 | 0.74894 | 3.9077 | 0 | 0 | 1.5386 | -1.2476 | -0.29104 | 0 | 0 | 0 | 0 | 2.2856 | 1.622 | 3.9077 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.7653 | 4.7653 | C4 | 0 | 0 | 2.8134 | 1.4503 | 0.50155 | 4.7653 | 0 | 0 | 2.1517 | 1.4503 | 1.1632 | 4.7653 | 0 | 0 | 1.1642 | -1.1642 | 0 | 0 | 0 | 0 | 0.71013 | 3.5536 | 0.50155 | 4.7653 | 0 | 0 | 1.4503 | -1.1642 | -0.28619 | 0 | 0 | 0 | 0.71013 | 2.1032 | 1.9519 | 4.7653 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 583.9075 | 583.9075 |  | 59.9479 | 156.8945 | 216.8026 | 61.2954 | 88.967 |  | 58.97 | 35.9218 | 130.737 | 165.3608 | 192.9179 |  | 0 | 7.2837 | 77.3335 | -12.145 | -72.4722 |  | 56.4923 | 21.8938 | 274.1138 | 87.8439 | 143.5637 |  | 0 | 11.7094 | 104.6959 | -38.8797 | -77.5256 |  | 56.4923 | 13.4634 | 240.5154 | 124.3478 | 149.0886 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 |  | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 |  | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 |  | 96027.8379 | 262760.9376 | 47006.5306 | 51567.2319 | 112305.0015 | 569667.5395 |  | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 |  | 121255.8882 | 259237.886 | 57174.9498 | 73244.314 | 112305.0015 | 623218.0394
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 241438.9569 | 239331.4414 |  | 79461.5571 | 63119.1043 | 62690.8796 | 28331.1633 | 7836.2525 |  | 72340.8732 | 62950.9887 | 64146.4037 | 31275.6199 | 11650.0551 |  | 9184.9964 | 365.8267 | -2147.7872 | -3178.727 | -5378.8243 |  | 69731.9612 | 33024.191 | 68678.0298 | 56487.4481 | 13538.3268 |  | 22458.69 | 408.2524 | -4320.2916 | -7473.9411 | -13180.2251 |  | 60791.0253 | 29640.0713 | 61151.9975 | 58228.2551 | 31648.6077 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 |  | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 |  | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 |  | 332934.0901 | 878152.9764 | 1049619.4263 | 1120996.0671 | 1066525.591 | 4448228.1508 |  | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 |  | 353451.7884 | 796920.1926 | 1038189.2497 | 1083236.7708 | 1857522.5155 | 5129320.517
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 | LV Network | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 | LV Network | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 | HV Network | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 175144.0071 | 455358.9556 | 612745.254 | 507514.351 | 687263.3378 | 2438025.9055 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 | HV Network | 168350.4533 | 423086.6854 | 571952.6995 | 450002.6259 | 1050379.2866 | 2663771.7507
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 | EHV Network | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 | EHV Network | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 | EHV Network | 58388.3536 | 156299.7581 | 338741.4417 | 399419.5526 | 228976.1753 | 1181825.2813 | EHV Network | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 | EHV Network | 60055.0137 | 111868.8737 | 369936.8043 | 407738.6894 | 603981.058 | 1553580.439
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 | 132kV Network | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 | 132kV Network | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 | 132kV Network | 96027.8379 | 262760.9376 | 47006.5306 | 51567.2319 | 112305.0015 | 569667.5395 | 132kV Network | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 | 132kV Network | 121255.8882 | 259237.886 | 57174.9498 | 73244.314 | 112305.0015 | 623218.0394
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 | Total | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 | Total | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 | Total | 332934.0901 | 878152.9764 | 1049619.4263 | 1120996.0671 | 1066525.591 | 4448228.1508 | Total | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 | Total | 353451.7884 | 796920.1926 | 1038189.2497 | 1083236.7708 | 1857522.5155 | 5129320.517
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## NPgN - Asset Rep
HI3: Secondary deliverables RIIO-ED1 - Asset replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
NPGN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 32035 | 32630 | C1 | 9664 | 7276 | 12171 | 1565 | 1359 | 32035 | 8728 | 7327 | 12342 | 1906 | 1617 | 31920 | 1661 | -39 | -244 | -480 | -670 | 228 | 8443 | 1599 | 8642 | 10620 | 2211 | 31515 | 3901 | -87 | -560 | -1110 | -1549 | 595 | 7452 | 1226 | 6986 | 10535 | 5206 | 31405 |  |  | C1 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C1 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | C1 | 0.12877 | 0.55385 | 1.5985 | 3.5782 | 6.808 | C1 | 1123.9253 | 4058.0377 | 19729.2174 | 6819.9924 | 11008.5989 | 42739.7717 |  | 1244.4562 | 4029.7915 | 19455.8666 | 5599.8363 | 9252.1249 | 39582.0755 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 1301.1161 | 864.0015 | 13424.5639 | 36282.6457 | 10491.1879 | 62363.5151 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723 |  | 1461.9528 | 630.8318 | 10272.2372 | 33724.254 | 24896.9983 | 70986.2741
|  |  | 23767 | 22983 | C2 | 6593 | 5704 | 9745 | 886 | 839 | 23767 | 5948 | 5742 | 9876 | 1268 | 1127 | 23961 | 1145 | -23 | -190 | -538 | -750 | -356 | 5770 | 1274 | 6931 | 7777 | 1467 | 23219 | 2684 | -55 | -434 | -1242 | -1737 | -784 | 5104 | 992 | 5617 | 7720 | 3656 | 23089 |  |  | C2 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C2 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | C2 | 0.18396 | 0.79121 | 2.2836 | 5.1117 | 9.7258 | C2 | 1094.1973 | 4543.1286 | 22553.1578 | 6481.5997 | 10960.9426 | 45633.026 |  | 1212.8518 | 4513.0626 | 22254.0019 | 4528.9411 | 8159.9209 | 40668.7784 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 1272.0871 | 989.8039 | 15393.9689 | 37003.3914 | 6973.377 | 61632.6283 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007 |  | 1432.6847 | 741.3639 | 11836.0689 | 33113.4092 | 18663.7524 | 65787.2791
|  |  | 6362 | 6508 | C3 | 761 | 1889 | 2641 | 666 | 405 | 6362 | 689 | 1903 | 2679 | 666 | 405 | 6342 | 128 | -13 | -54 | 0 | 0 | 61 | 662 | 410 | 1873 | 3143 | 598 | 6686 | 301 | -29 | -126 | 0 | 0 | 146 | 582 | 312 | 1512 | 3118 | 1282 | 6806 |  |  | C3 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C3 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | C3 | 0.27594 | 1.1868 | 3.4254 | 7.6675 | 14.5887 | C3 | 190.1232 | 2258.5093 | 9176.7785 | 5106.56 | 5908.4052 | 22640.3763 |  | 209.991 | 2241.8939 | 9046.6114 | 5106.56 | 5908.4052 | 22513.4615 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 217.9932 | 471.1656 | 6230.8922 | 24098.9762 | 8724.0156 | 39743.0428 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071 |  | 243.6557 | 335.8687 | 4747.6726 | 23907.2885 | 18702.6554 | 47937.141
|  |  | 9964 | 9207 | C4 | 1217 | 3352 | 4087 | 861 | 447 | 9964 | 1100 | 3376 | 4145 | 989 | 545 | 10155 | 206 | -21 | -84 | -182 | -252 | -333 | 1061 | 733 | 2900 | 5277 | 737 | 10708 | 484 | -45 | -192 | -421 | -583 | -757 | 934 | 560 | 2341 | 5234 | 1759 | 10828 |  |  | C4 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C4 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | C4 | 0.4599 | 1.978 | 5.7091 | 12.7792 | 24.3144 | C4 | 505.8915 | 6677.8136 | 23664.1451 | 12638.6083 | 13251.3614 | 56737.8199 |  | 559.6999 | 6630.341 | 23333.0184 | 11002.8733 | 10868.5478 | 52394.4804 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 582.695 | 1408.354 | 16076.7751 | 65109.9182 | 11792.496 | 94970.2383 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003 |  | 652.1401 | 1018.6831 | 12268.8173 | 61506.1897 | 28593.7634 | 104039.5936
|  |  | 72128 | 71328 |  | 18235 | 18221 | 28644 | 3978 | 3050 |  | 16465 | 18348 | 29042 | 4829 | 3694 |  | 3140 | -96 | -572 | -1200 | -1672 |  | 15936 | 4016 | 20346 | 26817 | 5013 |  | 7370 | -216 | -1312 | -2773 | -3869 |  | 14072 | 3090 | 16456 | 26607 | 11903 | [22 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1598 | 1589 | C1 | 200 | 510 | 480 | 286 | 122 | 1598 | 168 | 514 | 493 | 307 | 134 | 1616 | 58 | -1 | -4 | -21 | -37 | -5 | 168 | 430 | 357 | 375 | 286 | 1616 | 181 | -1 | -6 | -34 | -149 | -9 | 145 | 299 | 379 | 303 | 490 | 1616 |  |  | C1 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C1 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | C1 | 7.6091 | 32.7266 | 94.4572 | 211.4325 | 402.2841 | C1 | 1278.3294 | 16821.4644 | 46567.4046 | 64909.7843 | 53906.0643 | 183483.0471 |  | 1521.8208 | 16690.5581 | 45339.4609 | 60469.7014 | 49078.6555 | 173100.1966 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1719.6575 | 14039.7047 | 33343.3952 | 74847.1129 | 100168.7314 | 224118.6017 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096 |  | 2480.5678 | 9752.5222 | 35232.5394 | 56875.3485 | 137178.8651 | 241519.843
|  |  | 565 | 562 | C2 | 93 | 126 | 180 | 125 | 41 | 565 | 81 | 126 | 181 | 135 | 42 | 565 | 43 | -3 | -7 | -22 | -12 | -1 | 80 | 82 | 150 | 160 | 93 | 565 | 93 | -3 | -8 | -42 | -43 | -3 | 67 | 81 | 104 | 134 | 179 | 565 |  |  | C2 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C2 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | C2 | 10.8701 | 46.7523 | 134.9389 | 302.0465 | 574.6915 | C2 | 880.482 | 5890.7852 | 24423.9358 | 40776.2721 | 24137.0437 | 96108.5189 |  | 1010.9238 | 5890.7852 | 24288.9969 | 37755.8075 | 23562.3522 | 92508.8656 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 1337.0282 | 3693.4288 | 19296.2587 | 41682.4115 | 46550.0129 | 112559.1401 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831 |  | 1739.2237 | 3646.6766 | 12954.1317 | 27788.2744 | 78158.0463 | 124286.3526
|  |  | 111 | 111 | C3 | 4 | 64 | 41 | 2 | 0 | 111 | 4 | 64 | 41 | 2 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 58 | 39 | 10 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 32 | 20 | 4 | 111 |  |  | C3 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C3 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | C3 | 16.3052 | 70.1284 | 202.4083 | 453.0697 | 862.0373 | C3 | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473
|  |  | 267 | 255 | C4 | 47 | 50 | 66 | 74 | 30 | 267 | 36 | 50 | 70 | 80 | 34 | 270 | 23 | 0 | -2 | -13 | -14 | -6 | 36 | 42 | 28 | 97 | 67 | 270 | 42 | 0 | -2 | -24 | -28 | -12 | 35 | 36 | 23 | 38 | 138 | 270 |  |  | C4 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C4 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | C4 | 27.1754 | 116.8807 | 337.3472 | 755.1162 | 1436.7288 | C4 | 978.3133 | 5844.0329 | 23614.3026 | 60409.2921 | 48848.7789 | 139694.7198 |  | 1277.2424 | 5844.0329 | 22264.9138 | 55878.5952 | 43101.8638 | 128366.6481 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 1603.3469 | 4908.9877 | 8771.0267 | 63429.7567 | 76146.626 | 154859.7439 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139 |  | 2092.5035 | 4207.7037 | 7084.2908 | 10571.6261 | 158040.1671 | 181996.2913
|  |  | 2541 | 2517 |  | 344 | 750 | 767 | 487 | 193 |  | 289 | 754 | 785 | 524 | 210 |  | 124 | -4 | -13 | -56 | -63 |  | 288 | 612 | 574 | 642 | 446 |  | 316 | -4 | -16 | -100 | -220 |  | 248 | 470 | 538 | 495 | 811 | [22 empty] | 3202.3457 | 33044.4999 | 102904.3836 | 167001.4879 | 126891.8869 | 433044.604 |  | 3875.2078 | 32913.5935 | 100192.1123 | 155010.2435 | 115742.8715 | 407734.0286 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 4725.2534 | 26709.5682 | 69304.6045 | 184489.978 | 222865.3702 | 508094.7744 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404 |  | 6328.6003 | 21393.8358 | 61748.0277 | 104296.6428 | 376825.2276 | 570592.3342
| HV Switchgear (GM) - Distribution |  | 5352 | 5310 | C1 | 3986 | 1248 | 108 | 9 | 1 | 5352 | 3792 | 1272 | 172 | 49 | 123 | 5408 | 147 | -20 | -80 | -42 | -18 | -13 | 3745 | 1052 | 480 | 48 | 27 | 5352 | 291 | -41 | -147 | -83 | -62 | -42 | 3399 | 1205 | 588 | 96 | 64 | 5352 |  |  | C1 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C1 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | C1 | 10.5841 | 45.5219 | 131.3876 | 294.0973 | 559.567 | C1 | 40134.7977 | 57903.7962 | 22598.6661 | 14410.7676 | 68826.7371 | 203874.7647 |  | 42188.1075 | 56811.2717 | 14189.8601 | 2646.8757 | 559.567 | 116395.682 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 41193.2049 | 46978.5516 | 52555.0374 | 1764.5838 | 5036.1027 | 147527.4804 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214 |  | 39055.2225 | 52987.4361 | 57941.9287 | 3823.2649 | 1119.1339 | 154926.9861
|  |  | 6308 | 5809 | C2 | 3108 | 2682 | 458 | 22 | 38 | 6308 | 2935 | 2728 | 670 | 89 | 195 | 6617 | 137 | -34 | -275 | -64 | -16 | -252 | 2775 | 2151 | 1032 | 266 | 84 | 6308 | 273 | -70 | -507 | -132 | -63 | -499 | 2438 | 2053 | 1198 | 417 | 202 | 6308 |  |  | C2 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C2 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | C2 | 15.1201 | 65.0312 | 187.6966 | 420.139 | 799.3814 | C2 | 44377.4983 | 177405.1617 | 125756.6966 | 37392.3707 | 155879.3698 | 540811.0971 |  | 46993.2758 | 174413.7257 | 85965.0254 | 9243.0579 | 30376.4926 | 346991.5775 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 44029.7359 | 137671.0878 | 142086.2975 | 84868.0774 | 54357.9341 | 463013.1326 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801 |  | 40990.5955 | 128956.9046 | 129698.3244 | 119739.6141 | 111114.0123 | 530499.4509
|  |  | 2231 | 1899 | C3 | 924 | 1031 | 228 | 0 | 48 | 2231 | 880 | 1054 | 339 | 40 | 86 | 2399 | 33 | -18 | -139 | -42 | -8 | -174 | 789 | 765 | 488 | 111 | 78 | 2231 | 65 | -36 | -255 | -83 | -23 | -332 | 682 | 745 | 483 | 198 | 123 | 2231 |  |  | C3 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C3 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | C3 | 22.6802 | 97.5468 | 281.5448 | 630.2085 | 1199.0721 | C3 | 19958.5341 | 102814.3551 | 95443.7018 | 25208.3398 | 103120.1985 | 346545.1293 |  | 20956.4608 | 100570.7781 | 64192.2242 | 0 | 57555.4596 | 243274.9228 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 18643.0853 | 72867.4794 | 98259.1503 | 43484.3862 | 83935.0453 | 317189.1464 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562 |  | 16942.0739 | 69160.7 | 64192.2242 | 72473.9769 | 119907.2075 | 342676.1825
|  |  | 895 | 670 | C4 | 304 | 445 | 105 | 23 | 18 | 895 | 290 | 456 | 166 | 54 | 50 | 1016 | 9 | -8 | -76 | -34 | -6 | -115 | 233 | 358 | 194 | 55 | 55 | 895 | 17 | -16 | -140 | -69 | -17 | -225 | 199 | 292 | 226 | 90 | 88 | 895 |  |  | C4 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C4 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | C4 | 37.8003 | 162.578 | 469.2414 | 1050.3475 | 1998.4535 | C4 | 10962.0737 | 74135.5881 | 77894.0733 | 56718.7646 | 99922.6729 | 319633.1726 |  | 11491.2772 | 72347.2296 | 49270.3476 | 24157.9923 | 35972.1623 | 193239.009 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 9147.6615 | 56902.3154 | 55370.4858 | 22057.2973 | 97924.2195 | 241401.9796 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757 |  | 8164.8549 | 44871.5402 | 40354.7609 | 22057.2973 | 141890.1956 | 257338.6488
|  |  | 14786 | 13688 |  | 8322 | 5406 | 899 | 54 | 105 |  | 7897 | 5510 | 1347 | 232 | 454 |  | 326 | -80 | -570 | -182 | -48 |  | 7542 | 4326 | 2194 | 480 | 244 |  | 646 | -163 | -1049 | -367 | -165 |  | 6718 | 4295 | 2495 | 801 | 477 | [22 empty] | 115432.9038 | 412258.9011 | 321693.1378 | 133730.2427 | 427748.9783 | 1410864.1637 |  | 121629.1215 | 404143.0052 | 213617.4573 | 36047.9259 | 124463.6814 | 899901.1913 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 113013.6875 | 314419.4342 | 348270.971 | 152174.3446 | 241253.3016 | 1169131.7389 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334 |  | 105152.7467 | 295976.5809 | 292187.2382 | 218094.1532 | 374030.5494 | 1285441.2684
| HV Transformer (GM) |  | 3258 | 3451 | C1 | 2494 | 563 | 122 | 64 | 15 | 3258 | 2396 | 571 | 126 | 72 | 39 | 3204 | 144 | -1 | 0 | -12 | -38 | 93 | 2368 | 492 | 250 | 78 | 70 | 3258 | 296 | -1 | 0 | -24 | -78 | 193 | 2251 | 422 | 376 | 88 | 121 | 3258 |  |  | C1 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C1 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | C1 | 7.0107 | 30.1527 | 87.0284 | 194.8038 | 370.6454 | C1 | 16797.5544 | 17217.2001 | 10965.5746 | 14025.8769 | 14455.1688 | 73461.3748 |  | 17484.5996 | 16975.9783 | 10617.4612 | 12467.4461 | 5559.6803 | 63105.1655 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 17610.7916 | 14804.9829 | 21757.0925 | 12857.0538 | 11860.6514 | 78890.5722 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947 |  | 17856.1649 | 12694.2929 | 32722.6672 | 12467.4461 | 15937.7503 | 91678.3213
|  |  | 5365 | 5253 | C2 | 2652 | 1750 | 484 | 405 | 74 | 5365 | 2536 | 1753 | 478 | 446 | 166 | 5379 | 163 | 2 | 0 | -70 | -147 | -52 | 2335 | 1610 | 674 | 315 | 431 | 5365 | 335 | 2 | 0 | -146 | -303 | -112 | 2105 | 1538 | 788 | 263 | 671 | 5365 |  |  | C2 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C2 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | C2 | 10.0152 | 43.0753 | 124.3262 | 278.2912 | 529.4934 | C2 | 25398.6393 | 75511.0125 | 59427.9442 | 124117.8788 | 87895.8985 | 372351.3733 |  | 26560.4068 | 75381.7866 | 60173.9016 | 112707.9393 | 39182.509 | 314006.5432 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 25018.0604 | 69437.3943 | 83795.8878 | 68181.346 | 150376.1155 | 396808.8039 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088 |  | 24437.1767 | 66335.9722 | 97969.0795 | 32560.0713 | 194853.5581 | 416155.8578
|  |  | 914 | 889 | C3 | 498 | 275 | 75 | 57 | 9 | 914 | 480 | 281 | 79 | 65 | 25 | 930 | 27 | -1 | 0 | -12 | -27 | -13 | 460 | 202 | 145 | 48 | 59 | 914 | 55 | -1 | 0 | -24 | -55 | -25 | 428 | 159 | 190 | 43 | 94 | 914 |  |  | C3 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C3 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | C3 | 15.0229 | 64.613 | 186.4894 | 417.4368 | 794.24 | C3 | 7210.9702 | 18156.2417 | 14732.6598 | 27133.3928 | 19856.0012 | 87089.2657 |  | 7481.3815 | 17768.564 | 13986.7023 | 23793.8983 | 7148.1604 | 70178.7066 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 7316.1301 | 12987.205 | 27040.9579 | 15027.7252 | 25415.6815 | 87787.6997 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689 |  | 7256.0387 | 10208.8477 | 35432.9793 | 7931.2994 | 30975.3618 | 91804.5269
|  |  | 423 | 367 | C4 | 180 | 130 | 64 | 42 | 7 | 423 | 174 | 136 | 68 | 48 | 23 | 449 | 8 | -1 | 0 | -8 | -27 | -28 | 163 | 106 | 75 | 35 | 44 | 423 | 16 | -1 | 0 | -16 | -55 | -56 | 141 | 104 | 60 | 45 | 73 | 423 |  |  | C4 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C4 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | C4 | 25.0381 | 107.6883 | 310.8156 | 695.728 | 1323.7334 | C4 | 4356.6278 | 14645.6043 | 21135.4613 | 33394.945 | 30445.8685 | 103978.5068 |  | 4506.8563 | 13999.4747 | 19892.1989 | 29220.5768 | 9266.1339 | 76885.2406 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 4281.5135 | 11307.268 | 23311.1706 | 18784.6565 | 22503.468 | 80188.0766 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869 |  | 3930.9803 | 11091.8915 | 18648.9365 | 20176.1126 | 23827.2014 | 77675.1222
|  |  | 9960 | 9960 |  | 5824 | 2718 | 745 | 568 | 105 |  | 5586 | 2741 | 751 | 631 | 253 |  | 342 | -1 | 0 | -102 | -239 |  | 5326 | 2410 | 1144 | 476 | 604 |  | 702 | -1 | 0 | -210 | -491 |  | 4925 | 2223 | 1414 | 439 | 959 | [22 empty] | 53763.7917 | 125530.0586 | 106261.6399 | 198672.0934 | 152652.9369 | 636880.5206 |  | 56033.2442 | 124125.8036 | 104670.264 | 178189.8605 | 61156.4836 | 524175.6559 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 54226.4956 | 108536.8501 | 155905.1087 | 114850.7816 | 210155.9163 | 643675.1523 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116 |  | 53480.3605 | 100331.0042 | 184773.6624 | 73134.9295 | 265593.8716 | 677313.8281
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 42673 | 42754 | C1 | 14496 | 9898 | 9947 | 7197 | 1135 | 42673 | 13237 | 9960 | 10135 | 7612 | 1702 | 42646 | 1476 | -40 | -218 | -423 | -770 | 25 | 12621 | 5451 | 14288 | 8600 | 1822 | 42782 | 4196 | -80 | -558 | -1107 | -2370 | 81 | 10834 | 5196 | 12471 | 9058 | 5121 | 42680 |  |  | C1 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C1 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | C1 | 0.053585 | 0.23047 | 0.66519 | 1.489 | 2.833 | C1 | 709.303 | 2295.4547 | 6741.6714 | 11333.8975 | 4821.7101 | 25902.0367 |  | 776.7663 | 2281.1658 | 6616.6162 | 10715.9827 | 3215.4177 | 23605.9487 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 755.386 | 1247.0588 | 9359.1827 | 12175.155 | 2980.2814 | 26517.0639 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412 |  | 805.3807 | 1179.0709 | 7924.3741 | 11838.652 | 7793.4926 | 29540.9703
|  |  | 56579 | 56824 | C2 | 19086 | 13113 | 12487 | 10437 | 1456 | 56579 | 17419 | 13191 | 12717 | 11032 | 2157 | 56516 | 1966 | -44 | -261 | -603 | -961 | 97 | 16628 | 7242 | 17935 | 12476 | 2327 | 56608 | 5558 | -88 | -681 | -1583 | -2961 | 245 | 14288 | 6915 | 15666 | 13149 | 6479 | 56497 |  |  | C2 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C2 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | C2 | 0.07655 | 0.32924 | 0.95027 | 2.1271 | 4.0471 | C2 | 1333.4213 | 4342.9924 | 12084.5493 | 23465.873 | 8729.5859 | 49956.4219 |  | 1461.0299 | 4317.3118 | 11865.9878 | 22200.2643 | 5892.5717 | 45737.1655 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1423.3674 | 2369.8628 | 16795.0243 | 25254.7416 | 5528.333 | 51371.3291 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412 |  | 1519.2077 | 2247.7151 | 14239.7555 | 24601.7301 | 14237.6835 | 56846.0919
|  |  | 23551 | 23321 | C3 | 7796 | 5437 | 5297 | 4320 | 701 | 23551 | 7119 | 5471 | 5397 | 4570 | 1053 | 23610 | 792 | -24 | -116 | -257 | -477 | -82 | 6787 | 2993 | 7607 | 5162 | 1125 | 23674 | 2252 | -48 | -300 | -669 | -1465 | -230 | 5824 | 2852 | 6638 | 5437 | 3165 | 23916 |  |  | C3 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C3 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | C3 | 0.11482 | 0.49386 | 1.4254 | 3.1906 | 6.0706 | C3 | 817.4373 | 2701.9004 | 7692.8889 | 14581.0877 | 6392.388 | 32185.7022 |  | 895.1736 | 2685.1092 | 7550.3489 | 13783.4352 | 4255.5214 | 29169.5882 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 870.2566 | 1466.2662 | 10677.6785 | 15649.942 | 3933.7772 | 32597.9206 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699 |  | 927.3245 | 1384.7795 | 9034.1912 | 15212.8284 | 10320.0946 | 36879.2183
|  |  | 3346 | 3250 | C4 | 705 | 1366 | 725 | 486 | 64 | 3346 | 645 | 1375 | 740 | 516 | 101 | 3377 | 66 | -8 | -17 | -31 | -50 | -40 | 611 | 749 | 1041 | 580 | 104 | 3085 | 194 | -16 | -45 | -79 | -150 | -96 | 521 | 713 | 906 | 610 | 306 | 3056 |  |  | C4 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C4 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | C4 | 0.19137 | 0.8231 | 2.3757 | 5.3177 | 10.1177 | C4 | 123.4366 | 1131.7593 | 1757.9945 | 2743.9246 | 1021.8917 | 6779.0067 |  | 134.9191 | 1124.3514 | 1722.3595 | 2584.3941 | 647.5353 | 6213.5594 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 129.5606 | 609.9154 | 2432.6843 | 2919.4081 | 546.3579 | 6637.9263 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454 |  | 136.8328 | 573.6991 | 2045.4504 | 2823.6898 | 1578.3674 | 7158.0395
|  |  | 126149 | 126149 |  | 42083 | 29814 | 28456 | 22440 | 3356 |  | 38420 | 29997 | 28989 | 23730 | 5013 |  | 4300 | -116 | -612 | -1314 | -2258 |  | 36647 | 16435 | 40871 | 26818 | 5378 |  | 12200 | -232 | -1584 | -3438 | -6946 |  | 31467 | 15676 | 35681 | 28254 | 15071 | [22 empty] | 2983.5982 | 10472.1068 | 28277.1041 | 52124.7828 | 20965.5757 | 114823.1676 |  | 3267.8889 | 10407.9381 | 27755.3123 | 49284.0763 | 14011.0461 | 104726.2617 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 3178.5706 | 5693.1031 | 39264.5698 | 55999.2468 | 12988.7497 | 117124.2399 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977 |  | 3388.7457 | 5385.2645 | 33243.7712 | 54476.9004 | 33929.6381 | 130424.32
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 |  | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 175144.0071 | 455358.9556 | 612745.254 | 507514.351 | 687263.3378 | 2438025.9055 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 |  | 168350.4533 | 423086.6854 | 571952.6995 | 450002.6259 | 1050379.2866 | 2663771.7507
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 267 | 267 | C1 | 134 | 87 | 42 | 4 | 0 | 267 | 126 | 87 | 50 | 4 | 0 | 267 | 1 | 0 | 0 | 0 | -1 | 0 | 119 | 62 | 43 | 42 | 1 | 267 | 12 | 0 | 0 | -8 | -4 | 0 | 113 | 46 | 64 | 40 | 4 | 267 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 239 | 238 | C2 | 79 | 57 | 72 | 23 | 8 | 239 | 45 | 57 | 81 | 30 | 26 | 239 | 14 | 0 | -1 | -3 | -10 | 0 | 45 | 23 | 34 | 86 | 51 | 239 | 38 | 0 | -1 | -16 | -22 | -1 | 39 | 18 | 45 | 81 | 56 | 239 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 109 | 109 | C3 | 1 | 51 | 51 | 6 | 0 | 109 | 1 | 51 | 51 | 6 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | 46 | 23 | 3 | 109 | 8 | 0 | 0 | -2 | -6 | 0 | 0 | 19 | 35 | 49 | 6 | 109 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44 | 47 | C4 | 2 | 0 | 42 | 0 | 0 | 44 | 2 | 0 | 42 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 | 18 | 0 | 0 | -15 | 0 | 3 | 2 | 0 | 0 | 42 | 0 | 44 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 659 | 661 |  | 216 | 195 | 207 | 33 | 8 |  | 174 | 195 | 224 | 40 | 26 |  | 15 | 0 | -1 | -3 | -11 |  | 167 | 121 | 123 | 193 | 55 |  | 76 | 0 | -1 | -41 | -32 |  | 154 | 83 | 144 | 212 | 66 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV Transformer |  | 103 | 103 | C1 | 37 | 47 | 14 | 5 | 0 | 103 | 37 | 47 | 14 | 5 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 24 | 11 | 0 | 103 | 2 | 0 | 0 | 0 | -2 | 0 | 34 | 17 | 35 | 12 | 5 | 103 |  |  | C1 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C1 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | C1 | 130.7046 | 562.1576 | 1622.5291 | 3631.8605 | 6910.1933 | C1 | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 9556.6785 | 56788.5173 | 43582.3262 | 34550.9666 | 148922.445 |  | 4705.3657 | 9556.6785 | 56788.5173 | 43582.3262 | 20730.5799 | 135363.4676
|  |  | 194 | 194 | C2 | 53 | 54 | 65 | 22 | 0 | 194 | 46 | 54 | 70 | 24 | 0 | 194 | 14 | 0 | -1 | -8 | -5 | 0 | 39 | 40 | 65 | 43 | 7 | 194 | 20 | 0 | -1 | -10 | -9 | 0 | 34 | 29 | 61 | 42 | 28 | 194 |  |  | C2 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C2 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | C2 | 186.7209 | 803.0822 | 2317.8987 | 5188.3722 | 9871.7047 | C2 | 8589.1595 | 43366.4401 | 162252.9065 | 124520.9321 | 0 | 338729.4383 |  | 9896.2055 | 43366.4401 | 150663.4132 | 114144.1878 | 0 | 318070.2466 |  | 7282.1135 | 32123.289 | 150663.4132 | 223100.0034 | 69101.9332 | 482270.7522 |  | 9896.2055 | 32123.289 | 148345.5145 | 181593.026 | 19743.4095 | 391701.4445 |  | 6348.5092 | 23289.3845 | 141391.8185 | 217911.6312 | 276407.7327 | 665349.0761 |  | 10082.9264 | 23289.3845 | 139073.9199 | 166027.9095 | 187562.39 | 526036.5303
|  |  | 16 | 16 | C3 | 9 | 2 | 2 | 3 | 0 | 16 | 8 | 2 | 3 | 3 | 0 | 16 | 4 | 0 | 0 | -2 | -2 | 0 | 8 | 2 | 2 | 2 | 2 | 16 | 4 | 0 | 0 | -2 | -2 | 0 | 8 | 2 | 0 | 3 | 3 | 16 |  |  | C3 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C3 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | C3 | 280.0813 | 1204.6233 | 3476.848 | 7782.5583 | 14807.5571 | C3 | 2240.6503 | 2409.2467 | 10430.544 | 23347.6748 | 0 | 38428.1157 |  | 2520.7316 | 2409.2467 | 6953.696 | 23347.6748 | 0 | 35231.349 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 3360.9755 | 2409.2467 | 6953.696 | 0 | 0 | 12723.9181 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431 |  | 3360.9755 | 2409.2467 | 0 | 7782.5583 | 14807.5571 | 28360.3375
|  |  | 28 | 28 | C4 | 10 | 7 | 9 | 2 | 0 | 28 | 6 | 7 | 11 | 4 | 0 | 28 | 2 | 0 | 0 | -2 | 0 | 0 | 4 | 7 | 10 | 6 | 1 | 28 | 2 | 0 | 0 | -2 | 0 | 0 | 4 | 4 | 7 | 9 | 4 | 28 |  |  | C4 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C4 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | C4 | 466.8021 | 2007.7056 | 5794.7467 | 12970.9304 | 24679.2618 | C4 | 2800.8129 | 14053.9389 | 63742.2133 | 51883.7217 | 0 | 132480.6868 |  | 4668.0215 | 14053.9389 | 52152.72 | 25941.8609 | 0 | 96816.5412 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 2800.8129 | 14053.9389 | 57947.4666 | 51883.7217 | 24679.2618 | 151365.202 |  | 1867.2086 | 8030.8222 | 40563.2266 | 116738.3739 | 98717.0474 | 265916.6787 |  | 2800.8129 | 8030.8222 | 40563.2266 | 90796.513 | 98717.0474 | 240908.4221
|  |  | 341 | 341 |  | 109 | 110 | 90 | 32 | 0 |  | 97 | 110 | 98 | 36 | 0 |  | 20 | 0 | -1 | -12 | -7 |  | 85 | 83 | 101 | 62 | 10 |  | 28 | 0 | -1 | -14 | -13 |  | 80 | 52 | 103 | 66 | 40 | [22 empty] | 18466.693 | 86251.0309 | 259141.0707 | 217911.6312 | 0 | 581770.4258 |  | 21921.0289 | 86251.0309 | 232485.2361 | 181593.026 | 0 | 522250.3218 |  | 15833.9289 | 67699.8315 | 254505.2734 | 356441.1682 | 123396.3092 | 817876.5111 |  | 20501.9503 | 67699.8315 | 252187.3747 | 273427.2135 | 44422.6713 | 658239.0413 |  | 14900.3246 | 43286.1319 | 238743.5624 | 401580.0061 | 454098.4179 | 1152608.4429 |  | 20950.0804 | 43286.1319 | 236425.6638 | 308189.307 | 321817.5744 | 930668.7575
| EHV UG Cable (Gas) |  | 6.4128 | 6.0584 | C1 | 0 | 4.5123 | 0.72891 | 0 | 1.1715 | 6.4128 | 0 | 4.5123 | 0.98216 | 0 | 2.3941 | 7.8886 | 0 | 0 | -0.03329 | 0 | -0.32106 | -0.35435 | 0 | 2.4022 | 3.4025 | 0 | 1.1715 | 6.9762 | 0 | 0 | -0.03329 | 0 | -0.32106 | -0.35435 | 0 | 0.0013324 | 7.0872 | 0 | 1.5485 | 8.6371 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 22.4586 | 21.4054 | C2 | 0.097004 | 16.0222 | 2.797 | 1.9898 | 1.5526 | 22.4586 | 0.097004 | 16.0222 | 3.7687 | 2.9407 | 3.1729 | 26.0015 | 0 | 0 | -0.12774 | -0.5 | -0.42551 | -1.0533 | 0.097004 | 8.5295 | 13.056 | 6.2328 | 1.5526 | 29.4679 | 0 | 0 | -0.12774 | -0.5 | -0.42551 | -1.0533 | 0.097004 | 0.004731 | 27.1948 | 4.1778 | 2.0523 | 33.5266 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 37.0822 | 35.9898 | C3 | 0 | 31.4728 | 1.9481 | 0 | 3.6613 | 37.0822 | 0 | 31.4728 | 2.6249 | 0 | 7.4822 | 41.5799 | 0 | 0 | -0.08897 | 0 | -1.0034 | -1.0924 | 0 | 16.7547 | 9.0934 | 0 | 3.6613 | 29.5095 | 0 | 0 | -0.08897 | 0 | -1.0034 | -1.0924 | 0 | 0.0092933 | 18.941 | 0 | 4.8396 | 23.7899 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 65.9536 | 63.4536 |  | 0.097004 | 52.0074 | 5.474 | 1.9898 | 6.3855 |  | 0.097004 | 52.0074 | 7.3758 | 2.9407 | 13.0492 |  | 0 | 0 | -0.25 | -0.5 | -1.75 |  | 0.097004 | 27.6864 | 25.552 | 6.2328 | 6.3855 |  | 0 | 0 | -0.25 | -0.5 | -1.75 |  | 0.097004 | 0.015357 | 53.223 | 4.1778 | 8.4405 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 76.0126 | 70.4969 | C1 | 9.9431 | 39.0737 | 14.5585 | 1.188 | 11.2492 | 76.0126 | 9.9388 | 39.0737 | 15.2955 | 2.2227 | 17.0115 | 83.5423 | 0 | 0 | -0.32942 | -0.4625 | -2.5725 | -3.3644 | 6.9676 | 31.7613 | 18.3957 | 4.3897 | 12.4727 | 73.987 | 0 | 0 | -0.54006 | -0.75824 | -4.2174 | -5.5157 | 6.9676 | 21.5006 | 25.67 | 4.2208 | 16.4892 | 74.8482 |  |  | C1 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C1 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | C1 | 22.4315 | 96.4774 | 278.4582 | 623.2993 | 1185.9263 | C1 | 222.9432 | 3769.7333 | 4259.1647 | 1385.4153 | 20174.4041 | 29811.6606 |  | 223.0388 | 3769.7333 | 4053.9411 | 740.4654 | 13340.7556 | 22127.9343 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 3064.2429 | 5030.7142 | 2447.812 | 11740.9925 | 22440.055 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826 |  | 156.2934 | 2074.3195 | 6997.6362 | 2158.2394 | 14553.5165 | 25940.0049
|  |  | 136.6281 | 124.5747 | C2 | 5.0986 | 76.2932 | 29.9538 | 5.5582 | 19.7242 | 136.6281 | 5.0965 | 76.2932 | 31.4701 | 10.3995 | 29.8278 | 153.087 | 0 | 0 | -0.67777 | -2.1639 | -4.5105 | -7.3522 | 3.5729 | 62.0152 | 37.8487 | 20.5382 | 21.8695 | 145.8445 | 0 | 0 | -1.1112 | -3.5476 | -7.3947 | -12.0534 | 3.5729 | 41.9808 | 52.8153 | 19.7482 | 28.912 | 147.0291 |  |  | C2 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C2 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | C2 | 32.045 | 137.8248 | 397.7974 | 890.4276 | 1694.1804 | C2 | 163.3161 | 10515.0973 | 12518.7377 | 9259.9833 | 50533.6075 | 82990.7419 |  | 163.3862 | 10515.0973 | 11915.5351 | 4949.2 | 33416.4272 | 60959.6459 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 8547.2391 | 14786.5126 | 16360.9414 | 29409.2802 | 69218.4654 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254 |  | 114.4921 | 5785.9984 | 20567.7824 | 14425.466 | 36454.1963 | 77347.9352
|  |  | 182.0691 | 169.9895 | C3 | 5.2629 | 106.478 | 45.3634 | 3.9391 | 21.0257 | 182.0691 | 5.2606 | 106.478 | 47.6598 | 7.3702 | 31.7959 | 198.5645 | 0 | 0 | -1.0265 | -1.5336 | -4.8082 | -7.3682 | 3.6879 | 86.5511 | 57.3199 | 14.5555 | 23.3126 | 185.4269 | 0 | 0 | -1.6828 | -2.5142 | -7.8826 | -12.0796 | 3.6879 | 58.5902 | 79.986 | 13.9956 | 30.8197 | 187.0794 |  |  | C3 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C3 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | C3 | 48.0675 | 206.7373 | 596.6961 | 1335.6414 | 2541.2706 | C3 | 252.8657 | 22012.9658 | 28438.4362 | 9843.8816 | 80801.9857 | 141350.1351 |  | 252.9741 | 22012.9658 | 27068.1591 | 5261.2773 | 53432.0388 | 108027.4152 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 17893.3278 | 33590.0715 | 17392.5985 | 47024.7101 | 116077.9782 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677 |  | 177.2704 | 12112.7728 | 46723.2065 | 15335.0795 | 58289.3563 | 132637.6856
|  |  | 67.6959 | 63.2445 | C4 | 20.1271 | 33.8496 | 2.0485 | 0 | 11.6707 | 67.6959 | 20.1185 | 33.8496 | 2.1522 | 0 | 17.6488 | 73.7691 | 0 | 0 | -0.046353 | 0 | -2.6688 | -2.7152 | 14.104 | 27.5148 | 2.5885 | 0 | 12.94 | 57.1472 | 0 | 0 | -0.075992 | 0 | -4.3754 | -4.4514 | 14.104 | 18.626 | 3.612 | 0 | 17.107 | 53.4489 |  |  | C4 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C4 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | C4 | 80.1125 | 344.5621 | 994.4935 | 2226.069 | 4235.451 | C4 | 1611.7417 | 11663.2874 | 2140.3925 | 0 | 74750.6707 | 90166.0923 |  | 1612.4329 | 11663.2874 | 2037.2599 | 0 | 49430.4775 | 64743.4578 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 9480.5501 | 2528.1256 | 0 | 43502.9979 | 56641.578 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041 |  | 1129.9045 | 6417.7972 | 3516.5788 | 0 | 53924.0273 | 64988.3078
|  |  | 462.4057 | 428.3057 |  | 40.4318 | 255.6945 | 91.9242 | 10.6853 | 63.6698 |  | 40.4144 | 255.6945 | 96.5777 | 19.9923 | 96.284 |  | 0 | 0 | -2.08 | -4.16 | -14.56 |  | 28.3324 | 207.8423 | 116.1528 | 39.4833 | 70.5948 |  | 0 | 0 | -3.41 | -6.82 | -23.87 |  | 28.3324 | 140.6975 | 162.0833 | 37.9646 | 93.3278 | [22 empty] | 2250.8667 | 47961.0839 | 47356.7311 | 20489.2802 | 226260.668 | 344318.6299 |  | 2251.8321 | 47961.0839 | 45074.8952 | 10950.9427 | 149619.6993 | 255858.4532 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 38985.3599 | 55935.4239 | 36201.3519 | 131677.9806 | 264378.0767 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798 |  | 1577.9603 | 26390.8878 | 77805.204 | 31918.785 | 163221.0964 | 300913.9335
| EHV UG Cable (Non Pressurised) |  | 55.8648 | 60.7939 | C1 | 20.28 | 31.8691 | 0.49426 | 3.1782 | 0.043172 | 55.8648 | 15.4973 | 31.8691 | 0.52291 | 3.2075 | 0.050667 | 51.1475 | 5.0876 | 0 | -0.23393 | -1.0753 | 0 | 3.7783 | 19.8549 | 31.5642 | 1.0578 | 3.4079 | 0.043172 | 55.928 | 6.3115 | 0 | -0.26598 | -1.1081 | -0.0083129 | 4.9291 | 19.6892 | 26.0768 | 2.3638 | 2.9471 | 0.14836 | 51.2253 |  |  | C1 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C1 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | C1 | 38.0736 | 163.7538 | 472.6349 | 1057.9435 | 2012.9061 | C1 | 590.0392 | 5218.6824 | 247.147 | 3393.3298 | 101.9869 | 9551.1853 |  | 772.1344 | 5218.6824 | 233.6066 | 3362.3692 | 86.9003 | 9673.6929 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 949.65 | 5168.7648 | 389.3817 | 2467.7516 | 86.9003 | 9062.4484 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524 |  | 989.9409 | 4270.1698 | 991.5227 | 1945.5783 | 281.8949 | 8479.1065
|  |  | 65.5759 | 73.4791 | C2 | 31.9175 | 27.5701 | 0.87467 | 3.5588 | 1.6548 | 65.5759 | 24.3903 | 27.5701 | 0.92537 | 3.5916 | 1.942 | 58.4194 | 8.0071 | 0 | -0.41398 | -1.2041 | 0 | 6.389 | 31.2484 | 27.3064 | 1.8719 | 3.8161 | 1.6548 | 65.8975 | 9.9333 | 0 | -0.47069 | -1.2408 | -0.31863 | 7.9032 | 30.9877 | 22.5591 | 4.1831 | 3.3 | 5.6865 | 66.7165 |  |  | C2 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C2 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | C2 | 54.3909 | 233.934 | 675.1927 | 1511.3479 | 2875.5801 | C2 | 1326.6111 | 6449.5749 | 624.8015 | 5428.1624 | 5584.5139 | 19413.6637 |  | 1736.0237 | 6449.5749 | 590.5706 | 5378.6361 | 4758.4114 | 18913.2167 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 2135.1397 | 6387.8836 | 984.3788 | 3947.5552 | 4758.4114 | 18213.3687 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267 |  | 2225.7274 | 5277.3436 | 2506.6251 | 3112.2571 | 15435.7586 | 28557.7118
|  |  | 77.7419 | 91.3793 | C3 | 51.2718 | 20.023 | 0.37769 | 6.0695 | 0 | 77.7419 | 39.1802 | 20.023 | 0.39959 | 6.1254 | 0 | 65.7281 | 12.8624 | 0 | -0.17876 | -2.0536 | 0 | 10.6301 | 50.1969 | 19.8314 | 0.80831 | 6.5082 | 0 | 77.3448 | 15.9567 | 0 | -0.20325 | -2.1161 | 0 | 13.6373 | 49.7781 | 16.3837 | 1.8063 | 5.6281 | 0 | 73.5962 |  |  | C3 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C3 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | C3 | 81.5863 | 350.901 | 1012.7891 | 2267.0218 | 4313.3702 | C3 | 3196.5691 | 7026.074 | 404.6965 | 13886.3435 | 0 | 24513.6831 |  | 4183.0795 | 7026.074 | 382.5244 | 13759.6454 | 0 | 25351.3233 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 5144.7794 | 6958.8685 | 637.6019 | 10098.6492 | 0 | 22839.899 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393 |  | 5363.0573 | 5749.0621 | 1623.5914 | 7961.7868 | 0 | 20697.4976
|  |  | 209.0164 | 244.8468 | C4 | 150.0512 | 26.0249 | 1.3381 | 26.0295 | 5.5727 | 209.0164 | 114.6641 | 26.0249 | 1.4157 | 26.2691 | 6.5402 | 174.914 | 37.6429 | 0 | -0.63333 | -8.807 | 0 | 28.2026 | 146.9054 | 25.7759 | 2.8638 | 27.9108 | 5.5727 | 209.0287 | 46.6985 | 0 | -0.72009 | -9.0751 | -1.0731 | 35.8303 | 145.6797 | 21.2948 | 6.3997 | 24.1366 | 19.1504 | 216.6611 |  |  | C4 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C4 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | C4 | 135.9772 | 584.835 | 1687.9818 | 3778.3697 | 7188.9503 | C4 | 15591.7087 | 15220.2533 | 2389.6645 | 99254.5314 | 47017.1975 | 179473.3554 |  | 20403.55 | 15220.2533 | 2258.7424 | 98348.939 | 40062.0667 | 176293.5514 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 25094.3749 | 15074.6691 | 3764.9319 | 72181.4706 | 40062.0667 | 156177.5132 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899 |  | 26159.0557 | 12453.9225 | 9587.034 | 56907.9552 | 129956.8984 | 235064.8659
|  |  | 408.199 | 470.499 |  | 253.5206 | 105.487 | 3.0848 | 38.836 | 7.2707 |  | 193.732 | 105.487 | 3.2636 | 39.1936 | 8.5329 |  | 63.6 | 0 | -1.46 | -13.14 | 0 |  | 248.2056 | 104.478 | 6.6018 | 41.643 | 7.2707 |  | 78.9 | 0 | -1.66 | -13.54 | -1.4 |  | 246.1346 | 86.3144 | 14.753 | 36.0118 | 24.9852 | [22 empty] | 20704.9281 | 33914.5845 | 3666.3094 | 121962.3671 | 52703.6984 | 232951.8875 |  | 27094.7876 | 33914.5845 | 3465.444 | 120849.5897 | 44907.3784 | 230231.7843 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 33323.944 | 33590.186 | 5776.2942 | 88695.4267 | 44907.3784 | 206293.2294 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799 |  | 34737.7814 | 27750.498 | 14708.7732 | 69927.5773 | 145674.5519 | 292799.1818
| EHV OHL Support - Towers |  | 637 | 637 | C1 | 103 | 280 | 61 | 33 | 160 | 637 | 61 | 85 | 118 | 81 | 292 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 266 | 96 | 24 | 195 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 96 | 221 | 96 | 219 | 637 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 561 | 561 | C2 | 77 | 171 | 92 | 96 | 125 | 561 | 35 | 97 | 106 | 109 | 214 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 116 | 104 | 42 | 239 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 67 | 106 | 104 | 281 | 561 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18 | 18 | C3 | 4 | 5 | 1 | 7 | 1 | 18 | 3 | 2 | 2 | 7 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 3 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 3 | 8 | 18 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 212 | 75 | C4 | 10 | 27 | 1 | 2 | 172 | 212 | 10 | 27 | 1 | 2 | 172 | 212 | 0 | 2 | 0 | 0 | -139 | -137 | 5 | 6 | 27 | 0 | 174 | 212 | 0 | 2 | 0 | 0 | -139 | -137 | 2 | 3 | 6 | 27 | 174 | 212 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1428 | 1291 |  | 194 | 483 | 155 | 138 | 458 |  | 109 | 211 | 227 | 199 | 682 |  | 0 | 2 | 0 | 0 | -139 |  | 122 | 394 | 230 | 66 | 616 |  | 0 | 2 | 0 | 0 | -139 |  | 10 | 170 | 336 | 230 | 682 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Poles |  | 4038 | 3971 | C1 | 1046 | 1806 | 1095 | 69 | 22 | 4038 | 925 | 1817 | 1103 | 151 | 75 | 4071 | 117 | -30 | -93 | -43 | -10 | -59 | 936 | 1591 | 1154 | 219 | 163 | 4063 | 121 | -30 | -93 | -47 | -18 | -67 | 861 | 1220 | 1485 | 243 | 334 | 4143 |  |  | C1 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C1 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | C1 | 0.58127 | 2.5 | 7.2157 | 16.1517 | 30.7311 | C1 | 537.6765 | 4542.5678 | 7958.962 | 2438.9031 | 2304.8353 | 17782.9447 |  | 608.0104 | 4515.0674 | 7901.2361 | 1114.4657 | 676.085 | 14814.8646 |  | 544.0705 | 3977.5594 | 8326.9648 | 3537.2171 | 5009.1754 | 21394.9871 |  | 612.0793 | 3902.5582 | 7655.9009 | 2842.695 | 4701.864 | 19715.0975 |  | 500.4751 | 3050.0455 | 10715.375 | 3924.8573 | 10264.1999 | 28454.9528 |  | 570.809 | 2975.0444 | 10044.3111 | 3165.7285 | 9711.0394 | 26466.9324
|  |  | 4370 | 4445 | C2 | 1624 | 1865 | 758 | 111 | 12 | 4370 | 1433 | 1874 | 762 | 214 | 58 | 4341 | 191 | -25 | -56 | -49 | -2 | 59 | 1463 | 1655 | 804 | 312 | 141 | 4375 | 207 | -25 | -56 | -49 | -2 | 75 | 1357 | 1287 | 1033 | 349 | 298 | 4324 |  |  | C2 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C2 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | C2 | 0.83039 | 3.5715 | 10.3082 | 23.0738 | 43.9016 | C2 | 1189.9466 | 6692.957 | 7854.8492 | 4937.7981 | 2546.2942 | 23221.8452 |  | 1348.5508 | 6660.8137 | 7813.6164 | 2561.1944 | 526.8195 | 18910.9947 |  | 1214.8582 | 5910.8025 | 8287.7937 | 7199.0328 | 6190.1291 | 28802.6163 |  | 1373.4624 | 5821.5154 | 7710.5344 | 6068.4155 | 6102.3258 | 27076.2536 |  | 1126.8371 | 4596.4972 | 10648.3717 | 8052.7642 | 13082.6842 | 37507.1543 |  | 1298.7275 | 4507.2101 | 10071.1124 | 6922.1469 | 12994.8809 | 35794.0779
|  |  | 123 | 119 | C3 | 57 | 55 | 9 | 0 | 2 | 123 | 51 | 56 | 10 | 0 | 2 | 119 | 3 | -3 | -4 | 0 | 0 | -4 | 49 | 46 | 9 | 0 | 2 | 106 | 3 | -3 | -4 | 0 | 0 | -4 | 42 | 31 | 12 | 0 | 2 | 87 |  |  | C3 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C3 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | C3 | 1.2456 | 5.3572 | 15.4623 | 34.6107 | 65.8524 | C3 | 63.5247 | 300.0045 | 154.623 | 0 | 131.7049 | 649.8571 |  | 70.9982 | 294.6473 | 139.1607 | 0 | 131.7049 | 636.5111 |  | 61.0335 | 246.4322 | 139.1607 | 0 | 131.7049 | 578.3314 |  | 64.7703 | 230.3606 | 77.3115 | 0 | 131.7049 | 504.1473 |  | 52.3145 | 166.0739 | 185.5476 | 0 | 131.7049 | 535.6409 |  | 56.0512 | 150.0022 | 123.6984 | 0 | 131.7049 | 461.4567
|  |  | 1365 | 1339 | C4 | 451 | 525 | 357 | 28 | 4 | 1365 | 399 | 528 | 360 | 67 | 11 | 1365 | 48 | -9 | -32 | -21 | -4 | -18 | 402 | 461 | 376 | 96 | 17 | 1352 | 48 | -9 | -32 | -25 | -8 | -26 | 368 | 351 | 484 | 107 | 32 | 1342 |  |  | C4 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C4 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | C4 | 2.076 | 8.9287 | 25.7705 | 57.6846 | 109.7541 | C4 | 828.3124 | 4714.3561 | 9277.381 | 3864.8654 | 1207.2947 | 19892.2095 |  | 936.2629 | 4687.5699 | 9200.0695 | 1615.1676 | 439.0162 | 16878.0862 |  | 834.5403 | 4116.1328 | 9689.709 | 5537.7175 | 1865.8191 | 22043.9188 |  | 934.1869 | 4035.7745 | 8865.0529 | 4326.3418 | 1426.8028 | 19588.159 |  | 763.9573 | 3133.9753 | 12472.9233 | 6172.2477 | 3512.13 | 26055.2336 |  | 863.6039 | 3053.617 | 11648.2672 | 4730.1337 | 2634.0975 | 22929.7194
|  |  | 9896 | 9874 |  | 3178 | 4251 | 2219 | 208 | 40 |  | 2808 | 4275 | 2235 | 432 | 146 |  | 359 | -67 | -185 | -113 | -16 |  | 2850 | 3753 | 2343 | 627 | 323 |  | 379 | -67 | -185 | -121 | -28 |  | 2628 | 2889 | 3014 | 699 | 666 | [22 empty] | 2619.4602 | 16249.8853 | 25245.8153 | 11241.5666 | 6190.1291 | 61546.8565 |  | 2963.8223 | 16158.0983 | 25054.0827 | 5290.8276 | 1773.6256 | 51240.4565 |  | 2654.5026 | 14250.9269 | 26443.6282 | 16273.9674 | 13196.8284 | 72819.8535 |  | 2984.4989 | 13990.2088 | 24308.7998 | 13237.4523 | 12362.6975 | 66883.6573 |  | 2443.5839 | 10946.5919 | 34022.2176 | 18149.8692 | 26990.7189 | 92552.9816 |  | 2789.1916 | 10685.8737 | 31887.3892 | 14818.0092 | 25471.7227 | 85652.1864
| EHV OHL Fittings and Conductors (Tower Lines) |  | 591.3506 | 536.1351 | C1 | 2.2333 | 172.982 | 97.1676 | 158.0498 | 160.9179 | 591.3506 | 2.2333 | 90.3849 | 47.0231 | 230.8255 | 220.8837 | 591.3506 | 102.8067 | 0 | -1.7317 | -27.9955 | -128.2949 | -55.2155 | 1.9354 | 41.9414 | 191.087 | 41.7973 | 314.5894 | 591.3506 | 118.5467 | 0 | -1.7317 | -28.5894 | -143.441 | -55.2155 | 1.0705 | 4.1592 | 181.3945 | 85.7587 | 318.9677 | 591.3506 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.4348 | 6.4348 | C3 | 0 | 0.83798 | 0.69576 | 1.2627 | 3.6383 | 6.4348 | 0 | 0.29214 | 0.69576 | 1.2627 | 4.1841 | 6.4348 | 0.72651 | 0 | -0.32289 | 0 | -0.40362 | 0 | 0 | 0.29214 | 0.91871 | 0.32289 | 4.901 | 6.4348 | 0.98982 | 0 | -0.32289 | 0 | -0.66693 | 0 | 0 | 0 | 0.83798 | 0.69576 | 4.901 | 6.4348 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.5628 | 4.5628 | C4 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0.36325 | 0 | 0 | 0 | -0.36325 | 0 | 0 | 0.73612 | 0.59389 | 0.29022 | 2.9425 | 4.5628 | 0.65347 | 0 | 0 | 0 | -0.65347 | 0 | 0 | 0.29791 | 0.43821 | 0.59389 | 3.2328 | 4.5628 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 602.3481 | 547.1327 |  | 2.2333 | 174.5561 | 98.4572 | 161.171 | 165.9304 |  | 2.2333 | 91.4132 | 48.3128 | 233.9468 | 226.442 |  | 103.8964 | 0 | -2.0546 | -27.9955 | -129.0617 |  | 1.9354 | 42.9697 | 192.5996 | 42.4104 | 322.433 |  | 120.19 | 0 | -2.0546 | -28.5894 | -144.7614 |  | 1.0705 | 4.4571 | 182.6707 | 87.0484 | 327.1015 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 |  | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 |  | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 |  | 58388.3536 | 154265.5861 | 338207.8926 | 411561.4444 | 233370.7279 | 1195794.0047 |  | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 |  | 60055.0137 | 108113.3914 | 360827.0302 | 424853.6785 | 656184.9454 | 1610034.0592
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 32 | 32 | C1 | 30 | 0 | 2 | 0 | 0 | 32 | 30 | 0 | 2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 2 | 0 | 2 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 3 | 0 | 2 | 0 | 32 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23 | 23 | C2 | 23 | 0 | 0 | 0 | 0 | 23 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 8 | 23 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26 | 27 | C3 | 18 | 0 | 0 | 8 | 0 | 26 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 0 | 26 | 9 | 0 | 0 | 0 | -8 | 1 | 18 | 0 | 0 | 0 | 8 | 26 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 83 | 84 |  | 73 | 0 | 2 | 8 | 0 |  | 63 | 0 | 4 | 8 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 2 | 0 | 12 | 8 |  | 9 | 0 | 0 | 0 | -8 |  | 55 | 8 | 0 | 4 | 16 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Transformer |  | 30 | 30 | C1 | 18 | 9 | 3 | 0 | 0 | 30 | 16 | 9 | 3 | 1 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 1 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 4 | 3 | 2 | 30 |  |  | C1 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C1 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | C1 | 273.0427 | 1174.3506 | 3389.4731 | 7586.9787 | 14435.4359 | C1 | 4368.6833 | 10569.155 | 10168.4193 | 7586.9787 | 14435.4359 | 47128.6721 |  | 4914.7687 | 10569.155 | 10168.4193 | 0 | 0 | 25652.343 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441
|  |  | 34 | 34 | C2 | 12 | 10 | 8 | 4 | 0 | 34 | 12 | 10 | 8 | 4 | 0 | 34 | 2 | 0 | 0 | 0 | -2 | 0 | 10 | 11 | 8 | 2 | 3 | 34 | 2 | 0 | 0 | 0 | -2 | 0 | 8 | 11 | 8 | 3 | 4 | 34 |  |  | C2 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C2 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | C2 | 390.061 | 1677.6436 | 4842.1044 | 10838.541 | 20622.0512 | C2 | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 3900.6101 | 18454.0801 | 38736.8352 | 21677.082 | 61866.1537 | 144634.7612 |  | 4680.7321 | 18454.0801 | 38736.8352 | 21677.082 | 20622.0512 | 104170.7808 |  | 3120.4881 | 18454.0801 | 38736.8352 | 32515.6231 | 82488.2049 | 175315.2315 |  | 3900.6101 | 18454.0801 | 38736.8352 | 32515.6231 | 41244.1025 | 134851.251
|  |  | 13 | 13 | C3 | 7 | 4 | 2 | 0 | 0 | 13 | 5 | 4 | 2 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 |  |  | C3 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C3 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | C3 | 585.0915 | 2516.4655 | 7263.1566 | 16257.8115 | 30933.0768 | C3 | 2925.4576 | 10065.8619 | 14526.3132 | 32515.6231 | 0 | 60033.2558 |  | 4095.6406 | 10065.8619 | 14526.3132 | 0 | 0 | 28687.8157 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 |  |  | C4 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C4 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | C4 | 975.1525 | 4194.1091 | 12105.261 | 27096.3525 | 51555.1281 | C4 | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051
|  |  | 79 | 79 |  | 39 | 23 | 13 | 4 | 0 |  | 35 | 23 | 13 | 7 | 1 |  | 2 | 0 | 0 | 0 | -2 |  | 32 | 24 | 11 | 5 | 7 |  | 2 | 0 | 0 | 0 | -2 |  | 30 | 21 | 14 | 6 | 8 | [22 empty] | 13925.1781 | 37411.4534 | 63431.5677 | 83456.7658 | 14435.4359 | 212660.4009 |  | 15641.4465 | 37411.4534 | 63431.5677 | 43354.1641 | 0 | 159838.6317 |  | 12872.0133 | 39089.097 | 56652.6215 | 44438.0182 | 152603.1791 | 305654.9292 |  | 13652.1354 | 39089.097 | 56652.6215 | 44438.0182 | 111359.0766 | 265190.9488 |  | 12091.8913 | 35566.0454 | 66821.0408 | 55276.5592 | 173225.2303 | 342980.767 |  | 12872.0133 | 35566.0454 | 66821.0408 | 55276.5592 | 131981.1279 | 302516.7866
| 132kV UG Cable (Gas) |  | 0.0030333 | 0.0030333 | C1 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0.67969 | 0.67969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0011431 | 0.0011431 | C2 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0.25615 | 0.25615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.016356 | 0.016356 | C3 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 3.6651 | 3.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0054672 | 0.0054672 | C4 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 1.2251 | 1.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.026 | 0.026 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 5.826 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 6.9437 | 3.5895 | C1 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 0 | -0.048089 | -0.23887 | -1.264 | -1.5509 | 0 | 2.7908 | 0.70587 | 1.9907 | 1.6982 | 7.1857 | 0 | 0 | -0.12567 | -1.0489 | -2.1796 | -3.3542 | 0 | 0.64753 | 1.6511 | 1.1276 | 4.3905 | 7.8167 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23.6291 | 13.5056 | C2 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 0 | 0 | -0.29466 | -1.4717 | -1.6764 | -3.4428 | 1.3281 | 3.2115 | 4.3252 | 12.2653 | 2.2523 | 23.3825 | 0 | 0 | -0.77005 | -6.4626 | -2.8908 | -10.1235 | 1.3281 | 0.74514 | 10.1171 | 6.9474 | 5.823 | 24.9608 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26.675 | 20.5527 | C3 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 0 | -0.40725 | -0.53938 | -1.5597 | -2.5063 | 0 | 14.1616 | 5.9778 | 4.4951 | 2.0955 | 26.73 | 0 | 0 | -1.0643 | -2.3685 | -2.6895 | -6.1223 | 0 | 3.2858 | 13.9829 | 2.5462 | 5.4176 | 25.2324 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.97712 | 0.97712 | C4 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21505 | 0 | 0 | 0 | 0.21505 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 58.225 | 38.625 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 0 | 0 | -0.75 | -2.25 | -4.5 |  | 1.3281 | 21.0908 | 11.0088 | 18.7512 | 6.0461 |  | 0 | 0 | -1.96 | -9.88 | -7.76 |  | 1.3281 | 4.8935 | 25.7511 | 10.6212 | 15.6311 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  | 32.1946 | 51.7946 | C1 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 24.6703 | 1.6243 | 0 | 0 | 0 | 26.2946 | 7.5 | 0 | 0 | 0 | 0 | 7.5 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 19.6 | 0 | 0 | 0 | 0 | 19.6 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 |  |  | C1 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C1 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | C1 | 2149.4357 | 9244.6748 | 26682.4726 | 59725.9062 | 94592.4846 | C1 | 53027.1783 | 15016.3613 | 0 | 0 | 0 | 68043.5396 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 81829.6171 | 15016.3613 | 0 | 0 | 0 | 96845.9784 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 107837.7894 | 15016.3613 | 0 | 0 | 0 | 122854.1507
|  |  | 0.61927 | 0.61927 | C2 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 |  |  | C2 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C2 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | C2 | 3070.6225 | 13206.6783 | 38117.818 | 85322.7231 | 135132.1208 | C2 | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C3 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | C3 | 4605.9337 | 19810.0175 | 57176.727 | 127984.0847 | 202698.1813 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.0781 | 6.0781 | C4 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 |  |  | C4 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C4 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | C4 | 7676.5562 | 33016.6958 | 95294.5449 | 213306.8078 | 337830.3021 | C4 | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825
|  |  | 38.892 | 58.492 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 24.6703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 7.5 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 19.6 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 | [22 empty] | 53027.1783 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 283805.6892 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 81829.6171 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 312608.1279 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 107837.7894 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 338616.3003
| 132kV OHL Support - Tower |  | 572 | 572 | C1 | 145 | 227 | 58 | 28 | 114 | 572 | 52 | 139 | 94 | 35 | 252 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 237 | 56 | 46 | 145 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 111 | 180 | 56 | 191 | 572 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 363 | 363 | C2 | 184 | 73 | 9 | 41 | 56 | 363 | 17 | 67 | 23 | 48 | 208 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 88 | 56 | 7 | 97 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 171 | 28 | 56 | 104 | 363 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 122 | 122 | C3 | 28 | 66 | 0 | 23 | 5 | 122 | 4 | 8 | 13 | 26 | 71 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 2 | 0 | 28 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 64 | 2 | 28 | 122 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 112 | 112 | C4 | 97 | 7 | 0 | 0 | 8 | 112 | 1 | 2 | 4 | 22 | 83 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 7 | 1 | 0 | 8 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 6 | 1 | 8 | 112 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1169 | 1169 |  | 454 | 373 | 67 | 92 | 183 |  | 74 | 216 | 134 | 131 | 614 |  | 0 | 0 | 0 | 0 | 0 |  | 309 | 414 | 115 | 53 | 278 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 405 | 278 | 115 | 331 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 535.0969 | 535.0969 | C1 | 59.426 | 153.5999 | 184.0823 | 56.0422 | 81.9465 | 535.0969 | 58.4481 | 35.9218 | 99.5766 | 159.0191 | 182.1313 | 535.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9704 | 21.8938 | 243.6033 | 80.0159 | 133.6134 | 535.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9704 | 13.4634 | 234.4327 | 94.4155 | 136.8148 | 535.0969 |  | 234.4327 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 40.1377 | 40.1377 | C2 | 0.52193 | 3.2945 | 27.6214 | 2.1808 | 6.5189 | 40.1377 | 0.52193 | 0 | 26.7231 | 3.2693 | 9.6234 | 40.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52193 | 0 | 29.3017 | 1.6143 | 8.6998 | 40.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52193 | 0 | 5.3726 | 25.5434 | 8.6998 | 40.1377 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.9077 | 3.9077 | C3 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49864 | 2.6601 | 0.74894 | 3.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2856 | 1.622 | 3.9077 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.7653 | 4.7653 | C4 | 0 | 0 | 2.8134 | 1.4503 | 0.50155 | 4.7653 | 0 | 0 | 2.1517 | 1.4503 | 1.1632 | 4.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71013 | 3.5536 | 0.50155 | 4.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71013 | 2.1032 | 1.9519 | 4.7653 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 583.9075 | 583.9075 |  | 59.9479 | 156.8945 | 216.8026 | 61.2954 | 88.967 |  | 58.97 | 35.9218 | 130.737 | 165.3608 | 192.9179 |  | 0 | 0 | 0 | 0 | 0 |  | 56.4923 | 21.8938 | 274.1138 | 87.8439 | 143.5637 |  | 0 | 0 | 0 | 0 | 0 |  | 56.4923 | 13.4634 | 240.5154 | 124.3478 | 149.0886 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 |  | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 |  | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 |  | 95481.7525 | 261754.3515 | 56690.7394 | 51567.2319 | 112305.0015 | 577799.0767 |  | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 |  | 120709.8028 | 258231.2998 | 66859.1586 | 62405.7729 | 132927.0527 | 641133.0869
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 241438.9569 | 239331.4414 |  | 79461.5571 | 63119.1043 | 62690.8796 | 28331.1633 | 7836.2525 |  | 72340.8732 | 62950.9887 | 64146.4037 | 31275.6199 | 11650.0551 |  | 8802.9964 | -362 | -1960.5946 | -3030.0455 | -4604.8717 |  | 69731.9612 | 33024.191 | 68678.0298 | 56487.4481 | 13538.3268 |  | 21946.69 | -681 | -4157.3346 | -7123.3294 | -12092.5414 |  | 60791.0253 | 29640.0713 | 61151.9975 | 58228.2551 | 31648.6077 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 |  | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 |  | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 |  | 332388.0047 | 875112.2182 | 1058770.0861 | 1133137.9589 | 1070920.1436 | 4470328.4114 |  | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 |  | 352905.703 | 792158.1242 | 1038763.6844 | 1089513.2188 | 1930348.4542 | 5203689.1846
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 | LV Network | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 3373.8914 | 3733.325 | 51126.2 | 162494.9315 | 37981.0765 | 258709.4245 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 | LV Network | 3790.4333 | 2726.7475 | 39124.7961 | 152251.1415 | 90857.1695 | 288750.2878
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 | HV Network | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 175144.0071 | 455358.9556 | 612745.254 | 507514.351 | 687263.3378 | 2438025.9055 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 | HV Network | 168350.4533 | 423086.6854 | 571952.6995 | 450002.6259 | 1050379.2866 | 2663771.7507
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 | EHV Network | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 | EHV Network | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 | EHV Network | 58388.3536 | 154265.5861 | 338207.8926 | 411561.4444 | 233370.7279 | 1195794.0047 | EHV Network | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 | EHV Network | 60055.0137 | 108113.3914 | 360827.0302 | 424853.6785 | 656184.9454 | 1610034.0592
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 | 132kV Network | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 | 132kV Network | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 | 132kV Network | 95481.7525 | 261754.3515 | 56690.7394 | 51567.2319 | 112305.0015 | 577799.0767 | 132kV Network | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 | 132kV Network | 120709.8028 | 258231.2998 | 66859.1586 | 62405.7729 | 132927.0527 | 641133.0869
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 | Total | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 | Total | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 | Total | 332388.0047 | 875112.2182 | 1058770.0861 | 1133137.9589 | 1070920.1436 | 4470328.4114 | Total | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 | Total | 352905.703 | 792158.1242 | 1038763.6844 | 1089513.2188 | 1930348.4542 | 5203689.1846
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## NPgN - Refurb
HI4: Secondary deliverables RIIO-ED1 - refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
NPGN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 32035 | 32035 | C1 | 9664 | 7276 | 12171 | 1565 | 1359 | 32035 | 8728 | 7327 | 12342 | 1906 | 1617 | 31920 | 0 | 0 | 0 | 0 | 0 | 0 | 8443 | 1599 | 8642 | 10620 | 2211 | 31515 | 0 | 0 | 0 | 0 | 0 | 0 | 7452 | 1226 | 6986 | 10535 | 5206 | 31405 |  |  | C1 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C1 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | C1 | 0.12877 | 0.55385 | 1.5985 | 3.5782 | 6.808 | C1 | 1123.9253 | 4058.0377 | 19729.2174 | 6819.9924 | 11008.5989 | 42739.7717 |  | 1244.4562 | 4029.7915 | 19455.8666 | 5599.8363 | 9252.1249 | 39582.0755 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723
|  |  | 23767 | 23767 | C2 | 6593 | 5704 | 9745 | 886 | 839 | 23767 | 5948 | 5742 | 9876 | 1268 | 1127 | 23961 | 0 | 0 | 0 | 0 | 0 | 0 | 5770 | 1274 | 6931 | 7777 | 1467 | 23219 | 0 | 0 | 0 | 0 | 0 | 0 | 5104 | 992 | 5617 | 7720 | 3656 | 23089 |  |  | C2 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C2 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | C2 | 0.18396 | 0.79121 | 2.2836 | 5.1117 | 9.7258 | C2 | 1094.1973 | 4543.1286 | 22553.1578 | 6481.5997 | 10960.9426 | 45633.026 |  | 1212.8518 | 4513.0626 | 22254.0019 | 4528.9411 | 8159.9209 | 40668.7784 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007
|  |  | 6362 | 6362 | C3 | 761 | 1889 | 2641 | 666 | 405 | 6362 | 689 | 1903 | 2679 | 666 | 405 | 6342 | 0 | 0 | 0 | 0 | 0 | 0 | 662 | 410 | 1873 | 3143 | 598 | 6686 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 312 | 1512 | 3118 | 1282 | 6806 |  |  | C3 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C3 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | C3 | 0.27594 | 1.1868 | 3.4254 | 7.6675 | 14.5887 | C3 | 190.1232 | 2258.5093 | 9176.7785 | 5106.56 | 5908.4052 | 22640.3763 |  | 209.991 | 2241.8939 | 9046.6114 | 5106.56 | 5908.4052 | 22513.4615 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071
|  |  | 9964 | 9964 | C4 | 1217 | 3352 | 4087 | 861 | 447 | 9964 | 1100 | 3376 | 4145 | 989 | 545 | 10155 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 733 | 2900 | 5277 | 737 | 10708 | 0 | 0 | 0 | 0 | 0 | 0 | 934 | 560 | 2341 | 5234 | 1759 | 10828 |  |  | C4 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C4 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | C4 | 0.4599 | 1.978 | 5.7091 | 12.7792 | 24.3144 | C4 | 505.8915 | 6677.8136 | 23664.1451 | 12638.6083 | 13251.3614 | 56737.8199 |  | 559.6999 | 6630.341 | 23333.0184 | 11002.8733 | 10868.5478 | 52394.4804 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003
|  |  | 72128 | 72128 |  | 18235 | 18221 | 28644 | 3978 | 3050 |  | 16465 | 18348 | 29042 | 4829 | 3694 |  | 0 | 0 | 0 | 0 | 0 |  | 15936 | 4016 | 20346 | 26817 | 5013 |  | 0 | 0 | 0 | 0 | 0 |  | 14072 | 3090 | 16456 | 26607 | 11903 | [22 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1598 | 1598 | C1 | 200 | 510 | 480 | 286 | 122 | 1598 | 168 | 514 | 493 | 307 | 134 | 1616 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 430 | 357 | 375 | 286 | 1616 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 299 | 379 | 303 | 490 | 1616 |  |  | C1 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C1 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | C1 | 7.6091 | 32.7266 | 94.4572 | 211.4325 | 402.2841 | C1 | 1278.3294 | 16821.4644 | 46567.4046 | 64909.7843 | 53906.0643 | 183483.0471 |  | 1521.8208 | 16690.5581 | 45339.4609 | 60469.7014 | 49078.6555 | 173100.1966 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096
|  |  | 565 | 565 | C2 | 93 | 126 | 180 | 125 | 41 | 565 | 81 | 126 | 181 | 135 | 42 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 82 | 150 | 160 | 93 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 81 | 104 | 134 | 179 | 565 |  |  | C2 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C2 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | C2 | 10.8701 | 46.7523 | 134.9389 | 302.0465 | 574.6915 | C2 | 880.482 | 5890.7852 | 24423.9358 | 40776.2721 | 24137.0437 | 96108.5189 |  | 1010.9238 | 5890.7852 | 24288.9969 | 37755.8075 | 23562.3522 | 92508.8656 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831
|  |  | 111 | 111 | C3 | 4 | 64 | 41 | 2 | 0 | 111 | 4 | 64 | 41 | 2 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 58 | 39 | 10 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 32 | 20 | 4 | 111 |  |  | C3 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C3 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | C3 | 16.3052 | 70.1284 | 202.4083 | 453.0697 | 862.0373 | C3 | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473
|  |  | 267 | 267 | C4 | 47 | 50 | 66 | 74 | 30 | 267 | 36 | 50 | 70 | 80 | 34 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 42 | 28 | 97 | 67 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 36 | 23 | 38 | 138 | 270 |  |  | C4 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C4 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | C4 | 27.1754 | 116.8807 | 337.3472 | 755.1162 | 1436.7288 | C4 | 978.3133 | 5844.0329 | 23614.3026 | 60409.2921 | 48848.7789 | 139694.7198 |  | 1277.2424 | 5844.0329 | 22264.9138 | 55878.5952 | 43101.8638 | 128366.6481 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139
|  |  | 2541 | 2541 |  | 344 | 750 | 767 | 487 | 193 |  | 289 | 754 | 785 | 524 | 210 |  | 0 | 0 | 0 | 0 | 0 |  | 288 | 612 | 574 | 642 | 446 |  | 0 | 0 | 0 | 0 | 0 |  | 248 | 470 | 538 | 495 | 811 | [22 empty] | 3202.3457 | 33044.4999 | 102904.3836 | 167001.4879 | 126891.8869 | 433044.604 |  | 3875.2078 | 32913.5935 | 100192.1123 | 155010.2435 | 115742.8715 | 407734.0286 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404
| HV Switchgear (GM) - Distribution |  | 5352 | 5352 | C1 | 3986 | 1248 | 108 | 9 | 1 | 5352 | 3792 | 1272 | 172 | 49 | 123 | 5408 | 0 | 0 | 0 | 0 | 0 | 0 | 3745 | 1052 | 480 | 48 | 27 | 5352 | 0 | 0 | 0 | 0 | 0 | 0 | 3399 | 1205 | 588 | 96 | 64 | 5352 |  |  | C1 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C1 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | C1 | 10.5841 | 45.5219 | 131.3876 | 294.0973 | 559.567 | C1 | 40134.7977 | 57903.7962 | 22598.6661 | 14410.7676 | 68826.7371 | 203874.7647 |  | 42188.1075 | 56811.2717 | 14189.8601 | 2646.8757 | 559.567 | 116395.682 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214
|  |  | 6308 | 6308 | C2 | 3108 | 2682 | 458 | 22 | 38 | 6308 | 2935 | 2728 | 670 | 89 | 195 | 6617 | 0 | 0 | 0 | 0 | 0 | 0 | 2775 | 2151 | 1032 | 266 | 84 | 6308 | 0 | 0 | 0 | 0 | 0 | 0 | 2438 | 2053 | 1198 | 417 | 202 | 6308 |  |  | C2 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C2 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | C2 | 15.1201 | 65.0312 | 187.6966 | 420.139 | 799.3814 | C2 | 44377.4983 | 177405.1617 | 125756.6966 | 37392.3707 | 155879.3698 | 540811.0971 |  | 46993.2758 | 174413.7257 | 85965.0254 | 9243.0579 | 30376.4926 | 346991.5775 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801
|  |  | 2231 | 2231 | C3 | 924 | 1031 | 228 | 0 | 48 | 2231 | 880 | 1054 | 339 | 40 | 86 | 2399 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 765 | 488 | 111 | 78 | 2231 | 0 | 0 | 0 | 0 | 0 | 0 | 682 | 745 | 483 | 198 | 123 | 2231 |  |  | C3 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C3 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | C3 | 22.6802 | 97.5468 | 281.5448 | 630.2085 | 1199.0721 | C3 | 19958.5341 | 102814.3551 | 95443.7018 | 25208.3398 | 103120.1985 | 346545.1293 |  | 20956.4608 | 100570.7781 | 64192.2242 | 0 | 57555.4596 | 243274.9228 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562
|  |  | 895 | 895 | C4 | 304 | 445 | 105 | 23 | 18 | 895 | 290 | 456 | 166 | 54 | 50 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 358 | 194 | 55 | 55 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 292 | 226 | 90 | 88 | 895 |  |  | C4 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C4 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | C4 | 37.8003 | 162.578 | 469.2414 | 1050.3475 | 1998.4535 | C4 | 10962.0737 | 74135.5881 | 77894.0733 | 56718.7646 | 99922.6729 | 319633.1726 |  | 11491.2772 | 72347.2296 | 49270.3476 | 24157.9923 | 35972.1623 | 193239.009 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757
|  |  | 14786 | 14786 |  | 8322 | 5406 | 899 | 54 | 105 |  | 7897 | 5510 | 1347 | 232 | 454 |  | 0 | 0 | 0 | 0 | 0 |  | 7542 | 4326 | 2194 | 480 | 244 |  | 0 | 0 | 0 | 0 | 0 |  | 6718 | 4295 | 2495 | 801 | 477 | [22 empty] | 115432.9038 | 412258.9011 | 321693.1378 | 133730.2427 | 427748.9783 | 1410864.1637 |  | 121629.1215 | 404143.0052 | 213617.4573 | 36047.9259 | 124463.6814 | 899901.1913 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334
| HV Transformer (GM) |  | 3258 | 3258 | C1 | 2494 | 563 | 122 | 64 | 15 | 3258 | 2396 | 571 | 126 | 72 | 39 | 3204 | 0 | 0 | 0 | 0 | 0 | 0 | 2368 | 492 | 250 | 78 | 70 | 3258 | 0 | 0 | 0 | 0 | 0 | 0 | 2251 | 422 | 376 | 88 | 121 | 3258 |  |  | C1 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C1 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | C1 | 7.0107 | 30.1527 | 87.0284 | 194.8038 | 370.6454 | C1 | 16797.5544 | 17217.2001 | 10965.5746 | 14025.8769 | 14455.1688 | 73461.3748 |  | 17484.5996 | 16975.9783 | 10617.4612 | 12467.4461 | 5559.6803 | 63105.1655 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947
|  |  | 5365 | 5365 | C2 | 2652 | 1750 | 484 | 405 | 74 | 5365 | 2536 | 1753 | 478 | 446 | 166 | 5379 | 0 | 0 | 0 | 0 | 0 | 0 | 2335 | 1610 | 674 | 315 | 431 | 5365 | 0 | 0 | 0 | 0 | 0 | 0 | 2105 | 1538 | 788 | 263 | 671 | 5365 |  |  | C2 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C2 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | C2 | 10.0152 | 43.0753 | 124.3262 | 278.2912 | 529.4934 | C2 | 25398.6393 | 75511.0125 | 59427.9442 | 124117.8788 | 87895.8985 | 372351.3733 |  | 26560.4068 | 75381.7866 | 60173.9016 | 112707.9393 | 39182.509 | 314006.5432 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088
|  |  | 914 | 914 | C3 | 498 | 275 | 75 | 57 | 9 | 914 | 480 | 281 | 79 | 65 | 25 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 202 | 145 | 48 | 59 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 428 | 159 | 190 | 43 | 94 | 914 |  |  | C3 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C3 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | C3 | 15.0229 | 64.613 | 186.4894 | 417.4368 | 794.24 | C3 | 7210.9702 | 18156.2417 | 14732.6598 | 27133.3928 | 19856.0012 | 87089.2657 |  | 7481.3815 | 17768.564 | 13986.7023 | 23793.8983 | 7148.1604 | 70178.7066 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689
|  |  | 423 | 423 | C4 | 180 | 130 | 64 | 42 | 7 | 423 | 174 | 136 | 68 | 48 | 23 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 106 | 75 | 35 | 44 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 104 | 60 | 45 | 73 | 423 |  |  | C4 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C4 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | C4 | 25.0381 | 107.6883 | 310.8156 | 695.728 | 1323.7334 | C4 | 4356.6278 | 14645.6043 | 21135.4613 | 33394.945 | 30445.8685 | 103978.5068 |  | 4506.8563 | 13999.4747 | 19892.1989 | 29220.5768 | 9266.1339 | 76885.2406 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869
|  |  | 9960 | 9960 |  | 5824 | 2718 | 745 | 568 | 105 |  | 5586 | 2741 | 751 | 631 | 253 |  | 0 | 0 | 0 | 0 | 0 |  | 5326 | 2410 | 1144 | 476 | 604 |  | 0 | 0 | 0 | 0 | 0 |  | 4925 | 2223 | 1414 | 439 | 959 | [22 empty] | 53763.7917 | 125530.0586 | 106261.6399 | 198672.0934 | 152652.9369 | 636880.5206 |  | 56033.2442 | 124125.8036 | 104670.264 | 178189.8605 | 61156.4836 | 524175.6559 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 42673 | 42673 | C1 | 14496 | 9898 | 9947 | 7197 | 1135 | 42673 | 13237 | 9960 | 10135 | 7612 | 1702 | 42646 | 0 | 0 | 0 | 0 | 0 | 0 | 12621 | 5451 | 14288 | 8600 | 1822 | 42782 | 0 | 0 | 0 | 0 | 0 | 0 | 10834 | 5196 | 12471 | 9058 | 5121 | 42680 |  |  | C1 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C1 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | C1 | 0.053585 | 0.23047 | 0.66519 | 1.489 | 2.833 | C1 | 709.303 | 2295.4547 | 6741.6714 | 11333.8975 | 4821.7101 | 25902.0367 |  | 776.7663 | 2281.1658 | 6616.6162 | 10715.9827 | 3215.4177 | 23605.9487 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412
|  |  | 56579 | 56579 | C2 | 19086 | 13113 | 12487 | 10437 | 1456 | 56579 | 17419 | 13191 | 12717 | 11032 | 2157 | 56516 | 0 | 0 | 0 | 0 | 0 | 0 | 16628 | 7242 | 17935 | 12476 | 2327 | 56608 | 0 | 0 | 0 | 0 | 0 | 0 | 14288 | 6915 | 15666 | 13149 | 6479 | 56497 |  |  | C2 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C2 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | C2 | 0.07655 | 0.32924 | 0.95027 | 2.1271 | 4.0471 | C2 | 1333.4213 | 4342.9924 | 12084.5493 | 23465.873 | 8729.5859 | 49956.4219 |  | 1461.0299 | 4317.3118 | 11865.9878 | 22200.2643 | 5892.5717 | 45737.1655 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412
|  |  | 23551 | 23551 | C3 | 7796 | 5437 | 5297 | 4320 | 701 | 23551 | 7119 | 5471 | 5397 | 4570 | 1053 | 23610 | 0 | 0 | 0 | 0 | 0 | 0 | 6787 | 2993 | 7607 | 5162 | 1125 | 23674 | 0 | 0 | 0 | 0 | 0 | 0 | 5824 | 2852 | 6638 | 5437 | 3165 | 23916 |  |  | C3 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C3 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | C3 | 0.11482 | 0.49386 | 1.4254 | 3.1906 | 6.0706 | C3 | 817.4373 | 2701.9004 | 7692.8889 | 14581.0877 | 6392.388 | 32185.7022 |  | 895.1736 | 2685.1092 | 7550.3489 | 13783.4352 | 4255.5214 | 29169.5882 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699
|  |  | 3346 | 3346 | C4 | 705 | 1366 | 725 | 486 | 64 | 3346 | 645 | 1375 | 740 | 516 | 101 | 3377 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 749 | 1041 | 580 | 104 | 3085 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 713 | 906 | 610 | 306 | 3056 |  |  | C4 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C4 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | C4 | 0.19137 | 0.8231 | 2.3757 | 5.3177 | 10.1177 | C4 | 123.4366 | 1131.7593 | 1757.9945 | 2743.9246 | 1021.8917 | 6779.0067 |  | 134.9191 | 1124.3514 | 1722.3595 | 2584.3941 | 647.5353 | 6213.5594 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454
|  |  | 126149 | 126149 |  | 42083 | 29814 | 28456 | 22440 | 3356 |  | 38420 | 29997 | 28989 | 23730 | 5013 |  | 0 | 0 | 0 | 0 | 0 |  | 36647 | 16435 | 40871 | 26818 | 5378 |  | 0 | 0 | 0 | 0 | 0 |  | 31467 | 15676 | 35681 | 28254 | 15071 | [22 empty] | 2983.5982 | 10472.1068 | 28277.1041 | 52124.7828 | 20965.5757 | 114823.1676 |  | 3267.8889 | 10407.9381 | 27755.3123 | 49284.0763 | 14011.0461 | 104726.2617 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 |  | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 267 | 267 | C1 | 134 | 87 | 42 | 4 | 0 | 267 | 126 | 87 | 50 | 4 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 62 | 43 | 42 | 1 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 46 | 64 | 40 | 4 | 267 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 239 | 239 | C2 | 79 | 57 | 72 | 23 | 8 | 239 | 45 | 57 | 81 | 30 | 26 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 23 | 34 | 86 | 51 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 18 | 45 | 81 | 56 | 239 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 109 | 109 | C3 | 1 | 51 | 51 | 6 | 0 | 109 | 1 | 51 | 51 | 6 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | 46 | 23 | 3 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 49 | 6 | 109 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44 | 44 | C4 | 2 | 0 | 42 | 0 | 0 | 44 | 2 | 0 | 42 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 659 | 659 |  | 216 | 195 | 207 | 33 | 8 |  | 174 | 195 | 224 | 40 | 26 |  | 0 | 0 | 0 | 0 | 0 |  | 167 | 121 | 123 | 193 | 55 |  | 0 | 0 | 0 | 0 | 0 |  | 154 | 83 | 144 | 212 | 66 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV Transformer |  | 103 | 103 | C1 | 37 | 47 | 14 | 5 | 0 | 103 | 37 | 47 | 14 | 5 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 24 | 11 | 0 | 103 | 0 | 0 | 1 | 0 | -1 | 0 | 34 | 17 | 35 | 12 | 5 | 103 |  |  | C1 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C1 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | C1 | 130.7046 | 562.1576 | 1622.5291 | 3631.8605 | 6910.1933 | C1 | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 9556.6785 | 56788.5173 | 43582.3262 | 34550.9666 | 148922.445 |  | 4443.9565 | 9556.6785 | 58411.0463 | 43582.3262 | 27640.7733 | 143634.7808
|  |  | 194 | 194 | C2 | 53 | 54 | 65 | 22 | 0 | 194 | 46 | 54 | 70 | 24 | 0 | 194 | 0 | 1 | 1 | -2 | 0 | 0 | 39 | 40 | 65 | 43 | 7 | 194 | 0 | 2 | 4 | -5 | -1 | 0 | 34 | 29 | 61 | 42 | 28 | 194 |  |  | C2 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C2 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | C2 | 186.7209 | 803.0822 | 2317.8987 | 5188.3722 | 9871.7047 | C2 | 8589.1595 | 43366.4401 | 162252.9065 | 124520.9321 | 0 | 338729.4383 |  | 9896.2055 | 43366.4401 | 150663.4132 | 114144.1878 | 0 | 318070.2466 |  | 7282.1135 | 32123.289 | 150663.4132 | 223100.0034 | 69101.9332 | 482270.7522 |  | 7282.1135 | 32926.3712 | 152981.3119 | 212723.2591 | 69101.9332 | 475014.9888 |  | 6348.5092 | 23289.3845 | 141391.8185 | 217911.6312 | 276407.7327 | 665349.0761 |  | 6348.5092 | 24895.5489 | 150663.4132 | 191969.7704 | 266536.0279 | 640413.2696
|  |  | 16 | 16 | C3 | 9 | 2 | 2 | 3 | 0 | 16 | 8 | 2 | 3 | 3 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | 2 | 2 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | 0 | 3 | 3 | 16 |  |  | C3 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C3 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | C3 | 280.0813 | 1204.6233 | 3476.848 | 7782.5583 | 14807.5571 | C3 | 2240.6503 | 2409.2467 | 10430.544 | 23347.6748 | 0 | 38428.1157 |  | 2520.7316 | 2409.2467 | 6953.696 | 23347.6748 | 0 | 35231.349 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431
|  |  | 28 | 28 | C4 | 10 | 7 | 9 | 2 | 0 | 28 | 6 | 7 | 11 | 4 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7 | 10 | 6 | 1 | 28 | 0 | 0 | 0 | 1 | -1 | 0 | 4 | 4 | 7 | 9 | 4 | 28 |  |  | C4 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C4 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | C4 | 466.8021 | 2007.7056 | 5794.7467 | 12970.9304 | 24679.2618 | C4 | 2800.8129 | 14053.9389 | 63742.2133 | 51883.7217 | 0 | 132480.6868 |  | 4668.0215 | 14053.9389 | 52152.72 | 25941.8609 | 0 | 96816.5412 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 1867.2086 | 8030.8222 | 40563.2266 | 116738.3739 | 98717.0474 | 265916.6787 |  | 1867.2086 | 8030.8222 | 40563.2266 | 129709.3043 | 74037.7855 | 254208.3473
|  |  | 341 | 341 |  | 109 | 110 | 90 | 32 | 0 |  | 97 | 110 | 98 | 36 | 0 |  | 0 | 1 | 1 | -2 | 0 |  | 85 | 83 | 101 | 62 | 10 |  | 0 | 2 | 5 | -4 | -3 |  | 80 | 52 | 103 | 66 | 40 | [22 empty] | 18466.693 | 86251.0309 | 259141.0707 | 217911.6312 | 0 | 581770.4258 |  | 21921.0289 | 86251.0309 | 232485.2361 | 181593.026 | 0 | 522250.3218 |  | 15833.9289 | 67699.8315 | 254505.2734 | 356441.1682 | 123396.3092 | 817876.5111 |  | 15833.9289 | 68502.9137 | 256823.172 | 346064.4239 | 123396.3092 | 810620.7477 |  | 14900.3246 | 43286.1319 | 238743.5624 | 401580.0061 | 454098.4179 | 1152608.4429 |  | 14900.3246 | 44892.2963 | 249637.6862 | 388609.0757 | 412637.258 | 1110676.6408
| EHV UG Cable (Gas) |  | 6.4128 | 6.4128 | C1 | 0 | 4.5123 | 0.72891 | 0 | 1.1715 | 6.4128 | 0 | 4.5123 | 0.98216 | 0 | 2.3941 | 7.8886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4022 | 3.4025 | 0 | 1.1715 | 6.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013324 | 7.0872 | 0 | 1.5485 | 8.6371 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 22.4586 | 22.4586 | C2 | 0.097004 | 16.0222 | 2.797 | 1.9898 | 1.5526 | 22.4586 | 0.097004 | 16.0222 | 3.7687 | 2.9407 | 3.1729 | 26.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097004 | 8.5295 | 13.056 | 6.2328 | 1.5526 | 29.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097004 | 0.004731 | 27.1948 | 4.1778 | 2.0523 | 33.5266 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 37.0822 | 37.0822 | C3 | 0 | 31.4728 | 1.9481 | 0 | 3.6613 | 37.0822 | 0 | 31.4728 | 2.6249 | 0 | 7.4822 | 41.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7547 | 9.0934 | 0 | 3.6613 | 29.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092933 | 18.941 | 0 | 4.8396 | 23.7899 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 65.9536 | 65.9536 |  | 0.097004 | 52.0074 | 5.474 | 1.9898 | 6.3855 |  | 0.097004 | 52.0074 | 7.3758 | 2.9407 | 13.0492 |  | 0 | 0 | 0 | 0 | 0 |  | 0.097004 | 27.6864 | 25.552 | 6.2328 | 6.3855 |  | 0 | 0 | 0 | 0 | 0 |  | 0.097004 | 0.015357 | 53.223 | 4.1778 | 8.4405 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 76.0126 | 76.0126 | C1 | 9.9431 | 39.0737 | 14.5585 | 1.188 | 11.2492 | 76.0126 | 9.9388 | 39.0737 | 15.2955 | 2.2227 | 17.0115 | 83.5423 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9676 | 31.7613 | 18.3957 | 4.3897 | 12.4727 | 73.987 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9676 | 21.5006 | 25.67 | 4.2208 | 16.4892 | 74.8482 |  |  | C1 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C1 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | C1 | 22.4315 | 96.4774 | 278.4582 | 623.2993 | 1185.9263 | C1 | 222.9432 | 3769.7333 | 4259.1647 | 1385.4153 | 20174.4041 | 29811.6606 |  | 223.0388 | 3769.7333 | 4053.9411 | 740.4654 | 13340.7556 | 22127.9343 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826
|  |  | 136.6281 | 136.6281 | C2 | 5.0986 | 76.2932 | 29.9538 | 5.5582 | 19.7242 | 136.6281 | 5.0965 | 76.2932 | 31.4701 | 10.3995 | 29.8278 | 153.087 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5729 | 62.0152 | 37.8487 | 20.5382 | 21.8695 | 145.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5729 | 41.9808 | 52.8153 | 19.7482 | 28.912 | 147.0291 |  |  | C2 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C2 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | C2 | 32.045 | 137.8248 | 397.7974 | 890.4276 | 1694.1804 | C2 | 163.3161 | 10515.0973 | 12518.7377 | 9259.9833 | 50533.6075 | 82990.7419 |  | 163.3862 | 10515.0973 | 11915.5351 | 4949.2 | 33416.4272 | 60959.6459 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254
|  |  | 182.0691 | 182.0691 | C3 | 5.2629 | 106.478 | 45.3634 | 3.9391 | 21.0257 | 182.0691 | 5.2606 | 106.478 | 47.6598 | 7.3702 | 31.7959 | 198.5645 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6879 | 86.5511 | 57.3199 | 14.5555 | 23.3126 | 185.4269 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6879 | 58.5902 | 79.986 | 13.9956 | 30.8197 | 187.0794 |  |  | C3 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C3 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | C3 | 48.0675 | 206.7373 | 596.6961 | 1335.6414 | 2541.2706 | C3 | 252.8657 | 22012.9658 | 28438.4362 | 9843.8816 | 80801.9857 | 141350.1351 |  | 252.9741 | 22012.9658 | 27068.1591 | 5261.2773 | 53432.0388 | 108027.4152 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677
|  |  | 67.6959 | 67.6959 | C4 | 20.1271 | 33.8496 | 2.0485 | 0 | 11.6707 | 67.6959 | 20.1185 | 33.8496 | 2.1522 | 0 | 17.6488 | 73.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 14.104 | 27.5148 | 2.5885 | 0 | 12.94 | 57.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 14.104 | 18.626 | 3.612 | 0 | 17.107 | 53.4489 |  |  | C4 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C4 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | C4 | 80.1125 | 344.5621 | 994.4935 | 2226.069 | 4235.451 | C4 | 1611.7417 | 11663.2874 | 2140.3925 | 0 | 74750.6707 | 90166.0923 |  | 1612.4329 | 11663.2874 | 2037.2599 | 0 | 49430.4775 | 64743.4578 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041
|  |  | 462.4057 | 462.4057 |  | 40.4318 | 255.6945 | 91.9242 | 10.6853 | 63.6698 |  | 40.4144 | 255.6945 | 96.5777 | 19.9923 | 96.284 |  | 0 | 0 | 0 | 0 | 0 |  | 28.3324 | 207.8423 | 116.1528 | 39.4833 | 70.5948 |  | 0 | 0 | 0 | 0 | 0 |  | 28.3324 | 140.6975 | 162.0833 | 37.9646 | 93.3278 | [22 empty] | 2250.8667 | 47961.0839 | 47356.7311 | 20489.2802 | 226260.668 | 344318.6299 |  | 2251.8321 | 47961.0839 | 45074.8952 | 10950.9427 | 149619.6993 | 255858.4532 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798
| EHV UG Cable (Non Pressurised) |  | 55.8648 | 55.8648 | C1 | 20.28 | 31.8691 | 0.49426 | 3.1782 | 0.043172 | 55.8648 | 15.4973 | 31.8691 | 0.52291 | 3.2075 | 0.050667 | 51.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8549 | 31.5642 | 1.0578 | 3.4079 | 0.043172 | 55.928 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6892 | 26.0768 | 2.3638 | 2.9471 | 0.14836 | 51.2253 |  |  | C1 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C1 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | C1 | 38.0736 | 163.7538 | 472.6349 | 1057.9435 | 2012.9061 | C1 | 590.0392 | 5218.6824 | 247.147 | 3393.3298 | 101.9869 | 9551.1853 |  | 772.1344 | 5218.6824 | 233.6066 | 3362.3692 | 86.9003 | 9673.6929 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524
|  |  | 65.5759 | 65.5759 | C2 | 31.9175 | 27.5701 | 0.87467 | 3.5588 | 1.6548 | 65.5759 | 24.3903 | 27.5701 | 0.92537 | 3.5916 | 1.942 | 58.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 31.2484 | 27.3064 | 1.8719 | 3.8161 | 1.6548 | 65.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9877 | 22.5591 | 4.1831 | 3.3 | 5.6865 | 66.7165 |  |  | C2 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C2 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | C2 | 54.3909 | 233.934 | 675.1927 | 1511.3479 | 2875.5801 | C2 | 1326.6111 | 6449.5749 | 624.8015 | 5428.1624 | 5584.5139 | 19413.6637 |  | 1736.0237 | 6449.5749 | 590.5706 | 5378.6361 | 4758.4114 | 18913.2167 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267
|  |  | 77.7419 | 77.7419 | C3 | 51.2718 | 20.023 | 0.37769 | 6.0695 | 0 | 77.7419 | 39.1802 | 20.023 | 0.39959 | 6.1254 | 0 | 65.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1969 | 19.8314 | 0.80831 | 6.5082 | 0 | 77.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7781 | 16.3837 | 1.8063 | 5.6281 | 0 | 73.5962 |  |  | C3 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C3 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | C3 | 81.5863 | 350.901 | 1012.7891 | 2267.0218 | 4313.3702 | C3 | 3196.5691 | 7026.074 | 404.6965 | 13886.3435 | 0 | 24513.6831 |  | 4183.0795 | 7026.074 | 382.5244 | 13759.6454 | 0 | 25351.3233 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393
|  |  | 209.0164 | 209.0164 | C4 | 150.0512 | 26.0249 | 1.3381 | 26.0295 | 5.5727 | 209.0164 | 114.6641 | 26.0249 | 1.4157 | 26.2691 | 6.5402 | 174.914 | 0 | 0 | 0 | 0 | 0 | 0 | 146.9054 | 25.7759 | 2.8638 | 27.9108 | 5.5727 | 209.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 145.6797 | 21.2948 | 6.3997 | 24.1366 | 19.1504 | 216.6611 |  |  | C4 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C4 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | C4 | 135.9772 | 584.835 | 1687.9818 | 3778.3697 | 7188.9503 | C4 | 15591.7087 | 15220.2533 | 2389.6645 | 99254.5314 | 47017.1975 | 179473.3554 |  | 20403.55 | 15220.2533 | 2258.7424 | 98348.939 | 40062.0667 | 176293.5514 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899
|  |  | 408.199 | 408.199 |  | 253.5206 | 105.487 | 3.0848 | 38.836 | 7.2707 |  | 193.732 | 105.487 | 3.2636 | 39.1936 | 8.5329 |  | 0 | 0 | 0 | 0 | 0 |  | 248.2056 | 104.478 | 6.6018 | 41.643 | 7.2707 |  | 0 | 0 | 0 | 0 | 0 |  | 246.1346 | 86.3144 | 14.753 | 36.0118 | 24.9852 | [22 empty] | 20704.9281 | 33914.5845 | 3666.3094 | 121962.3671 | 52703.6984 | 232951.8875 |  | 27094.7876 | 33914.5845 | 3465.444 | 120849.5897 | 44907.3784 | 230231.7843 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799
| EHV OHL Support - Towers |  | 637 | 637 | C1 | 103 | 280 | 61 | 33 | 160 | 637 | 61 | 85 | 118 | 81 | 292 | 637 | 95 | 134 | -63 | -13 | -153 | 0 | 56 | 266 | 96 | 24 | 195 | 637 | 95 | 145 | -63 | -13 | -164 | 0 | 5 | 96 | 221 | 96 | 219 | 637 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 561 | 561 | C2 | 77 | 171 | 92 | 96 | 125 | 561 | 35 | 97 | 106 | 109 | 214 | 561 | 140 | 194 | -91 | -42 | -201 | 0 | 60 | 116 | 104 | 42 | 239 | 561 | 159 | 221 | -106 | -53 | -221 | 0 | 3 | 67 | 106 | 104 | 281 | 561 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18 | 18 | C3 | 4 | 5 | 1 | 7 | 1 | 18 | 3 | 2 | 2 | 7 | 4 | 18 | 2 | 4 | -3 | 0 | -3 | 0 | 1 | 6 | 3 | 0 | 8 | 18 | 2 | 5 | -3 | 0 | -4 | 0 | 0 | 4 | 3 | 3 | 8 | 18 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 212 | 212 | C4 | 10 | 27 | 1 | 2 | 172 | 212 | 10 | 27 | 1 | 2 | 172 | 212 | 7 | 30 | -4 | 0 | -33 | 0 | 5 | 6 | 27 | 0 | 174 | 212 | 25 | 31 | -6 | -17 | -33 | 0 | 2 | 3 | 6 | 27 | 174 | 212 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1428 | 1428 |  | 194 | 483 | 155 | 138 | 458 |  | 109 | 211 | 227 | 199 | 682 |  | 244 | 362 | -161 | -55 | -390 |  | 122 | 394 | 230 | 66 | 616 |  | 281 | 402 | -178 | -83 | -422 |  | 10 | 170 | 336 | 230 | 682 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Poles |  | 4038 | 4010 | C1 | 1046 | 1806 | 1095 | 69 | 22 | 4038 | 925 | 1817 | 1103 | 151 | 75 | 4071 | 0 | 136 | -78 | -25 | -53 | -20 | 936 | 1591 | 1154 | 219 | 163 | 4063 | 0 | 239 | -78 | -58 | -131 | -28 | 861 | 1220 | 1485 | 243 | 334 | 4143 |  |  | C1 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C1 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | C1 | 0.58127 | 2.5 | 7.2157 | 16.1517 | 30.7311 | C1 | 537.6765 | 4542.5678 | 7958.962 | 2438.9031 | 2304.8353 | 17782.9447 |  | 608.0104 | 4515.0674 | 7901.2361 | 1114.4657 | 676.085 | 14814.8646 |  | 544.0705 | 3977.5594 | 8326.9648 | 3537.2171 | 5009.1754 | 21394.9871 |  | 544.0705 | 4317.5644 | 7764.137 | 3133.4252 | 3380.4251 | 19139.6222 |  | 500.4751 | 3050.0455 | 10715.375 | 3924.8573 | 10264.1999 | 28454.9528 |  | 500.4751 | 3647.5544 | 10152.5472 | 2988.0601 | 6238.4209 | 23527.0577
|  |  | 4370 | 4398 | C2 | 1624 | 1865 | 758 | 111 | 12 | 4370 | 1433 | 1874 | 762 | 214 | 58 | 4341 | 0 | 146 | -48 | -29 | -43 | 26 | 1463 | 1655 | 804 | 312 | 141 | 4375 | 0 | 258 | -48 | -69 | -113 | 28 | 1357 | 1287 | 1033 | 349 | 298 | 4324 |  |  | C2 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C2 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | C2 | 0.83039 | 3.5715 | 10.3082 | 23.0738 | 43.9016 | C2 | 1189.9466 | 6692.957 | 7854.8492 | 4937.7981 | 2546.2942 | 23221.8452 |  | 1348.5508 | 6660.8137 | 7813.6164 | 2561.1944 | 526.8195 | 18910.9947 |  | 1214.8582 | 5910.8025 | 8287.7937 | 7199.0328 | 6190.1291 | 28802.6163 |  | 1214.8582 | 6432.2388 | 7793 | 6529.8919 | 4302.3592 | 26272.3482 |  | 1126.8371 | 4596.4972 | 10648.3717 | 8052.7642 | 13082.6842 | 37507.1543 |  | 1126.8371 | 5517.9395 | 10153.5781 | 6460.6704 | 8121.8006 | 31380.8256
|  |  | 123 | 127 | C3 | 57 | 55 | 9 | 0 | 2 | 123 | 51 | 56 | 10 | 0 | 2 | 119 | 0 | 4 | -2 | 0 | 0 | 2 | 49 | 46 | 9 | 0 | 2 | 106 | 0 | 6 | -2 | 0 | 0 | 4 | 42 | 31 | 12 | 0 | 2 | 87 |  |  | C3 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C3 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | C3 | 1.2456 | 5.3572 | 15.4623 | 34.6107 | 65.8524 | C3 | 63.5247 | 300.0045 | 154.623 | 0 | 131.7049 | 649.8571 |  | 70.9982 | 294.6473 | 139.1607 | 0 | 131.7049 | 636.5111 |  | 61.0335 | 246.4322 | 139.1607 | 0 | 131.7049 | 578.3314 |  | 61.0335 | 267.8611 | 108.2361 | 0 | 131.7049 | 568.8357 |  | 52.3145 | 166.0739 | 185.5476 | 0 | 131.7049 | 535.6409 |  | 52.3145 | 198.2172 | 154.623 | 0 | 131.7049 | 536.8596
|  |  | 1365 | 1361 | C4 | 451 | 525 | 357 | 28 | 4 | 1365 | 399 | 528 | 360 | 67 | 11 | 1365 | 0 | 39 | -27 | -12 | -8 | -8 | 402 | 461 | 376 | 96 | 17 | 1352 | 0 | 67 | -27 | -28 | -16 | -4 | 368 | 351 | 484 | 107 | 32 | 1342 |  |  | C4 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C4 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | C4 | 2.076 | 8.9287 | 25.7705 | 57.6846 | 109.7541 | C4 | 828.3124 | 4714.3561 | 9277.381 | 3864.8654 | 1207.2947 | 19892.2095 |  | 936.2629 | 4687.5699 | 9200.0695 | 1615.1676 | 439.0162 | 16878.0862 |  | 834.5403 | 4116.1328 | 9689.709 | 5537.7175 | 1865.8191 | 22043.9188 |  | 834.5403 | 4464.3523 | 8993.9054 | 4845.5028 | 987.7866 | 20126.0875 |  | 763.9573 | 3133.9753 | 12472.9233 | 6172.2477 | 3512.13 | 26055.2336 |  | 763.9573 | 3732.1985 | 11777.1197 | 4557.08 | 1756.065 | 22586.4206
|  |  | 9896 | 9896 |  | 3178 | 4251 | 2219 | 208 | 40 |  | 2808 | 4275 | 2235 | 432 | 146 |  | 0 | 325 | -155 | -66 | -104 |  | 2850 | 3753 | 2343 | 627 | 323 |  | 0 | 570 | -155 | -155 | -260 |  | 2628 | 2889 | 3014 | 699 | 666 | [22 empty] | 2619.4602 | 16249.8853 | 25245.8153 | 11241.5666 | 6190.1291 | 61546.8565 |  | 2963.8223 | 16158.0983 | 25054.0827 | 5290.8276 | 1773.6256 | 51240.4565 |  | 2654.5026 | 14250.9269 | 26443.6282 | 16273.9674 | 13196.8284 | 72819.8535 |  | 2654.5026 | 15482.0167 | 24659.2786 | 14508.8199 | 8802.2758 | 66106.8936 |  | 2443.5839 | 10946.5919 | 34022.2176 | 18149.8692 | 26990.7189 | 92552.9816 |  | 2443.5839 | 13095.9097 | 32237.868 | 14005.8106 | 16247.9913 | 78031.1636
| EHV OHL Fittings and Conductors (Tower Lines) |  | 591.3506 | 591.3506 | C1 | 2.2333 | 172.982 | 97.1676 | 158.0498 | 160.9179 | 591.3506 | 2.2333 | 90.3849 | 47.0231 | 230.8255 | 220.8837 | 591.3506 | 0 | 32.543 | 47.5248 | -13.5365 | -66.5312 | 0 | 1.9354 | 41.9414 | 191.087 | 41.7973 | 314.5894 | 591.3506 | 0 | 32.543 | 57.398 | -14.732 | -75.209 | 0 | 1.0705 | 4.1592 | 181.3945 | 85.7587 | 318.9677 | 591.3506 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.4348 | 6.4348 | C3 | 0 | 0.83798 | 0.69576 | 1.2627 | 3.6383 | 6.4348 | 0 | 0.29214 | 0.69576 | 1.2627 | 4.1841 | 6.4348 | 0 | 0 | 3.0117 | 0 | -3.0117 | 0 | 0 | 0.29214 | 0.91871 | 0.32289 | 4.901 | 6.4348 | 0 | 0 | 3.0117 | 0 | -3.0117 | 0 | 0 | 0 | 0.83798 | 0.69576 | 4.901 | 6.4348 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.5628 | 4.5628 | C4 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0 | 1.9374 | 0 | -1.9374 | 0 | 0 | 0.73612 | 0.59389 | 0.29022 | 2.9425 | 4.5628 | 0 | 0 | 1.9374 | 0 | -1.9374 | 0 | 0 | 0.29791 | 0.43821 | 0.59389 | 3.2328 | 4.5628 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 602.3481 | 602.3481 |  | 2.2333 | 174.5561 | 98.4572 | 161.171 | 165.9304 |  | 2.2333 | 91.4132 | 48.3128 | 233.9468 | 226.442 |  | 0 | 32.543 | 52.4739 | -13.5365 | -71.4803 |  | 1.9354 | 42.9697 | 192.5996 | 42.4104 | 322.433 |  | 0 | 32.543 | 62.3471 | -14.732 | -80.1581 |  | 1.0705 | 4.4571 | 182.6707 | 87.0484 | 327.1015 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 |  | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 |  | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 |  | 46593.1435 | 156560.4763 | 345854.2689 | 530622.3922 | 342998.9307 | 1422629.2117 |  | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 |  | 45227.2843 | 112129.5918 | 377926.4764 | 553584.4534 | 802520.858 | 1891388.6641
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 32 | 32 | C1 | 30 | 0 | 2 | 0 | 0 | 32 | 30 | 0 | 2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 2 | 0 | 2 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 3 | 0 | 2 | 0 | 32 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23 | 23 | C2 | 23 | 0 | 0 | 0 | 0 | 23 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 8 | 23 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26 | 26 | C3 | 18 | 0 | 0 | 8 | 0 | 26 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 8 | 26 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 83 | 83 |  | 73 | 0 | 2 | 8 | 0 |  | 63 | 0 | 4 | 8 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 2 | 0 | 12 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 55 | 8 | 0 | 4 | 16 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Transformer |  | 30 | 30 | C1 | 18 | 9 | 3 | 0 | 0 | 30 | 16 | 9 | 3 | 1 | 1 | 30 | 2 | -2 | 0 | 0 | 0 | 0 | 15 | 9 | 1 | 3 | 2 | 30 | 2 | -2 | 0 | 0 | 0 | 0 | 15 | 6 | 4 | 3 | 2 | 30 |  |  | C1 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C1 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | C1 | 273.0427 | 1174.3506 | 3389.4731 | 7586.9787 | 14435.4359 | C1 | 4368.6833 | 10569.155 | 10168.4193 | 7586.9787 | 14435.4359 | 47128.6721 |  | 4914.7687 | 10569.155 | 10168.4193 | 0 | 0 | 25652.343 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4641.726 | 8220.4539 | 3389.4731 | 22760.9361 | 28870.8717 | 67883.4609 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441 |  | 4641.726 | 4697.4022 | 13557.8923 | 22760.9361 | 28870.8717 | 74528.8284
|  |  | 34 | 34 | C2 | 12 | 10 | 8 | 4 | 0 | 34 | 12 | 10 | 8 | 4 | 0 | 34 | 0 | 2 | -2 | 0 | 0 | 0 | 10 | 11 | 8 | 2 | 3 | 34 | 0 | 2 | -2 | 1 | -1 | 0 | 8 | 11 | 8 | 3 | 4 | 34 |  |  | C2 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C2 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | C2 | 390.061 | 1677.6436 | 4842.1044 | 10838.541 | 20622.0512 | C2 | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 3900.6101 | 18454.0801 | 38736.8352 | 21677.082 | 61866.1537 | 144634.7612 |  | 3900.6101 | 21809.3674 | 29052.6264 | 21677.082 | 61866.1537 | 138305.8397 |  | 3120.4881 | 18454.0801 | 38736.8352 | 32515.6231 | 82488.2049 | 175315.2315 |  | 3120.4881 | 21809.3674 | 29052.6264 | 43354.1641 | 61866.1537 | 159202.7997
|  |  | 13 | 13 | C3 | 7 | 4 | 2 | 0 | 0 | 13 | 5 | 4 | 2 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 |  |  | C3 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C3 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | C3 | 585.0915 | 2516.4655 | 7263.1566 | 16257.8115 | 30933.0768 | C3 | 2925.4576 | 10065.8619 | 14526.3132 | 32515.6231 | 0 | 60033.2558 |  | 4095.6406 | 10065.8619 | 14526.3132 | 0 | 0 | 28687.8157 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 |  |  | C4 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C4 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | C4 | 975.1525 | 4194.1091 | 12105.261 | 27096.3525 | 51555.1281 | C4 | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051
|  |  | 79 | 79 |  | 39 | 23 | 13 | 4 | 0 |  | 35 | 23 | 13 | 7 | 1 |  | 2 | 0 | -2 | 0 | 0 |  | 32 | 24 | 11 | 5 | 7 |  | 2 | 0 | -2 | 1 | -1 |  | 30 | 21 | 14 | 6 | 8 | [22 empty] | 13925.1781 | 37411.4534 | 63431.5677 | 83456.7658 | 14435.4359 | 212660.4009 |  | 15641.4465 | 37411.4534 | 63431.5677 | 43354.1641 | 0 | 159838.6317 |  | 12872.0133 | 39089.097 | 56652.6215 | 44438.0182 | 152603.1791 | 305654.9292 |  | 13418.0988 | 40095.6832 | 46968.4127 | 44438.0182 | 152603.1791 | 297523.392 |  | 12091.8913 | 35566.0454 | 66821.0408 | 55276.5592 | 173225.2303 | 342980.767 |  | 12637.9767 | 36572.6316 | 57136.832 | 66115.1002 | 152603.1791 | 325065.7196
| 132kV UG Cable (Gas) |  | 0.0030333 | 0.0030333 | C1 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0.67969 | 0.67969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0011431 | 0.0011431 | C2 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0.25615 | 0.25615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.016356 | 0.016356 | C3 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 3.6651 | 3.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0054672 | 0.0054672 | C4 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 1.2251 | 1.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.026 | 0.026 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 5.826 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 6.9437 | 6.9437 | C1 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7908 | 0.70587 | 1.9907 | 1.6982 | 7.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64753 | 1.6511 | 1.1276 | 4.3905 | 7.8167 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23.6291 | 23.6291 | C2 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3281 | 3.2115 | 4.3252 | 12.2653 | 2.2523 | 23.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3281 | 0.74514 | 10.1171 | 6.9474 | 5.823 | 24.9608 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26.675 | 26.675 | C3 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1616 | 5.9778 | 4.4951 | 2.0955 | 26.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2858 | 13.9829 | 2.5462 | 5.4176 | 25.2324 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.97712 | 0.97712 | C4 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21505 | 0 | 0 | 0 | 0.21505 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 58.225 | 58.225 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 0 | 0 | 0 | 0 | 0 |  | 1.3281 | 21.0908 | 11.0088 | 18.7512 | 6.0461 |  | 0 | 0 | 0 | 0 | 0 |  | 1.3281 | 4.8935 | 25.7511 | 10.6212 | 15.6311 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  | 32.1946 | 32.1946 | C1 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 24.6703 | 1.6243 | 0 | 0 | 0 | 26.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 |  |  | C1 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C1 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | C1 | 2149.4357 | 9244.6748 | 26682.4726 | 59725.9062 | 94592.4846 | C1 | 53027.1783 | 15016.3613 | 0 | 0 | 0 | 68043.5396 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104
|  |  | 0.61927 | 0.61927 | C2 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 |  |  | C2 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C2 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | C2 | 3070.6225 | 13206.6783 | 38117.818 | 85322.7231 | 135132.1208 | C2 | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C3 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | C3 | 4605.9337 | 19810.0175 | 57176.727 | 127984.0847 | 202698.1813 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.0781 | 6.0781 | C4 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 |  |  | C4 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C4 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | C4 | 7676.5562 | 33016.6958 | 95294.5449 | 213306.8078 | 337830.3021 | C4 | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825
|  |  | 38.892 | 38.892 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 24.6703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 0 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 0 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 | [22 empty] | 53027.1783 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 283805.6892 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36
| 132kV OHL Support - Tower |  | 572 | 572 | C1 | 145 | 227 | 58 | 28 | 114 | 572 | 52 | 139 | 94 | 35 | 252 | 572 | 116 | 0 | 0 | 0 | -116 | 0 | 88 | 237 | 56 | 46 | 145 | 572 | 119 | 34 | 0 | -21 | -132 | 0 | 34 | 111 | 180 | 56 | 191 | 572 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 363 | 363 | C2 | 184 | 73 | 9 | 41 | 56 | 363 | 17 | 67 | 23 | 48 | 208 | 363 | 18 | 0 | 0 | 0 | -18 | 0 | 115 | 88 | 56 | 7 | 97 | 363 | 96 | 36 | 0 | -34 | -98 | 0 | 4 | 171 | 28 | 56 | 104 | 363 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 122 | 122 | C3 | 28 | 66 | 0 | 23 | 5 | 122 | 4 | 8 | 13 | 26 | 71 | 122 | 2 | 0 | 0 | 0 | -2 | 0 | 10 | 82 | 2 | 0 | 28 | 122 | 5 | 1 | 0 | 0 | -6 | 0 | 2 | 26 | 64 | 2 | 28 | 122 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 112 | 112 | C4 | 97 | 7 | 0 | 0 | 8 | 112 | 1 | 2 | 4 | 22 | 83 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 7 | 1 | 0 | 8 | 112 | 9 | 0 | 0 | -1 | -8 | 0 | 0 | 97 | 6 | 1 | 8 | 112 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1169 | 1169 |  | 454 | 373 | 67 | 92 | 183 |  | 74 | 216 | 134 | 131 | 614 |  | 136 | 0 | 0 | 0 | -136 |  | 309 | 414 | 115 | 53 | 278 |  | 229 | 71 | 0 | -56 | -244 |  | 40 | 405 | 278 | 115 | 331 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 535.0969 | 535.0969 | C1 | 59.426 | 153.5999 | 184.0823 | 56.0422 | 81.9465 | 535.0969 | 58.4481 | 35.9218 | 99.5766 | 159.0191 | 182.1313 | 535.0969 | 0 | 7.2837 | 70.9715 | -9.4694 | -68.7858 | 0 | 55.9704 | 21.8938 | 243.6033 | 80.0159 | 133.6134 | 535.0969 | 0 | 11.7094 | 73.1077 | -11.7764 | -73.0407 | 0 | 55.9704 | 13.4634 | 234.4327 | 94.4155 | 136.8148 | 535.0969 |  | 307.5404 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 40.1377 | 40.1377 | C2 | 0.52193 | 3.2945 | 27.6214 | 2.1808 | 6.5189 | 40.1377 | 0.52193 | 0 | 26.7231 | 3.2693 | 9.6234 | 40.1377 | 0 | 0 | 4.449 | -0.76252 | -3.6865 | 0 | 0.52193 | 0 | 29.3017 | 1.6143 | 8.6998 | 40.1377 | 0 | 0 | 28.5993 | -24.6916 | -3.9077 | 0 | 0.52193 | 0 | 5.3726 | 25.5434 | 8.6998 | 40.1377 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.9077 | 3.9077 | C3 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 0.74894 | -0.74894 | 0 | 0 | 0 | 0 | 0.49864 | 2.6601 | 0.74894 | 3.9077 | 0 | 0 | 1.5386 | -1.2476 | -0.29104 | 0 | 0 | 0 | 0 | 2.2856 | 1.622 | 3.9077 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.7653 | 4.7653 | C4 | 0 | 0 | 2.8134 | 1.4503 | 0.50155 | 4.7653 | 0 | 0 | 2.1517 | 1.4503 | 1.1632 | 4.7653 | 0 | 0 | 1.1642 | -1.1642 | 0 | 0 | 0 | 0 | 0.71013 | 3.5536 | 0.50155 | 4.7653 | 0 | 0 | 1.4503 | -1.1642 | -0.28619 | 0 | 0 | 0 | 0.71013 | 2.1032 | 1.9519 | 4.7653 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 583.9075 | 583.9075 |  | 59.9479 | 156.8945 | 216.8026 | 61.2954 | 88.967 |  | 58.97 | 35.9218 | 130.737 | 165.3608 | 192.9179 |  | 0 | 7.2837 | 77.3335 | -12.145 | -72.4722 |  | 56.4923 | 21.8938 | 274.1138 | 87.8439 | 143.5637 |  | 0 | 11.7094 | 104.6959 | -38.8797 | -77.5256 |  | 56.4923 | 13.4634 | 240.5154 | 124.3478 | 149.0886 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 |  | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 |  | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 |  | 79126.9479 | 262760.9376 | 47006.5306 | 51567.2319 | 153549.1039 | 594010.752 |  | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 |  | 78346.8259 | 259237.886 | 57174.9498 | 73244.314 | 153549.1039 | 621553.0796
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 241438.9569 | 241438.9569 |  | 79461.5571 | 63119.1043 | 62690.8796 | 28331.1633 | 7836.2525 |  | 72340.8732 | 62950.9887 | 64146.4037 | 31275.6199 | 11650.0551 |  | 382 | 727.8267 | -187.1926 | -148.6815 | -773.9526 |  | 69731.9612 | 33024.191 | 68678.0298 | 56487.4481 | 13538.3268 |  | 512 | 1089.2524 | -162.957 | -350.6117 | -1087.6837 |  | 60791.0253 | 29640.0713 | 61151.9975 | 58228.2551 | 31648.6077 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 |  | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 |  | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 |  | 293852.5653 | 885019.8546 | 1197741.2262 | 1416605.8704 | 1484693.5733 | 5277913.0897 |  | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 |  | 273956.0058 | 810301.1283 | 1305430.5982 | 1561456.1662 | 2745352.1592 | 6696496.0578
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 | LV Network | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 | HV Network | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 | EHV Network | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 | EHV Network | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 | EHV Network | 46593.1435 | 156560.4763 | 345854.2689 | 530622.3922 | 342998.9307 | 1422629.2117 | EHV Network | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 | EHV Network | 45227.2843 | 112129.5918 | 377926.4764 | 553584.4534 | 802520.858 | 1891388.6641
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 | 132kV Network | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 | 132kV Network | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 | 132kV Network | 79126.9479 | 262760.9376 | 47006.5306 | 51567.2319 | 153549.1039 | 594010.752 | 132kV Network | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 | 132kV Network | 78346.8259 | 259237.886 | 57174.9498 | 73244.314 | 153549.1039 | 621553.0796
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 | Total | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 | Total | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 | Total | 293852.5653 | 885019.8546 | 1197741.2262 | 1416605.8704 | 1484693.5733 | 5277913.0897 | Total | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 | Total | 273956.0058 | 810301.1283 | 1305430.5982 | 1561456.1662 | 2745352.1592 | 6696496.0578
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## NPgN - HVP
HI7: Secondary deliverables RIIO-ED1 - HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
NPGN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 32035 | 32035 | C1 | 9664 | 7276 | 12171 | 1565 | 1359 | 32035 | 8728 | 7327 | 12342 | 1906 | 1617 | 31920 | 0 | 0 | 0 | 0 | 0 | 0 | 8443 | 1599 | 8642 | 10620 | 2211 | 31515 | 0 | 0 | 0 | 0 | 0 | 0 | 7452 | 1226 | 6986 | 10535 | 5206 | 31405 |  |  | C1 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C1 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | 8575.4095 | C1 | 0.12877 | 0.55385 | 1.5985 | 3.5782 | 6.808 | C1 | 1123.9253 | 4058.0377 | 19729.2174 | 6819.9924 | 11008.5989 | 42739.7717 |  | 1244.4562 | 4029.7915 | 19455.8666 | 5599.8363 | 9252.1249 | 39582.0755 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 1087.2252 | 885.6015 | 13814.6084 | 38000.1674 | 15052.574 | 68840.1765 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723 |  | 959.6117 | 679.0165 | 11167.4212 | 37696.0229 | 35442.6505 | 85944.723
|  |  | 23767 | 23767 | C2 | 6593 | 5704 | 9745 | 886 | 839 | 23767 | 5948 | 5742 | 9876 | 1268 | 1127 | 23961 | 0 | 0 | 0 | 0 | 0 | 0 | 5770 | 1274 | 6931 | 7777 | 1467 | 23219 | 0 | 0 | 0 | 0 | 0 | 0 | 5104 | 992 | 5617 | 7720 | 3656 | 23089 |  |  | C2 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C2 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | 12250.5851 | C2 | 0.18396 | 0.79121 | 2.2836 | 5.1117 | 9.7258 | C2 | 1094.1973 | 4543.1286 | 22553.1578 | 6481.5997 | 10960.9426 | 45633.026 |  | 1212.8518 | 4513.0626 | 22254.0019 | 4528.9411 | 8159.9209 | 40668.7784 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 1061.4523 | 1008.0017 | 15827.8591 | 39753.4708 | 14267.7044 | 71918.4883 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007 |  | 938.9346 | 784.8805 | 12827.1656 | 39462.1055 | 35557.4146 | 89570.5007
|  |  | 6362 | 6362 | C3 | 761 | 1889 | 2641 | 666 | 405 | 6362 | 689 | 1903 | 2679 | 666 | 405 | 6342 | 0 | 0 | 0 | 0 | 0 | 0 | 662 | 410 | 1873 | 3143 | 598 | 6686 | 0 | 0 | 0 | 0 | 0 | 0 | 582 | 312 | 1512 | 3118 | 1282 | 6806 |  |  | C3 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C3 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | 18375.8776 | C3 | 0.27594 | 1.1868 | 3.4254 | 7.6675 | 14.5887 | C3 | 190.1232 | 2258.5093 | 9176.7785 | 5106.56 | 5908.4052 | 22640.3763 |  | 209.991 | 2241.8939 | 9046.6114 | 5106.56 | 5908.4052 | 22513.4615 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 182.6728 | 486.5942 | 6415.8664 | 24098.9762 | 8724.0156 | 39908.1252 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071 |  | 160.5975 | 370.2863 | 5179.2792 | 23907.2885 | 18702.6554 | 48320.1071
|  |  | 9964 | 9964 | C4 | 1217 | 3352 | 4087 | 861 | 447 | 9964 | 1100 | 3376 | 4145 | 989 | 545 | 10155 | 0 | 0 | 0 | 0 | 0 | 0 | 1061 | 733 | 2900 | 5277 | 737 | 10708 | 0 | 0 | 0 | 0 | 0 | 0 | 934 | 560 | 2341 | 5234 | 1759 | 10828 |  |  | C4 | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939 | C4 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | 30626.4626 | C4 | 0.4599 | 1.978 | 5.7091 | 12.7792 | 24.3144 | C4 | 505.8915 | 6677.8136 | 23664.1451 | 12638.6083 | 13251.3614 | 56737.8199 |  | 559.6999 | 6630.341 | 23333.0184 | 11002.8733 | 10868.5478 | 52394.4804 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 487.9553 | 1449.8926 | 16556.338 | 67435.7288 | 17919.731 | 103849.6457 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003 |  | 429.5479 | 1107.6942 | 13364.9611 | 66886.2241 | 42769.073 | 124557.5003
|  |  | 72128 | 72128 |  | 18235 | 18221 | 28644 | 3978 | 3050 |  | 16465 | 18348 | 29042 | 4829 | 3694 |  | 0 | 0 | 0 | 0 | 0 |  | 15936 | 4016 | 20346 | 26817 | 5013 |  | 0 | 0 | 0 | 0 | 0 |  | 14072 | 3090 | 16456 | 26607 | 11903 | [22 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 |  | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 |  | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1598 | 1598 | C1 | 200 | 510 | 480 | 286 | 122 | 1598 | 168 | 514 | 493 | 307 | 134 | 1616 | 0 | 0 | 0 | 0 | 0 | 0 | 168 | 430 | 357 | 375 | 286 | 1616 | 0 | 0 | 0 | 0 | 0 | 0 | 145 | 299 | 379 | 303 | 490 | 1616 |  |  | C1 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C1 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | 116980.9788 | C1 | 7.6091 | 32.7266 | 94.4572 | 211.4325 | 402.2841 | C1 | 1278.3294 | 16821.4644 | 46567.4046 | 64909.7843 | 53906.0643 | 183483.0471 |  | 1521.8208 | 16690.5581 | 45339.4609 | 60469.7014 | 49078.6555 | 173100.1966 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1278.3294 | 14072.4313 | 33721.224 | 79287.1958 | 115053.2417 | 243412.4223 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096 |  | 1103.32 | 9785.2488 | 35799.2827 | 64064.0542 | 197119.1903 | 307871.096
|  |  | 565 | 565 | C2 | 93 | 126 | 180 | 125 | 41 | 565 | 81 | 126 | 181 | 135 | 42 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 82 | 150 | 160 | 93 | 565 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 81 | 104 | 134 | 179 | 565 |  |  | C2 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C2 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | 167115.684 | C2 | 10.8701 | 46.7523 | 134.9389 | 302.0465 | 574.6915 | C2 | 880.482 | 5890.7852 | 24423.9358 | 40776.2721 | 24137.0437 | 96108.5189 |  | 1010.9238 | 5890.7852 | 24288.9969 | 37755.8075 | 23562.3522 | 92508.8656 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 869.6119 | 3833.6856 | 20240.8308 | 48327.4337 | 53446.3111 | 126717.873 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831 |  | 728.2999 | 3786.9333 | 14033.6427 | 40474.2257 | 102869.7815 | 161892.8831
|  |  | 111 | 111 | C3 | 4 | 64 | 41 | 2 | 0 | 111 | 4 | 64 | 41 | 2 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 58 | 39 | 10 | 0 | 111 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 54 | 32 | 20 | 4 | 111 |  |  | C3 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C3 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | 250673.526 | C3 | 16.3052 | 70.1284 | 202.4083 | 453.0697 | 862.0373 | C3 | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4488.2173 | 8298.7406 | 906.1394 | 0 | 13758.3182 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 65.2209 | 4067.4469 | 7893.924 | 4530.6969 | 0 | 16557.2887 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473 |  | 16.3052 | 3786.9333 | 6477.0658 | 9061.3938 | 3448.1491 | 22789.8473
|  |  | 267 | 267 | C4 | 47 | 50 | 66 | 74 | 30 | 267 | 36 | 50 | 70 | 80 | 34 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 36 | 42 | 28 | 97 | 67 | 270 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 36 | 23 | 38 | 138 | 270 |  |  | C4 | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389 | C4 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | 417789.21 | C4 | 27.1754 | 116.8807 | 337.3472 | 755.1162 | 1436.7288 | C4 | 978.3133 | 5844.0329 | 23614.3026 | 60409.2921 | 48848.7789 | 139694.7198 |  | 1277.2424 | 5844.0329 | 22264.9138 | 55878.5952 | 43101.8638 | 128366.6481 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 978.3133 | 4908.9877 | 9445.721 | 73246.2666 | 96260.8291 | 184840.1177 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139 |  | 951.138 | 4207.7037 | 7758.9851 | 28694.4137 | 198268.5733 | 239880.8139
|  |  | 2541 | 2541 |  | 344 | 750 | 767 | 487 | 193 |  | 289 | 754 | 785 | 524 | 210 |  | 0 | 0 | 0 | 0 | 0 |  | 288 | 612 | 574 | 642 | 446 |  | 0 | 0 | 0 | 0 | 0 |  | 248 | 470 | 538 | 495 | 811 | [22 empty] | 3202.3457 | 33044.4999 | 102904.3836 | 167001.4879 | 126891.8869 | 433044.604 |  | 3875.2078 | 32913.5935 | 100192.1123 | 155010.2435 | 115742.8715 | 407734.0286 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 3191.4755 | 26882.5515 | 71301.6998 | 205391.593 | 264760.3818 | 571527.7018 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404 |  | 2799.0632 | 21566.8192 | 64068.9763 | 142294.0875 | 501705.6942 | 732434.6404
| HV Switchgear (GM) - Distribution |  | 5352 | 5352 | C1 | 3986 | 1248 | 108 | 9 | 1 | 5352 | 3792 | 1272 | 172 | 49 | 123 | 5408 | 0 | 0 | 0 | 0 | 0 | 0 | 3745 | 1052 | 480 | 48 | 27 | 5352 | 0 | 0 | 0 | 0 | 0 | 0 | 3399 | 1205 | 588 | 96 | 64 | 5352 |  |  | C1 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C1 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | 60745.6552 | C1 | 10.5841 | 45.5219 | 131.3876 | 294.0973 | 559.567 | C1 | 40134.7977 | 57903.7962 | 22598.6661 | 14410.7676 | 68826.7371 | 203874.7647 |  | 42188.1075 | 56811.2717 | 14189.8601 | 2646.8757 | 559.567 | 116395.682 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 39637.3464 | 47888.9887 | 63066.0449 | 14116.6703 | 15108.3081 | 179817.3584 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214 |  | 35975.2578 | 54853.8321 | 77255.905 | 28233.3406 | 35812.286 | 232130.6214
|  |  | 6308 | 6308 | C2 | 3108 | 2682 | 458 | 22 | 38 | 6308 | 2935 | 2728 | 670 | 89 | 195 | 6617 | 0 | 0 | 0 | 0 | 0 | 0 | 2775 | 2151 | 1032 | 266 | 84 | 6308 | 0 | 0 | 0 | 0 | 0 | 0 | 2438 | 2053 | 1198 | 417 | 202 | 6308 |  |  | C2 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C2 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | 86779.5074 | C2 | 15.1201 | 65.0312 | 187.6966 | 420.139 | 799.3814 | C2 | 44377.4983 | 177405.1617 | 125756.6966 | 37392.3707 | 155879.3698 | 540811.0971 |  | 46993.2758 | 174413.7257 | 85965.0254 | 9243.0579 | 30376.4926 | 346991.5775 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 41958.282 | 139882.1492 | 193702.8521 | 111756.9731 | 67148.0362 | 554448.2926 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801 |  | 36862.8077 | 133509.0898 | 224860.4814 | 175197.9617 | 161475.0395 | 731905.3801
|  |  | 2231 | 2231 | C3 | 924 | 1031 | 228 | 0 | 48 | 2231 | 880 | 1054 | 339 | 40 | 86 | 2399 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 765 | 488 | 111 | 78 | 2231 | 0 | 0 | 0 | 0 | 0 | 0 | 682 | 745 | 483 | 198 | 123 | 2231 |  |  | C3 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C3 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | 130169.261 | C3 | 22.6802 | 97.5468 | 281.5448 | 630.2085 | 1199.0721 | C3 | 19958.5341 | 102814.3551 | 95443.7018 | 25208.3398 | 103120.1985 | 346545.1293 |  | 20956.4608 | 100570.7781 | 64192.2242 | 0 | 57555.4596 | 243274.9228 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 17894.6403 | 74623.3222 | 137393.8835 | 69953.143 | 93527.6219 | 393392.6108 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562 |  | 15467.864 | 72672.3857 | 135986.1592 | 124781.282 | 147485.8653 | 496393.5562
|  |  | 895 | 895 | C4 | 304 | 445 | 105 | 23 | 18 | 895 | 290 | 456 | 166 | 54 | 50 | 1016 | 0 | 0 | 0 | 0 | 0 | 0 | 233 | 358 | 194 | 55 | 55 | 895 | 0 | 0 | 0 | 0 | 0 | 0 | 199 | 292 | 226 | 90 | 88 | 895 |  |  | C4 | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116 | C4 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | 216948.7684 | C4 | 37.8003 | 162.578 | 469.2414 | 1050.3475 | 1998.4535 | C4 | 10962.0737 | 74135.5881 | 77894.0733 | 56718.7646 | 99922.6729 | 319633.1726 |  | 11491.2772 | 72347.2296 | 49270.3476 | 24157.9923 | 35972.1623 | 193239.009 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 8807.4592 | 58202.9398 | 91032.8326 | 57769.1121 | 109914.9402 | 325727.2839 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757 |  | 7522.2506 | 47472.7889 | 106048.5576 | 94531.2743 | 175863.9044 | 431438.7757
|  |  | 14786 | 14786 |  | 8322 | 5406 | 899 | 54 | 105 |  | 7897 | 5510 | 1347 | 232 | 454 |  | 0 | 0 | 0 | 0 | 0 |  | 7542 | 4326 | 2194 | 480 | 244 |  | 0 | 0 | 0 | 0 | 0 |  | 6718 | 4295 | 2495 | 801 | 477 | [22 empty] | 115432.9038 | 412258.9011 | 321693.1378 | 133730.2427 | 427748.9783 | 1410864.1637 |  | 121629.1215 | 404143.0052 | 213617.4573 | 36047.9259 | 124463.6814 | 899901.1913 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 108297.7279 | 320597.3999 | 485195.613 | 253595.8985 | 285698.9065 | 1453385.5457 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334 |  | 95828.18 | 308508.0965 | 544151.1032 | 422743.8586 | 520637.0951 | 1891868.3334
| HV Transformer (GM) |  | 3258 | 3258 | C1 | 2494 | 563 | 122 | 64 | 15 | 3258 | 2396 | 571 | 126 | 72 | 39 | 3204 | 0 | 0 | 0 | 0 | 0 | 0 | 2368 | 492 | 250 | 78 | 70 | 3258 | 0 | 0 | 0 | 0 | 0 | 0 | 2251 | 422 | 376 | 88 | 121 | 3258 |  |  | C1 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C1 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | 46738.6571 | C1 | 7.0107 | 30.1527 | 87.0284 | 194.8038 | 370.6454 | C1 | 16797.5544 | 17217.2001 | 10965.5746 | 14025.8769 | 14455.1688 | 73461.3748 |  | 17484.5996 | 16975.9783 | 10617.4612 | 12467.4461 | 5559.6803 | 63105.1655 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 16601.2557 | 14835.1356 | 21757.0925 | 15194.7 | 25945.1749 | 94333.3587 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947 |  | 15781.0079 | 12724.4456 | 32722.6672 | 17142.7384 | 44848.088 | 123218.947
|  |  | 5365 | 5365 | C2 | 2652 | 1750 | 484 | 405 | 74 | 5365 | 2536 | 1753 | 478 | 446 | 166 | 5379 | 0 | 0 | 0 | 0 | 0 | 0 | 2335 | 1610 | 674 | 315 | 431 | 5365 | 0 | 0 | 0 | 0 | 0 | 0 | 2105 | 1538 | 788 | 263 | 671 | 5365 |  |  | C2 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C2 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | 66769.5101 | C2 | 10.0152 | 43.0753 | 124.3262 | 278.2912 | 529.4934 | C2 | 25398.6393 | 75511.0125 | 59427.9442 | 124117.8788 | 87895.8985 | 372351.3733 |  | 26560.4068 | 75381.7866 | 60173.9016 | 112707.9393 | 39182.509 | 314006.5432 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 23385.5768 | 69351.2437 | 83795.8878 | 87661.7305 | 228211.64 | 492406.0789 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088 |  | 21082.0725 | 66249.8216 | 97969.0795 | 73190.5877 | 355290.0475 | 613781.6088
|  |  | 914 | 914 | C3 | 498 | 275 | 75 | 57 | 9 | 914 | 480 | 281 | 79 | 65 | 25 | 930 | 0 | 0 | 0 | 0 | 0 | 0 | 460 | 202 | 145 | 48 | 59 | 914 | 0 | 0 | 0 | 0 | 0 | 0 | 428 | 159 | 190 | 43 | 94 | 914 |  |  | C3 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C3 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | 100154.2651 | C3 | 15.0229 | 64.613 | 186.4894 | 417.4368 | 794.24 | C3 | 7210.9702 | 18156.2417 | 14732.6598 | 27133.3928 | 19856.0012 | 87089.2657 |  | 7481.3815 | 17768.564 | 13986.7023 | 23793.8983 | 7148.1604 | 70178.7066 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 6910.5131 | 13051.8179 | 27040.9579 | 20036.967 | 46860.1627 | 113900.4186 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689 |  | 6429.7817 | 10273.4606 | 35432.9793 | 17949.7829 | 74658.5644 | 144744.5689
|  |  | 423 | 423 | C4 | 180 | 130 | 64 | 42 | 7 | 423 | 174 | 136 | 68 | 48 | 23 | 449 | 0 | 0 | 0 | 0 | 0 | 0 | 163 | 106 | 75 | 35 | 44 | 423 | 0 | 0 | 0 | 0 | 0 | 0 | 141 | 104 | 60 | 45 | 73 | 423 |  |  | C4 | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302 | C4 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | 166923.7752 | C4 | 25.0381 | 107.6883 | 310.8156 | 695.728 | 1323.7334 | C4 | 4356.6278 | 14645.6043 | 21135.4613 | 33394.945 | 30445.8685 | 103978.5068 |  | 4506.8563 | 13999.4747 | 19892.1989 | 29220.5768 | 9266.1339 | 76885.2406 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 4081.2088 | 11414.9563 | 23311.1706 | 24350.4807 | 58244.2701 | 121402.0864 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869 |  | 3530.3708 | 11199.5797 | 18648.9365 | 31307.7609 | 96632.539 | 161319.1869
|  |  | 9960 | 9960 |  | 5824 | 2718 | 745 | 568 | 105 |  | 5586 | 2741 | 751 | 631 | 253 |  | 0 | 0 | 0 | 0 | 0 |  | 5326 | 2410 | 1144 | 476 | 604 |  | 0 | 0 | 0 | 0 | 0 |  | 4925 | 2223 | 1414 | 439 | 959 | [22 empty] | 53763.7917 | 125530.0586 | 106261.6399 | 198672.0934 | 152652.9369 | 636880.5206 |  | 56033.2442 | 124125.8036 | 104670.264 | 178189.8605 | 61156.4836 | 524175.6559 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 50978.5545 | 108653.1535 | 155905.1087 | 147243.8782 | 359261.2477 | 822041.9426 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116 |  | 46823.2329 | 100447.3076 | 184773.6624 | 139590.87 | 571429.2388 | 1043064.3116
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 42673 | 42673 | C1 | 14496 | 9898 | 9947 | 7197 | 1135 | 42673 | 13237 | 9960 | 10135 | 7612 | 1702 | 42646 | 0 | 0 | 0 | 0 | 0 | 0 | 12621 | 5451 | 14288 | 8600 | 1822 | 42782 | 0 | 0 | 0 | 0 | 0 | 0 | 10834 | 5196 | 12471 | 9058 | 5121 | 42680 |  |  | C1 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C1 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | 7410.1626 | C1 | 0.053585 | 0.23047 | 0.66519 | 1.489 | 2.833 | C1 | 709.303 | 2295.4547 | 6741.6714 | 11333.8975 | 4821.7101 | 25902.0367 |  | 776.7663 | 2281.1658 | 6616.6162 | 10715.9827 | 3215.4177 | 23605.9487 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 676.2947 | 1256.2775 | 9504.1935 | 12804.9814 | 5161.6661 | 29403.4132 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412 |  | 580.5385 | 1197.5083 | 8295.5485 | 13486.9212 | 14507.6248 | 38068.1412
|  |  | 56579 | 56579 | C2 | 19086 | 13113 | 12487 | 10437 | 1456 | 56579 | 17419 | 13191 | 12717 | 11032 | 2157 | 56516 | 0 | 0 | 0 | 0 | 0 | 0 | 16628 | 7242 | 17935 | 12476 | 2327 | 56608 | 0 | 0 | 0 | 0 | 0 | 0 | 14288 | 6915 | 15666 | 13149 | 6479 | 56497 |  |  | C2 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C2 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | 10585.9466 | C2 | 0.07655 | 0.32924 | 0.95027 | 2.1271 | 4.0471 | C2 | 1333.4213 | 4342.9924 | 12084.5493 | 23465.873 | 8729.5859 | 49956.4219 |  | 1461.0299 | 4317.3118 | 11865.9878 | 22200.2643 | 5892.5717 | 45737.1655 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1272.8704 | 2384.3493 | 17043.0441 | 26537.3669 | 9417.5922 | 56655.2228 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412 |  | 1093.7438 | 2276.6881 | 14886.8876 | 27968.8872 | 26221.1345 | 72447.3412
|  |  | 23551 | 23551 | C3 | 7796 | 5437 | 5297 | 4320 | 701 | 23551 | 7119 | 5471 | 5397 | 4570 | 1053 | 23610 | 0 | 0 | 0 | 0 | 0 | 0 | 6787 | 2993 | 7607 | 5162 | 1125 | 23674 | 0 | 0 | 0 | 0 | 0 | 0 | 5824 | 2852 | 6638 | 5437 | 3165 | 23916 |  |  | C3 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C3 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | 15878.9199 | C3 | 0.11482 | 0.49386 | 1.4254 | 3.1906 | 6.0706 | C3 | 817.4373 | 2701.9004 | 7692.8889 | 14581.0877 | 6392.388 | 32185.7022 |  | 895.1736 | 2685.1092 | 7550.3489 | 13783.4352 | 4255.5214 | 29169.5882 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 779.3155 | 1478.1188 | 10843.0251 | 16469.9288 | 6829.4744 | 36399.8624 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699 |  | 668.7392 | 1408.4847 | 9461.8115 | 17347.3465 | 19213.5879 | 48099.9699
|  |  | 3346 | 3346 | C4 | 705 | 1366 | 725 | 486 | 64 | 3346 | 645 | 1375 | 740 | 516 | 101 | 3377 | 0 | 0 | 0 | 0 | 0 | 0 | 611 | 749 | 1041 | 580 | 104 | 3085 | 0 | 0 | 0 | 0 | 0 | 0 | 521 | 713 | 906 | 610 | 306 | 3056 |  |  | C4 | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231 | C4 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | 26464.8664 | C4 | 0.19137 | 0.8231 | 2.3757 | 5.3177 | 10.1177 | C4 | 123.4366 | 1131.7593 | 1757.9945 | 2743.9246 | 1021.8917 | 6779.0067 |  | 134.9191 | 1124.3514 | 1722.3595 | 2584.3941 | 647.5353 | 6213.5594 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 116.9299 | 616.5001 | 2473.0707 | 3084.2563 | 1052.2449 | 7343.0019 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454 |  | 99.7061 | 586.8686 | 2152.3554 | 3243.7868 | 3096.0284 | 9178.7454
|  |  | 126149 | 126149 |  | 42083 | 29814 | 28456 | 22440 | 3356 |  | 38420 | 29997 | 28989 | 23730 | 5013 |  | 0 | 0 | 0 | 0 | 0 |  | 36647 | 16435 | 40871 | 26818 | 5378 |  | 0 | 0 | 0 | 0 | 0 |  | 31467 | 15676 | 35681 | 28254 | 15071 | [22 empty] | 2983.5982 | 10472.1068 | 28277.1041 | 52124.7828 | 20965.5757 | 114823.1676 |  | 3267.8889 | 10407.9381 | 27755.3123 | 49284.0763 | 14011.0461 | 104726.2617 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 2845.4104 | 5735.2457 | 39863.3332 | 58896.5334 | 22460.9777 | 129801.5004 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977 |  | 2442.7277 | 5469.5497 | 34796.603 | 62046.9417 | 63038.3755 | 167794.1977
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 |  | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 |  | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 267 | 267 | C1 | 134 | 87 | 42 | 4 | 0 | 267 | 126 | 87 | 50 | 4 | 0 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 119 | 62 | 43 | 42 | 1 | 267 | 0 | 0 | 0 | 0 | 0 | 0 | 113 | 46 | 64 | 40 | 4 | 267 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | 128048.4915 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 239 | 239 | C2 | 79 | 57 | 72 | 23 | 8 | 239 | 45 | 57 | 81 | 30 | 26 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 23 | 34 | 86 | 51 | 239 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 18 | 45 | 81 | 56 | 239 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | 182926.4165 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 109 | 109 | C3 | 1 | 51 | 51 | 6 | 0 | 109 | 1 | 51 | 51 | 6 | 0 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 36 | 46 | 23 | 3 | 109 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 35 | 49 | 6 | 109 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | 274389.6247 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44 | 44 | C4 | 2 | 0 | 42 | 0 | 0 | 44 | 2 | 0 | 42 | 0 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 42 | 0 | 44 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | 457316.0412 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 659 | 659 |  | 216 | 195 | 207 | 33 | 8 |  | 174 | 195 | 224 | 40 | 26 |  | 0 | 0 | 0 | 0 | 0 |  | 167 | 121 | 123 | 193 | 55 |  | 0 | 0 | 0 | 0 | 0 |  | 154 | 83 | 144 | 212 | 66 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV Transformer |  | 103 | 103 | C1 | 37 | 47 | 14 | 5 | 0 | 103 | 37 | 47 | 14 | 5 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 24 | 11 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 17 | 35 | 12 | 5 | 103 |  |  | C1 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C1 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | 99918.7612 | C1 | 130.7046 | 562.1576 | 1622.5291 | 3631.8605 | 6910.1933 | C1 | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4836.0703 | 26421.4052 | 22715.4069 | 18159.3026 | 0 | 72132.1849 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 19113.3569 | 38940.6976 | 39950.4657 | 0 | 102448.4767 |  | 4443.9565 | 9556.6785 | 56788.5173 | 43582.3262 | 34550.9666 | 148922.445 |  | 4443.9565 | 9556.6785 | 56788.5173 | 43582.3262 | 34550.9666 | 148922.445
|  |  | 194 | 194 | C2 | 53 | 54 | 65 | 22 | 0 | 194 | 46 | 54 | 70 | 24 | 0 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 40 | 65 | 43 | 7 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 29 | 61 | 42 | 28 | 194 |  |  | C2 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C2 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | 142741.0874 | C2 | 186.7209 | 803.0822 | 2317.8987 | 5188.3722 | 9871.7047 | C2 | 8589.1595 | 43366.4401 | 162252.9065 | 124520.9321 | 0 | 338729.4383 |  | 9896.2055 | 43366.4401 | 150663.4132 | 114144.1878 | 0 | 318070.2466 |  | 7282.1135 | 32123.289 | 150663.4132 | 223100.0034 | 69101.9332 | 482270.7522 |  | 7282.1135 | 32123.289 | 150663.4132 | 223100.0034 | 69101.9332 | 482270.7522 |  | 6348.5092 | 23289.3845 | 141391.8185 | 217911.6312 | 276407.7327 | 665349.0761 |  | 6348.5092 | 23289.3845 | 141391.8185 | 217911.6312 | 276407.7327 | 665349.0761
|  |  | 16 | 16 | C3 | 9 | 2 | 2 | 3 | 0 | 16 | 8 | 2 | 3 | 3 | 0 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | 2 | 2 | 2 | 16 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 2 | 0 | 3 | 3 | 16 |  |  | C3 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C3 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | 214111.631 | C3 | 280.0813 | 1204.6233 | 3476.848 | 7782.5583 | 14807.5571 | C3 | 2240.6503 | 2409.2467 | 10430.544 | 23347.6748 | 0 | 38428.1157 |  | 2520.7316 | 2409.2467 | 6953.696 | 23347.6748 | 0 | 35231.349 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 2240.6503 | 2409.2467 | 6953.696 | 15565.1165 | 29615.1142 | 56783.8237 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431 |  | 2240.6503 | 2409.2467 | 0 | 23347.6748 | 44422.6713 | 72420.2431
|  |  | 28 | 28 | C4 | 10 | 7 | 9 | 2 | 0 | 28 | 6 | 7 | 11 | 4 | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 7 | 10 | 6 | 1 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 7 | 9 | 4 | 28 |  |  | C4 | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158 | C4 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | 356852.7184 | C4 | 466.8021 | 2007.7056 | 5794.7467 | 12970.9304 | 24679.2618 | C4 | 2800.8129 | 14053.9389 | 63742.2133 | 51883.7217 | 0 | 132480.6868 |  | 4668.0215 | 14053.9389 | 52152.72 | 25941.8609 | 0 | 96816.5412 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 1867.2086 | 14053.9389 | 57947.4666 | 77825.5826 | 24679.2618 | 176373.4585 |  | 1867.2086 | 8030.8222 | 40563.2266 | 116738.3739 | 98717.0474 | 265916.6787 |  | 1867.2086 | 8030.8222 | 40563.2266 | 116738.3739 | 98717.0474 | 265916.6787
|  |  | 341 | 341 |  | 109 | 110 | 90 | 32 | 0 |  | 97 | 110 | 98 | 36 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 85 | 83 | 101 | 62 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 80 | 52 | 103 | 66 | 40 | [22 empty] | 18466.693 | 86251.0309 | 259141.0707 | 217911.6312 | 0 | 581770.4258 |  | 21921.0289 | 86251.0309 | 232485.2361 | 181593.026 | 0 | 522250.3218 |  | 15833.9289 | 67699.8315 | 254505.2734 | 356441.1682 | 123396.3092 | 817876.5111 |  | 15833.9289 | 67699.8315 | 254505.2734 | 356441.1682 | 123396.3092 | 817876.5111 |  | 14900.3246 | 43286.1319 | 238743.5624 | 401580.0061 | 454098.4179 | 1152608.4429 |  | 14900.3246 | 43286.1319 | 238743.5624 | 401580.0061 | 454098.4179 | 1152608.4429
| EHV UG Cable (Gas) |  | 6.4128 | 6.4128 | C1 | 0 | 4.5123 | 0.72891 | 0 | 1.1715 | 6.4128 | 0 | 4.5123 | 0.98216 | 0 | 2.3941 | 7.8886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.4022 | 3.4025 | 0 | 1.1715 | 6.9762 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0013324 | 7.0872 | 0 | 1.5485 | 8.6371 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | 97306.3911 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 22.4586 | 22.4586 | C2 | 0.097004 | 16.0222 | 2.797 | 1.9898 | 1.5526 | 22.4586 | 0.097004 | 16.0222 | 3.7687 | 2.9407 | 3.1729 | 26.0015 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097004 | 8.5295 | 13.056 | 6.2328 | 1.5526 | 29.4679 | 0 | 0 | 0 | 0 | 0 | 0 | 0.097004 | 0.004731 | 27.1948 | 4.1778 | 2.0523 | 33.5266 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | 139009.1302 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 37.0822 | 37.0822 | C3 | 0 | 31.4728 | 1.9481 | 0 | 3.6613 | 37.0822 | 0 | 31.4728 | 2.6249 | 0 | 7.4822 | 41.5799 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.7547 | 9.0934 | 0 | 3.6613 | 29.5095 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0092933 | 18.941 | 0 | 4.8396 | 23.7899 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | 208513.6952 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | 347522.8254 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 65.9536 | 65.9536 |  | 0.097004 | 52.0074 | 5.474 | 1.9898 | 6.3855 |  | 0.097004 | 52.0074 | 7.3758 | 2.9407 | 13.0492 |  | 0 | 0 | 0 | 0 | 0 |  | 0.097004 | 27.6864 | 25.552 | 6.2328 | 6.3855 |  | 0 | 0 | 0 | 0 | 0 |  | 0.097004 | 0.015357 | 53.223 | 4.1778 | 8.4405 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 76.0126 | 76.0126 | C1 | 9.9431 | 39.0737 | 14.5585 | 1.188 | 11.2492 | 76.0126 | 9.9388 | 39.0737 | 15.2955 | 2.2227 | 17.0115 | 83.5423 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9676 | 31.7613 | 18.3957 | 4.3897 | 12.4727 | 73.987 | 0 | 0 | 0 | 0 | 0 | 0 | 6.9676 | 21.5006 | 25.67 | 4.2208 | 16.4892 | 74.8482 |  |  | C1 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C1 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | 162628.08 | C1 | 22.4315 | 96.4774 | 278.4582 | 623.2993 | 1185.9263 | C1 | 222.9432 | 3769.7333 | 4259.1647 | 1385.4153 | 20174.4041 | 29811.6606 |  | 223.0388 | 3769.7333 | 4053.9411 | 740.4654 | 13340.7556 | 22127.9343 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 3064.2429 | 5122.4441 | 2736.0888 | 14791.7523 | 25870.8214 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826 |  | 156.2934 | 2074.3195 | 7148.0202 | 2630.847 | 19555.0026 | 31564.4826
|  |  | 136.6281 | 136.6281 | C2 | 5.0986 | 76.2932 | 29.9538 | 5.5582 | 19.7242 | 136.6281 | 5.0965 | 76.2932 | 31.4701 | 10.3995 | 29.8278 | 153.087 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5729 | 62.0152 | 37.8487 | 20.5382 | 21.8695 | 145.8445 | 0 | 0 | 0 | 0 | 0 | 0 | 3.5729 | 41.9808 | 52.8153 | 19.7482 | 28.912 | 147.0291 |  |  | C2 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C2 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | 232325.8286 | C2 | 32.045 | 137.8248 | 397.7974 | 890.4276 | 1694.1804 | C2 | 163.3161 | 10515.0973 | 12518.7377 | 9259.9833 | 50533.6075 | 82990.7419 |  | 163.3862 | 10515.0973 | 11915.5351 | 4949.2 | 33416.4272 | 60959.6459 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 8547.2391 | 15056.1293 | 18287.7555 | 37050.9385 | 79056.5545 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254 |  | 114.4921 | 5785.9984 | 21009.7983 | 17584.3294 | 48982.1073 | 93476.7254
|  |  | 182.0691 | 182.0691 | C3 | 5.2629 | 106.478 | 45.3634 | 3.9391 | 21.0257 | 182.0691 | 5.2606 | 106.478 | 47.6598 | 7.3702 | 31.7959 | 198.5645 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6879 | 86.5511 | 57.3199 | 14.5555 | 23.3126 | 185.4269 | 0 | 0 | 0 | 0 | 0 | 0 | 3.6879 | 58.5902 | 79.986 | 13.9956 | 30.8197 | 187.0794 |  |  | C3 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C3 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | 348488.7428 | C3 | 48.0675 | 206.7373 | 596.6961 | 1335.6414 | 2541.2706 | C3 | 252.8657 | 22012.9658 | 28438.4362 | 9843.8816 | 80801.9857 | 141350.1351 |  | 252.9741 | 22012.9658 | 27068.1591 | 5261.2773 | 53432.0388 | 108027.4152 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 17893.3278 | 34202.5516 | 19440.9099 | 59243.5322 | 130957.5919 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677 |  | 177.2704 | 12112.7728 | 47727.3206 | 18693.1285 | 78321.1754 | 157031.6677
|  |  | 67.6959 | 67.6959 | C4 | 20.1271 | 33.8496 | 2.0485 | 0 | 11.6707 | 67.6959 | 20.1185 | 33.8496 | 2.1522 | 0 | 17.6488 | 73.7691 | 0 | 0 | 0 | 0 | 0 | 0 | 14.104 | 27.5148 | 2.5885 | 0 | 12.94 | 57.1472 | 0 | 0 | 0 | 0 | 0 | 0 | 14.104 | 18.626 | 3.612 | 0 | 17.107 | 53.4489 |  |  | C4 | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923 | C4 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | 580814.5714 | C4 | 80.1125 | 344.5621 | 994.4935 | 2226.069 | 4235.451 | C4 | 1611.7417 | 11663.2874 | 2140.3925 | 0 | 74750.6707 | 90166.0923 |  | 1612.4329 | 11663.2874 | 2037.2599 | 0 | 49430.4775 | 64743.4578 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 9480.5501 | 2574.2233 | 0 | 54806.7443 | 67991.4222 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041 |  | 1129.9045 | 6417.7972 | 3592.1525 | 0 | 72455.6499 | 83595.5041
|  |  | 462.4057 | 462.4057 |  | 40.4318 | 255.6945 | 91.9242 | 10.6853 | 63.6698 |  | 40.4144 | 255.6945 | 96.5777 | 19.9923 | 96.284 |  | 0 | 0 | 0 | 0 | 0 |  | 28.3324 | 207.8423 | 116.1528 | 39.4833 | 70.5948 |  | 0 | 0 | 0 | 0 | 0 |  | 28.3324 | 140.6975 | 162.0833 | 37.9646 | 93.3278 | [22 empty] | 2250.8667 | 47961.0839 | 47356.7311 | 20489.2802 | 226260.668 | 344318.6299 |  | 2251.8321 | 47961.0839 | 45074.8952 | 10950.9427 | 149619.6993 | 255858.4532 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 38985.3599 | 56955.3484 | 40464.7541 | 165892.9673 | 303876.39 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798 |  | 1577.9603 | 26390.8878 | 79477.2917 | 38908.3048 | 219313.9351 | 365668.3798
| EHV UG Cable (Non Pressurised) |  | 55.8648 | 55.8648 | C1 | 20.28 | 31.8691 | 0.49426 | 3.1782 | 0.043172 | 55.8648 | 15.4973 | 31.8691 | 0.52291 | 3.2075 | 0.050667 | 51.1475 | 0 | 0 | 0 | 0 | 0 | 0 | 19.8549 | 31.5642 | 1.0578 | 3.4079 | 0.043172 | 55.928 | 0 | 0 | 0 | 0 | 0 | 0 | 19.6892 | 26.0768 | 2.3638 | 2.9471 | 0.14836 | 51.2253 |  |  | C1 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C1 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | 73518.6461 | C1 | 38.0736 | 163.7538 | 472.6349 | 1057.9435 | 2012.9061 | C1 | 590.0392 | 5218.6824 | 247.147 | 3393.3298 | 101.9869 | 9551.1853 |  | 772.1344 | 5218.6824 | 233.6066 | 3362.3692 | 86.9003 | 9673.6929 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 755.9468 | 5168.7648 | 499.9464 | 3605.3956 | 86.9003 | 10116.9539 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524 |  | 749.6393 | 4270.1698 | 1117.2333 | 3117.8537 | 298.6279 | 9553.524
|  |  | 65.5759 | 65.5759 | C2 | 31.9175 | 27.5701 | 0.87467 | 3.5588 | 1.6548 | 65.5759 | 24.3903 | 27.5701 | 0.92537 | 3.5916 | 1.942 | 58.4194 | 0 | 0 | 0 | 0 | 0 | 0 | 31.2484 | 27.3064 | 1.8719 | 3.8161 | 1.6548 | 65.8975 | 0 | 0 | 0 | 0 | 0 | 0 | 30.9877 | 22.5591 | 4.1831 | 3.3 | 5.6865 | 66.7165 |  |  | C2 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C2 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | 105026.6373 | C2 | 54.3909 | 233.934 | 675.1927 | 1511.3479 | 2875.5801 | C2 | 1326.6111 | 6449.5749 | 624.8015 | 5428.1624 | 5584.5139 | 19413.6637 |  | 1736.0237 | 6449.5749 | 590.5706 | 5378.6361 | 4758.4114 | 18913.2167 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 1699.6284 | 6387.8836 | 1263.8926 | 5767.3949 | 4758.4114 | 19877.2109 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267 |  | 1685.4469 | 5277.3436 | 2824.4285 | 4987.4952 | 16352.0125 | 31126.7267
|  |  | 77.7419 | 77.7419 | C3 | 51.2718 | 20.023 | 0.37769 | 6.0695 | 0 | 77.7419 | 39.1802 | 20.023 | 0.39959 | 6.1254 | 0 | 65.7281 | 0 | 0 | 0 | 0 | 0 | 0 | 50.1969 | 19.8314 | 0.80831 | 6.5082 | 0 | 77.3448 | 0 | 0 | 0 | 0 | 0 | 0 | 49.7781 | 16.3837 | 1.8063 | 5.6281 | 0 | 73.5962 |  |  | C3 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C3 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | 157539.9559 | C3 | 81.5863 | 350.901 | 1012.7891 | 2267.0218 | 4313.3702 | C3 | 3196.5691 | 7026.074 | 404.6965 | 13886.3435 | 0 | 24513.6831 |  | 4183.0795 | 7026.074 | 382.5244 | 13759.6454 | 0 | 25351.3233 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 4095.3822 | 6958.8685 | 818.6486 | 14754.1693 | 0 | 26627.0686 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393 |  | 4061.2108 | 5749.0621 | 1829.439 | 12759.0274 | 0 | 24398.7393
|  |  | 209.0164 | 209.0164 | C4 | 150.0512 | 26.0249 | 1.3381 | 26.0295 | 5.5727 | 209.0164 | 114.6641 | 26.0249 | 1.4157 | 26.2691 | 6.5402 | 174.914 | 0 | 0 | 0 | 0 | 0 | 0 | 146.9054 | 25.7759 | 2.8638 | 27.9108 | 5.5727 | 209.0287 | 0 | 0 | 0 | 0 | 0 | 0 | 145.6797 | 21.2948 | 6.3997 | 24.1366 | 19.1504 | 216.6611 |  |  | C4 | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738 | C4 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | 262566.5932 | C4 | 135.9772 | 584.835 | 1687.9818 | 3778.3697 | 7188.9503 | C4 | 15591.7087 | 15220.2533 | 2389.6645 | 99254.5314 | 47017.1975 | 179473.3554 |  | 20403.55 | 15220.2533 | 2258.7424 | 98348.939 | 40062.0667 | 176293.5514 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 19975.7944 | 15074.6691 | 4833.9823 | 105457.4345 | 40062.0667 | 185403.9469 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899 |  | 19809.1186 | 12453.9225 | 10802.5297 | 91196.8859 | 137671.0331 | 271933.4899
|  |  | 408.199 | 408.199 |  | 253.5206 | 105.487 | 3.0848 | 38.836 | 7.2707 |  | 193.732 | 105.487 | 3.2636 | 39.1936 | 8.5329 |  | 0 | 0 | 0 | 0 | 0 |  | 248.2056 | 104.478 | 6.6018 | 41.643 | 7.2707 |  | 0 | 0 | 0 | 0 | 0 |  | 246.1346 | 86.3144 | 14.753 | 36.0118 | 24.9852 | [22 empty] | 20704.9281 | 33914.5845 | 3666.3094 | 121962.3671 | 52703.6984 | 232951.8875 |  | 27094.7876 | 33914.5845 | 3465.444 | 120849.5897 | 44907.3784 | 230231.7843 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 26526.7518 | 33590.186 | 7416.4699 | 129584.3943 | 44907.3784 | 242025.1804 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799 |  | 26305.4155 | 27750.498 | 16573.6305 | 112061.2623 | 154321.6736 | 337012.4799
| EHV OHL Support - Towers |  | 637 | 637 | C1 | 103 | 280 | 61 | 33 | 160 | 637 | 61 | 85 | 118 | 81 | 292 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 56 | 266 | 96 | 24 | 195 | 637 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 96 | 221 | 96 | 219 | 637 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | 26323.5227 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 561 | 561 | C2 | 77 | 171 | 92 | 96 | 125 | 561 | 35 | 97 | 106 | 109 | 214 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 116 | 104 | 42 | 239 | 561 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 67 | 106 | 104 | 281 | 561 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | 37605.0325 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18 | 18 | C3 | 4 | 5 | 1 | 7 | 1 | 18 | 3 | 2 | 2 | 7 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 3 | 0 | 8 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 3 | 8 | 18 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | 56407.5487 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 212 | 212 | C4 | 10 | 27 | 1 | 2 | 172 | 212 | 10 | 27 | 1 | 2 | 172 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 27 | 0 | 174 | 212 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 6 | 27 | 174 | 212 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | 94012.5812 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1428 | 1428 |  | 194 | 483 | 155 | 138 | 458 |  | 109 | 211 | 227 | 199 | 682 |  | 0 | 0 | 0 | 0 | 0 |  | 122 | 394 | 230 | 66 | 616 |  | 0 | 0 | 0 | 0 | 0 |  | 10 | 170 | 336 | 230 | 682 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Poles |  | 4038 | 4038 | C1 | 1046 | 1806 | 1095 | 69 | 22 | 4038 | 925 | 1817 | 1103 | 151 | 75 | 4071 | 0 | 0 | 0 | 0 | 0 | 0 | 936 | 1591 | 1154 | 219 | 163 | 4063 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 1220 | 1485 | 243 | 334 | 4143 |  |  | C1 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C1 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | 30797.263 | C1 | 0.58127 | 2.5 | 7.2157 | 16.1517 | 30.7311 | C1 | 537.6765 | 4542.5678 | 7958.962 | 2438.9031 | 2304.8353 | 17782.9447 |  | 608.0104 | 4515.0674 | 7901.2361 | 1114.4657 | 676.085 | 14814.8646 |  | 544.0705 | 3977.5594 | 8326.9648 | 3537.2171 | 5009.1754 | 21394.9871 |  | 544.0705 | 3977.5594 | 8326.9648 | 3537.2171 | 5009.1754 | 21394.9871 |  | 500.4751 | 3050.0455 | 10715.375 | 3924.8573 | 10264.1999 | 28454.9528 |  | 500.4751 | 3050.0455 | 10715.375 | 3924.8573 | 10264.1999 | 28454.9528
|  |  | 4370 | 4370 | C2 | 1624 | 1865 | 758 | 111 | 12 | 4370 | 1433 | 1874 | 762 | 214 | 58 | 4341 | 0 | 0 | 0 | 0 | 0 | 0 | 1463 | 1655 | 804 | 312 | 141 | 4375 | 0 | 0 | 0 | 0 | 0 | 0 | 1357 | 1287 | 1033 | 349 | 298 | 4324 |  |  | C2 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C2 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | 43996.09 | C2 | 0.83039 | 3.5715 | 10.3082 | 23.0738 | 43.9016 | C2 | 1189.9466 | 6692.957 | 7854.8492 | 4937.7981 | 2546.2942 | 23221.8452 |  | 1348.5508 | 6660.8137 | 7813.6164 | 2561.1944 | 526.8195 | 18910.9947 |  | 1214.8582 | 5910.8025 | 8287.7937 | 7199.0328 | 6190.1291 | 28802.6163 |  | 1214.8582 | 5910.8025 | 8287.7937 | 7199.0328 | 6190.1291 | 28802.6163 |  | 1126.8371 | 4596.4972 | 10648.3717 | 8052.7642 | 13082.6842 | 37507.1543 |  | 1126.8371 | 4596.4972 | 10648.3717 | 8052.7642 | 13082.6842 | 37507.1543
|  |  | 123 | 123 | C3 | 57 | 55 | 9 | 0 | 2 | 123 | 51 | 56 | 10 | 0 | 2 | 119 | 0 | 0 | 0 | 0 | 0 | 0 | 49 | 46 | 9 | 0 | 2 | 106 | 0 | 0 | 0 | 0 | 0 | 0 | 42 | 31 | 12 | 0 | 2 | 87 |  |  | C3 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C3 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | 65994.1351 | C3 | 1.2456 | 5.3572 | 15.4623 | 34.6107 | 65.8524 | C3 | 63.5247 | 300.0045 | 154.623 | 0 | 131.7049 | 649.8571 |  | 70.9982 | 294.6473 | 139.1607 | 0 | 131.7049 | 636.5111 |  | 61.0335 | 246.4322 | 139.1607 | 0 | 131.7049 | 578.3314 |  | 61.0335 | 246.4322 | 139.1607 | 0 | 131.7049 | 578.3314 |  | 52.3145 | 166.0739 | 185.5476 | 0 | 131.7049 | 535.6409 |  | 52.3145 | 166.0739 | 185.5476 | 0 | 131.7049 | 535.6409
|  |  | 1365 | 1365 | C4 | 451 | 525 | 357 | 28 | 4 | 1365 | 399 | 528 | 360 | 67 | 11 | 1365 | 0 | 0 | 0 | 0 | 0 | 0 | 402 | 461 | 376 | 96 | 17 | 1352 | 0 | 0 | 0 | 0 | 0 | 0 | 368 | 351 | 484 | 107 | 32 | 1342 |  |  | C4 | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785 | C4 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | 109990.2251 | C4 | 2.076 | 8.9287 | 25.7705 | 57.6846 | 109.7541 | C4 | 828.3124 | 4714.3561 | 9277.381 | 3864.8654 | 1207.2947 | 19892.2095 |  | 936.2629 | 4687.5699 | 9200.0695 | 1615.1676 | 439.0162 | 16878.0862 |  | 834.5403 | 4116.1328 | 9689.709 | 5537.7175 | 1865.8191 | 22043.9188 |  | 834.5403 | 4116.1328 | 9689.709 | 5537.7175 | 1865.8191 | 22043.9188 |  | 763.9573 | 3133.9753 | 12472.9233 | 6172.2477 | 3512.13 | 26055.2336 |  | 763.9573 | 3133.9753 | 12472.9233 | 6172.2477 | 3512.13 | 26055.2336
|  |  | 9896 | 9896 |  | 3178 | 4251 | 2219 | 208 | 40 |  | 2808 | 4275 | 2235 | 432 | 146 |  | 0 | 0 | 0 | 0 | 0 |  | 2850 | 3753 | 2343 | 627 | 323 |  | 0 | 0 | 0 | 0 | 0 |  | 2628 | 2889 | 3014 | 699 | 666 | [22 empty] | 2619.4602 | 16249.8853 | 25245.8153 | 11241.5666 | 6190.1291 | 61546.8565 |  | 2963.8223 | 16158.0983 | 25054.0827 | 5290.8276 | 1773.6256 | 51240.4565 |  | 2654.5026 | 14250.9269 | 26443.6282 | 16273.9674 | 13196.8284 | 72819.8535 |  | 2654.5026 | 14250.9269 | 26443.6282 | 16273.9674 | 13196.8284 | 72819.8535 |  | 2443.5839 | 10946.5919 | 34022.2176 | 18149.8692 | 26990.7189 | 92552.9816 |  | 2443.5839 | 10946.5919 | 34022.2176 | 18149.8692 | 26990.7189 | 92552.9816
| EHV OHL Fittings and Conductors (Tower Lines) |  | 591.3506 | 591.3506 | C1 | 2.2333 | 172.982 | 97.1676 | 158.0498 | 160.9179 | 591.3506 | 2.2333 | 90.3849 | 47.0231 | 230.8255 | 220.8837 | 591.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9354 | 41.9414 | 191.087 | 41.7973 | 314.5894 | 591.3506 | 0 | 0 | 0 | 0 | 0 | 0 | 1.0705 | 4.1592 | 181.3945 | 85.7587 | 318.9677 | 591.3506 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | 69351.1929 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | 99073.1327 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.4348 | 6.4348 | C3 | 0 | 0.83798 | 0.69576 | 1.2627 | 3.6383 | 6.4348 | 0 | 0.29214 | 0.69576 | 1.2627 | 4.1841 | 6.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29214 | 0.91871 | 0.32289 | 4.901 | 6.4348 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.83798 | 0.69576 | 4.901 | 6.4348 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | 148609.6991 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.5628 | 4.5628 | C4 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0.73612 | 0.59389 | 1.8586 | 1.3742 | 4.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.73612 | 0.59389 | 0.29022 | 2.9425 | 4.5628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.29791 | 0.43821 | 0.59389 | 3.2328 | 4.5628 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | 247682.8318 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 602.3481 | 602.3481 |  | 2.2333 | 174.5561 | 98.4572 | 161.171 | 165.9304 |  | 2.2333 | 91.4132 | 48.3128 | 233.9468 | 226.442 |  | 0 | 0 | 0 | 0 | 0 |  | 1.9354 | 42.9697 | 192.5996 | 42.4104 | 322.433 |  | 0 | 0 | 0 | 0 | 0 |  | 1.0705 | 4.4571 | 182.6707 | 87.0484 | 327.1015 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 |  | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 |  | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 |  | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 |  | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 |  | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 32 | 32 | C1 | 30 | 0 | 2 | 0 | 0 | 32 | 30 | 0 | 2 | 0 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 2 | 0 | 2 | 0 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 3 | 0 | 2 | 0 | 32 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | 127042.0461 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23 | 23 | C2 | 23 | 0 | 0 | 0 | 0 | 23 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 0 | 0 | 0 | 8 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 5 | 0 | 0 | 8 | 23 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | 181488.6372 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26 | 26 | C3 | 18 | 0 | 0 | 8 | 0 | 26 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 8 | 0 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 0 | 0 | 0 | 8 | 26 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | 272232.9558 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 2 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | 453721.5931 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 83 | 83 |  | 73 | 0 | 2 | 8 | 0 |  | 63 | 0 | 4 | 8 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 61 | 2 | 0 | 12 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 55 | 8 | 0 | 4 | 16 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Transformer |  | 30 | 30 | C1 | 18 | 9 | 3 | 0 | 0 | 30 | 16 | 9 | 3 | 1 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 1 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 6 | 4 | 3 | 2 | 30 |  |  | C1 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C1 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | 110661.2361 | C1 | 273.0427 | 1174.3506 | 3389.4731 | 7586.9787 | 14435.4359 | C1 | 4368.6833 | 10569.155 | 10168.4193 | 7586.9787 | 14435.4359 | 47128.6721 |  | 4914.7687 | 10569.155 | 10168.4193 | 0 | 0 | 25652.343 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4095.6406 | 10569.155 | 3389.4731 | 22760.9361 | 28870.8717 | 69686.0765 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441 |  | 4095.6406 | 7046.1033 | 13557.8923 | 22760.9361 | 28870.8717 | 76331.4441
|  |  | 34 | 34 | C2 | 12 | 10 | 8 | 4 | 0 | 34 | 12 | 10 | 8 | 4 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 8 | 2 | 3 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 11 | 8 | 3 | 4 | 34 |  |  | C2 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C2 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | 158087.4802 | C2 | 390.061 | 1677.6436 | 4842.1044 | 10838.541 | 20622.0512 | C2 | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 4680.7321 | 16776.4365 | 38736.8352 | 43354.1641 | 0 | 103548.1679 |  | 3900.6101 | 18454.0801 | 38736.8352 | 21677.082 | 61866.1537 | 144634.7612 |  | 3900.6101 | 18454.0801 | 38736.8352 | 21677.082 | 61866.1537 | 144634.7612 |  | 3120.4881 | 18454.0801 | 38736.8352 | 32515.6231 | 82488.2049 | 175315.2315 |  | 3120.4881 | 18454.0801 | 38736.8352 | 32515.6231 | 82488.2049 | 175315.2315
|  |  | 13 | 13 | C3 | 7 | 4 | 2 | 0 | 0 | 13 | 5 | 4 | 2 | 2 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 4 | 2 | 0 | 2 | 13 |  |  | C3 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C3 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | 237131.2203 | C3 | 585.0915 | 2516.4655 | 7263.1566 | 16257.8115 | 30933.0768 | C3 | 2925.4576 | 10065.8619 | 14526.3132 | 32515.6231 | 0 | 60033.2558 |  | 4095.6406 | 10065.8619 | 14526.3132 | 0 | 0 | 28687.8157 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864 |  | 2925.4576 | 10065.8619 | 14526.3132 | 0 | 61866.1537 | 89383.7864
|  |  | 2 | 2 | C4 | 2 | 0 | 0 | 0 | 0 | 2 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 2 |  |  | C4 | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045 | C4 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | 395218.7004 | C4 | 975.1525 | 4194.1091 | 12105.261 | 27096.3525 | 51555.1281 | C4 | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051 |  | 1950.3051 | 0 | 0 | 0 | 0 | 1950.3051
|  |  | 79 | 79 |  | 39 | 23 | 13 | 4 | 0 |  | 35 | 23 | 13 | 7 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 24 | 11 | 5 | 7 |  | 0 | 0 | 0 | 0 | 0 |  | 30 | 21 | 14 | 6 | 8 | [22 empty] | 13925.1781 | 37411.4534 | 63431.5677 | 83456.7658 | 14435.4359 | 212660.4009 |  | 15641.4465 | 37411.4534 | 63431.5677 | 43354.1641 | 0 | 159838.6317 |  | 12872.0133 | 39089.097 | 56652.6215 | 44438.0182 | 152603.1791 | 305654.9292 |  | 12872.0133 | 39089.097 | 56652.6215 | 44438.0182 | 152603.1791 | 305654.9292 |  | 12091.8913 | 35566.0454 | 66821.0408 | 55276.5592 | 173225.2303 | 342980.767 |  | 12091.8913 | 35566.0454 | 66821.0408 | 55276.5592 | 173225.2303 | 342980.767
| 132kV UG Cable (Gas) |  | 0.0030333 | 0.0030333 | C1 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0.67969 | 0.67969 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0030333 | 0.0030333 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | 208642.8096 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0011431 | 0.0011431 | C2 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0.25615 | 0.25615 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011431 | 0.0011431 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | 298061.1565 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.016356 | 0.016356 | C3 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 3.6651 | 3.6651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.016356 | 0.016356 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | 447091.7348 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.0054672 | 0.0054672 | C4 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 1.2251 | 1.2251 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0054672 | 0.0054672 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | 745152.8913 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.026 | 0.026 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 5.826 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0.026 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 6.9437 | 6.9437 | C1 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 2.9422 | 0.71401 | 1.6033 | 1.6842 | 6.9437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.7908 | 0.70587 | 1.9907 | 1.6982 | 7.1857 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.64753 | 1.6511 | 1.1276 | 4.3905 | 7.8167 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | 280678.8728 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 23.6291 | 23.6291 | C2 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 3.7561 | 3.3857 | 4.3751 | 9.8785 | 2.2337 | 23.6291 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3281 | 3.2115 | 4.3252 | 12.2653 | 2.2523 | 23.3825 | 0 | 0 | 0 | 0 | 0 | 0 | 1.3281 | 0.74514 | 10.1171 | 6.9474 | 5.823 | 24.9608 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | 400969.8182 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 26.675 | 26.675 | C3 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 14.9297 | 6.0468 | 3.6204 | 2.0782 | 26.675 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.1616 | 5.9778 | 4.4951 | 2.0955 | 26.73 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.2858 | 13.9829 | 2.5462 | 5.4176 | 25.2324 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | 601454.7273 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.97712 | 0.97712 | C4 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0.97712 | 0 | 0 | 0 | 0.97712 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0.92685 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.21505 | 0 | 0 | 0 | 0.21505 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | 1002424.5456 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 58.225 | 58.225 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 3.7561 | 22.2348 | 11.1358 | 15.1022 | 5.9961 |  | 0 | 0 | 0 | 0 | 0 |  | 1.3281 | 21.0908 | 11.0088 | 18.7512 | 6.0461 |  | 0 | 0 | 0 | 0 | 0 |  | 1.3281 | 4.8935 | 25.7511 | 10.6212 | 15.6311 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Non Pressurised) |  | 32.1946 | 32.1946 | C1 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 24.6703 | 1.6243 | 0 | 0 | 0 | 26.2946 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 | 0 | 0 | 0 | 0 | 0 | 0 | 30.5703 | 1.6243 | 0 | 0 | 0 | 32.1946 |  |  | C1 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C1 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | 108378.0526 | C1 | 2149.4357 | 9244.6748 | 26682.4726 | 59725.9062 | 94592.4846 | C1 | 53027.1783 | 15016.3613 | 0 | 0 | 0 | 68043.5396 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104 |  | 65708.8492 | 15016.3613 | 0 | 0 | 0 | 80725.2104
|  |  | 0.61927 | 0.61927 | C2 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52772 | 0.001 | 0.083556 | 0.007 | 0.61927 |  |  | C2 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C2 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | 154825.7894 | C2 | 3070.6225 | 13206.6783 | 38117.818 | 85322.7231 | 135132.1208 | C2 | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667 |  | 0 | 6969.4106 | 38.1178 | 7129.2137 | 945.9248 | 15082.667
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C3 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | 232238.6841 | C3 | 4605.9337 | 19810.0175 | 57176.727 | 127984.0847 | 202698.1813 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6.0781 | 6.0781 | C4 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.0781 | 0 | 0 | 0 | 6.0781 |  |  | C4 | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728 | C4 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | 387064.4735 | C4 | 7676.5562 | 33016.6958 | 95294.5449 | 213306.8078 | 337830.3021 | C4 | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825 |  | 0 | 200679.4825 | 0 | 0 | 0 | 200679.4825
|  |  | 38.892 | 38.892 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 24.6703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 0 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 |  | 0 | 0 | 0 | 0 | 0 |  | 30.5703 | 8.2302 | 0.001 | 0.083556 | 0.007 | [22 empty] | 53027.1783 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 283805.6892 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36 |  | 65708.8492 | 222665.2544 | 38.1178 | 7129.2137 | 945.9248 | 296487.36
| 132kV OHL Support - Tower |  | 572 | 572 | C1 | 145 | 227 | 58 | 28 | 114 | 572 | 52 | 139 | 94 | 35 | 252 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 88 | 237 | 56 | 46 | 145 | 572 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 111 | 180 | 56 | 191 | 572 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | 66033.5592 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 363 | 363 | C2 | 184 | 73 | 9 | 41 | 56 | 363 | 17 | 67 | 23 | 48 | 208 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 115 | 88 | 56 | 7 | 97 | 363 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 171 | 28 | 56 | 104 | 363 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | 94333.656 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 122 | 122 | C3 | 28 | 66 | 0 | 23 | 5 | 122 | 4 | 8 | 13 | 26 | 71 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 82 | 2 | 0 | 28 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 26 | 64 | 2 | 28 | 122 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | 141500.4841 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 112 | 112 | C4 | 97 | 7 | 0 | 0 | 8 | 112 | 1 | 2 | 4 | 22 | 83 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 96 | 7 | 1 | 0 | 8 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 6 | 1 | 8 | 112 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | 235834.1401 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1169 | 1169 |  | 454 | 373 | 67 | 92 | 183 |  | 74 | 216 | 134 | 131 | 614 |  | 0 | 0 | 0 | 0 | 0 |  | 309 | 414 | 115 | 53 | 278 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 405 | 278 | 115 | 331 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 535.0969 | 535.0969 | C1 | 59.426 | 153.5999 | 184.0823 | 56.0422 | 81.9465 | 535.0969 | 58.4481 | 35.9218 | 99.5766 | 159.0191 | 182.1313 | 535.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9704 | 21.8938 | 243.6033 | 80.0159 | 133.6134 | 535.0969 | 0 | 0 | 0 | 0 | 0 | 0 | 55.9704 | 13.4634 | 234.4327 | 94.4155 | 136.8148 | 535.0969 |  | 234.4327 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | 153343.6753 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 40.1377 | 40.1377 | C2 | 0.52193 | 3.2945 | 27.6214 | 2.1808 | 6.5189 | 40.1377 | 0.52193 | 0 | 26.7231 | 3.2693 | 9.6234 | 40.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52193 | 0 | 29.3017 | 1.6143 | 8.6998 | 40.1377 | 0 | 0 | 0 | 0 | 0 | 0 | 0.52193 | 0 | 5.3726 | 25.5434 | 8.6998 | 40.1377 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | 219062.3934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.9077 | 3.9077 | C3 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 2.2856 | 1.622 | 0 | 3.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49864 | 2.6601 | 0.74894 | 3.9077 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.2856 | 1.622 | 3.9077 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | 328593.59 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4.7653 | 4.7653 | C4 | 0 | 0 | 2.8134 | 1.4503 | 0.50155 | 4.7653 | 0 | 0 | 2.1517 | 1.4503 | 1.1632 | 4.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71013 | 3.5536 | 0.50155 | 4.7653 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.71013 | 2.1032 | 1.9519 | 4.7653 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | 547655.9834 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 583.9075 | 583.9075 |  | 59.9479 | 156.8945 | 216.8026 | 61.2954 | 88.967 |  | 58.97 | 35.9218 | 130.737 | 165.3608 | 192.9179 |  | 0 | 0 | 0 | 0 | 0 |  | 56.4923 | 21.8938 | 274.1138 | 87.8439 | 143.5637 |  | 0 | 0 | 0 | 0 | 0 |  | 56.4923 | 13.4634 | 240.5154 | 124.3478 | 149.0886 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 |  | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 |  | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 |  | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 |  | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 |  | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 241438.9569 | 241438.9569 |  | 79461.5571 | 63119.1043 | 62690.8796 | 28331.1633 | 7836.2525 |  | 72340.8732 | 62950.9887 | 64146.4037 | 31275.6199 | 11650.0551 |  | 0 | 0 | 0 | 0 | 0 |  | 69731.9612 | 33024.191 | 68678.0298 | 56487.4481 | 13538.3268 |  | 0 | 0 | 0 | 0 | 0 |  | 60791.0253 | 29640.0713 | 61151.9975 | 58228.2551 | 31648.6077 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 |  | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 |  | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 |  | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 |  | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 |  | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 2914.1373 | 17537.4892 | 75123.2988 | 31046.7604 | 41129.3082 | 167750.9939 | LV Network | 3226.9989 | 17415.089 | 74089.4983 | 26238.2108 | 34188.9988 | 155158.7959 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 2819.3056 | 3830.09 | 52614.6719 | 169288.3432 | 55964.0249 | 284516.4357 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311 | LV Network | 2488.6917 | 2941.8775 | 42538.8272 | 167951.6411 | 132471.7935 | 348392.8311
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 175382.6393 | 581305.5664 | 559136.2654 | 551528.6068 | 728259.3779 | 2595612.4558 | HV Network | 184805.4624 | 571590.3404 | 446235.1459 | 418532.1062 | 315374.0826 | 1936537.1376 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 165313.1683 | 461868.3505 | 752265.7548 | 665127.9031 | 932181.5137 | 2976756.6904 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831 | HV Network | 147893.2039 | 435991.773 | 827790.3449 | 766675.7577 | 1656810.4037 | 3835161.4831
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 44041.948 | 184376.5847 | 335409.9264 | 371604.8451 | 285154.4955 | 1220587.7997 | EHV Network | 54231.4708 | 184284.7976 | 306079.658 | 318684.3861 | 196300.7033 | 1059581.0158 | EHV Network | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 | EHV Network | 46593.1435 | 154526.3043 | 345320.7199 | 542764.284 | 347393.4833 | 1436597.935 | EHV Network | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842 | EHV Network | 45227.2843 | 108374.1096 | 368816.7023 | 570699.4425 | 854724.7455 | 1947842.2842
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 66952.3564 | 260076.7078 | 63469.6855 | 90585.9796 | 15381.3607 | 496466.0901 | 132kV Network | 81350.2957 | 260076.7078 | 63469.6855 | 50483.3778 | 945.9248 | 456325.9917 | 132kV Network | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 | 132kV Network | 78580.8625 | 261754.3515 | 56690.7394 | 51567.2319 | 153549.1039 | 602142.2892 | 132kV Network | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127 | 132kV Network | 77800.7405 | 258231.2998 | 66859.1586 | 62405.7729 | 174171.1552 | 639468.127
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 289291.081 | 1043296.3481 | 1033139.1762 | 1044766.1919 | 1069924.5423 | 4480417.3395 | Total | 323614.2279 | 1033366.9348 | 889873.9877 | 813938.0809 | 546809.7095 | 3607602.9409 | Total | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 | Total | 293306.4799 | 881979.0963 | 1206891.886 | 1428747.7622 | 1489088.1259 | 5300013.3503 | Total | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254 | Total | 273409.9204 | 805539.0599 | 1306005.0329 | 1567732.6142 | 2818178.0979 | 6770864.7254
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## NPgN - Ave Crit
HI8: Secondary deliverables RIIO-ED1 - Average Criticality | [6 empty] | HI8: Secondary deliverables RIIO-ED1
NPGN | [6 empty] | NPGN
Price base (2012/13) | [6 empty] | Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period | [5 empty] | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure |  |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Overall Consequence Of Failure
| LV Network | [6 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 |  | LV Switchgear and Other |  |  |  |  | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 |  | LV UGB |  |  |  |  | 0
| LV OHL Support | 4923.145 | 4327.4401 | 0 | 3000 | 12250.5851 |  | LV OHL Support | 4923.145 | 4327.4401 |  | 3000 | 12250.5851
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| HV Network | 0 | 0 | 0 | 0 | 0 |  | HV Network
| HV Switchgear (GM) - Primary | 139929.347 | 10718.0515 | 468.2855 | 16000 | 167115.684 |  | HV Switchgear (GM) - Primary | 139929.347 | 10718.0515 | 468.2855 | 16000 | 167115.684
| HV Switchgear (GM) - Distribution | 33129.3773 | 45407.6775 | 242.4526 | 8000 | 86779.5074 |  | HV Switchgear (GM) - Distribution | 33129.3773 | 45407.6775 | 242.4526 | 8000 | 86779.5074
| HV Transformer (GM) | 13684.602 | 44809.2831 | 275.625 | 8000 | 66769.5101 |  | HV Transformer (GM) | 13684.602 | 44809.2831 | 275.625 | 8000 | 66769.5101
| HV UG Cable | 0 | 0 | 0 | 0 | 0 |  | HV UG Cable |  |  |  |  | 0
| HV OHL Support - Poles | 5571.7737 | 1014.1729 | 0 | 4000 | 10585.9466 |  | HV OHL Support - Poles | 5571.7737 | 1014.1729 |  | 4000 | 10585.9466
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| EHV Network | 0 | 0 | 0 | 0 | 0 |  | EHV Network
| EHV Switchgear (GM) | 112453.5154 | 11182.3059 | 38740.5952 | 20550 | 182926.4165 |  | EHV Switchgear (GM) | 112453.5154 | 11182.3059 | 38740.5952 | 20550 | 182926.4165
| EHV Transformer | 63786.4036 | 12761.7256 | 29202.9582 | 36990 | 142741.0874 |  | EHV Transformer | 63786.4036 | 12761.7256 | 29202.9582 | 36990 | 142741.0874
| EHV UG Cable (Gas) | 79007.6152 | 1.515 | 0 | 60000 | 139009.1302 |  | EHV UG Cable (Gas) | 79007.6152 | 1.515 |  | 60000 | 139009.1302
| EHV UG Cable (Oil) | 67227.4463 | 1.515 | 115096.8673 | 50000 | 232325.8286 |  | EHV UG Cable (Oil) | 67227.4463 | 1.515 | 115096.8673 | 50000 | 232325.8286
| EHV UG Cable (Non Pressurised) | 75025.1223 | 1.515 | 0 | 30000 | 105026.6373 |  | EHV UG Cable (Non Pressurised) | 75025.1223 | 1.515 |  | 30000 | 105026.6373
| EHV OHL Support - Towers | 29985.8582 | 619.1743 | 0 | 7000 | 37605.0325 |  | EHV OHL Support - Towers | 29985.8582 | 619.1743 |  | 7000 | 37605.0325
| EHV OHL Support - Poles | 37948.2252 | 1047.8648 | 0 | 5000 | 43996.09 |  | EHV OHL Support - Poles | 37948.2252 | 1047.8648 |  | 5000 | 43996.09
| EHV OHL Fittings and Conductors (Tower Lines) | 50718.9313 | 18354.2015 | 0 | 30000 | 99073.1327 |  | EHV OHL Fittings and Conductors (Tower Lines) | 50718.9313 | 18354.2015 |  | 30000 | 99073.1327
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| 132kV Network | 0 | 0 | 0 | 0 | 0 |  | 132kV Network
| 132kV CBs | 122281.5134 | 13905.2845 | 24751.8393 | 20550 | 181488.6372 |  | 132kV CBs | 122281.5134 | 13905.2845 | 24751.8393 | 20550 | 181488.6372
| 132kV Transformer | 87884.1378 | 20115.2673 | 768.075 | 49320 | 158087.4802 |  | 132kV Transformer | 87884.1378 | 20115.2673 | 768.075 | 49320 | 158087.4802
| 132kV UG Cable (Gas) | 198059.6415 | 1.515 | 0 | 100000 | 298061.1565 |  | 132kV UG Cable (Gas) | 198059.6415 | 1.515 |  | 100000 | 298061.1565
| 132kV UG Cable (Oil) | 135407.2471 | 1.515 | 185561.0561 | 80000 | 400969.8182 |  | 132kV UG Cable (Oil) | 135407.2471 | 1.515 | 185561.0561 | 80000 | 400969.8182
| 132kV UG Cable (Non Pressurised) | 104824.2744 | 1.515 | 0 | 50000 | 154825.7894 |  | 132kV UG Cable (Non Pressurised) | 104824.2744 | 1.515 |  | 50000 | 154825.7894
| 132kV OHL Support - Tower | 81755.2444 | 2578.4117 | 0 | 10000 | 94333.656 |  | 132kV OHL Support - Tower | 81755.2444 | 2578.4117 |  | 10000 | 94333.656
| 132kV OHL Fittings and Conductors (Tower Lines) | 139013.283 | 30049.1103 | 0 | 50000 | 219062.3934 |  | 132kV OHL Fittings and Conductors (Tower Lines) | 139013.283 | 30049.1103 |  | 50000 | 219062.3934
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 |  | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 |  | Submarine Cables
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 |  | [Please insert new asset category as required]

## NPgN - HI Probs. of Failure
CM105: HI Ratings Probabilities of Failure
NPGN
Price base (2012/13)
Average Probabilities of Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other | 0 | 0 | 0 | 0 | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB | 0 | 0 | 0 | 0 | 0
| LV OHL Support | 3.6997e-06 | 2.6333e-05 | 2.6333e-05 | 0.00010284 | 0.00010284 | 0.00026998 | 0.00026998 | 0.00056454 | 0.00056454 | 0.0010233 | LV OHL Support | 1.5016e-05 | 6.4585e-05 | 0.00018641 | 0.00041726 | 0.0007939
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear (at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB and LV Pillar OD (not at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV Network
| HV Switchgear (GM) - Primary | 1.6026e-05 | 0.00011407 | 0.00011407 | 0.00044545 | 0.00044545 | 0.0011695 | 0.0011695 | 0.0024454 | 0.0024454 | 0.0044324 | HV Switchgear (GM) - Primary | 6.5046e-05 | 0.00027976 | 0.00080746 | 0.0018074 | 0.0034389
| HV Switchgear (GM) - Distribution | 4.2928e-05 | 0.00030554 | 0.00030554 | 0.0011932 | 0.0011932 | 0.0031326 | 0.0031326 | 0.0065503 | 0.0065503 | 0.011873 | HV Switchgear (GM) - Distribution | 0.00017424 | 0.00074938 | 0.0021629 | 0.0048415 | 0.0092116
| HV Transformer (GM) | 3.6956e-05 | 0.00026304 | 0.00026304 | 0.0010272 | 0.0010272 | 0.0026968 | 0.0026968 | 0.0056391 | 0.0056391 | 0.010221 | HV Transformer (GM) | 0.00015 | 0.00064513 | 0.001862 | 0.0041679 | 0.0079302
| HV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV UG Cable | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles | 1.7816e-06 | 1.2681e-05 | 1.2681e-05 | 4.9522e-05 | 4.9522e-05 | 0.00013001 | 0.00013001 | 0.00027186 | 0.00027186 | 0.00049276 | HV OHL Support - Poles | 7.2313e-06 | 3.1102e-05 | 8.9767e-05 | 0.00020093 | 0.00038231
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV Network
| EHV Switchgear (GM) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV Switchgear (GM) | 0 | 0 | 0 | 0 | 0
| EHV Transformer | 0.00032229 | 0.0022939 | 0.0022939 | 0.0089584 | 0.0089584 | 0.023519 | 0.023519 | 0.049178 | 0.049178 | 0.089139 | EHV Transformer | 0.0013081 | 0.0056261 | 0.016238 | 0.036348 | 0.069158
| EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) | 3.3983e-05 | 0.00024188 | 0.00024188 | 0.0009446 | 0.0009446 | 0.0024799 | 0.0024799 | 0.0051855 | 0.0051855 | 0.0093991 | EHV UG Cable (Oil) | 0.00013793 | 0.00059324 | 0.0017122 | 0.0038327 | 0.0072923
| EHV UG Cable (Non Pressurised) | 0.00012759 | 0.00090816 | 0.00090816 | 0.0035466 | 0.0035466 | 0.009311 | 0.009311 | 0.019469 | 0.019469 | 0.03529 | EHV UG Cable (Non Pressurised) | 0.00051788 | 0.0022274 | 0.0064288 | 0.01439 | 0.02738
| EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Poles | 4.6502e-06 | 3.3098e-05 | 3.3098e-05 | 0.00012926 | 0.00012926 | 0.00033934 | 0.00033934 | 0.00070956 | 0.00070956 | 0.0012861 | EHV OHL Support - Poles | 1.8874e-05 | 8.1177e-05 | 0.0002343 | 0.00052445 | 0.00099785
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV Network
| 132kV CBs | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV CBs | 0 | 0 | 0 | 0 | 0
| 132kV Transformer | 0.0006079 | 0.0043268 | 0.0043268 | 0.016897 | 0.016897 | 0.044361 | 0.044361 | 0.09276 | 0.09276 | 0.16813 | 132kV Transformer | 0.0024674 | 0.010612 | 0.030629 | 0.06856 | 0.13045
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Oil) | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Non Pressurised) | 0.0048863 | 0.034779 | 0.034779 | 0.13582 | 0.13582 | 0.35657 | 0.35657 | 0.7456 | 0.7456 | 1 | 132kV UG Cable (Non Pressurised) | 0.019833 | 0.0853 | 0.2462 | 0.55109 | 0.8728
| 132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 155158.7959 | 284516.4357 | 258709.4245 | 348392.8311 | 288750.2878
HV Network | 1936537.1376 | 2976756.6904 | 2438025.9055 | 3835161.4831 | 2663771.7507
EHV Network | 1059581.0158 | 1436597.935 | 1181825.2813 | 1947842.2842 | 1553580.439
132kV Network | 456325.9917 | 602142.2892 | 569667.5395 | 639468.127 | 623218.0394
Other | 0 | 0 | 0 | 0 | 0
Total | 3607602.9409 | 5300013.3503 | 4448228.1508 | 6770864.7254 | 5129320.517
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary deliverables target)
LV Network |  | 129357.6399 | -25807.0112 | 193234.0352 | -59642.5433
HV Network |  | 1040219.5528 | -538730.7849 | 1898624.3455 | -1171389.7323
EHV Network |  | 377016.9192 | -254772.6537 | 888261.2685 | -394261.8452
132kV Network |  | 145816.2975 | -32474.7497 | 183142.1353 | -16250.0876
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 1692410.4094 | -851785.1995 | 3163261.7845 | -1641544.2084