## ENWL - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
ENWL | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 3251 | 3251 | C1 | 365 | 1078 | 581 | 295 | 932 | 3251 | 228 | 1082 | 597 | 295 | 1019 | 3221 | 179.9037 | 333.9413 | -25.8058 | 0 | -488.0391 | 0 | 325 | 750 | 949 | 211 | 1017 | 3252 | 359.8073 | 667.8826 | -51.6117 | 0 | -976.0782 | 0 | 216 | 696 | 981 | 132 | 1227 | 3252 | Yes |  | C1 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C1 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | C1 | 10.03 | 17.3692 | 18.0526 | 30.8232 | 94.9612 | C1 | 2286.8431 | 18793.4975 | 10777.4025 | 9092.8586 | 96765.4981 | 137716.0998 |  | 3660.9549 | 18724.0206 | 10488.5609 | 9092.8586 | 88503.8707 | 130470.2657 |  | 3259.7544 | 13026.916 | 17131.9179 | 6503.7056 | 96575.5757 | 136497.8695 |  | 5064.1904 | 18827.2165 | 16666.0552 | 6503.7056 | 50230.7791 | 97291.9468 |  | 2166.4829 | 12088.978 | 17709.6011 | 4068.6689 | 116517.4349 | 152551.1659 |  | 5775.355 | 23689.579 | 16777.8758 | 4068.6689 | 23827.8418 | 74139.3205
|  |  | 9179 | 9179 | C2 | 1032 | 3044 | 1640 | 833 | 2630 | 9179 | 642 | 3055 | 1684 | 834 | 2878 | 9093 | 507.8643 | 942.7094 | -72.8494 | 0 | -1377.7243 | 0 | 918 | 2118 | 2678 | 594 | 2870 | 9178 | 1015.7286 | 1885.4188 | -145.6987 | 0 | -2755.4486 | 0 | 610 | 1964 | 2769 | 371 | 3462 | 9176 | No |  | C2 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C2 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | C2 | 14.3286 | 24.8132 | 25.7894 | 44.0332 | 135.6589 | C2 | 9198.9552 | 75804.2445 | 43429.399 | 36723.6999 | 390426.3334 | 555582.632 |  | 14787.1056 | 75531.2996 | 42294.6641 | 36679.6667 | 356782.9245 | 526075.6605 |  | 13153.6462 | 52554.3011 | 69064.0918 | 26155.7287 | 389341.0621 | 550268.83 |  | 20430.6257 | 75945.9127 | 67185.348 | 26155.7287 | 202440.4892 | 392158.1043 |  | 8740.4403 | 48733.0724 | 71410.9298 | 16336.3221 | 469651.1349 | 614871.8996 |  | 23294.3992 | 95516.2957 | 67653.4423 | 16336.3221 | 95849.989 | 298650.4483
|  |  | 3561 | 3561 | C3 | 400 | 1181 | 637 | 323 | 1020 | 3561 | 249 | 1185 | 653 | 324 | 1116 | 3527 | 197.0287 | 365.7293 | -28.2623 | 0 | -534.4957 | 0 | 356 | 822 | 1039 | 231 | 1113 | 3561 | 394.0575 | 731.4586 | -56.5246 | 0 | -1068.9915 | 0 | 237 | 762 | 1075 | 144 | 1344 | 3562 |  |  | C3 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C3 | 15254 | 15254 | 15254 | 15254 | 15254 | C3 | 21.4929 | 37.2198 | 38.6841 | 66.0498 | 203.4884 | C3 | 5351.7286 | 44105.4156 | 25260.746 | 21400.1417 | 227093.0098 | 323211.0417 |  | 8597.1544 | 43956.5366 | 24641.7997 | 21334.0919 | 207558.1272 | 306087.7097 |  | 7651.4674 | 30594.6427 | 40192.8256 | 15257.5084 | 226482.5447 | 320178.9889 |  | 11886.1839 | 44206.9998 | 39099.5221 | 15257.5084 | 117718.8831 | 228169.0972 |  | 5093.814 | 28361.4571 | 41585.4548 | 9511.1741 | 273488.3558 | 358040.2558 |  | 13563.2469 | 55586.1712 | 39398.8478 | 9511.1741 | 55961.0326 | 174020.4726
|  |  | 781 | 781 | C4 | 88 | 258 | 140 | 71 | 224 | 781 | 55 | 260 | 143 | 71 | 245 | 774 | 43.2033 | 80.195 | -6.1972 | 0 | -117.2011 | 0 | 78 | 180 | 228 | 51 | 244 | 781 | 86.4066 | 160.39 | -12.3944 | 0 | -234.4022 | 0 | 52 | 167 | 236 | 32 | 295 | 782 |  |  | C4 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C4 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | C4 | 35.8215 | 62.0329 | 64.4736 | 110.083 | 339.1473 | C4 | 1970.1812 | 16128.5627 | 9219.721 | 7815.8954 | 83091.0803 | 118225.4406 |  | 3152.2899 | 16004.4968 | 9026.3003 | 7815.8954 | 75968.9877 | 111967.9701 |  | 2794.0752 | 11165.928 | 14699.9747 | 5614.2347 | 82751.9331 | 117026.1457 |  | 4341.6817 | 16140.6585 | 14300.4194 | 5614.2347 | 43003.4972 | 83400.4915 |  | 1862.7168 | 10359.4999 | 15215.7633 | 3522.6571 | 100048.4437 | 131009.0807 |  | 4957.9299 | 20308.9608 | 14416.6526 | 3522.6571 | 20551.572 | 63757.7723
|  |  | 16772 | 16772 |  | 1885 | 5561 | 2998 | 1522 | 4806 |  | 1174 | 5582 | 3077 | 1524 | 5258 |  | 928 | 1722.575 | -133.1147 | 0 | -2517.4603 |  | 1677 | 3870 | 4894 | 1087 | 5244 |  | 1856 | 3445.15 | -266.2295 | 0 | -5034.9205 |  | 1115 | 3589 | 5061 | 679 | 6328 | [22 empty] | 18807.7081 | 154831.7203 | 88687.2685 | 75032.5955 | 797375.9216 | 1134735.2141 |  | 30197.5048 | 154216.3536 | 86451.325 | 74922.5125 | 728813.9102 | 1074601.6061 |  | 26858.9432 | 107341.7878 | 141088.81 | 53531.1774 | 795151.1155 | 1123971.834 |  | 41722.6817 | 155120.7875 | 137251.3447 | 53531.1774 | 413393.6486 | 801019.6398 |  | 17863.454 | 99543.0075 | 145921.7491 | 33438.8222 | 959705.3693 | 1256472.402 |  | 47590.9309 | 195101.0067 | 138246.8184 | 33438.8222 | 196190.4354 | 610568.0137
| LV UGB |  | 1539 | 1539 | C1 | 860 | 217 | 86 | 115 | 261 | 1539 | 817 | 217 | 86 | 115 | 302 | 1537 | 67.0845 | 0 | 0 | 0 | -67.0845 | 0 | 860 | 188 | 111 | 35 | 345 | 1539 | 134.169 | 0 | 0 | 0 | -134.169 | 0 | 658 | 379 | 44 | 77 | 380 | 1538 |  |  | C1 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C1 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | C1 | 5.8409 | 5.8409 | 10.1144 | 21.2659 | 48.5832 | C1 | 4772.0163 | 1267.4756 | 869.8342 | 2445.5752 | 14672.1255 | 24027.0268 |  | 5023.1751 | 1267.4756 | 869.8342 | 2445.5752 | 12680.2145 | 22286.2745 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 5415.0091 | 1098.0894 | 1122.693 | 744.3055 | 13502.0228 | 21882.1198 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133 |  | 4626.9811 | 2213.7016 | 445.0314 | 1637.4721 | 11943.2545 | 20866.4407
|  |  | 10442 | 10442 | C2 | 5837 | 1470 | 580 | 784 | 1771 | 10442 | 5541 | 1470 | 580 | 784 | 2051 | 10426 | 455.242 | 0 | 0 | 0 | -455.242 | 0 | 5837 | 1273 | 749 | 237 | 2344 | 10440 | 910.484 | 0 | 0 | 0 | -910.484 | 0 | 4465 | 2572 | 299 | 524 | 2580 | 10440 |  |  | C2 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C2 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | C2 | 8.3441 | 8.3441 | 14.4491 | 30.3798 | 69.4046 | C2 | 46234.9053 | 12265.8926 | 8380.4623 | 23817.7759 | 142348.7677 | 233047.8039 |  | 48704.7721 | 12265.8926 | 8380.4623 | 23817.7759 | 122915.4889 | 216084.3918 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 52503.377 | 10622.0961 | 10822.3556 | 7200.0165 | 131088.4336 | 212236.2787 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261 |  | 44853.8155 | 21461.14 | 4320.2728 | 15919.0237 | 115872.0391 | 202426.2911
|  |  | 8109 | 8109 | C3 | 4534 | 1142 | 451 | 608 | 1374 | 8109 | 4305 | 1142 | 451 | 608 | 1593 | 8099 | 353.6735 | 0 | 0 | 0 | -353.6735 | 0 | 4534 | 990 | 583 | 184 | 1820 | 8111 | 707.347 | 0 | 0 | 0 | -707.347 | 0 | 3469 | 1998 | 233 | 407 | 2005 | 8112 |  |  | C3 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C3 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | C3 | 12.5162 | 12.5162 | 21.6736 | 45.5697 | 104.1069 | C3 | 53882.3139 | 14293.5197 | 9774.7978 | 27706.3924 | 165842.2138 | 271499.2376 |  | 56748.5276 | 14293.5197 | 9774.7978 | 27706.3924 | 143042.8134 | 251566.0509 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 61175.1819 | 12391.0548 | 12635.7142 | 8384.8293 | 152654.6337 | 247241.4138 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232 |  | 52272.0653 | 25007.4014 | 5049.951 | 18546.8778 | 135094.5658 | 235970.8612
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C4 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | C4 | 20.8604 | 20.8604 | 36.1227 | 75.9495 | 173.5114 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20090 | 20090 |  | 11231 | 2829 | 1117 | 1507 | 3406 |  | 10663 | 2829 | 1117 | 1507 | 3946 |  | 876 | 0 | 0 | 0 | -876 |  | 11231 | 2451 | 1443 | 456 | 4509 |  | 1752 | 0 | 0 | 0 | -1752 |  | 8592 | 4949 | 576 | 1008 | 4965 | [22 empty] | 104889.2355 | 27826.8879 | 19025.0942 | 53969.7436 | 322863.1071 | 528574.0683 |  | 110476.4748 | 27826.8879 | 19025.0942 | 53969.7436 | 278638.5167 | 489936.7172 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 119093.568 | 24111.2403 | 24580.7627 | 16329.1512 | 297245.09 | 481359.8124 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823 |  | 101752.8618 | 48682.243 | 9815.2552 | 36103.3736 | 262909.8593 | 459263.5929
| LV OHL Support |  | 28539 | 28539 | C1 | 3308 | 4632 | 13014 | 4744 | 2841 | 28539 | 657 | 4886 | 13689 | 5431 | 3966 | 28629 | 1074.7295 | 0 | 0 | -322.4189 | -752.3107 | 0 | 3150 | 4107 | 12747 | 4305 | 4229 | 28538 | 2009.4448 | 0 | 0 | -602.8334 | -1406.6114 | 0 | 3052 | 3425 | 13256 | 3830 | 4976 | 28539 |  |  | C1 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C1 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | C1 | 12.4899 | 12.6968 | 21.5987 | 42.1194 | 71.1283 | C1 | 8205.8724 | 62036.6 | 295664.9903 | 228750.6004 | 282094.657 | 876752.7201 |  | 41316.6302 | 58811.611 | 281085.8488 | 199814.555 | 202075.3708 | 783104.0158 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 52766.5014 | 52145.7872 | 275318.9884 | 167744.0304 | 247290.8445 | 795266.1518 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123 |  | 63217.0025 | 43486.5647 | 286312.741 | 135926.4015 | 253884.3819 | 782827.0916
|  |  | 9423 | 9423 | C2 | 1092 | 1530 | 4297 | 1566 | 938 | 9423 | 216 | 1613 | 4520 | 1794 | 1309 | 9452 | 354.8824 | 0 | 0 | -106.4647 | -248.4177 | 0 | 1040 | 1356 | 4209 | 1422 | 1397 | 9424 | 663.5312 | 0 | 0 | -199.0594 | -464.4719 | 0 | 1008 | 1131 | 4377 | 1264 | 1643 | 9423 |  |  | C2 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C2 | 7778 | 7778 | 7778 | 7778 | 7778 | C2 | 17.8427 | 18.1383 | 30.8553 | 60.1706 | 101.6118 | C2 | 3854.0301 | 29257.0714 | 139466.0735 | 107946.0708 | 133009.8357 | 413533.0816 |  | 19484.2633 | 27751.5929 | 132585.3358 | 94227.1721 | 95311.8609 | 369360.2251 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 24888.5127 | 24595.5294 | 129870.0671 | 79156.5578 | 116709.5083 | 375220.1753 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713 |  | 29824.6838 | 20514.4128 | 135053.7619 | 64078.1253 | 119752.3561 | 369223.3398
|  |  | 21147 | 21147 | C3 | 2451 | 3433 | 9643 | 3515 | 2105 | 21147 | 487 | 3621 | 10144 | 4025 | 2939 | 21216 | 796.3881 | 0 | 0 | -238.9164 | -557.4717 | 0 | 2334 | 3043 | 9445 | 3191 | 3134 | 21147 | 1489.0239 | 0 | 0 | -446.7072 | -1042.3168 | 0 | 2262 | 2538 | 9823 | 2837 | 3687 | 21147 |  |  | C3 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C3 | 11667 | 11667 | 11667 | 11667 | 11667 | C3 | 26.7641 | 27.2074 | 46.283 | 90.2559 | 152.4177 | C3 | 13034.1157 | 98518.1547 | 469494.6404 | 363280.0458 | 447955.585 | 1392282.5417 |  | 65598.8042 | 93403.1553 | 446306.8629 | 317249.5307 | 320839.2332 | 1243397.5863 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 83782.0141 | 82792.2521 | 437142.8311 | 266442.9947 | 392708.4905 | 1262868.5825 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215 |  | 100392.7724 | 69052.4929 | 454637.8009 | 215738.0581 | 403096.5049 | 1242917.6293
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C4 | 19445 | 19445 | 19445 | 19445 | 19445 | C4 | 44.6068 | 45.3457 | 77.1383 | 150.4265 | 254.0295 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 59109 | 59109 |  | 6851 | 9595 | 26954 | 9825 | 5884 |  | 1360 | 10120 | 28353 | 11250 | 8214 |  | 2226 | 0 | 0 | -667.8 | -1558.2 |  | 6524 | 8506 | 26401 | 8918 | 8760 |  | 4162 | 0 | 0 | -1248.6 | -2913.4 |  | 6322 | 7094 | 27456 | 7931 | 10306 | [22 empty] | 25094.0183 | 189811.8262 | 904625.7043 | 699976.717 | 863060.0777 | 2682568.3434 |  | 126399.6978 | 179966.3591 | 859978.0475 | 611291.2579 | 618226.4649 | 2395861.8271 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 161437.0281 | 159533.5686 | 842331.8866 | 513343.5829 | 756708.8433 | 2433354.9096 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051 |  | 193434.4587 | 133053.4703 | 876004.3039 | 415742.5849 | 776733.2429 | 2394968.0607
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 |  | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 |  | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 |  | 322253.2779 | 338765.5964 | 1004163.994 | 583203.9116 | 1467347.5819 | 3715734.3618 |  | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 |  | 342778.2514 | 376836.72 | 1024066.3775 | 485284.7807 | 1235833.5377 | 3464799.6673
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1899 | 1899 | C1 | 312 | 461 | 253 | 229 | 644 | 1899 | 239 | 463 | 254 | 233 | 678 | 1867 | 172.718 | 25.3737 | -5.3221 | -16.131 | -176.6385 | 0 | 161 | 561 | 185 | 129 | 864 | 1900 | 350.2899 | 50.5097 | -10.7939 | -32.7154 | -357.2903 | 0 | 106 | 578 | 142 | 93 | 981 | 1900 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C1 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | C1 | 6.1027 | 79.5042 | 139.3443 | 269.1109 | 467.1086 | C1 | 1458.5385 | 36810.4663 | 35393.4599 | 62702.8297 | 316699.658 | 453064.9523 |  | 1904.0335 | 36651.4578 | 35254.1156 | 61626.3862 | 300817.9642 | 436253.9573 |  | 982.5301 | 44601.8825 | 25778.7011 | 34715.3005 | 403581.865 | 509660.2792 |  | 2036.5712 | 46619.2011 | 25037.0897 | 30374.267 | 321072.4774 | 425139.6065 |  | 646.8832 | 45953.4547 | 19786.8949 | 25027.3097 | 458233.5759 | 549648.1184 |  | 2784.5872 | 49969.1873 | 18282.8306 | 16223.2465 | 291340.1905 | 378600.0421
|  |  | 451 | 451 | C2 | 74 | 110 | 60 | 54 | 153 | 451 | 57 | 110 | 60 | 55 | 161 | 443 | 41.0292 | 13.668 | -1.2643 | -3.8319 | -49.601 | 0 | 38 | 133 | 44 | 31 | 205 | 451 | 83.2114 | 27.2795 | -2.5641 | -7.7715 | -100.1552 | 0 | 25 | 137 | 34 | 22 | 233 | 451 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C2 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | C2 | 8.7181 | 113.5775 | 199.0633 | 384.4441 | 667.2981 | C2 | 496.9318 | 12493.5245 | 11943.7997 | 21144.4245 | 107434.9872 | 153513.6677 |  | 645.1395 | 12493.5245 | 11943.7997 | 20759.9804 | 102096.6028 | 147939.0469 |  | 331.2879 | 15105.8069 | 8758.7865 | 11917.7665 | 136796.1017 | 172909.7495 |  | 688.9844 | 16658.182 | 8507.1153 | 10444.6053 | 103697.4832 | 139996.3701 |  | 217.9526 | 15560.1169 | 6768.1532 | 8457.7698 | 155480.4473 | 186484.4397 |  | 943.3979 | 18658.4516 | 6257.738 | 5470.047 | 88647.0477 | 119976.6822
|  |  | 2347 | 2347 | C3 | 386 | 569 | 313 | 283 | 796 | 2347 | 295 | 572 | 315 | 288 | 838 | 2308 | 213.2528 | 71.0406 | -6.5712 | -19.9168 | -257.8054 | 0 | 200 | 692 | 228 | 160 | 1066 | 2346 | 432.4987 | 141.7875 | -13.3271 | -40.3933 | -520.5659 | 0 | 132 | 713 | 174 | 116 | 1211 | 2346 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C3 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | C3 | 13.0772 | 170.3662 | 298.595 | 576.6661 | 1000.9471 | C3 | 3857.7601 | 97449.4911 | 94057.423 | 166079.8431 | 838793.658 | 1200238.1753 |  | 5047.7811 | 96938.3924 | 93460.233 | 163196.5125 | 796753.8804 | 1155396.7993 |  | 2615.4306 | 117893.4403 | 68079.6585 | 92266.5795 | 1067009.5935 | 1347864.7025 |  | 5404.1706 | 129996.3548 | 66117.5328 | 80781.2464 | 808960.0023 | 1091259.3068 |  | 1726.1842 | 121471.1314 | 51955.5289 | 66893.2701 | 1212146.921 | 1454193.0356 |  | 7382.0362 | 145626.9434 | 47976.1357 | 43599.8311 | 691087.9701 | 935672.9164
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C4 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | C4 | 21.7953 | 283.9437 | 497.6583 | 961.1102 | 1668.2451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4697 | 4697 |  | 772 | 1140 | 626 | 566 | 1593 |  | 591 | 1145 | 629 | 576 | 1677 |  | 427 | 110.0823 | -13.1576 | -39.8797 | -484.0449 |  | 399 | 1386 | 457 | 320 | 2135 |  | 866 | 219.5767 | -26.685 | -80.8802 | -978.0115 |  | 263 | 1428 | 350 | 231 | 2425 | [22 empty] | 5813.2304 | 146753.4819 | 141394.6826 | 249927.0972 | 1262928.3032 | 1806816.7953 |  | 7596.9541 | 146083.3747 | 140658.1483 | 245582.8791 | 1199668.4473 | 1739589.8035 |  | 3929.2486 | 177601.1297 | 102617.1461 | 138899.6466 | 1607387.5603 | 2030434.7312 |  | 8129.7262 | 193273.7379 | 99661.7378 | 121600.1187 | 1233729.9628 | 1656395.2834 |  | 2591.0199 | 182984.703 | 78510.577 | 100378.3496 | 1825860.9442 | 2190325.5937 |  | 11110.0214 | 214254.5822 | 72516.7043 | 65293.1245 | 1071075.2083 | 1434249.6407
| HV Switchgear (GM) - Distribution |  | 12 | 11.2924 | C1 | 1 | 6 | 3 | 1 | 1 | 12 | 1 | 6 | 3 | 1 | 1 | 12 | 1.2526 | -0.064586 | -0.21955 | -0.26213 | -1.0601 | -0.35381 | 1 | 5 | 3 | 1 | 2 | 12 | 2.4988 | -0.12892 | -0.43823 | -0.52323 | -2.1161 | -0.70762 | 1 | 5 | 2 | 1 | 3 | 12 |  |  | C1 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C1 | 22715 | 22715 | 22715 | 22715 | 22715 | C1 | 19.285 | 19.285 | 33.3683 | 65.6463 | 121.5252 | C1 | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 43.4407 | 95.1796 | 92.7791 | 48.4385 | 114.2204 | 394.0583 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669 |  | 67.4745 | 93.939 | 52.1138 | 31.2984 | 107.4222 | 352.2477
|  |  | 28964 | 27263.1656 | C2 | 2639 | 14945 | 6789 | 1775 | 2816 | 28964 | 1310 | 15230 | 7011 | 1941 | 3415 | 28907 | 3010.6287 | -155.2379 | -527.6952 | -630.0499 | -2548.0628 | -850.4172 | 2555 | 13020 | 6152 | 2634 | 4601 | 28962 | 6006.0714 | -309.8653 | -1053.315 | -1257.6217 | -5086.1038 | -1700.8344 | 2437 | 11427 | 5340 | 2529 | 7229 | 28962 |  |  | C2 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C2 | 32450 | 32450 | 32450 | 32450 | 32450 | C2 | 27.55 | 27.55 | 47.669 | 93.7805 | 173.6075 | C2 | 36090.5655 | 419587.2615 | 334207.7095 | 182027.9505 | 592869.6125 | 1564783.0995 |  | 72704.5819 | 411735.4972 | 323625.1804 | 166460.3875 | 488878.72 | 1463404.3671 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 153333.3494 | 354424.8383 | 268105.2654 | 187931.4418 | 356405.2876 | 1320200.1824 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222 |  | 232607.0394 | 306277.6173 | 204342.2036 | 119230.4889 | 372022.8511 | 1234480.2003
|  |  | 1505 | 1416.6059 | C3 | 137 | 777 | 353 | 92 | 146 | 1505 | 68 | 792 | 364 | 101 | 177 | 1502 | 156.4654 | -8.0679 | -27.4249 | -32.7443 | -132.4254 | -44.197 | 133 | 677 | 320 | 137 | 239 | 1506 | 312.1416 | -16.104 | -54.7418 | -65.3599 | -264.33 | -88.3941 | 127 | 594 | 278 | 131 | 376 | 1506 |  |  | C3 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C3 | 48675 | 48675 | 48675 | 48675 | 48675 | C3 | 41.3251 | 41.3251 | 71.5036 | 140.6707 | 260.4112 | C3 | 2810.1051 | 32729.4594 | 26027.3013 | 14207.7458 | 46092.7912 | 121867.4028 |  | 5661.5353 | 32109.5833 | 25240.762 | 12941.709 | 38020.0425 | 113973.632 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 11962.1807 | 27643.6703 | 20920.1687 | 14665.7228 | 27753.2213 | 102944.9638 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712 |  | 18147.5608 | 23881.595 | 15963.756 | 9233.6451 | 29080.1296 | 96306.6864
|  |  | 34 | 31.9361 | C4 | 3 | 18 | 8 | 2 | 3 | 34 | 2 | 18 | 9 | 2 | 4 | 35 | 3.6533 | -0.18838 | -0.64034 | -0.76454 | -3.092 | -1.032 | 3 | 16 | 7 | 3 | 6 | 35 | 7.2882 | -0.37601 | -1.2782 | -1.5261 | -6.1718 | -2.0639 | 3 | 14 | 6 | 3 | 9 | 35 |  |  | C4 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C4 | 81125 | 81125 | 81125 | 81125 | 81125 | C4 | 68.8751 | 68.8751 | 119.1726 | 234.4512 | 434.0187 | C4 | 137.7502 | 1239.7523 | 1072.5536 | 468.9025 | 1736.075 | 4655.0336 |  | 206.6254 | 1239.7523 | 953.381 | 468.9025 | 1302.0562 | 4170.7174 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 458.2466 | 1089.0276 | 757.8973 | 524.1054 | 1262.1319 | 4091.4088 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354 |  | 708.5985 | 938.3539 | 562.7138 | 345.5621 | 1227.4857 | 3782.7142
|  |  | 30515 | 28723 |  | 2780 | 15746 | 7153 | 1870 | 2966 |  | 1381 | 16046 | 7387 | 2045 | 3597 |  | 3172 | -163.5588 | -555.98 | -663.8209 | -2684.6404 |  | 2692 | 13718 | 6482 | 2775 | 4848 |  | 6328 | -326.4742 | -1109.7732 | -1325.0309 | -5358.7216 |  | 2568 | 12040 | 5626 | 2664 | 7617 | [22 empty] | 39057.7059 | 453672.1834 | 361407.6695 | 196770.2451 | 640820.004 | 1691727.8078 |  | 78592.0276 | 445200.543 | 349919.4284 | 179936.6453 | 528322.344 | 1581970.9884 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 165797.2173 | 383252.7159 | 289876.1106 | 203169.7085 | 385534.8612 | 1427630.6134 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977 |  | 251530.6732 | 331191.5052 | 220920.7872 | 128840.9944 | 402437.8886 | 1334921.8487
| HV Transformer (GM) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C1 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | C1 | 17.5777 | 17.5777 | 30.3869 | 59.8934 | 168.7346 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14545 | 14541.5442 | C2 | 4823 | 6506 | 2560 | 334 | 322 | 14545 | 4284 | 6630 | 2571 | 336 | 588 | 14409 | 307.5687 | -68.3015 | 0 | 0 | -242.7231 | -3.4558 | 4178 | 6111 | 3001 | 644 | 613 | 14547 | 1216.4515 | -267.8935 | 0 | 0 | -952.0139 | -3.4558 | 3436 | 5557 | 3195 | 1197 | 1161 | 14546 |  |  | C2 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C2 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | C2 | 25.1111 | 25.1111 | 43.4099 | 85.5621 | 241.0494 | C2 | 107575.7912 | 166486.3434 | 111606.7455 | 28748.8546 | 141737.0648 | 556154.7995 |  | 121110.6538 | 163372.5717 | 111129.237 | 28577.7305 | 77617.9165 | 501808.1094 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 112637.3957 | 151738.5798 | 130272.9845 | 55101.9713 | 89255.0407 | 539005.972 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635 |  | 116828.0009 | 132815.0827 | 138694.497 | 102417.7945 | 50375.9911 | 541131.3661
|  |  | 2292 | 2291.4558 | C3 | 760 | 1025 | 403 | 53 | 51 | 2292 | 675 | 1044 | 405 | 53 | 93 | 2270 | 48.4313 | -10.7551 | 0 | 0 | -38.2204 | -0.54417 | 658 | 962 | 473 | 101 | 96 | 2290 | 191.5485 | -42.1838 | 0 | 0 | -149.9088 | -0.54417 | 541 | 875 | 503 | 189 | 183 | 2291 |  |  | C3 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C3 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | C3 | 37.6666 | 37.6666 | 65.1148 | 128.3431 | 361.5741 | C3 | 25424.9506 | 39323.9237 | 26371.4889 | 6802.1843 | 33626.3955 | 131548.943 |  | 28626.6111 | 38608.2584 | 26241.2593 | 6802.1843 | 18440.2814 | 118718.5945 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 26608.8601 | 35830.1556 | 30799.2944 | 12962.6532 | 20891.6197 | 127092.5829 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491 |  | 27592.6048 | 31369.348 | 32752.738 | 24256.8461 | 11964.9254 | 127936.4623
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C4 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | C4 | 62.7777 | 62.7777 | 108.5246 | 213.9052 | 602.6236 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 16837 | 16833 |  | 5583 | 7531 | 2963 | 387 | 373 |  | 4959 | 7674 | 2976 | 389 | 681 |  | 356 | -79.0565 | 0 | 0 | -280.9435 |  | 4836 | 7073 | 3474 | 745 | 709 |  | 1408 | -310.0774 | 0 | 0 | -1101.9226 |  | 3977 | 6432 | 3698 | 1386 | 1344 | [22 empty] | 133000.7418 | 205810.2671 | 137978.2344 | 35551.0389 | 175363.4603 | 687703.7425 |  | 149737.2649 | 201980.8301 | 137370.4963 | 35379.9148 | 96058.1979 | 620526.7039 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 139246.2558 | 187568.7353 | 161072.2789 | 68064.6245 | 110146.6604 | 666098.5549 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126 |  | 144420.6058 | 164184.4307 | 171447.235 | 126674.6405 | 62340.9164 | 669067.8285
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 3628 | 3628 | C1 | 204 | 1790 | 1305 | 281 | 48 | 3628 | 44 | 1814 | 1321 | 320 | 128 | 3627 | 23.3161 | 0 | 0 | -6.9948 | -16.3213 | 0 | 192 | 1677 | 1326 | 316 | 117 | 3628 | 46.6323 | 0 | 0 | -13.9897 | -32.6426 | 0 | 185 | 1663 | 1340 | 304 | 137 | 3629 |  |  | C1 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C1 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | C1 | 27.1392 | 27.1879 | 46.931 | 91.5265 | 143.007 | C1 | 1194.1258 | 49318.8161 | 61995.8864 | 29288.4641 | 18304.9008 | 160102.1933 |  | 5536.4014 | 48666.307 | 61244.99 | 25718.9326 | 6864.3378 | 148030.9687 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5843.5125 | 45594.0764 | 62230.5415 | 28282.1454 | 14397.7634 | 156348.0393 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833 |  | 6286.3198 | 45213.4461 | 62887.5759 | 26543.6151 | 14923.8441 | 155854.801
|  |  | 75099 | 75099 | C2 | 4224 | 37056 | 27000 | 5822 | 997 | 75099 | 902 | 37540 | 27350 | 6618 | 2653 | 75063 | 482.6015 | 0 | 0 | -144.7805 | -337.8211 | 0 | 3970 | 34721 | 27449 | 6541 | 2419 | 75100 | 965.2031 | 0 | 0 | -289.5609 | -675.6421 | 0 | 3829 | 34431 | 27726 | 6284 | 2830 | 75100 |  |  | C2 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C2 | 17378 | 17378 | 17378 | 17378 | 17378 | C2 | 38.7703 | 38.8398 | 67.0443 | 130.7521 | 204.2958 | C2 | 34970.8268 | 1458047.2182 | 1833662.2614 | 865317.2125 | 541996.6725 | 4733994.1914 |  | 163765.8232 | 1439248.7405 | 1810196.748 | 761238.5632 | 203682.8807 | 4378132.7556 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 172628.7774 | 1348557.7374 | 1840299.6495 | 836318.9578 | 425176.047 | 4622981.1691 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055 |  | 185872.7776 | 1337294.1867 | 1858870.9272 | 783785.3301 | 440126.1918 | 4605949.4134
|  |  | 20166 | 20166 | C3 | 1134 | 9950 | 7251 | 1563 | 268 | 20166 | 242 | 10080 | 7344 | 1777 | 712 | 20155 | 129.5903 | 0 | 0 | -38.8771 | -90.7132 | 0 | 1066 | 9323 | 7371 | 1757 | 649 | 20166 | 259.1805 | 0 | 0 | -77.7542 | -181.4264 | 0 | 1028 | 9245 | 7445 | 1687 | 760 | 20165 |  |  | C3 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C3 | 26067 | 26067 | 26067 | 26067 | 26067 | C3 | 58.1555 | 58.2597 | 100.5665 | 196.1281 | 306.4437 | C3 | 14073.6254 | 587258.2296 | 738560.2732 | 348519.6479 | 218187.8802 | 1906599.6564 |  | 65948.3109 | 579684.4628 | 729207.59 | 306548.2328 | 82126.8987 | 1763515.4952 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 69530.1217 | 543155.6026 | 741275.5683 | 336972.1981 | 171083.4519 | 1862016.9427 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549 |  | 74856.5969 | 538611.3425 | 748717.4883 | 315618.343 | 177300.2189 | 1855103.9895
|  |  | 77 | 77 | C4 | 4 | 38 | 28 | 6 | 1 | 77 | 1 | 38 | 28 | 7 | 3 | 77 | 0.49207 | 0 | 0 | -0.14762 | -0.34445 | 0 | 4 | 35 | 28 | 7 | 2 | 76 | 0.98414 | 0 | 0 | -0.29524 | -0.6889 | 0 | 4 | 35 | 28 | 6 | 3 | 76 |  |  | C4 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C4 | 43445 | 43445 | 43445 | 43445 | 43445 | C4 | 96.9258 | 97.0996 | 167.6108 | 326.8802 | 510.7394 | C4 | 96.9258 | 3689.7839 | 4693.1027 | 2288.1613 | 1532.2183 | 12300.1918 |  | 387.7032 | 3689.7839 | 4693.1027 | 1961.2811 | 510.7394 | 11242.6102 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 435.3977 | 3398.4851 | 4693.1027 | 2239.9067 | 845.5544 | 11612.4465 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903 |  | 483.0922 | 3398.4851 | 4693.1027 | 1864.7719 | 1180.3693 | 11619.8211
|  |  | 98970 | 98970 |  | 5566 | 48834 | 35584 | 7672 | 1314 |  | 1189 | 49472 | 36043 | 8722 | 3496 |  | 636 | 0 | 0 | -190.8 | -445.2 |  | 5232 | 45756 | 36174 | 8621 | 3187 |  | 1272 | 0 | 0 | -381.6 | -890.4 |  | 5046 | 45374 | 36539 | 8281 | 3730 | [22 empty] | 50335.5039 | 2098314.0478 | 2638911.5237 | 1245413.4858 | 780021.6718 | 6812996.2329 |  | 235638.2387 | 2071289.2941 | 2605342.4306 | 1095467.0096 | 293184.8567 | 6300921.8297 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 248437.8094 | 1940705.9016 | 2648498.862 | 1203813.208 | 611502.8166 | 6652958.5975 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339 |  | 267498.7863 | 1924517.4605 | 2675169.0941 | 1127812.06 | 633530.6242 | 6628528.0251
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 |  | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 |  | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 |  | 561611.0086 | 2704801.0907 | 3199108.9893 | 1596647.6597 | 2340914.3009 | 10403083.0492 |  | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 |  | 674560.0867 | 2634147.9786 | 3140053.8206 | 1448620.8195 | 2169384.6375 | 10066767.3429
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 937 | 937 | C1 | 215 | 458 | 214 | 23 | 27 | 937 | 174 | 460 | 214 | 24 | 45 | 917 | 17.3464 | 23.1285 | 0 | -1.9081 | -38.5668 | 0 | 184 | 319 | 345 | 45 | 41 | 934 | 36.2697 | 46.257 | 0 | -3.9897 | -78.5371 | 0 | 170 | 231 | 377 | 75 | 83 | 936 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C1 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | C1 | 4.7176 | 61.4602 | 105.2948 | 208.0341 | 361.0949 | C1 | 820.8667 | 28271.6771 | 22533.0796 | 4992.8196 | 16249.2689 | 72867.7119 |  | 1014.2893 | 28148.7567 | 22533.0796 | 4784.7854 | 9749.5614 | 66230.4725 |  | 868.043 | 19605.7934 | 36326.6938 | 9361.5367 | 14804.8895 | 80966.9564 |  | 949.8767 | 21027.2759 | 36326.6938 | 8964.5862 | 878.6157 | 68147.0484 |  | 801.9962 | 14197.2987 | 39696.1263 | 15602.5612 | 29970.8738 | 100268.8562 |  | 973.1031 | 17040.2637 | 39696.1263 | 14772.5738 | 1611.5367 | 74093.6036
|  |  | 333 | 333 | C2 | 77 | 163 | 76 | 8 | 9 | 333 | 62 | 164 | 77 | 9 | 16 | 328 | 6.1886 | 8.2515 | 0 | -0.68075 | -13.7594 | 0 | 66 | 114 | 123 | 17 | 15 | 335 | 12.9399 | 16.503 | 0 | -1.4234 | -28.0195 | 0 | 60 | 82 | 135 | 27 | 30 | 334 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C2 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | C2 | 6.7395 | 87.8002 | 150.4211 | 297.1916 | 515.8498 | C2 | 417.8468 | 14399.2393 | 11582.4241 | 2674.7248 | 8253.5969 | 37327.8318 |  | 518.9387 | 14311.439 | 11432.003 | 2377.5331 | 4642.6483 | 33282.5622 |  | 444.8046 | 10009.2273 | 18501.7944 | 5052.2579 | 7737.7471 | 41745.8313 |  | 486.5127 | 10733.7124 | 18501.7944 | 4849.9447 | 639.9611 | 35211.9252 |  | 404.3678 | 7199.6196 | 20306.8475 | 8024.1743 | 15475.4942 | 51410.5035 |  | 491.5757 | 8648.5899 | 20306.8475 | 7601.1557 | 1021.6273 | 38069.7961
|  |  | 294 | 294 | C3 | 68 | 144 | 67 | 7 | 8 | 294 | 55 | 144 | 67 | 8 | 14 | 288 | 5.4424 | 7.2565 | 0 | -0.59866 | -12.1002 | 0 | 58 | 100 | 108 | 15 | 13 | 294 | 11.3795 | 14.513 | 0 | -1.2517 | -24.6407 | 0 | 53 | 72 | 119 | 24 | 26 | 294 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C3 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | C3 | 10.1092 | 131.7004 | 225.6316 | 445.7875 | 773.7747 | C3 | 556.0058 | 18964.8517 | 15117.3198 | 3566.2997 | 10832.8459 | 49037.3229 |  | 687.4253 | 18964.8517 | 15117.3198 | 3120.5122 | 6190.1977 | 44080.3067 |  | 586.3334 | 13170.0359 | 24368.217 | 6686.8119 | 10059.0712 | 54870.4694 |  | 641.3513 | 14125.717 | 24368.217 | 6419.937 | 696.2564 | 46251.4786 |  | 535.7874 | 9482.4258 | 26850.165 | 10698.8991 | 20118.1425 | 67685.4198 |  | 650.8248 | 11393.7881 | 26850.165 | 10140.8878 | 1051.7916 | 50087.4573
|  |  | 217 | 217 | C4 | 50 | 106 | 50 | 5 | 6 | 217 | 40 | 107 | 50 | 6 | 10 | 213 | 4.0226 | 5.3635 | 0 | -0.44249 | -8.9436 | 0 | 43 | 74 | 80 | 11 | 10 | 218 | 8.4109 | 10.727 | 0 | -0.9252 | -18.2127 | 0 | 39 | 53 | 88 | 18 | 19 | 217 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C4 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | C4 | 16.8487 | 219.5006 | 376.0527 | 742.9791 | 1289.6245 | C4 | 673.9464 | 23486.564 | 18802.6365 | 4457.8746 | 12896.2452 | 60317.2668 |  | 842.433 | 23267.0634 | 18802.6365 | 3714.8955 | 7737.7471 | 54364.7756 |  | 724.4924 | 16243.0443 | 30084.2185 | 8172.7701 | 12896.2452 | 68120.7704 |  | 792.268 | 17420.3326 | 30084.2185 | 7844.0111 | 1362.3428 | 57503.1731 |  | 657.0977 | 11633.5317 | 33092.6403 | 13373.6239 | 24502.8658 | 83259.7595 |  | 798.8105 | 13988.1085 | 33092.6403 | 12686.2186 | 1015.3321 | 61581.11
|  |  | 1781 | 1781 |  | 410 | 871 | 407 | 43 | 50 |  | 331 | 875 | 408 | 47 | 85 |  | 33 | 44 | 0 | -3.63 | -73.37 |  | 351 | 607 | 656 | 88 | 79 |  | 69 | 88 | 0 | -7.59 | -149.41 |  | 322 | 438 | 719 | 144 | 158 | [22 empty] | 2468.6657 | 85122.332 | 68035.4601 | 15691.7187 | 48231.957 | 219550.1334 |  | 3063.0864 | 84692.1109 | 67885.039 | 13997.7263 | 28320.1544 | 197958.1169 |  | 2623.6733 | 59028.1009 | 109280.9236 | 29273.3767 | 45497.953 | 245704.0275 |  | 2870.0087 | 63307.0381 | 109280.9236 | 28078.4789 | 3577.176 | 207113.6253 |  | 2399.2492 | 42512.8759 | 119945.779 | 47699.2585 | 90067.3763 | 302624.5389 |  | 2914.3141 | 51070.7502 | 119945.779 | 45200.8359 | 4700.2877 | 223831.967
| EHV Transformer |  | 439 | 439 | C1 | 45 | 96 | 206 | 43 | 49 | 439 | 35 | 95 | 206 | 43 | 59 | 438 | 18.9226 | 16.6336 | 16.6336 | 0 | -52.1899 | 0 | 29 | 75 | 143 | 90 | 102 | 439 | 53.1055 | 33.2672 | 33.2672 | 0 | -119.6399 | 0 | 20 | 76 | 45 | 88 | 210 | 439 |  |  | C1 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C1 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | C1 | 267.4477 | 270.1797 | 467.4393 | 909.7131 | 1679.1834 | C1 | 9360.6698 | 25667.0727 | 96292.5028 | 39117.6645 | 99071.8178 | 269509.7276 |  | 12035.1469 | 25937.2524 | 96292.5028 | 39117.6645 | 82279.9842 | 255662.5509 |  | 7755.9835 | 20263.4785 | 66843.8247 | 81874.1816 | 171276.7019 | 348014.1703 |  | 12816.8014 | 24757.5437 | 74619.0305 | 81874.1816 | 83640.3353 | 277707.8925 |  | 5348.9542 | 20533.6582 | 21034.77 | 80054.7553 | 352628.5039 | 479600.6416 |  | 19551.8945 | 29521.7886 | 36585.1815 | 80054.7553 | 151731.1022 | 317444.7221
|  |  | 192 | 192 | C2 | 19 | 42 | 90 | 19 | 22 | 192 | 15 | 42 | 90 | 19 | 25 | 191 | 8.2405 | 7.2437 | 7.2437 | 0 | -22.7278 | 0 | 13 | 33 | 62 | 39 | 45 | 192 | 23.1266 | 14.4873 | 14.4873 | 0 | -52.1013 | 0 | 9 | 33 | 19 | 39 | 92 | 192 |  |  | C2 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C2 | 317306 | 317306 | 317306 | 317306 | 317306 | C2 | 382.0682 | 385.971 | 667.7705 | 1299.5902 | 2398.8334 | C2 | 5731.0223 | 16210.7828 | 60099.3429 | 24692.2135 | 59970.834 | 166704.1955 |  | 7259.2949 | 16210.7828 | 60099.3429 | 24692.2135 | 52774.3339 | 161035.9681 |  | 4966.886 | 12737.0436 | 41401.7696 | 50684.0172 | 107947.5012 | 217737.2176 |  | 8115.3211 | 15532.8906 | 46238.8791 | 50684.0172 | 53427.181 | 173998.289 |  | 3438.6134 | 12737.0436 | 12687.6391 | 50684.0172 | 220692.6691 | 300239.9824 |  | 12274.544 | 18328.7377 | 22361.8582 | 50684.0172 | 95710.4146 | 199359.5716
|  |  | 53 | 53 | C3 | 5 | 12 | 25 | 5 | 6 | 53 | 4 | 12 | 25 | 5 | 7 | 53 | 2.3108 | 2.0313 | 2.0313 | 0 | -6.3734 | 0 | 4 | 9 | 17 | 11 | 13 | 54 | 6.4852 | 4.0626 | 4.0626 | 0 | -14.6104 | 0 | 2 | 9 | 5 | 11 | 26 | 53 |  |  | C3 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C3 | 475959 | 475959 | 475959 | 475959 | 475959 | C3 | 573.1022 | 578.9565 | 1001.6557 | 1949.3853 | 3598.25 | C3 | 2292.4089 | 6947.4783 | 25041.3929 | 9746.9264 | 25187.7503 | 69215.9568 |  | 2865.5112 | 6947.4783 | 25041.3929 | 9746.9264 | 21589.5002 | 66190.809 |  | 2292.4089 | 5210.6087 | 17028.1472 | 21443.238 | 46777.2505 | 92751.6534 |  | 3616.7507 | 6386.6396 | 19062.8044 | 21443.238 | 23844.0999 | 74353.5326 |  | 1146.2045 | 5210.6087 | 5008.2786 | 21443.238 | 93554.501 | 126362.8309 |  | 4862.9054 | 7562.6705 | 9077.593 | 21443.238 | 40982.6003 | 83929.0073
|  |  | 36 | 36 | C4 | 4 | 8 | 17 | 3 | 4 | 36 | 3 | 8 | 17 | 3 | 5 | 36 | 1.526 | 1.3414 | 1.3414 | 0 | -4.2089 | 0 | 2 | 6 | 12 | 7 | 8 | 35 | 4.2827 | 2.6828 | 2.6828 | 0 | -9.6484 | 0 | 2 | 6 | 4 | 7 | 17 | 36 |  |  | C4 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C4 | 793265 | 793265 | 793265 | 793265 | 793265 | C4 | 955.1704 | 964.9275 | 1669.4262 | 3248.9755 | 5997.0834 | C4 | 2865.5112 | 7719.4204 | 28380.2453 | 9746.9264 | 29985.417 | 78697.5202 |  | 3820.6815 | 7719.4204 | 28380.2453 | 9746.9264 | 23988.3336 | 73655.6072 |  | 1910.3408 | 5789.5653 | 20033.1143 | 22742.8282 | 47976.6672 | 98452.5158 |  | 3367.9496 | 7083.9389 | 22272.5169 | 22742.8282 | 22735.7782 | 78203.0118 |  | 1910.3408 | 5789.5653 | 6677.7048 | 22742.8282 | 101950.4178 | 139070.8568 |  | 6001.0494 | 8378.3125 | 11156.5099 | 22742.8282 | 44088.2629 | 92366.963
|  |  | 720 | 720 |  | 73 | 158 | 338 | 70 | 81 |  | 57 | 157 | 338 | 70 | 96 |  | 31 | 27.25 | 27.25 | 0 | -85.5 |  | 48 | 123 | 234 | 147 | 168 |  | 87 | 54.5 | 54.5 | 0 | -196 |  | 33 | 124 | 73 | 145 | 345 | [22 empty] | 20249.6122 | 56544.7542 | 209813.4839 | 83303.7308 | 214215.819 | 584127.4001 |  | 25980.6345 | 56814.9339 | 209813.4839 | 83303.7308 | 180632.152 | 556544.9351 |  | 16925.6192 | 44000.6961 | 145306.8558 | 176744.2651 | 373978.1208 | 756955.557 |  | 27916.8227 | 53761.0129 | 162193.2309 | 176744.2651 | 183647.3944 | 604262.7259 |  | 11844.1128 | 44270.8758 | 45408.3924 | 174924.8388 | 768826.0919 | 1045274.3117 |  | 42690.3933 | 63791.5094 | 79181.1426 | 174924.8388 | 332512.38 | 693100.264
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | C1 | 87.4881 | 87.4881 | 262.4643 | 612.4167 | 874.881 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 211.0678 | C2 | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 | 227.0678 | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 | 234.2399 | 0 | 0 | 0 | -8.0372 | 0 | -8.0372 | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 | 227.0675 | 0 | 0 | 0 | -16 | 0 | -16 | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | 227.0675 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 124983 | 124983 | 124983 | 124983 | 124983 | C2 | 124.983 | 124.983 | 374.949 | 874.881 | 1249.83 | C2 | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 61957.3853 | 104042.3694 | 183553.1507 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 8492.1828 | 185361.3897 | 210455.7784
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | C3 | 187.4745 | 187.4745 | 562.4235 | 1312.3215 | 1874.745 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | C4 | 312.4575 | 312.4575 | 937.3725 | 2187.2025 | 3124.575 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 211.0678 |  | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 |  | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 |  | 0 | 0 | 0 | -8.0372 | 0 |  | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 |  | 0 | 0 | 0 | -16 | 0 |  | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | [22 empty] | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 61957.3853 | 104042.3694 | 183553.1507 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 8492.1828 | 185361.3897 | 210455.7784
| EHV UG Cable (Oil) |  | 17.0815 | 14.4653 | C1 | 1.6369 | 2.5218 | 2.8663 | 6.9395 | 3.1171 | 17.0815 | 1.63 | 2.5796 | 3.0569 | 8.8085 | 4.8454 | 20.9204 | 0 | 0 | 0 | -0.65712 | -0.65712 | -1.3142 | 0.0090919 | 3.5395 | 2.8444 | 5.6227 | 5.0659 | 17.0815 | 0 | 0 | 0 | -1.3081 | -1.3081 | -2.6163 | 0.0090919 | 2.2753 | 3.4238 | 1.729 | 9.6443 | 17.0815 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | C1 | 194.5762 | 194.5762 | 583.7286 | 1362.0334 | 1945.762 | C1 | 317.1507 | 501.9325 | 1784.4163 | 11997.4175 | 9428.0449 | 24028.9618 |  | 318.5082 | 490.6886 | 1673.1151 | 9451.7929 | 6065.0403 | 17999.1451 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 688.6955 | 1660.3527 | 6763.2526 | 8578.4252 | 17692.4951 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996 |  | 1.7691 | 442.7288 | 1998.557 | 573.2222 | 16220.1442 | 19236.4212
|  |  | 246.8 | 208.9989 | C2 | 23.651 | 36.4363 | 41.4126 | 100.2639 | 45.0362 | 246.8 | 23.5502 | 37.2712 | 44.1675 | 127.2676 | 70.0084 | 302.2649 | 0 | 0 | 0 | -9.4942 | -9.4942 | -18.9884 | 0.13136 | 51.1394 | 41.0967 | 81.2383 | 73.1937 | 246.7995 | 0 | 0 | 0 | -18.9005 | -18.9005 | -37.8011 | 0.13136 | 32.875 | 49.4679 | 24.9812 | 139.3439 | 246.7995 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 277966 | 277966 | 277966 | 277966 | 277966 | C2 | 277.966 | 277.966 | 833.898 | 1945.762 | 2779.66 | C2 | 6546.1447 | 10360.1311 | 36831.2217 | 247632.544 | 194599.4408 | 495969.4824 |  | 6574.1645 | 10128.0511 | 34533.9105 | 195089.612 | 125185.3879 | 371511.126 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 14215.0116 | 34270.4888 | 139596.8301 | 177062.8758 | 365181.7207 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146 |  | 36.5144 | 9138.1382 | 41251.1898 | 11831.5859 | 334791.6804 | 397049.1086
|  |  | 29.9197 | 25.337 | C3 | 2.8672 | 4.4172 | 5.0205 | 12.155 | 5.4598 | 29.9197 | 2.855 | 4.5184 | 5.3544 | 15.4287 | 8.4871 | 36.6437 | 0 | 0 | 0 | -1.151 | -1.151 | -2.302 | 0.015925 | 6.1996 | 4.9822 | 9.8485 | 8.8733 | 29.9196 | 0 | 0 | 0 | -2.2913 | -2.2913 | -4.5826 | 0.015925 | 3.9855 | 5.997 | 3.0285 | 16.8927 | 29.9196 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 416949 | 416949 | 416949 | 416949 | 416949 | C3 | 416.949 | 416.949 | 1250.847 | 2918.643 | 4169.49 | C3 | 1190.3873 | 1883.9438 | 6697.5938 | 45030.8766 | 35387.0427 | 90189.8443 |  | 1195.4826 | 1841.741 | 6279.838 | 35476.1782 | 22764.406 | 67557.6458 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 2584.9366 | 6231.936 | 25385.0626 | 32198.0964 | 66406.6716 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872 |  | 6.64 | 1661.7298 | 7501.3454 | 2151.5213 | 60880.3779 | 72201.6143
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 694915 | 694915 | 694915 | 694915 | 694915 | C4 | 694.915 | 694.915 | 2084.745 | 4864.405 | 6949.15 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293.8012 | 248.8012 |  | 28.1551 | 43.3753 | 49.2994 | 119.3584 | 53.613 |  | 28.0351 | 44.3692 | 52.5789 | 151.5048 | 83.3409 |  | 0 | 0 | 0 | -11.3023 | -11.3023 |  | 0.15638 | 60.8785 | 48.9233 | 96.7095 | 87.1329 |  | 0 | 0 | 0 | -22.5 | -22.5 |  | 0.15638 | 39.1358 | 58.8887 | 29.7387 | 165.8809 | [22 empty] | 8053.6827 | 12746.0073 | 45313.2319 | 304660.8381 | 239414.5284 | 610188.2884 |  | 8088.1553 | 12460.4808 | 42486.8636 | 240017.583 | 154014.8342 | 457067.9168 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 17488.6438 | 42162.7775 | 171745.1453 | 217839.3974 | 449280.8874 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013 |  | 44.9234 | 11242.5968 | 50751.0921 | 14556.3294 | 411892.2025 | 488487.1442
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 693 | 693 | C1 | 26 | 441 | 68 | 24 | 134 | 693 | 26 | 395 | 94 | 40 | 140 | 695 | 74.5178 | 101.6361 | -47.9834 | -40.2396 | -87.931 | 0 | 0 | 261 | 208 | 52 | 171 | 692 | 149.0355 | 205.3753 | -96.8774 | -81.3734 | -176.16 | 0 | 0 | 170 | 162 | 127 | 233 | 692 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | C1 | 3.0023 | 3.0023 | 6.0045 | 40.0303 | 150.4138 | C1 | 78.0591 | 1185.8974 | 564.4271 | 1601.2117 | 21057.9358 | 24487.5312 |  | 78.0591 | 1324.002 | 408.309 | 960.727 | 20155.4528 | 22926.5499 |  | 0 | 783.593 | 1248.9452 | 2081.5753 | 25720.7645 | 29834.8778 |  | 223.7226 | 1088.7323 | 960.827 | 470.7725 | 12494.7316 | 15238.786 |  | 0 | 510.3862 | 972.7361 | 5083.8473 | 35046.4217 | 41613.3914 |  | 447.4452 | 1126.9788 | 391.0313 | 1826.4461 | 8549.5219 | 12341.4233
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 428896 | 428896 | 428896 | 428896 | 428896 | C2 | 4.289 | 4.289 | 8.5779 | 57.1861 | 214.8769 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6 | 6 | C3 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 4 | 1 | 0 | 1 | 6 | 0.71066 | 1.1257 | -0.61401 | -0.38376 | -0.83858 | 0 | 0 | 2 | 2 | 1 | 2 | 7 | 1.4213 | 2.2764 | -1.2417 | -0.77604 | -1.68 | 0 | 0 | 2 | 2 | 1 | 2 | 7 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 643344 | 643344 | 643344 | 643344 | 643344 | C3 | 6.4334 | 6.4334 | 12.8669 | 85.7792 | 322.3153 | C3 | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 4.572 | 20.1089 | 17.8334 | 52.8609 | 374.3439 | 469.7191 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 9.144 | 27.5119 | 9.7574 | 19.2111 | 103.1409 | 168.7652
|  |  | 231 | 231 | C4 | 8 | 147 | 23 | 8 | 45 | 231 | 8 | 131 | 31 | 13 | 46 | 229 | 24.7716 | 39.2382 | -21.4026 | -13.3766 | -29.2305 | 0 | 0 | 87 | 69 | 18 | 57 | 231 | 49.5431 | 79.3483 | -43.2809 | -27.0506 | -58.56 | 0 | 0 | 57 | 54 | 42 | 78 | 231 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 1072240 | 1072240 | 1072240 | 1072240 | 1072240 | C4 | 10.7224 | 10.7224 | 21.4448 | 142.9653 | 537.1922 | C4 | 85.7792 | 1404.6344 | 664.7888 | 1858.5493 | 24710.843 | 28724.5948 |  | 85.7792 | 1576.1928 | 493.2304 | 1143.7227 | 24173.6508 | 27472.5759 |  | 0 | 932.8488 | 1479.6912 | 2573.376 | 30619.9577 | 35605.8737 |  | 265.6107 | 1353.5762 | 1020.7159 | 660.9788 | 14917.5831 | 18218.4647 |  | 0 | 611.1768 | 1158.0192 | 6004.544 | 41900.9947 | 49674.7347 |  | 531.2214 | 1461.9811 | 229.8691 | 2137.2519 | 10443.0171 | 14803.3407
|  |  | 930 | 930 |  | 34 | 592 | 92 | 32 | 180 |  | 34 | 530 | 126 | 53 | 187 |  | 100 | 142 | -70 | -54 | -118 |  | 0 | 350 | 279 | 71 | 230 |  | 200 | 287 | -141.4 | -109.2 | -236.4 |  | 0 | 229 | 218 | 170 | 313 | [22 empty] | 163.8383 | 2616.2656 | 1242.0828 | 3459.7611 | 46091.0942 | 53573.0419 |  | 163.8383 | 2925.9285 | 914.4063 | 2104.4497 | 44651.419 | 50760.0418 |  | 0 | 1729.3087 | 2754.3701 | 4740.7305 | 56985.3528 | 66209.7621 |  | 493.9053 | 2462.4174 | 1999.3763 | 1184.6122 | 27786.6586 | 33926.9698 |  | 0 | 1134.4299 | 2156.4891 | 11174.1705 | 77592.0471 | 92057.1366 |  | 987.8106 | 2616.4717 | 630.6578 | 3982.9091 | 19095.68 | 27313.5292
| EHV OHL Support - Poles |  | 263 | 263 | C1 | 12 | 112 | 108 | 21 | 10 | 263 | 2 | 114 | 110 | 24 | 15 | 265 | 5.1855 | 0 | 0 | -1.5557 | -3.6299 | 0 | 12 | 94 | 122 | 25 | 12 | 265 | 10.4132 | 0 | 0 | -3.124 | -7.2892 | 0 | 12 | 82 | 127 | 28 | 16 | 265 |  |  | C1 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C1 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | C1 | 65.7424 | 66.812 | 113.6298 | 243.7157 | 330.7688 | C1 | 131.4847 | 7616.5691 | 12499.2763 | 5849.1775 | 4961.5322 | 31058.0399 |  | 788.9083 | 7482.9451 | 12272.0168 | 5118.0303 | 3307.6882 | 28969.5886 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 1129.8163 | 6280.3289 | 13862.8337 | 5713.7557 | 2768.581 | 29755.3157 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173 |  | 1473.496 | 5478.5848 | 14430.9827 | 6062.683 | 2881.2501 | 30326.9965
|  |  | 8940 | 8940 | C2 | 423 | 3799 | 3664 | 722 | 332 | 8940 | 52 | 3863 | 3736 | 805 | 507 | 8963 | 175.4469 | 0 | 0 | -52.6341 | -122.8128 | 0 | 417 | 3167 | 4116 | 846 | 393 | 8939 | 352.3201 | 0 | 0 | -105.696 | -246.6241 | 0 | 413 | 2761 | 4281 | 959 | 525 | 8939 |  |  | C2 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C2 | 117544 | 117544 | 117544 | 117544 | 117544 | C2 | 93.9177 | 95.4457 | 162.3283 | 348.1653 | 472.5269 | C2 | 4883.7181 | 368706.8473 | 606458.3943 | 280273.089 | 239571.1282 | 1499893.1769 |  | 39727.1685 | 362598.3207 | 594770.7593 | 251375.3668 | 156878.9242 | 1405350.5394 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 55641.2208 | 302276.6206 | 668143.1346 | 276222.513 | 127670.7123 | 1429954.2012 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067 |  | 71877.0723 | 263525.655 | 694927.2982 | 297090.8539 | 131540.1011 | 1458960.9805
|  |  | 3324 | 3324 | C3 | 157 | 1412 | 1363 | 268 | 124 | 3324 | 19 | 1436 | 1389 | 300 | 188 | 3332 | 65.2385 | 0 | 0 | -19.5716 | -45.667 | 0 | 155 | 1178 | 1530 | 315 | 146 | 3324 | 131.0074 | 0 | 0 | -39.3022 | -91.7052 | 0 | 154 | 1027 | 1591 | 357 | 195 | 3324 |  |  | C3 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C3 | 176316 | 176316 | 176316 | 176316 | 176316 | C3 | 140.8765 | 143.1686 | 243.4924 | 522.248 | 708.7903 | C3 | 2676.6532 | 205590.0981 | 338210.938 | 156674.3976 | 133252.5802 | 836404.6671 |  | 22117.608 | 202154.0519 | 331880.1357 | 139962.4619 | 87889.9997 | 784004.2572 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 31026.4283 | 168652.6014 | 372543.3659 | 154286.9116 | 71115.0847 | 797624.3919 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701 |  | 40150.8453 | 147034.144 | 387396.402 | 165917.0222 | 73214.3513 | 813712.7649
|  |  | 7 | 7 | C4 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 3 | 3 | 1 | 0 | 7 | 0.1291 | 0 | 0 | -0.03873 | -0.09037 | 0 | 0 | 2 | 3 | 1 | 0 | 6 | 0.25925 | 0 | 0 | -0.077775 | -0.18147 | 0 | 0 | 2 | 3 | 1 | 0 | 6 |  |  | C4 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C4 | 293860 | 293860 | 293860 | 293860 | 293860 | C4 | 234.7941 | 238.6143 | 405.8207 | 870.4133 | 1181.3172 | C4 | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 30.3119 | 477.2286 | 1217.462 | 836.7022 | -106.7556 | 2454.9491 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 60.8703 | 477.2286 | 1217.462 | 802.717 | -214.3792 | 2343.8988
|  |  | 12534 | 12534 |  | 592 | 5326 | 5138 | 1012 | 466 |  | 73 | 5416 | 5238 | 1130 | 710 |  | 246 | 0 | 0 | -73.8 | -172.2 |  | 584 | 4441 | 5771 | 1187 | 551 |  | 494 | 0 | 0 | -148.2 | -345.8 |  | 579 | 3872 | 6002 | 1345 | 736 | [22 empty] | 7691.856 | 582629.3574 | 958386.0707 | 443667.0775 | 377785.2406 | 2370159.6021 |  | 62633.6848 | 572951.1606 | 940140.3738 | 397326.2723 | 248076.612 | 2221128.1035 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 87827.7774 | 477686.7795 | 1055766.7962 | 437059.8826 | 201447.6223 | 2259788.858 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198 |  | 113562.2839 | 416515.6124 | 1097972.1449 | 469873.2762 | 207421.3234 | 2305344.6407
| EHV OHL Fittings and Conductors (Tower Lines) |  | 264.3928 | 264.3928 | C1 | 60.0911 | 197.1135 | 4.2075 | 0.74518 | 2.2355 | 264.3928 | 0 | 235.0812 | 14.1584 | 0.74518 | 2.2355 | 252.2203 | 2.2355 | -0.44711 | -1.7884 | 0 | 0 | -4.4409e-16 | 60.0911 | 168.7967 | 25.0724 | 4.4711 | 5.9614 | 264.3928 | 2.2355 | -0.44711 | -1.7884 | 0 | 0 | -4.4409e-16 | 60.0911 | 147.1866 | 18.3658 | 18.6294 | 20.1198 | 264.3928 |  |  | C1 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C1 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | C1 | 1.5983 | 36.9203 | 128.5019 | 559.3987 | 1552.0917 | C1 | 0 | 8679.2717 | 1819.3778 | 416.8514 | 3469.7521 | 14385.253 |  | 96.0426 | 7277.491 | 540.6664 | 416.8514 | 3469.7521 | 11800.8035 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 99.6156 | 6215.5204 | 2992.0386 | 2501.1085 | 9252.6723 | 21060.9553 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151 |  | 99.6156 | 5417.6668 | 2130.228 | 10421.2854 | 31227.7689 | 49296.5647
|  |  | 0.36021 | 0.36021 | C2 | 0.081868 | 0.26855 | 0.0057322 | 0.0010152 | 0.0030457 | 0.36021 | 0 | 0.32027 | 0.019289 | 0.0010152 | 0.0030457 | 0.34362 | 0.0030457 | -0.00060914 | -0.0024365 | 0 | 0 | -4.3368e-19 | 0.081868 | 0.22997 | 0.034159 | 0.0060914 | 0.0081218 | 0.36021 | 0.0030457 | -0.00060914 | -0.0024365 | 0 | 0 | -4.3368e-19 | 0.081868 | 0.20053 | 0.025022 | 0.025381 | 0.027411 | 0.36021 |  |  | C2 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C2 | 228326 | 228326 | 228326 | 228326 | 228326 | C2 | 2.2833 | 52.7433 | 183.5741 | 799.141 | 2217.2738 | C2 | 0 | 16.8923 | 3.541 | 0.81131 | 6.7531 | 27.9978 |  | 0.18693 | 14.1641 | 1.0523 | 0.81131 | 6.7531 | 22.9677 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.19388 | 12.0972 | 5.8234 | 4.8679 | 18.0083 | 40.9906 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175 |  | 0.19388 | 10.5443 | 4.146 | 20.2828 | 60.7781 | 95.945
|  |  | 2.1612 | 2.1612 | C3 | 0.49121 | 1.6113 | 0.034393 | 0.0060914 | 0.018274 | 2.1612 | 0 | 1.9216 | 0.11574 | 0.0060914 | 0.018274 | 2.0617 | 0.018274 | -0.0036548 | -0.014619 | 0 | 0 | -1.7347e-18 | 0.49121 | 1.3798 | 0.20495 | 0.036548 | 0.048731 | 2.1612 | 0.018274 | -0.0036548 | -0.014619 | 0 | 0 | -1.7347e-18 | 0.49121 | 1.2032 | 0.15013 | 0.15228 | 0.16447 | 2.1612 |  |  | C3 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C3 | 342489 | 342489 | 342489 | 342489 | 342489 | C3 | 3.4249 | 79.115 | 275.3612 | 1198.7115 | 3325.9107 | C3 | 0 | 152.0308 | 31.8692 | 7.3018 | 60.7781 | 251.9799 |  | 1.6823 | 127.4765 | 9.4706 | 7.3018 | 60.7781 | 206.7093 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.7449 | 108.8744 | 52.4102 | 43.8108 | 162.0748 | 368.9151 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576 |  | 1.7449 | 94.8988 | 37.3142 | 182.5449 | 547.0026 | 863.5054
|  |  | 87.8908 | 87.8908 | C4 | 19.9758 | 65.5255 | 1.3987 | 0.24772 | 0.74315 | 87.8908 | 0 | 78.1469 | 4.7066 | 0.24772 | 0.74315 | 83.8443 | 0.74315 | -0.14863 | -0.59452 | 0 | 0 | 0 | 19.9758 | 56.1123 | 8.3347 | 1.4863 | 1.9817 | 87.8908 | 0.74315 | -0.14863 | -0.59452 | 0 | 0 | 0 | 19.9758 | 48.9285 | 6.1053 | 6.1929 | 6.6883 | 87.8908 |  |  | C4 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C4 | 570815 | 570815 | 570815 | 570815 | 570815 | C4 | 5.7082 | 131.8583 | 458.9353 | 1997.8525 | 5543.1845 | C4 | 0 | 10304.3124 | 2160.0242 | 494.8995 | 4119.4021 | 17078.6382 |  | 114.0248 | 8640.0731 | 641.8966 | 494.8995 | 4119.4021 | 14010.2961 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 118.2668 | 7379.2671 | 3552.2451 | 2969.397 | 10985.0722 | 25004.2482 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793 |  | 118.2668 | 6432.0294 | 2529.0757 | 12372.4876 | 37074.6185 | 58526.4781
|  |  | 354.805 | 354.805 |  | 80.64 | 264.5188 | 5.6462 | 1 | 3 |  | 0 | 315.47 | 19 | 1 | 3 |  | 3 | -0.6 | -2.4 | 0 | 0 |  | 80.64 | 226.5188 | 33.6462 | 6 | 8 |  | 3 | -0.6 | -2.4 | 0 | 0 |  | 80.64 | 197.5188 | 24.6462 | 25 | 27 | [22 empty] | 0 | 19152.5073 | 4014.8122 | 919.864 | 7656.6853 | 31743.8689 |  | 211.9367 | 16059.2047 | 1193.0859 | 919.864 | 7656.6853 | 26040.7766 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 219.8212 | 13715.7591 | 6602.5172 | 5519.1842 | 20417.8276 | 46475.1092 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694 |  | 219.8212 | 11955.1393 | 4700.764 | 22996.6007 | 68910.168 | 108782.4932
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 |  | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 |  | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 |  | 119415.9203 | 631781.9442 | 1392156.0625 | 882288.9535 | 758758.4456 | 3784401.3262 |  | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 |  | 160462.2081 | 558794.1242 | 1368139.0802 | 740026.9728 | 1229893.4312 | 4057315.8166
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 77 | 76.199 | C1 | 43 | 16 | 2 | 2 | 14 | 77 | 40 | 16 | 2 | 2 | 15 | 75 | 8.0103 | 1.6021 | 0 | -1.6021 | -8.8114 | -0.80103 | 32 | 20 | 4 | 4 | 16 | 76 | 12.416 | 3.2041 | 0 | -3.2041 | -13.2171 | -0.80103 | 29 | 23 | 4 | 5 | 16 | 77 |  |  | C1 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C1 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | C1 | 1145.2464 | 1145.2464 | 2032.8759 | 3954.8992 | 7511.4217 | C1 | 45809.8574 | 18323.943 | 4065.7519 | 7909.7984 | 112671.3259 | 188780.6766 |  | 49245.5968 | 18323.943 | 4065.7519 | 7909.7984 | 105159.9042 | 184704.9942 |  | 36647.886 | 22904.9287 | 8131.5037 | 15819.5969 | 120182.7476 | 203686.6629 |  | 45821.6946 | 24739.6905 | 8131.5037 | 9483.5826 | 53996.8352 | 142173.3067 |  | 33212.1466 | 26340.668 | 8131.5037 | 19774.4961 | 120182.7476 | 207641.5621 |  | 47431.5501 | 30010.1915 | 8131.5037 | 7102.4676 | 20903.8791 | 113579.592
|  |  | 27 | 26.7192 | C2 | 15 | 6 | 1 | 0 | 5 | 27 | 14 | 6 | 1 | 0 | 5 | 26 | 2.8079 | 0.56158 | 0 | -0.56158 | -3.0887 | -0.28079 | 12 | 7 | 1 | 2 | 6 | 28 | 4.3523 | 1.1232 | 0 | -1.1232 | -4.6331 | -0.28079 | 10 | 8 | 2 | 2 | 6 | 28 |  |  | C2 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C2 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | C2 | 1636.0663 | 1636.0663 | 2904.1085 | 5649.856 | 10730.6025 | C2 | 22904.9287 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 89278.4475 |  | 24540.9951 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 90914.5139 |  | 19632.796 | 11452.4644 | 2904.1085 | 11299.7121 | 64383.6148 | 109672.6957 |  | 24226.7463 | 12371.2544 | 2904.1085 | 8126.8386 | 31239.8246 | 78868.7723 |  | 16360.6634 | 13088.5307 | 5808.217 | 11299.7121 | 64383.6148 | 110940.7379 |  | 23481.2863 | 14926.1108 | 5808.217 | 4953.9651 | 14667.9295 | 63837.5086
|  |  | 90 | 89.0818 | C3 | 50 | 21 | 3 | 1 | 15 | 90 | 46 | 18 | 3 | 1 | 17 | 85 | 9.1817 | 1.8363 | 0 | -1.8363 | -10.0999 | -0.91817 | 38 | 23 | 5 | 5 | 19 | 90 | 14.2317 | 3.6727 | 0 | -3.6727 | -15.1499 | -0.91817 | 33 | 27 | 5 | 5 | 19 | 89 |  |  | C3 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C3 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | C3 | 2454.0995 | 2454.0995 | 4356.1627 | 8474.784 | 16095.9037 | C3 | 112888.5773 | 44173.7911 | 13068.4881 | 8474.784 | 273630.3629 | 452236.0034 |  | 122704.9753 | 51536.0896 | 13068.4881 | 8474.784 | 241438.5555 | 437222.8926 |  | 93255.7812 | 56444.2886 | 21780.8136 | 42373.9202 | 305822.1703 | 519676.9739 |  | 115788.6845 | 60950.8693 | 21780.8136 | 26811.2677 | 143254.9293 | 368586.5644 |  | 80985.2837 | 66260.6867 | 21780.8136 | 42373.9202 | 305822.1703 | 517222.8744 |  | 115911.2838 | 75273.848 | 21780.8136 | 11248.6152 | 61971.3088 | 286185.8694
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C4 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | C4 | 4090.1658 | 4090.1658 | 7260.2712 | 14124.6401 | 26826.5062 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 194 | 192 |  | 108 | 43 | 6 | 3 | 34 |  | 100 | 40 | 6 | 3 | 37 |  | 20 | 4 | 0 | -4 | -22 |  | 82 | 50 | 10 | 11 | 41 |  | 31 | 8 | 0 | -8 | -33 |  | 72 | 58 | 11 | 12 | 41 | [22 empty] | 181603.3635 | 72314.1321 | 20038.3485 | 16384.5825 | 439954.7011 | 730295.1276 |  | 196491.5671 | 79676.4306 | 20038.3485 | 16384.5825 | 400251.4719 | 712842.4007 |  | 149536.4632 | 90801.6817 | 32816.4258 | 69493.2291 | 490388.5327 | 833036.3325 |  | 185837.1255 | 98061.8142 | 32816.4258 | 44421.6888 | 228491.5891 | 589628.6434 |  | 130558.0937 | 105689.8854 | 35720.5343 | 73448.1283 | 490388.5327 | 835805.1744 |  | 186824.1202 | 120210.1503 | 35720.5343 | 23305.0478 | 97543.1173 | 463602.9699
| 132kV Transformer |  | 59 | 59 | C1 | 12 | 19 | 15 | 7 | 6 | 59 | 5 | 19 | 15 | 7 | 11 | 57 | 2.1923 | 2.5577 | 0 | 0 | -4.75 | 0 | 11 | 10 | 16 | 16 | 7 | 60 | 6.2115 | 5.1154 | 0 | 0 | -11.3269 | 0 | 11 | 10 | 6 | 17 | 17 | 61 |  |  | C1 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C1 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | C1 | 1418.2655 | 1418.2655 | 2428.685 | 4604.9455 | 10096.9831 | C1 | 7091.3276 | 26947.0449 | 36430.2757 | 32234.6186 | 111066.8143 | 213770.0812 |  | 17019.1863 | 26947.0449 | 36430.2757 | 32234.6186 | 60581.8987 | 173213.0242 |  | 15600.9207 | 14182.6552 | 38858.9608 | 73679.1283 | 70678.8818 | 213000.5468 |  | 18710.1952 | 17810.142 | 38858.9608 | 73679.1283 | 22718.212 | 171776.6382 |  | 15600.9207 | 14182.6552 | 14572.1103 | 78284.0738 | 171648.713 | 294288.473 |  | 24410.5316 | 21437.6288 | 14572.1103 | 78284.0738 | 57280.9619 | 195985.3064
|  |  | 51 | 51 | C2 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 1.8462 | 2.1538 | 0 | 0 | -4 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 5.2308 | 4.3077 | 0 | 0 | -9.5385 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C2 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C2 | 858587 | 858587 | 858587 | 858587 | 858587 | C2 | 2026.0936 | 2026.0936 | 3469.5501 | 6578.4936 | 14424.2616 | C2 | 10130.468 | 30391.404 | 48573.7009 | 39470.9616 | 144242.616 | 272809.1506 |  | 20260.936 | 34443.5912 | 48573.7009 | 39470.9616 | 57697.0464 | 200446.2362 |  | 20260.936 | 18234.8424 | 45104.1509 | 85520.4167 | 72121.308 | 241241.654 |  | 24001.4165 | 22598.7363 | 45104.1509 | 85520.4167 | 14424.2616 | 191648.9821 |  | 18234.8424 | 14182.6552 | 17347.7503 | 92098.9103 | 216363.924 | 358228.0823 |  | 28832.8705 | 22910.443 | 17347.7503 | 92098.9103 | 78778.6595 | 239968.6337
|  |  | 51 | 51 | C3 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 1.8462 | 2.1538 | 0 | 0 | -4 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 5.2308 | 4.3077 | 0 | 0 | -9.5385 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C3 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C3 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | C3 | 3039.1404 | 3039.1404 | 5204.3251 | 9867.7404 | 21636.3924 | C3 | 15195.702 | 45587.1061 | 72860.5514 | 59206.4423 | 216363.924 | 409213.7258 |  | 30391.404 | 51665.3869 | 72860.5514 | 59206.4423 | 86545.5696 | 300669.3543 |  | 30391.404 | 27352.2636 | 67656.2263 | 128280.6251 | 108181.962 | 361862.4811 |  | 36002.1248 | 33898.1045 | 67656.2263 | 128280.6251 | 21636.3924 | 287473.4731 |  | 27352.2636 | 21273.9828 | 26021.6255 | 138148.3655 | 324545.886 | 537342.1234 |  | 43249.3057 | 34365.6646 | 26021.6255 | 138148.3655 | 118167.9893 | 359952.9506
|  |  | 3 | 3 | C4 | 1 | 1 | 1 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 3 | 0.11538 | 0.13462 | 0 | 0 | -0.25 | 0 | 1 | 1 | 1 | 1 | 0 | 4 | 0.32692 | 0.26923 | 0 | 0 | -0.59615 | 0 | 1 | 0 | 0 | 1 | 1 | 3 |  |  | C4 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C4 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | C4 | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 36060.654 | C4 | 0 | 5065.234 | 8673.8752 | 0 | 36060.654 | 49799.7632 |  | 5065.234 | 5065.234 | 8673.8752 | 0 | 0 | 18804.3432 |  | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 0 | 35250.5772 |  | 5649.6841 | 5747.0924 | 8673.8752 | 16446.234 | -9015.1635 | 27501.7222 |  | 5065.234 | 0 | 0 | 16446.234 | 36060.654 | 57572.122 |  | 6721.1759 | 1363.7168 | 0 | 16446.234 | 14562.9564 | 39094.0831
|  |  | 164 | 164 |  | 33 | 54 | 44 | 19 | 14 |  | 15 | 50 | 44 | 19 | 32 |  | 6 | 7 | 0 | 0 | -13 |  | 32 | 29 | 43 | 43 | 17 |  | 17 | 14 | 0 | 0 | -31 |  | 30 | 24 | 16 | 46 | 48 | [22 empty] | 32417.4976 | 107990.789 | 166538.4032 | 130912.0225 | 507734.0083 | 945592.7207 |  | 72736.7603 | 118121.257 | 166538.4032 | 130912.0225 | 204824.5147 | 693132.9578 |  | 71318.4948 | 64834.9953 | 160293.2131 | 303926.404 | 250982.1518 | 851355.2591 |  | 84363.4205 | 80054.0753 | 160293.2131 | 303926.404 | 49763.7025 | 678400.8155 |  | 66253.2608 | 49639.2933 | 57941.4861 | 324977.5835 | 748619.177 | 1247430.8008 |  | 103213.8837 | 80077.4533 | 57941.4861 | 324977.5835 | 268790.5671 | 835000.9738
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 10.9182 | 10.1281 | C1 | 0.069593 | 1.7577 | 3.5512 | 5.0591 | 0.48064 | 10.9182 | 0.068227 | 1.758 | 3.5519 | 5.1278 | 0.48064 | 10.9865 | 0 | 0 | 0 | -0.40769 | 0 | -0.40769 | 0.0009295 | 0.86512 | 2.3839 | 5.9513 | 1.717 | 10.9182 | 0 | 0 | 0 | -0.79012 | 0 | -0.79012 | 0.0009295 | 0.035179 | 2.2525 | 4.4407 | 4.1888 | 10.9182 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | C1 | 89.1849 | 89.1849 | 267.5547 | 624.2943 | 891.849 | C1 | 6.0848 | 156.7859 | 950.3179 | 3201.2465 | 428.6599 | 4743.0951 |  | 6.2066 | 156.7643 | 950.1285 | 3158.3535 | 428.6599 | 4700.1129 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 77.1561 | 637.8191 | 3460.8589 | 1531.2611 | 5707.1781 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239 |  | 0.082898 | 3.1375 | 602.679 | 2279.0617 | 3735.7979 | 6620.759
|  |  | 116.779 | 108.328 | C2 | 0.74435 | 18.8005 | 37.9824 | 54.1109 | 5.1408 | 116.779 | 0.72974 | 18.8031 | 37.99 | 54.8457 | 5.1408 | 117.5094 | 0 | 0 | 0 | -4.3606 | 0 | -4.3606 | 0.0099418 | 9.2532 | 25.4975 | 63.6541 | 18.3642 | 116.779 | 0 | 0 | 0 | -8.4509 | 0 | -8.4509 | 0.0099418 | 0.37627 | 24.0928 | 47.4972 | 44.8028 | 116.779 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 127407 | 127407 | 127407 | 127407 | 127407 | C2 | 127.407 | 127.407 | 382.221 | 891.849 | 1274.07 | C2 | 92.974 | 2395.6419 | 14520.5776 | 48914.1022 | 6549.7974 | 72473.0931 |  | 94.8352 | 2395.3128 | 14517.6837 | 48258.709 | 6549.7974 | 71816.3381 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 1178.9218 | 9745.6884 | 52880.9033 | 23397.2175 | 87203.9977 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186 |  | 1.2667 | 47.9394 | 9208.7573 | 34823.3911 | 57081.89 | 101163.2444
|  |  | 31.9588 | 29.646 | C3 | 0.2037 | 5.1451 | 10.3946 | 14.8085 | 1.4069 | 31.9588 | 0.19971 | 5.1458 | 10.3967 | 15.0096 | 1.4069 | 32.1587 | 0 | 0 | 0 | -1.1934 | 0 | -1.1934 | 0.0027208 | 2.5323 | 6.9779 | 17.4202 | 5.0257 | 31.9588 | 0 | 0 | 0 | -2.3128 | 0 | -2.3128 | 0.0027208 | 0.10297 | 6.5934 | 12.9985 | 12.2611 | 31.9588 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | C3 | 191.1105 | 191.1105 | 573.3315 | 1337.7735 | 1911.105 | C3 | 38.1661 | 983.4189 | 5960.7448 | 20079.3997 | 2688.7134 | 29750.4429 |  | 38.9302 | 983.2838 | 5959.5569 | 19810.3586 | 2688.7134 | 29480.8428 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 483.9513 | 4000.6371 | 21707.7846 | 9604.6347 | 35797.5276 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836 |  | 0.51997 | 19.6793 | 3780.2251 | 14295.1165 | 23432.3034 | 41527.8443
|  |  | 0.22406 | 0.20785 | C4 | 0.0014282 | 0.036072 | 0.072876 | 0.10382 | 0.0098637 | 0.22406 | 0.0014001 | 0.036077 | 0.072891 | 0.10523 | 0.0098637 | 0.22546 | 0 | 0 | 0 | -0.0083666 | 0 | -0.0083666 | 1.9075e-05 | 0.017754 | 0.048922 | 0.12213 | 0.035235 | 0.22406 | 0 | 0 | 0 | -0.016215 | 0 | -0.016215 | 1.9075e-05 | 0.00072194 | 0.046226 | 0.091132 | 0.085962 | 0.22406 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | C4 | 318.5175 | 318.5175 | 955.5525 | 2229.6225 | 3185.175 | C4 | 0.44597 | 11.4912 | 69.6511 | 234.627 | 31.4175 | 347.6328 |  | 0.4549 | 11.4896 | 69.6372 | 231.4833 | 31.4175 | 344.4825 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 5.655 | 46.7473 | 253.6546 | 112.2298 | 418.2927 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038 |  | 0.0060758 | 0.22995 | 44.1718 | 167.0379 | 273.8055 | 485.2512
|  |  | 159.88 | 148.31 |  | 1.0191 | 25.7394 | 52.0011 | 74.0822 | 7.0382 |  | 0.99907 | 25.7429 | 52.0114 | 75.0883 | 7.0382 |  | 0 | 0 | 0 | -5.97 | 0 |  | 0.013611 | 12.6684 | 34.9082 | 87.1478 | 25.142 |  | 0 | 0 | 0 | -11.57 | 0 |  | 0.013611 | 0.51514 | 32.985 | 65.0276 | 61.3387 | [22 empty] | 137.6709 | 3547.3379 | 21501.2914 | 72429.3754 | 9698.5882 | 107314.2638 |  | 140.4269 | 3546.8505 | 21497.0062 | 71458.9044 | 9698.5882 | 106341.7763 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 1745.6842 | 14430.8919 | 78303.2014 | 34645.343 | 129126.9961 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973 |  | 1.8756 | 70.9861 | 13635.8333 | 51564.6071 | 84523.7969 | 149797.0989
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 104 | 104 | C1 | 4 | 74 | 6 | 14 | 6 | 104 | 2 | 55 | 19 | 18 | 10 | 104 | 3.3091 | 8.7465 | 0 | -6.5599 | -5.4957 | 0 | 3 | 32 | 46 | 8 | 15 | 104 | 6.6181 | 17.5301 | 0 | -13.1476 | -11.0007 | 0 | 3 | 13 | 48 | 17 | 22 | 103 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | C1 | 9.0026 | 9.0026 | 18.0052 | 120.0344 | 451.0293 | C1 | 18.0052 | 495.142 | 342.0981 | 2160.6194 | 4510.2931 | 7526.1577 |  | 36.0103 | 666.191 | 108.031 | 1680.4818 | 2706.1758 | 5196.8899 |  | 27.0077 | 288.0826 | 828.2375 | 960.2753 | 6765.4396 | 8869.0427 |  | 56.7979 | 366.8239 | 828.2375 | 172.8623 | 4286.7187 | 5711.4402 |  | 27.0077 | 117.0336 | 864.2478 | 2040.585 | 9922.6448 | 12971.5189 |  | 86.588 | 274.8498 | 864.2478 | 462.4224 | 4961.0239 | 6649.132
|  |  | 2572 | 2572 | C2 | 102 | 1838 | 141 | 337 | 154 | 2572 | 43 | 1359 | 464 | 456 | 251 | 2573 | 82.3958 | 528.7394 | -310.9509 | -163.3414 | -136.8429 | 0 | 68 | 796 | 1135 | 190 | 384 | 2573 | 164.7915 | 1056.9522 | -620.4524 | -327.3749 | -273.9165 | 0 | 68 | 327 | 1202 | 426 | 551 | 2574 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 1286083 | 1286083 | 1286083 | 1286083 | 1286083 | C2 | 12.8608 | 12.8608 | 25.7217 | 171.4777 | 644.3276 | C2 | 553.0157 | 17477.868 | 11934.8502 | 78193.8464 | 161726.2233 | 269885.8036 |  | 1311.8047 | 23638.2055 | 3626.7541 | 57787.9961 | 99226.4478 | 185591.2082 |  | 874.5364 | 10237.2207 | 29194.0841 | 32580.7693 | 247421.7919 | 320308.4024 |  | 1934.2144 | 17037.2477 | 21195.9114 | 4571.3626 | 159250.1462 | 203988.8822 |  | 874.5364 | 4205.4914 | 30917.4353 | 73049.5144 | 355024.4982 | 464071.4758 |  | 2993.8923 | 17798.7739 | 14958.3698 | 16912.017 | 178532.5553 | 231195.6082
|  |  | 447 | 447 | C3 | 18 | 319 | 24 | 59 | 27 | 447 | 7 | 236 | 80 | 79 | 44 | 446 | 14.2952 | 115.5141 | -77.7291 | -28.3387 | -23.7414 | 0 | 12 | 138 | 197 | 33 | 66 | 446 | 28.5903 | 231.5177 | -155.7876 | -56.7976 | -47.5229 | 0 | 12 | 57 | 208 | 74 | 95 | 446 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | C3 | 19.2912 | 19.2912 | 38.5825 | 257.2166 | 966.4914 | C3 | 135.0387 | 4552.7338 | 3086.5992 | 20320.1114 | 42525.6205 | 70620.1036 |  | 347.2424 | 6153.9072 | 925.9798 | 15175.7794 | 26095.2671 | 48698.1758 |  | 231.4949 | 2662.1918 | 7600.7505 | 8488.1478 | 63788.4307 | 82771.0158 |  | 507.2665 | 4890.6029 | 4601.7674 | 1198.9528 | 40842.5567 | 52041.1463 |  | 231.4949 | 1099.601 | 8025.1579 | 19034.0284 | 91816.6806 | 120206.9628 |  | 783.0381 | 5565.8655 | 2014.4842 | 4424.752 | 45886.2472 | 58674.387
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | C4 | 32.1521 | 32.1521 | 64.3041 | 428.6943 | 1610.819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3123 | 3123 |  | 124 | 2231 | 171 | 410 | 187 |  | 52 | 1650 | 563 | 553 | 305 |  | 100 | 653 | -388.68 | -198.24 | -166.08 |  | 83 | 966 | 1378 | 231 | 465 |  | 200 | 1306 | -776.24 | -397.32 | -332.44 |  | 83 | 397 | 1458 | 517 | 668 | [22 empty] | 706.0596 | 22525.7437 | 15363.5475 | 100674.5772 | 208762.1369 | 348032.065 |  | 1695.0574 | 30458.3037 | 4660.7648 | 74644.2573 | 128027.8907 | 239486.2739 |  | 1133.0391 | 13187.4951 | 37623.0721 | 42029.1924 | 317975.6622 | 411948.4609 |  | 2498.2788 | 22294.6745 | 26625.9162 | 5943.1776 | 204379.4215 | 261741.4687 |  | 1133.0391 | 5422.1259 | 39806.841 | 94124.1278 | 456763.8236 | 597249.9575 |  | 3863.5185 | 23639.4892 | 17837.1017 | 21799.1914 | 229379.8264 | 296519.1272
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 52.7896 | 52.7896 | C1 | 2.6478 | 46.9644 | 1.6221 | 1.3898 | 0.16545 | 52.7896 | 1 | 47 | 3 | 1 | 0 | 52 | 1.456 | -0.2912 | -1.1648 | 0 | 0 | -2.2204e-16 | 2.6478 | 40.975 | 5.8908 | 1.5884 | 1.6876 | 52.7896 | 2.9782 | -0.59563 | -2.3825 | 0 | 0 | 0 | 2.6478 | 35.9122 | 4.6996 | 3.7062 | 5.824 | 52.7896 |  | 2.317 | C1 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C1 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | C1 | 4.7807 | 45.4166 | 384.3676 | 1185.1335 | 3214.107 | C1 | 4.7807 | 2134.579 | 1153.1029 | 1185.1335 | 0 | 4477.5961 |  | 12.6582 | 2132.9638 | 623.4996 | 1647.1082 | 531.7848 | 4948.0146 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 19.6189 | 1847.7201 | 1816.5401 | 1882.4093 | 5424.2045 | 10990.4929 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418 |  | 26.8959 | 1603.9554 | 890.5982 | 4392.2885 | 18718.8233 | 25632.5612
|  |  | 1314.4617 | 1314.4617 | C2 | 65.9298 | 1169.4145 | 40.3914 | 34.6062 | 4.1198 | 1314.4617 | 26 | 1178 | 70 | 35 | 7 | 1316 | 36.2541 | -7.2508 | -29.0033 | 0 | 0 | 0 | 65.9298 | 1020.2782 | 146.6819 | 39.55 | 42.0218 | 1314.4617 | 74.1562 | -14.8312 | -59.325 | 0 | 0 | 0 | 65.9298 | 894.2126 | 117.0194 | 92.2833 | 145.0165 | 1314.4617 |  |  | C2 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C2 | 682956 | 682956 | 682956 | 682956 | 682956 | C2 | 6.8296 | 64.8808 | 549.0966 | 1693.0479 | 4591.5815 | C2 | 177.5686 | 76429.606 | 38436.7637 | 59256.6773 | 32141.0704 | 206441.6859 |  | 450.2715 | 75872.571 | 22178.7704 | 58589.9907 | 18916.3433 | 176007.9469 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 697.8713 | 65726.0438 | 64616.9258 | 66959.9894 | 192946.7017 | 390947.5319 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601 |  | 956.7256 | 57054.9863 | 31679.8499 | 156239.9752 | 665855.2844 | 911786.8214
|  |  | 228.0512 | 228.0512 | C3 | 11.4384 | 202.8864 | 7.0077 | 6.004 | 0.71476 | 228.0512 | 5 | 204 | 12 | 6 | 1 | 228 | 6.2899 | -1.258 | -5.0319 | 0 | 0 | -1.7764e-15 | 11.4384 | 177.0121 | 25.4484 | 6.8617 | 7.2905 | 228.0512 | 12.8657 | -2.5731 | -10.2925 | 0 | 0 | 0 | 11.4384 | 155.1405 | 20.3022 | 16.0106 | 25.1595 | 228.0512 |  |  | C3 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C3 | 1024434 | 1024434 | 1024434 | 1024434 | 1024434 | C3 | 10.2443 | 97.3212 | 823.6449 | 2539.5719 | 6887.3722 | C3 | 51.2217 | 19853.5309 | 9883.7392 | 15237.4313 | 6887.3722 | 51913.2954 |  | 117.1791 | 19745.151 | 5771.8246 | 15247.5157 | 4922.8074 | 45804.4777 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 181.6147 | 17104.609 | 16815.971 | 17425.7322 | 50212.6356 | 101740.5625 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845 |  | 248.9792 | 14848.0446 | 8244.3947 | 40660.0417 | 173282.821 | 237284.2812
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C4 | 1707390 | 1707390 | 1707390 | 1707390 | 1707390 | C4 | 17.0739 | 162.2021 | 1372.7416 | 4232.6198 | 11478.9537 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1595.3025 | 1595.3025 |  | 80.016 | 1419.2653 | 49.0212 | 42 | 5 |  | 32 | 1429 | 85 | 42 | 8 |  | 44 | -8.8 | -35.2 | 0 | 0 |  | 80.016 | 1238.2653 | 178.0212 | 48 | 51 |  | 90 | -18 | -72 | 0 | 0 |  | 80.016 | 1085.2653 | 142.0212 | 112 | 176 | [22 empty] | 233.571 | 98417.7159 | 49473.6058 | 75679.2422 | 39028.4426 | 262832.5774 |  | 580.1088 | 97750.6859 | 28574.0945 | 75484.6145 | 24370.9355 | 226760.4392 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 899.1049 | 84678.3729 | 83249.4369 | 86268.1309 | 248583.5418 | 503678.5873 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865 |  | 1232.6007 | 73506.9863 | 40814.8428 | 201292.3054 | 857856.9286 | 1174703.6639
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 |  | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 |  | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 |  | 273599.8053 | 286834.621 | 317415.884 | 518862.6028 | 765863.598 | 2162576.5111 |  | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 |  | 295135.9987 | 297505.0652 | 165949.7982 | 622938.7353 | 1538094.2363 | 2919623.8337
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 269066.8564 | 267196.2864 |  | 36234.8093 | 102297.8188 | 83782.0698 | 25268.2431 | 21483.9155 |  | 22042.9663 | 103434.5141 | 86548.7282 | 28258.5442 | 28483.6662 |  | 9204 | 2457.892 | -1171.2823 | -1921.2802 | -9507.9413 |  | 33932.1673 | 90891.2169 | 88029.2386 | 25016.7125 | 31197.5201 |  | 18835 | 4767.0751 | -2340.2277 | -3756.4911 | -19375.9263 |  | 29163.1673 | 87383.2531 | 88101.4332 | 24816.473 | 39602.5289 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 |  | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 |  | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 |  | 1276880.0121 | 3962183.2523 | 5912844.9297 | 3581003.1277 | 5332883.9264 | 20065795.2482 |  | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 |  | 1472936.545 | 3867283.888 | 5698209.0765 | 3296871.3083 | 6173205.8428 | 20508506.6605
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 | LV Network | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 | LV Network | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 | LV Network | 322253.2779 | 338765.5964 | 1004163.994 | 583203.9116 | 1467347.5819 | 3715734.3618 | LV Network | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 | LV Network | 342778.2514 | 376836.72 | 1024066.3775 | 485284.7807 | 1235833.5377 | 3464799.6673
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 | HV Network | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 | HV Network | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 | HV Network | 561611.0086 | 2704801.0907 | 3199108.9893 | 1596647.6597 | 2340914.3009 | 10403083.0492 | HV Network | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 | HV Network | 674560.0867 | 2634147.9786 | 3140053.8206 | 1448620.8195 | 2169384.6375 | 10066767.3429
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 | EHV Network | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 | EHV Network | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 | EHV Network | 119415.9203 | 631781.9442 | 1392156.0625 | 882288.9535 | 758758.4456 | 3784401.3262 | EHV Network | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 | EHV Network | 160462.2081 | 558794.1242 | 1368139.0802 | 740026.9728 | 1229893.4312 | 4057315.8166
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 | 132kV Network | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 | 132kV Network | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 | 132kV Network | 273599.8053 | 286834.621 | 317415.884 | 518862.6028 | 765863.598 | 2162576.5111 | 132kV Network | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 | 132kV Network | 295135.9987 | 297505.0652 | 165949.7982 | 622938.7353 | 1538094.2363 | 2919623.8337
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 | Total | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 | Total | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 | Total | 1276880.0121 | 3962183.2523 | 5912844.9297 | 3581003.1277 | 5332883.9264 | 20065795.2482 | Total | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 | Total | 1472936.545 | 3867283.888 | 5698209.0765 | 3296871.3083 | 6173205.8428 | 20508506.6605
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## ENWL - Asset Rep
Secondary deliverables RIIO-ED1 - Asset Replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
ENWL | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 3251 | 3251 | C1 | 365 | 1078 | 581 | 295 | 932 | 3251 | 228 | 1082 | 597 | 295 | 1019 | 3221 | 179.9037 | 0 | -25.8058 | 0 | -154.0978 | 0 | 325 | 750 | 949 | 211 | 1017 | 3252 | 359.8073 | 0 | -51.6117 | 0 | -308.1956 | 0 | 216 | 696 | 981 | 132 | 1227 | 3252 | Yes |  | C1 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C1 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | C1 | 10.03 | 17.3692 | 18.0526 | 30.8232 | 94.9612 | C1 | 2286.8431 | 18793.4975 | 10777.4025 | 9092.8586 | 96765.4981 | 137716.0998 |  | 3660.9549 | 18724.0206 | 10488.5609 | 9092.8586 | 88503.8707 | 130470.2657 |  | 3259.7544 | 13026.916 | 17131.9179 | 6503.7056 | 96575.5757 | 136497.8695 |  | 5064.1904 | 13026.916 | 16666.0552 | 6503.7056 | 81942.2579 | 123203.1252 |  | 2166.4829 | 12088.978 | 17709.6011 | 4068.6689 | 116517.4349 | 152551.1659 |  | 5775.355 | 12088.978 | 16777.8758 | 4068.6689 | 87250.7995 | 125961.6772
|  |  | 9179 | 9179 | C2 | 1032 | 3044 | 1640 | 833 | 2630 | 9179 | 642 | 3055 | 1684 | 834 | 2878 | 9093 | 507.8643 | 0 | -72.8494 | 0 | -435.0149 | 0 | 918 | 2118 | 2678 | 594 | 2870 | 9178 | 1015.7286 | 0 | -145.6987 | 0 | -870.0298 | 0 | 610 | 1964 | 2769 | 371 | 3462 | 9176 | No |  | C2 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C2 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | C2 | 14.3286 | 24.8132 | 25.7894 | 44.0332 | 135.6589 | C2 | 9198.9552 | 75804.2445 | 43429.399 | 36723.6999 | 390426.3334 | 555582.632 |  | 14787.1056 | 75531.2996 | 42294.6641 | 36679.6667 | 356782.9245 | 526075.6605 |  | 13153.6462 | 52554.3011 | 69064.0918 | 26155.7287 | 389341.0621 | 550268.83 |  | 20430.6257 | 52554.3011 | 67185.348 | 26155.7287 | 330327.4151 | 496653.4186 |  | 8740.4403 | 48733.0724 | 71410.9298 | 16336.3221 | 469651.1349 | 614871.8996 |  | 23294.3992 | 48733.0724 | 67653.4423 | 16336.3221 | 351623.8408 | 507641.0768
|  |  | 3561 | 3561 | C3 | 400 | 1181 | 637 | 323 | 1020 | 3561 | 249 | 1185 | 653 | 324 | 1116 | 3527 | 197.0287 | 0 | -28.2623 | 0 | -168.7664 | 0 | 356 | 822 | 1039 | 231 | 1113 | 3561 | 394.0575 | 0 | -56.5246 | 0 | -337.5329 | 0 | 237 | 762 | 1075 | 144 | 1344 | 3562 |  |  | C3 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C3 | 15254 | 15254 | 15254 | 15254 | 15254 | C3 | 21.4929 | 37.2198 | 38.6841 | 66.0498 | 203.4884 | C3 | 5351.7286 | 44105.4156 | 25260.746 | 21400.1417 | 227093.0098 | 323211.0417 |  | 8597.1544 | 43956.5366 | 24641.7997 | 21334.0919 | 207558.1272 | 306087.7097 |  | 7651.4674 | 30594.6427 | 40192.8256 | 15257.5084 | 226482.5447 | 320178.9889 |  | 11886.1839 | 30594.6427 | 39099.5221 | 15257.5084 | 192140.5401 | 288978.3972 |  | 5093.814 | 28361.4571 | 41585.4548 | 9511.1741 | 273488.3558 | 358040.2558 |  | 13563.2469 | 28361.4571 | 39398.8478 | 9511.1741 | 204804.3466 | 295639.0724
|  |  | 781 | 781 | C4 | 88 | 258 | 140 | 71 | 224 | 781 | 55 | 260 | 143 | 71 | 245 | 774 | 43.2033 | 0 | -6.1972 | 0 | -37.0061 | 0 | 78 | 180 | 228 | 51 | 244 | 781 | 86.4066 | 0 | -12.3944 | 0 | -74.0122 | 0 | 52 | 167 | 236 | 32 | 295 | 782 |  |  | C4 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C4 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | C4 | 35.8215 | 62.0329 | 64.4736 | 110.083 | 339.1473 | C4 | 1970.1812 | 16128.5627 | 9219.721 | 7815.8954 | 83091.0803 | 118225.4406 |  | 3152.2899 | 16004.4968 | 9026.3003 | 7815.8954 | 75968.9877 | 111967.9701 |  | 2794.0752 | 11165.928 | 14699.9747 | 5614.2347 | 82751.9331 | 117026.1457 |  | 4341.6817 | 11165.928 | 14300.4194 | 5614.2347 | 70201.4089 | 105623.6726 |  | 1862.7168 | 10359.4999 | 15215.7633 | 3522.6571 | 100048.4437 | 131009.0807 |  | 4957.9299 | 10359.4999 | 14416.6526 | 3522.6571 | 74947.3953 | 108204.1346
|  |  | 16772 | 16772 |  | 1885 | 5561 | 2998 | 1522 | 4806 |  | 1174 | 5582 | 3077 | 1524 | 5258 |  | 928 | 0 | -133.1147 | 0 | -794.8853 |  | 1677 | 3870 | 4894 | 1087 | 5244 |  | 1856 | 0 | -266.2295 | 0 | -1589.7705 |  | 1115 | 3589 | 5061 | 679 | 6328 | [22 empty] | 18807.7081 | 154831.7203 | 88687.2685 | 75032.5955 | 797375.9216 | 1134735.2141 |  | 30197.5048 | 154216.3536 | 86451.325 | 74922.5125 | 728813.9102 | 1074601.6061 |  | 26858.9432 | 107341.7878 | 141088.81 | 53531.1774 | 795151.1155 | 1123971.834 |  | 41722.6817 | 107341.7878 | 137251.3447 | 53531.1774 | 674611.6219 | 1014458.6136 |  | 17863.454 | 99543.0075 | 145921.7491 | 33438.8222 | 959705.3693 | 1256472.402 |  | 47590.9309 | 99543.0075 | 138246.8184 | 33438.8222 | 718626.3821 | 1037445.9611
| LV UGB |  | 1539 | 1539 | C1 | 860 | 217 | 86 | 115 | 261 | 1539 | 817 | 217 | 86 | 115 | 302 | 1537 | 67.0845 | 0 | 0 | 0 | -67.0845 | 0 | 860 | 188 | 111 | 35 | 345 | 1539 | 134.169 | 0 | 0 | 0 | -134.169 | 0 | 658 | 379 | 44 | 77 | 380 | 1538 |  |  | C1 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C1 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | C1 | 5.8409 | 5.8409 | 10.1144 | 21.2659 | 48.5832 | C1 | 4772.0163 | 1267.4756 | 869.8342 | 2445.5752 | 14672.1255 | 24027.0268 |  | 5023.1751 | 1267.4756 | 869.8342 | 2445.5752 | 12680.2145 | 22286.2745 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 5415.0091 | 1098.0894 | 1122.693 | 744.3055 | 13502.0228 | 21882.1198 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133 |  | 4626.9811 | 2213.7016 | 445.0314 | 1637.4721 | 11943.2545 | 20866.4407
|  |  | 10442 | 10442 | C2 | 5837 | 1470 | 580 | 784 | 1771 | 10442 | 5541 | 1470 | 580 | 784 | 2051 | 10426 | 455.242 | 0 | 0 | 0 | -455.242 | 0 | 5837 | 1273 | 749 | 237 | 2344 | 10440 | 910.484 | 0 | 0 | 0 | -910.484 | 0 | 4465 | 2572 | 299 | 524 | 2580 | 10440 |  |  | C2 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C2 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | C2 | 8.3441 | 8.3441 | 14.4491 | 30.3798 | 69.4046 | C2 | 46234.9053 | 12265.8926 | 8380.4623 | 23817.7759 | 142348.7677 | 233047.8039 |  | 48704.7721 | 12265.8926 | 8380.4623 | 23817.7759 | 122915.4889 | 216084.3918 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 52503.377 | 10622.0961 | 10822.3556 | 7200.0165 | 131088.4336 | 212236.2787 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261 |  | 44853.8155 | 21461.14 | 4320.2728 | 15919.0237 | 115872.0391 | 202426.2911
|  |  | 8109 | 8109 | C3 | 4534 | 1142 | 451 | 608 | 1374 | 8109 | 4305 | 1142 | 451 | 608 | 1593 | 8099 | 353.6735 | 0 | 0 | 0 | -353.6735 | 0 | 4534 | 990 | 583 | 184 | 1820 | 8111 | 707.347 | 0 | 0 | 0 | -707.347 | 0 | 3469 | 1998 | 233 | 407 | 2005 | 8112 |  |  | C3 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C3 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | C3 | 12.5162 | 12.5162 | 21.6736 | 45.5697 | 104.1069 | C3 | 53882.3139 | 14293.5197 | 9774.7978 | 27706.3924 | 165842.2138 | 271499.2376 |  | 56748.5276 | 14293.5197 | 9774.7978 | 27706.3924 | 143042.8134 | 251566.0509 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 61175.1819 | 12391.0548 | 12635.7142 | 8384.8293 | 152654.6337 | 247241.4138 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232 |  | 52272.0653 | 25007.4014 | 5049.951 | 18546.8778 | 135094.5658 | 235970.8612
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C4 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | C4 | 20.8604 | 20.8604 | 36.1227 | 75.9495 | 173.5114 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20090 | 20090 |  | 11231 | 2829 | 1117 | 1507 | 3406 |  | 10663 | 2829 | 1117 | 1507 | 3946 |  | 876 | 0 | 0 | 0 | -876 |  | 11231 | 2451 | 1443 | 456 | 4509 |  | 1752 | 0 | 0 | 0 | -1752 |  | 8592 | 4949 | 576 | 1008 | 4965 | [22 empty] | 104889.2355 | 27826.8879 | 19025.0942 | 53969.7436 | 322863.1071 | 528574.0683 |  | 110476.4748 | 27826.8879 | 19025.0942 | 53969.7436 | 278638.5167 | 489936.7172 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 119093.568 | 24111.2403 | 24580.7627 | 16329.1512 | 297245.09 | 481359.8124 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823 |  | 101752.8618 | 48682.243 | 9815.2552 | 36103.3736 | 262909.8593 | 459263.5929
| LV OHL Support |  | 28539 | 28539 | C1 | 3308 | 4632 | 13014 | 4744 | 2841 | 28539 | 657 | 4886 | 13689 | 5431 | 3966 | 28629 | 1074.7295 | 0 | 0 | -322.4189 | -752.3107 | 0 | 3150 | 4107 | 12747 | 4305 | 4229 | 28538 | 2009.4448 | 0 | 0 | -602.8334 | -1406.6114 | 0 | 3052 | 3425 | 13256 | 3830 | 4976 | 28539 |  |  | C1 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C1 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | C1 | 12.4899 | 12.6968 | 21.5987 | 42.1194 | 71.1283 | C1 | 8205.8724 | 62036.6 | 295664.9903 | 228750.6004 | 282094.657 | 876752.7201 |  | 41316.6302 | 58811.611 | 281085.8488 | 199814.555 | 202075.3708 | 783104.0158 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 52766.5014 | 52145.7872 | 275318.9884 | 167744.0304 | 247290.8445 | 795266.1518 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123 |  | 63217.0025 | 43486.5647 | 286312.741 | 135926.4015 | 253884.3819 | 782827.0916
|  |  | 9423 | 9423 | C2 | 1092 | 1530 | 4297 | 1566 | 938 | 9423 | 216 | 1613 | 4520 | 1794 | 1309 | 9452 | 354.8824 | 0 | 0 | -106.4647 | -248.4177 | 0 | 1040 | 1356 | 4209 | 1422 | 1397 | 9424 | 663.5312 | 0 | 0 | -199.0594 | -464.4719 | 0 | 1008 | 1131 | 4377 | 1264 | 1643 | 9423 |  |  | C2 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C2 | 7778 | 7778 | 7778 | 7778 | 7778 | C2 | 17.8427 | 18.1383 | 30.8553 | 60.1706 | 101.6118 | C2 | 3854.0301 | 29257.0714 | 139466.0735 | 107946.0708 | 133009.8357 | 413533.0816 |  | 19484.2633 | 27751.5929 | 132585.3358 | 94227.1721 | 95311.8609 | 369360.2251 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 24888.5127 | 24595.5294 | 129870.0671 | 79156.5578 | 116709.5083 | 375220.1753 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713 |  | 29824.6838 | 20514.4128 | 135053.7619 | 64078.1253 | 119752.3561 | 369223.3398
|  |  | 21147 | 21147 | C3 | 2451 | 3433 | 9643 | 3515 | 2105 | 21147 | 487 | 3621 | 10144 | 4025 | 2939 | 21216 | 796.3881 | 0 | 0 | -238.9164 | -557.4717 | 0 | 2334 | 3043 | 9445 | 3191 | 3134 | 21147 | 1489.0239 | 0 | 0 | -446.7072 | -1042.3168 | 0 | 2262 | 2538 | 9823 | 2837 | 3687 | 21147 |  |  | C3 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C3 | 11667 | 11667 | 11667 | 11667 | 11667 | C3 | 26.7641 | 27.2074 | 46.283 | 90.2559 | 152.4177 | C3 | 13034.1157 | 98518.1547 | 469494.6404 | 363280.0458 | 447955.585 | 1392282.5417 |  | 65598.8042 | 93403.1553 | 446306.8629 | 317249.5307 | 320839.2332 | 1243397.5863 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 83782.0141 | 82792.2521 | 437142.8311 | 266442.9947 | 392708.4905 | 1262868.5825 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215 |  | 100392.7724 | 69052.4929 | 454637.8009 | 215738.0581 | 403096.5049 | 1242917.6293
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C4 | 19445 | 19445 | 19445 | 19445 | 19445 | C4 | 44.6068 | 45.3457 | 77.1383 | 150.4265 | 254.0295 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 59109 | 59109 |  | 6851 | 9595 | 26954 | 9825 | 5884 |  | 1360 | 10120 | 28353 | 11250 | 8214 |  | 2226 | 0 | 0 | -667.8 | -1558.2 |  | 6524 | 8506 | 26401 | 8918 | 8760 |  | 4162 | 0 | 0 | -1248.6 | -2913.4 |  | 6322 | 7094 | 27456 | 7931 | 10306 | [22 empty] | 25094.0183 | 189811.8262 | 904625.7043 | 699976.717 | 863060.0777 | 2682568.3434 |  | 126399.6978 | 179966.3591 | 859978.0475 | 611291.2579 | 618226.4649 | 2395861.8271 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 161437.0281 | 159533.5686 | 842331.8866 | 513343.5829 | 756708.8433 | 2433354.9096 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051 |  | 193434.4587 | 133053.4703 | 876004.3039 | 415742.5849 | 776733.2429 | 2394968.0607
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 |  | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 |  | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 |  | 322253.2779 | 290986.5968 | 1004163.994 | 583203.9116 | 1728565.5552 | 3929173.3355 |  | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 |  | 342778.2514 | 281278.7207 | 1024066.3775 | 485284.7807 | 1758269.4843 | 3891677.6147
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1899 | 1899 | C1 | 312 | 461 | 253 | 229 | 644 | 1899 | 239 | 463 | 254 | 233 | 678 | 1867 | 172.718 | -8.4611 | -5.3221 | -16.131 | -142.8038 | 0 | 161 | 561 | 185 | 129 | 864 | 1900 | 350.2899 | -17.1599 | -10.7939 | -32.7154 | -289.6208 | 0 | 106 | 578 | 142 | 93 | 981 | 1900 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C1 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | C1 | 6.1027 | 79.5042 | 139.3443 | 269.1109 | 467.1086 | C1 | 1458.5385 | 36810.4663 | 35393.4599 | 62702.8297 | 316699.658 | 453064.9523 |  | 1904.0335 | 36651.4578 | 35254.1156 | 61626.3862 | 300817.9642 | 436253.9573 |  | 982.5301 | 44601.8825 | 25778.7011 | 34715.3005 | 403581.865 | 509660.2792 |  | 2036.5712 | 43929.1931 | 25037.0897 | 30374.267 | 336876.9914 | 438254.1125 |  | 646.8832 | 45953.4547 | 19786.8949 | 25027.3097 | 458233.5759 | 549648.1184 |  | 2784.5872 | 44589.1712 | 18282.8306 | 16223.2465 | 322949.2187 | 404829.0543
|  |  | 451 | 451 | C2 | 74 | 110 | 60 | 54 | 153 | 451 | 57 | 110 | 60 | 55 | 161 | 443 | 41.0292 | -2.0099 | -1.2643 | -3.8319 | -33.923 | 0 | 38 | 133 | 44 | 31 | 205 | 451 | 83.2114 | -4.0763 | -2.5641 | -7.7715 | -68.7994 | 0 | 25 | 137 | 34 | 22 | 233 | 451 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C2 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | C2 | 8.7181 | 113.5775 | 199.0633 | 384.4441 | 667.2981 | C2 | 496.9318 | 12493.5245 | 11943.7997 | 21144.4245 | 107434.9872 | 153513.6677 |  | 645.1395 | 12493.5245 | 11943.7997 | 20759.9804 | 102096.6028 | 147939.0469 |  | 331.2879 | 15105.8069 | 8758.7865 | 11917.7665 | 136796.1017 | 172909.7495 |  | 688.9844 | 14877.5249 | 8507.1153 | 10444.6053 | 114159.3182 | 148677.548 |  | 217.9526 | 15560.1169 | 6768.1532 | 8457.7698 | 155480.4473 | 186484.4397 |  | 943.3979 | 15097.1374 | 6257.738 | 5470.047 | 109570.7178 | 137339.0382
|  |  | 2347 | 2347 | C3 | 386 | 569 | 313 | 283 | 796 | 2347 | 295 | 572 | 315 | 288 | 838 | 2308 | 213.2528 | -10.4468 | -6.5712 | -19.9168 | -176.3181 | 0 | 200 | 692 | 228 | 160 | 1066 | 2346 | 432.4987 | -21.1871 | -13.3271 | -40.3933 | -357.5913 | 0 | 132 | 713 | 174 | 116 | 1211 | 2346 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C3 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | C3 | 13.0772 | 170.3662 | 298.595 | 576.6661 | 1000.9471 | C3 | 3857.7601 | 97449.4911 | 94057.423 | 166079.8431 | 838793.658 | 1200238.1753 |  | 5047.7811 | 96938.3924 | 93460.233 | 163196.5125 | 796753.8804 | 1155396.7993 |  | 2615.4306 | 117893.4403 | 68079.6585 | 92266.5795 | 1067009.5935 | 1347864.7025 |  | 5404.1706 | 116113.6655 | 66117.5328 | 80781.2464 | 890524.502 | 1158941.1173 |  | 1726.1842 | 121471.1314 | 51955.5289 | 66893.2701 | 1212146.921 | 1454193.0356 |  | 7382.0362 | 117861.5648 | 47976.1357 | 43599.8311 | 854216.9695 | 1071036.5372
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C4 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | C4 | 21.7953 | 283.9437 | 497.6583 | 961.1102 | 1668.2451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4697 | 4697 |  | 772 | 1140 | 626 | 566 | 1593 |  | 591 | 1145 | 629 | 576 | 1677 |  | 427 | -20.9177 | -13.1576 | -39.8797 | -353.0449 |  | 399 | 1386 | 457 | 320 | 2135 |  | 866 | -42.4233 | -26.685 | -80.8802 | -716.0115 |  | 263 | 1428 | 350 | 231 | 2425 | [22 empty] | 5813.2304 | 146753.4819 | 141394.6826 | 249927.0972 | 1262928.3032 | 1806816.7953 |  | 7596.9541 | 146083.3747 | 140658.1483 | 245582.8791 | 1199668.4473 | 1739589.8035 |  | 3929.2486 | 177601.1297 | 102617.1461 | 138899.6466 | 1607387.5603 | 2030434.7312 |  | 8129.7262 | 174920.3835 | 99661.7378 | 121600.1187 | 1341560.8117 | 1745872.7778 |  | 2591.0199 | 182984.703 | 78510.577 | 100378.3496 | 1825860.9442 | 2190325.5937 |  | 11110.0214 | 177547.8734 | 72516.7043 | 65293.1245 | 1286736.9061 | 1613204.6297
| HV Switchgear (GM) - Distribution |  | 12 | 11.2924 | C1 | 1 | 6 | 3 | 1 | 1 | 12 | 1 | 6 | 3 | 1 | 1 | 12 | 1.2526 | -0.064586 | -0.21955 | -0.26213 | -1.0601 | -0.35381 | 1 | 5 | 3 | 1 | 2 | 12 | 2.4988 | -0.12892 | -0.43823 | -0.52323 | -2.1161 | -0.70762 | 1 | 5 | 2 | 1 | 3 | 12 |  |  | C1 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C1 | 22715 | 22715 | 22715 | 22715 | 22715 | C1 | 19.285 | 19.285 | 33.3683 | 65.6463 | 121.5252 | C1 | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 43.4407 | 95.1796 | 92.7791 | 48.4385 | 114.2204 | 394.0583 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669 |  | 67.4745 | 93.939 | 52.1138 | 31.2984 | 107.4222 | 352.2477
|  |  | 28964 | 27263.1656 | C2 | 2639 | 14945 | 6789 | 1775 | 2816 | 28964 | 1310 | 15230 | 7011 | 1941 | 3415 | 28907 | 3010.6287 | -155.2379 | -527.6952 | -630.0499 | -2548.0628 | -850.4172 | 2555 | 13020 | 6152 | 2634 | 4601 | 28962 | 6006.0714 | -309.8653 | -1053.315 | -1257.6217 | -5086.1038 | -1700.8344 | 2437 | 11427 | 5340 | 2529 | 7229 | 28962 |  |  | C2 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C2 | 32450 | 32450 | 32450 | 32450 | 32450 | C2 | 27.55 | 27.55 | 47.669 | 93.7805 | 173.6075 | C2 | 36090.5655 | 419587.2615 | 334207.7095 | 182027.9505 | 592869.6125 | 1564783.0995 |  | 72704.5819 | 411735.4972 | 323625.1804 | 166460.3875 | 488878.72 | 1463404.3671 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 153333.3494 | 354424.8383 | 268105.2654 | 187931.4418 | 356405.2876 | 1320200.1824 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222 |  | 232607.0394 | 306277.6173 | 204342.2036 | 119230.4889 | 372022.8511 | 1234480.2003
|  |  | 1505 | 1416.6059 | C3 | 137 | 777 | 353 | 92 | 146 | 1505 | 68 | 792 | 364 | 101 | 177 | 1502 | 156.4654 | -8.0679 | -27.4249 | -32.7443 | -132.4254 | -44.197 | 133 | 677 | 320 | 137 | 239 | 1506 | 312.1416 | -16.104 | -54.7418 | -65.3599 | -264.33 | -88.3941 | 127 | 594 | 278 | 131 | 376 | 1506 |  |  | C3 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C3 | 48675 | 48675 | 48675 | 48675 | 48675 | C3 | 41.3251 | 41.3251 | 71.5036 | 140.6707 | 260.4112 | C3 | 2810.1051 | 32729.4594 | 26027.3013 | 14207.7458 | 46092.7912 | 121867.4028 |  | 5661.5353 | 32109.5833 | 25240.762 | 12941.709 | 38020.0425 | 113973.632 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 11962.1807 | 27643.6703 | 20920.1687 | 14665.7228 | 27753.2213 | 102944.9638 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712 |  | 18147.5608 | 23881.595 | 15963.756 | 9233.6451 | 29080.1296 | 96306.6864
|  |  | 34 | 31.9361 | C4 | 3 | 18 | 8 | 2 | 3 | 34 | 2 | 18 | 9 | 2 | 4 | 35 | 3.6533 | -0.18838 | -0.64034 | -0.76454 | -3.092 | -1.032 | 3 | 16 | 7 | 3 | 6 | 35 | 7.2882 | -0.37601 | -1.2782 | -1.5261 | -6.1718 | -2.0639 | 3 | 14 | 6 | 3 | 9 | 35 |  |  | C4 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C4 | 81125 | 81125 | 81125 | 81125 | 81125 | C4 | 68.8751 | 68.8751 | 119.1726 | 234.4512 | 434.0187 | C4 | 137.7502 | 1239.7523 | 1072.5536 | 468.9025 | 1736.075 | 4655.0336 |  | 206.6254 | 1239.7523 | 953.381 | 468.9025 | 1302.0562 | 4170.7174 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 458.2466 | 1089.0276 | 757.8973 | 524.1054 | 1262.1319 | 4091.4088 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354 |  | 708.5985 | 938.3539 | 562.7138 | 345.5621 | 1227.4857 | 3782.7142
|  |  | 30515 | 28723 |  | 2780 | 15746 | 7153 | 1870 | 2966 |  | 1381 | 16046 | 7387 | 2045 | 3597 |  | 3172 | -163.5588 | -555.98 | -663.8209 | -2684.6404 |  | 2692 | 13718 | 6482 | 2775 | 4848 |  | 6328 | -326.4742 | -1109.7732 | -1325.0309 | -5358.7216 |  | 2568 | 12040 | 5626 | 2664 | 7617 | [22 empty] | 39057.7059 | 453672.1834 | 361407.6695 | 196770.2451 | 640820.004 | 1691727.8078 |  | 78592.0276 | 445200.543 | 349919.4284 | 179936.6453 | 528322.344 | 1581970.9884 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 165797.2173 | 383252.7159 | 289876.1106 | 203169.7085 | 385534.8612 | 1427630.6134 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977 |  | 251530.6732 | 331191.5052 | 220920.7872 | 128840.9944 | 402437.8886 | 1334921.8487
| HV Transformer (GM) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C1 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | C1 | 17.5777 | 17.5777 | 30.3869 | 59.8934 | 168.7346 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14545 | 14541.5442 | C2 | 4823 | 6506 | 2560 | 334 | 322 | 14545 | 4284 | 6630 | 2571 | 336 | 588 | 14409 | 307.5687 | -68.3015 | 0 | 0 | -242.7231 | -3.4558 | 4178 | 6111 | 3001 | 644 | 613 | 14547 | 1216.4515 | -267.8935 | 0 | 0 | -952.0139 | -3.4558 | 3436 | 5557 | 3195 | 1197 | 1161 | 14546 |  |  | C2 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C2 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | C2 | 25.1111 | 25.1111 | 43.4099 | 85.5621 | 241.0494 | C2 | 107575.7912 | 166486.3434 | 111606.7455 | 28748.8546 | 141737.0648 | 556154.7995 |  | 121110.6538 | 163372.5717 | 111129.237 | 28577.7305 | 77617.9165 | 501808.1094 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 112637.3957 | 151738.5798 | 130272.9845 | 55101.9713 | 89255.0407 | 539005.972 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635 |  | 116828.0009 | 132815.0827 | 138694.497 | 102417.7945 | 50375.9911 | 541131.3661
|  |  | 2292 | 2291.4558 | C3 | 760 | 1025 | 403 | 53 | 51 | 2292 | 675 | 1044 | 405 | 53 | 93 | 2270 | 48.4313 | -10.7551 | 0 | 0 | -38.2204 | -0.54417 | 658 | 962 | 473 | 101 | 96 | 2290 | 191.5485 | -42.1838 | 0 | 0 | -149.9088 | -0.54417 | 541 | 875 | 503 | 189 | 183 | 2291 |  |  | C3 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C3 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | C3 | 37.6666 | 37.6666 | 65.1148 | 128.3431 | 361.5741 | C3 | 25424.9506 | 39323.9237 | 26371.4889 | 6802.1843 | 33626.3955 | 131548.943 |  | 28626.6111 | 38608.2584 | 26241.2593 | 6802.1843 | 18440.2814 | 118718.5945 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 26608.8601 | 35830.1556 | 30799.2944 | 12962.6532 | 20891.6197 | 127092.5829 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491 |  | 27592.6048 | 31369.348 | 32752.738 | 24256.8461 | 11964.9254 | 127936.4623
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C4 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | C4 | 62.7777 | 62.7777 | 108.5246 | 213.9052 | 602.6236 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 16837 | 16833 |  | 5583 | 7531 | 2963 | 387 | 373 |  | 4959 | 7674 | 2976 | 389 | 681 |  | 356 | -79.0565 | 0 | 0 | -280.9435 |  | 4836 | 7073 | 3474 | 745 | 709 |  | 1408 | -310.0774 | 0 | 0 | -1101.9226 |  | 3977 | 6432 | 3698 | 1386 | 1344 | [22 empty] | 133000.7418 | 205810.2671 | 137978.2344 | 35551.0389 | 175363.4603 | 687703.7425 |  | 149737.2649 | 201980.8301 | 137370.4963 | 35379.9148 | 96058.1979 | 620526.7039 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 139246.2558 | 187568.7353 | 161072.2789 | 68064.6245 | 110146.6604 | 666098.5549 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126 |  | 144420.6058 | 164184.4307 | 171447.235 | 126674.6405 | 62340.9164 | 669067.8285
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 3628 | 3628 | C1 | 204 | 1790 | 1305 | 281 | 48 | 3628 | 44 | 1814 | 1321 | 320 | 128 | 3627 | 23.3161 | 0 | 0 | -6.9948 | -16.3213 | 0 | 192 | 1677 | 1326 | 316 | 117 | 3628 | 46.6323 | 0 | 0 | -13.9897 | -32.6426 | 0 | 185 | 1663 | 1340 | 304 | 137 | 3629 |  |  | C1 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C1 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | C1 | 27.1392 | 27.1879 | 46.931 | 91.5265 | 143.007 | C1 | 1194.1258 | 49318.8161 | 61995.8864 | 29288.4641 | 18304.9008 | 160102.1933 |  | 5536.4014 | 48666.307 | 61244.99 | 25718.9326 | 6864.3378 | 148030.9687 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5843.5125 | 45594.0764 | 62230.5415 | 28282.1454 | 14397.7634 | 156348.0393 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833 |  | 6286.3198 | 45213.4461 | 62887.5759 | 26543.6151 | 14923.8441 | 155854.801
|  |  | 75099 | 75099 | C2 | 4224 | 37056 | 27000 | 5822 | 997 | 75099 | 902 | 37540 | 27350 | 6618 | 2653 | 75063 | 482.6015 | 0 | 0 | -144.7805 | -337.8211 | 0 | 3970 | 34721 | 27449 | 6541 | 2419 | 75100 | 965.2031 | 0 | 0 | -289.5609 | -675.6421 | 0 | 3829 | 34431 | 27726 | 6284 | 2830 | 75100 |  |  | C2 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C2 | 17378 | 17378 | 17378 | 17378 | 17378 | C2 | 38.7703 | 38.8398 | 67.0443 | 130.7521 | 204.2958 | C2 | 34970.8268 | 1458047.2182 | 1833662.2614 | 865317.2125 | 541996.6725 | 4733994.1914 |  | 163765.8232 | 1439248.7405 | 1810196.748 | 761238.5632 | 203682.8807 | 4378132.7556 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 172628.7774 | 1348557.7374 | 1840299.6495 | 836318.9578 | 425176.047 | 4622981.1691 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055 |  | 185872.7776 | 1337294.1867 | 1858870.9272 | 783785.3301 | 440126.1918 | 4605949.4134
|  |  | 20166 | 20166 | C3 | 1134 | 9950 | 7251 | 1563 | 268 | 20166 | 242 | 10080 | 7344 | 1777 | 712 | 20155 | 129.5903 | 0 | 0 | -38.8771 | -90.7132 | 0 | 1066 | 9323 | 7371 | 1757 | 649 | 20166 | 259.1805 | 0 | 0 | -77.7542 | -181.4264 | 0 | 1028 | 9245 | 7445 | 1687 | 760 | 20165 |  |  | C3 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C3 | 26067 | 26067 | 26067 | 26067 | 26067 | C3 | 58.1555 | 58.2597 | 100.5665 | 196.1281 | 306.4437 | C3 | 14073.6254 | 587258.2296 | 738560.2732 | 348519.6479 | 218187.8802 | 1906599.6564 |  | 65948.3109 | 579684.4628 | 729207.59 | 306548.2328 | 82126.8987 | 1763515.4952 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 69530.1217 | 543155.6026 | 741275.5683 | 336972.1981 | 171083.4519 | 1862016.9427 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549 |  | 74856.5969 | 538611.3425 | 748717.4883 | 315618.343 | 177300.2189 | 1855103.9895
|  |  | 77 | 77 | C4 | 4 | 38 | 28 | 6 | 1 | 77 | 1 | 38 | 28 | 7 | 3 | 77 | 0.49207 | 0 | 0 | -0.14762 | -0.34445 | 0 | 4 | 35 | 28 | 7 | 2 | 76 | 0.98414 | 0 | 0 | -0.29524 | -0.6889 | 0 | 4 | 35 | 28 | 6 | 3 | 76 |  |  | C4 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C4 | 43445 | 43445 | 43445 | 43445 | 43445 | C4 | 96.9258 | 97.0996 | 167.6108 | 326.8802 | 510.7394 | C4 | 96.9258 | 3689.7839 | 4693.1027 | 2288.1613 | 1532.2183 | 12300.1918 |  | 387.7032 | 3689.7839 | 4693.1027 | 1961.2811 | 510.7394 | 11242.6102 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 435.3977 | 3398.4851 | 4693.1027 | 2239.9067 | 845.5544 | 11612.4465 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903 |  | 483.0922 | 3398.4851 | 4693.1027 | 1864.7719 | 1180.3693 | 11619.8211
|  |  | 98970 | 98970 |  | 5566 | 48834 | 35584 | 7672 | 1314 |  | 1189 | 49472 | 36043 | 8722 | 3496 |  | 636 | 0 | 0 | -190.8 | -445.2 |  | 5232 | 45756 | 36174 | 8621 | 3187 |  | 1272 | 0 | 0 | -381.6 | -890.4 |  | 5046 | 45374 | 36539 | 8281 | 3730 | [22 empty] | 50335.5039 | 2098314.0478 | 2638911.5237 | 1245413.4858 | 780021.6718 | 6812996.2329 |  | 235638.2387 | 2071289.2941 | 2605342.4306 | 1095467.0096 | 293184.8567 | 6300921.8297 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 248437.8094 | 1940705.9016 | 2648498.862 | 1203813.208 | 611502.8166 | 6652958.5975 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339 |  | 267498.7863 | 1924517.4605 | 2675169.0941 | 1127812.06 | 633530.6242 | 6628528.0251
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 |  | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 |  | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 |  | 561611.0086 | 2686447.7363 | 3199108.9893 | 1596647.6597 | 2448745.1498 | 10492560.5436 |  | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 |  | 674560.0867 | 2597441.2697 | 3140053.8206 | 1448620.8195 | 2385046.3353 | 10245722.3319
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 937 | 937 | C1 | 215 | 458 | 214 | 23 | 27 | 937 | 174 | 460 | 214 | 24 | 45 | 917 | 17.3464 | 0 | 0 | -1.9081 | -15.4383 | 0 | 184 | 319 | 345 | 45 | 41 | 934 | 36.2697 | 0 | 0 | -3.9897 | -32.28 | 0 | 170 | 231 | 377 | 75 | 83 | 936 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C1 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | C1 | 4.7176 | 61.4602 | 105.2948 | 208.0341 | 361.0949 | C1 | 820.8667 | 28271.6771 | 22533.0796 | 4992.8196 | 16249.2689 | 72867.7119 |  | 1014.2893 | 28148.7567 | 22533.0796 | 4784.7854 | 9749.5614 | 66230.4725 |  | 868.043 | 19605.7934 | 36326.6938 | 9361.5367 | 14804.8895 | 80966.9564 |  | 949.8767 | 19605.7934 | 36326.6938 | 8964.5862 | 9230.2042 | 75077.1543 |  | 801.9962 | 14197.2987 | 39696.1263 | 15602.5612 | 29970.8738 | 100268.8562 |  | 973.1031 | 14197.2987 | 39696.1263 | 14772.5738 | 18314.7136 | 87953.8155
|  |  | 333 | 333 | C2 | 77 | 163 | 76 | 8 | 9 | 333 | 62 | 164 | 77 | 9 | 16 | 328 | 6.1886 | 0 | 0 | -0.68075 | -5.5079 | 0 | 66 | 114 | 123 | 17 | 15 | 335 | 12.9399 | 0 | 0 | -1.4234 | -11.5165 | 0 | 60 | 82 | 135 | 27 | 30 | 334 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C2 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | C2 | 6.7395 | 87.8002 | 150.4211 | 297.1916 | 515.8498 | C2 | 417.8468 | 14399.2393 | 11582.4241 | 2674.7248 | 8253.5969 | 37327.8318 |  | 518.9387 | 14311.439 | 11432.003 | 2377.5331 | 4642.6483 | 33282.5622 |  | 444.8046 | 10009.2273 | 18501.7944 | 5052.2579 | 7737.7471 | 41745.8313 |  | 486.5127 | 10009.2273 | 18501.7944 | 4849.9447 | 4896.5044 | 38743.9834 |  | 404.3678 | 7199.6196 | 20306.8475 | 8024.1743 | 15475.4942 | 51410.5035 |  | 491.5757 | 7199.6196 | 20306.8475 | 7601.1557 | 9534.714 | 45133.9125
|  |  | 294 | 294 | C3 | 68 | 144 | 67 | 7 | 8 | 294 | 55 | 144 | 67 | 8 | 14 | 288 | 5.4424 | 0 | 0 | -0.59866 | -4.8437 | 0 | 58 | 100 | 108 | 15 | 13 | 294 | 11.3795 | 0 | 0 | -1.2517 | -10.1277 | 0 | 53 | 72 | 119 | 24 | 26 | 294 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C3 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | C3 | 10.1092 | 131.7004 | 225.6316 | 445.7875 | 773.7747 | C3 | 556.0058 | 18964.8517 | 15117.3198 | 3566.2997 | 10832.8459 | 49037.3229 |  | 687.4253 | 18964.8517 | 15117.3198 | 3120.5122 | 6190.1977 | 44080.3067 |  | 586.3334 | 13170.0359 | 24368.217 | 6686.8119 | 10059.0712 | 54870.4694 |  | 641.3513 | 13170.0359 | 24368.217 | 6419.937 | 6311.1379 | 50910.6789 |  | 535.7874 | 9482.4258 | 26850.165 | 10698.8991 | 20118.1425 | 67685.4198 |  | 650.8248 | 9482.4258 | 26850.165 | 10140.8878 | 12281.5545 | 59405.8579
|  |  | 217 | 217 | C4 | 50 | 106 | 50 | 5 | 6 | 217 | 40 | 107 | 50 | 6 | 10 | 213 | 4.0226 | 0 | 0 | -0.44249 | -3.5801 | 0 | 43 | 74 | 80 | 11 | 10 | 218 | 8.4109 | 0 | 0 | -0.9252 | -7.4857 | 0 | 39 | 53 | 88 | 18 | 19 | 217 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C4 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | C4 | 16.8487 | 219.5006 | 376.0527 | 742.9791 | 1289.6245 | C4 | 673.9464 | 23486.564 | 18802.6365 | 4457.8746 | 12896.2452 | 60317.2668 |  | 842.433 | 23267.0634 | 18802.6365 | 3714.8955 | 7737.7471 | 54364.7756 |  | 724.4924 | 16243.0443 | 30084.2185 | 8172.7701 | 12896.2452 | 68120.7704 |  | 792.268 | 16243.0443 | 30084.2185 | 7844.0111 | 8279.2258 | 63242.7677 |  | 657.0977 | 11633.5317 | 33092.6403 | 13373.6239 | 24502.8658 | 83259.7595 |  | 798.8105 | 11633.5317 | 33092.6403 | 12686.2186 | 14849.098 | 73060.2992
|  |  | 1781 | 1781 |  | 410 | 871 | 407 | 43 | 50 |  | 331 | 875 | 408 | 47 | 85 |  | 33 | 0 | 0 | -3.63 | -29.37 |  | 351 | 607 | 656 | 88 | 79 |  | 69 | 0 | 0 | -7.59 | -61.41 |  | 322 | 438 | 719 | 144 | 158 | [22 empty] | 2468.6657 | 85122.332 | 68035.4601 | 15691.7187 | 48231.957 | 219550.1334 |  | 3063.0864 | 84692.1109 | 67885.039 | 13997.7263 | 28320.1544 | 197958.1169 |  | 2623.6733 | 59028.1009 | 109280.9236 | 29273.3767 | 45497.953 | 245704.0275 |  | 2870.0087 | 59028.1009 | 109280.9236 | 28078.4789 | 28717.0722 | 227974.5844 |  | 2399.2492 | 42512.8759 | 119945.779 | 47699.2585 | 90067.3763 | 302624.5389 |  | 2914.3141 | 42512.8759 | 119945.779 | 45200.8359 | 54980.0802 | 265553.8851
| EHV Transformer |  | 439 | 439 | C1 | 45 | 96 | 206 | 43 | 49 | 439 | 35 | 95 | 206 | 43 | 59 | 438 | 18.9226 | 0 | 0 | 0 | -18.9226 | 0 | 29 | 75 | 143 | 90 | 102 | 439 | 53.1055 | 0 | 0 | 0 | -53.1055 | 0 | 20 | 76 | 45 | 88 | 210 | 439 |  |  | C1 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C1 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | C1 | 267.4477 | 270.1797 | 467.4393 | 909.7131 | 1679.1834 | C1 | 9360.6698 | 25667.0727 | 96292.5028 | 39117.6645 | 99071.8178 | 269509.7276 |  | 12035.1469 | 25937.2524 | 96292.5028 | 39117.6645 | 82279.9842 | 255662.5509 |  | 7755.9835 | 20263.4785 | 66843.8247 | 81874.1816 | 171276.7019 | 348014.1703 |  | 12816.8014 | 20263.4785 | 66843.8247 | 81874.1816 | 139502.1128 | 321300.399 |  | 5348.9542 | 20533.6582 | 21034.77 | 80054.7553 | 352628.5039 | 479600.6416 |  | 19551.8945 | 20533.6582 | 21034.77 | 80054.7553 | 263454.6572 | 404629.7353
|  |  | 192 | 192 | C2 | 19 | 42 | 90 | 19 | 22 | 192 | 15 | 42 | 90 | 19 | 25 | 191 | 8.2405 | 0 | 0 | 0 | -8.2405 | 0 | 13 | 33 | 62 | 39 | 45 | 192 | 23.1266 | 0 | 0 | 0 | -23.1266 | 0 | 9 | 33 | 19 | 39 | 92 | 192 |  |  | C2 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C2 | 317306 | 317306 | 317306 | 317306 | 317306 | C2 | 382.0682 | 385.971 | 667.7705 | 1299.5902 | 2398.8334 | C2 | 5731.0223 | 16210.7828 | 60099.3429 | 24692.2135 | 59970.834 | 166704.1955 |  | 7259.2949 | 16210.7828 | 60099.3429 | 24692.2135 | 52774.3339 | 161035.9681 |  | 4966.886 | 12737.0436 | 41401.7696 | 50684.0172 | 107947.5012 | 217737.2176 |  | 8115.3211 | 12737.0436 | 41401.7696 | 50684.0172 | 88179.8997 | 201118.0511 |  | 3438.6134 | 12737.0436 | 12687.6391 | 50684.0172 | 220692.6691 | 300239.9824 |  | 12274.544 | 12737.0436 | 12687.6391 | 50684.0172 | 165215.852 | 253599.0959
|  |  | 53 | 53 | C3 | 5 | 12 | 25 | 5 | 6 | 53 | 4 | 12 | 25 | 5 | 7 | 53 | 2.3108 | 0 | 0 | 0 | -2.3108 | 0 | 4 | 9 | 17 | 11 | 13 | 54 | 6.4852 | 0 | 0 | 0 | -6.4852 | 0 | 2 | 9 | 5 | 11 | 26 | 53 |  |  | C3 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C3 | 475959 | 475959 | 475959 | 475959 | 475959 | C3 | 573.1022 | 578.9565 | 1001.6557 | 1949.3853 | 3598.25 | C3 | 2292.4089 | 6947.4783 | 25041.3929 | 9746.9264 | 25187.7503 | 69215.9568 |  | 2865.5112 | 6947.4783 | 25041.3929 | 9746.9264 | 21589.5002 | 66190.809 |  | 2292.4089 | 5210.6087 | 17028.1472 | 21443.238 | 46777.2505 | 92751.6534 |  | 3616.7507 | 5210.6087 | 17028.1472 | 21443.238 | 38462.307 | 85761.0516 |  | 1146.2045 | 5210.6087 | 5008.2786 | 21443.238 | 93554.501 | 126362.8309 |  | 4862.9054 | 5210.6087 | 5008.2786 | 21443.238 | 70219.0145 | 106744.0453
|  |  | 36 | 36 | C4 | 4 | 8 | 17 | 3 | 4 | 36 | 3 | 8 | 17 | 3 | 5 | 36 | 1.526 | 0 | 0 | 0 | -1.526 | 0 | 2 | 6 | 12 | 7 | 8 | 35 | 4.2827 | 0 | 0 | 0 | -4.2827 | 0 | 2 | 6 | 4 | 7 | 17 | 36 |  |  | C4 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C4 | 793265 | 793265 | 793265 | 793265 | 793265 | C4 | 955.1704 | 964.9275 | 1669.4262 | 3248.9755 | 5997.0834 | C4 | 2865.5112 | 7719.4204 | 28380.2453 | 9746.9264 | 29985.417 | 78697.5202 |  | 3820.6815 | 7719.4204 | 28380.2453 | 9746.9264 | 23988.3336 | 73655.6072 |  | 1910.3408 | 5789.5653 | 20033.1143 | 22742.8282 | 47976.6672 | 98452.5158 |  | 3367.9496 | 5789.5653 | 20033.1143 | 22742.8282 | 38824.9998 | 90758.4572 |  | 1910.3408 | 5789.5653 | 6677.7048 | 22742.8282 | 101950.4178 | 139070.8568 |  | 6001.0494 | 5789.5653 | 6677.7048 | 22742.8282 | 76266.7062 | 117477.8539
|  |  | 720 | 720 |  | 73 | 158 | 338 | 70 | 81 |  | 57 | 157 | 338 | 70 | 96 |  | 31 | 0 | 0 | 0 | -31 |  | 48 | 123 | 234 | 147 | 168 |  | 87 | 0 | 0 | 0 | -87 |  | 33 | 124 | 73 | 145 | 345 | [22 empty] | 20249.6122 | 56544.7542 | 209813.4839 | 83303.7308 | 214215.819 | 584127.4001 |  | 25980.6345 | 56814.9339 | 209813.4839 | 83303.7308 | 180632.152 | 556544.9351 |  | 16925.6192 | 44000.6961 | 145306.8558 | 176744.2651 | 373978.1208 | 756955.557 |  | 27916.8227 | 44000.6961 | 145306.8558 | 176744.2651 | 304969.3194 | 698937.959 |  | 11844.1128 | 44270.8758 | 45408.3924 | 174924.8388 | 768826.0919 | 1045274.3117 |  | 42690.3933 | 44270.8758 | 45408.3924 | 174924.8388 | 575156.23 | 882450.7303
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | C1 | 87.4881 | 87.4881 | 262.4643 | 612.4167 | 874.881 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 211.0678 | C2 | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 | 227.0678 | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 | 234.2399 | 0 | 0 | 0 | -8.0372 | 0 | -8.0372 | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 | 227.0675 | 0 | 0 | 0 | -16 | 0 | -16 | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | 227.0675 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 124983 | 124983 | 124983 | 124983 | 124983 | C2 | 124.983 | 124.983 | 374.949 | 874.881 | 1249.83 | C2 | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 61957.3853 | 104042.3694 | 183553.1507 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 8492.1828 | 185361.3897 | 210455.7784
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | C3 | 187.4745 | 187.4745 | 562.4235 | 1312.3215 | 1874.745 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | C4 | 312.4575 | 312.4575 | 937.3725 | 2187.2025 | 3124.575 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 211.0678 |  | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 |  | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 |  | 0 | 0 | 0 | -8.0372 | 0 |  | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 |  | 0 | 0 | 0 | -16 | 0 |  | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | [22 empty] | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 61957.3853 | 104042.3694 | 183553.1507 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 8492.1828 | 185361.3897 | 210455.7784
| EHV UG Cable (Oil) |  | 17.0815 | 14.4653 | C1 | 1.6369 | 2.5218 | 2.8663 | 6.9395 | 3.1171 | 17.0815 | 1.63 | 2.5796 | 3.0569 | 8.8085 | 4.8454 | 20.9204 | 0 | 0 | 0 | -0.65712 | -0.65712 | -1.3142 | 0.0090919 | 3.5395 | 2.8444 | 5.6227 | 5.0659 | 17.0815 | 0 | 0 | 0 | -1.3081 | -1.3081 | -2.6163 | 0.0090919 | 2.2753 | 3.4238 | 1.729 | 9.6443 | 17.0815 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | C1 | 194.5762 | 194.5762 | 583.7286 | 1362.0334 | 1945.762 | C1 | 317.1507 | 501.9325 | 1784.4163 | 11997.4175 | 9428.0449 | 24028.9618 |  | 318.5082 | 490.6886 | 1673.1151 | 9451.7929 | 6065.0403 | 17999.1451 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 688.6955 | 1660.3527 | 6763.2526 | 8578.4252 | 17692.4951 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996 |  | 1.7691 | 442.7288 | 1998.557 | 573.2222 | 16220.1442 | 19236.4212
|  |  | 246.8 | 208.9989 | C2 | 23.651 | 36.4363 | 41.4126 | 100.2639 | 45.0362 | 246.8 | 23.5502 | 37.2712 | 44.1675 | 127.2676 | 70.0084 | 302.2649 | 0 | 0 | 0 | -9.4942 | -9.4942 | -18.9884 | 0.13136 | 51.1394 | 41.0967 | 81.2383 | 73.1937 | 246.7995 | 0 | 0 | 0 | -18.9005 | -18.9005 | -37.8011 | 0.13136 | 32.875 | 49.4679 | 24.9812 | 139.3439 | 246.7995 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 277966 | 277966 | 277966 | 277966 | 277966 | C2 | 277.966 | 277.966 | 833.898 | 1945.762 | 2779.66 | C2 | 6546.1447 | 10360.1311 | 36831.2217 | 247632.544 | 194599.4408 | 495969.4824 |  | 6574.1645 | 10128.0511 | 34533.9105 | 195089.612 | 125185.3879 | 371511.126 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 14215.0116 | 34270.4888 | 139596.8301 | 177062.8758 | 365181.7207 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146 |  | 36.5144 | 9138.1382 | 41251.1898 | 11831.5859 | 334791.6804 | 397049.1086
|  |  | 29.9197 | 25.337 | C3 | 2.8672 | 4.4172 | 5.0205 | 12.155 | 5.4598 | 29.9197 | 2.855 | 4.5184 | 5.3544 | 15.4287 | 8.4871 | 36.6437 | 0 | 0 | 0 | -1.151 | -1.151 | -2.302 | 0.015925 | 6.1996 | 4.9822 | 9.8485 | 8.8733 | 29.9196 | 0 | 0 | 0 | -2.2913 | -2.2913 | -4.5826 | 0.015925 | 3.9855 | 5.997 | 3.0285 | 16.8927 | 29.9196 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 416949 | 416949 | 416949 | 416949 | 416949 | C3 | 416.949 | 416.949 | 1250.847 | 2918.643 | 4169.49 | C3 | 1190.3873 | 1883.9438 | 6697.5938 | 45030.8766 | 35387.0427 | 90189.8443 |  | 1195.4826 | 1841.741 | 6279.838 | 35476.1782 | 22764.406 | 67557.6458 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 2584.9366 | 6231.936 | 25385.0626 | 32198.0964 | 66406.6716 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872 |  | 6.64 | 1661.7298 | 7501.3454 | 2151.5213 | 60880.3779 | 72201.6143
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 694915 | 694915 | 694915 | 694915 | 694915 | C4 | 694.915 | 694.915 | 2084.745 | 4864.405 | 6949.15 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293.8012 | 248.8012 |  | 28.1551 | 43.3753 | 49.2994 | 119.3584 | 53.613 |  | 28.0351 | 44.3692 | 52.5789 | 151.5048 | 83.3409 |  | 0 | 0 | 0 | -11.3023 | -11.3023 |  | 0.15638 | 60.8785 | 48.9233 | 96.7095 | 87.1329 |  | 0 | 0 | 0 | -22.5 | -22.5 |  | 0.15638 | 39.1358 | 58.8887 | 29.7387 | 165.8809 | [22 empty] | 8053.6827 | 12746.0073 | 45313.2319 | 304660.8381 | 239414.5284 | 610188.2884 |  | 8088.1553 | 12460.4808 | 42486.8636 | 240017.583 | 154014.8342 | 457067.9168 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 17488.6438 | 42162.7775 | 171745.1453 | 217839.3974 | 449280.8874 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013 |  | 44.9234 | 11242.5968 | 50751.0921 | 14556.3294 | 411892.2025 | 488487.1442
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 693 | 693 | C1 | 26 | 441 | 68 | 24 | 134 | 693 | 26 | 395 | 94 | 40 | 140 | 695 | 74.5178 | 0 | 0 | 0 | -74.5178 | 0 | 0 | 261 | 208 | 52 | 171 | 692 | 149.0355 | 0 | 0 | 0 | -149.0355 | 0 | 0 | 170 | 162 | 127 | 233 | 692 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | C1 | 3.0023 | 3.0023 | 6.0045 | 40.0303 | 150.4138 | C1 | 78.0591 | 1185.8974 | 564.4271 | 1601.2117 | 21057.9358 | 24487.5312 |  | 78.0591 | 1324.002 | 408.309 | 960.727 | 20155.4528 | 22926.5499 |  | 0 | 783.593 | 1248.9452 | 2081.5753 | 25720.7645 | 29834.8778 |  | 223.7226 | 783.593 | 1248.9452 | 2081.5753 | 14512.262 | 18850.098 |  | 0 | 510.3862 | 972.7361 | 5083.8473 | 35046.4217 | 41613.3914 |  | 447.4452 | 510.3862 | 972.7361 | 5083.8473 | 12629.4168 | 19643.8317
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 428896 | 428896 | 428896 | 428896 | 428896 | C2 | 4.289 | 4.289 | 8.5779 | 57.1861 | 214.8769 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6 | 6 | C3 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 4 | 1 | 0 | 1 | 6 | 0.71066 | 0 | 0 | 0 | -0.71066 | 0 | 0 | 2 | 2 | 1 | 2 | 7 | 1.4213 | 0 | 0 | 0 | -1.4213 | 0 | 0 | 2 | 2 | 1 | 2 | 7 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 643344 | 643344 | 643344 | 643344 | 643344 | C3 | 6.4334 | 6.4334 | 12.8669 | 85.7792 | 322.3153 | C3 | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 4.572 | 12.8669 | 25.7338 | 85.7792 | 415.5741 | 544.5259 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 9.144 | 12.8669 | 25.7338 | 85.7792 | 186.5175 | 320.0413
|  |  | 231 | 231 | C4 | 8 | 147 | 23 | 8 | 45 | 231 | 8 | 131 | 31 | 13 | 46 | 229 | 24.7716 | 0 | 0 | 0 | -24.7716 | 0 | 0 | 87 | 69 | 18 | 57 | 231 | 49.5431 | 0 | 0 | 0 | -49.5431 | 0 | 0 | 57 | 54 | 42 | 78 | 231 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 1072240 | 1072240 | 1072240 | 1072240 | 1072240 | C4 | 10.7224 | 10.7224 | 21.4448 | 142.9653 | 537.1922 | C4 | 85.7792 | 1404.6344 | 664.7888 | 1858.5493 | 24710.843 | 28724.5948 |  | 85.7792 | 1576.1928 | 493.2304 | 1143.7227 | 24173.6508 | 27472.5759 |  | 0 | 932.8488 | 1479.6912 | 2573.376 | 30619.9577 | 35605.8737 |  | 265.6107 | 932.8488 | 1479.6912 | 2573.376 | 17312.8606 | 22564.3873 |  | 0 | 611.1768 | 1158.0192 | 6004.544 | 41900.9947 | 49674.7347 |  | 531.2214 | 611.1768 | 1158.0192 | 6004.544 | 15286.8005 | 23591.7619
|  |  | 930 | 930 |  | 34 | 592 | 92 | 32 | 180 |  | 34 | 530 | 126 | 53 | 187 |  | 100 | 0 | 0 | 0 | -100 |  | 0 | 350 | 279 | 71 | 230 |  | 200 | 0 | 0 | 0 | -200 |  | 0 | 229 | 218 | 170 | 313 | [22 empty] | 163.8383 | 2616.2656 | 1242.0828 | 3459.7611 | 46091.0942 | 53573.0419 |  | 163.8383 | 2925.9285 | 914.4063 | 2104.4497 | 44651.419 | 50760.0418 |  | 0 | 1729.3087 | 2754.3701 | 4740.7305 | 56985.3528 | 66209.7621 |  | 493.9053 | 1729.3087 | 2754.3701 | 4740.7305 | 32240.6967 | 41959.0112 |  | 0 | 1134.4299 | 2156.4891 | 11174.1705 | 77592.0471 | 92057.1366 |  | 987.8106 | 1134.4299 | 2156.4891 | 11174.1705 | 28102.7348 | 43555.6349
| EHV OHL Support - Poles |  | 263 | 263 | C1 | 12 | 112 | 108 | 21 | 10 | 263 | 2 | 114 | 110 | 24 | 15 | 265 | 5.1855 | 0 | 0 | -1.5557 | -3.6299 | 0 | 12 | 94 | 122 | 25 | 12 | 265 | 10.4132 | 0 | 0 | -3.124 | -7.2892 | 0 | 12 | 82 | 127 | 28 | 16 | 265 |  |  | C1 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C1 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | C1 | 65.7424 | 66.812 | 113.6298 | 243.7157 | 330.7688 | C1 | 131.4847 | 7616.5691 | 12499.2763 | 5849.1775 | 4961.5322 | 31058.0399 |  | 788.9083 | 7482.9451 | 12272.0168 | 5118.0303 | 3307.6882 | 28969.5886 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 1129.8163 | 6280.3289 | 13862.8337 | 5713.7557 | 2768.581 | 29755.3157 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173 |  | 1473.496 | 5478.5848 | 14430.9827 | 6062.683 | 2881.2501 | 30326.9965
|  |  | 8940 | 8940 | C2 | 423 | 3799 | 3664 | 722 | 332 | 8940 | 52 | 3863 | 3736 | 805 | 507 | 8963 | 175.4469 | 0 | 0 | -52.6341 | -122.8128 | 0 | 417 | 3167 | 4116 | 846 | 393 | 8939 | 352.3201 | 0 | 0 | -105.696 | -246.6241 | 0 | 413 | 2761 | 4281 | 959 | 525 | 8939 |  |  | C2 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C2 | 117544 | 117544 | 117544 | 117544 | 117544 | C2 | 93.9177 | 95.4457 | 162.3283 | 348.1653 | 472.5269 | C2 | 4883.7181 | 368706.8473 | 606458.3943 | 280273.089 | 239571.1282 | 1499893.1769 |  | 39727.1685 | 362598.3207 | 594770.7593 | 251375.3668 | 156878.9242 | 1405350.5394 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 55641.2208 | 302276.6206 | 668143.1346 | 276222.513 | 127670.7123 | 1429954.2012 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067 |  | 71877.0723 | 263525.655 | 694927.2982 | 297090.8539 | 131540.1011 | 1458960.9805
|  |  | 3324 | 3324 | C3 | 157 | 1412 | 1363 | 268 | 124 | 3324 | 19 | 1436 | 1389 | 300 | 188 | 3332 | 65.2385 | 0 | 0 | -19.5716 | -45.667 | 0 | 155 | 1178 | 1530 | 315 | 146 | 3324 | 131.0074 | 0 | 0 | -39.3022 | -91.7052 | 0 | 154 | 1027 | 1591 | 357 | 195 | 3324 |  |  | C3 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C3 | 176316 | 176316 | 176316 | 176316 | 176316 | C3 | 140.8765 | 143.1686 | 243.4924 | 522.248 | 708.7903 | C3 | 2676.6532 | 205590.0981 | 338210.938 | 156674.3976 | 133252.5802 | 836404.6671 |  | 22117.608 | 202154.0519 | 331880.1357 | 139962.4619 | 87889.9997 | 784004.2572 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 31026.4283 | 168652.6014 | 372543.3659 | 154286.9116 | 71115.0847 | 797624.3919 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701 |  | 40150.8453 | 147034.144 | 387396.402 | 165917.0222 | 73214.3513 | 813712.7649
|  |  | 7 | 7 | C4 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 3 | 3 | 1 | 0 | 7 | 0.1291 | 0 | 0 | -0.03873 | -0.09037 | 0 | 0 | 2 | 3 | 1 | 0 | 6 | 0.25925 | 0 | 0 | -0.077775 | -0.18147 | 0 | 0 | 2 | 3 | 1 | 0 | 6 |  |  | C4 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C4 | 293860 | 293860 | 293860 | 293860 | 293860 | C4 | 234.7941 | 238.6143 | 405.8207 | 870.4133 | 1181.3172 | C4 | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 30.3119 | 477.2286 | 1217.462 | 836.7022 | -106.7556 | 2454.9491 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 60.8703 | 477.2286 | 1217.462 | 802.717 | -214.3792 | 2343.8988
|  |  | 12534 | 12534 |  | 592 | 5326 | 5138 | 1012 | 466 |  | 73 | 5416 | 5238 | 1130 | 710 |  | 246 | 0 | 0 | -73.8 | -172.2 |  | 584 | 4441 | 5771 | 1187 | 551 |  | 494 | 0 | 0 | -148.2 | -345.8 |  | 579 | 3872 | 6002 | 1345 | 736 | [22 empty] | 7691.856 | 582629.3574 | 958386.0707 | 443667.0775 | 377785.2406 | 2370159.6021 |  | 62633.6848 | 572951.1606 | 940140.3738 | 397326.2723 | 248076.612 | 2221128.1035 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 87827.7774 | 477686.7795 | 1055766.7962 | 437059.8826 | 201447.6223 | 2259788.858 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198 |  | 113562.2839 | 416515.6124 | 1097972.1449 | 469873.2762 | 207421.3234 | 2305344.6407
| EHV OHL Fittings and Conductors (Tower Lines) |  | 264.3928 | 264.3928 | C1 | 60.0911 | 197.1135 | 4.2075 | 0.74518 | 2.2355 | 264.3928 | 0 | 235.0812 | 14.1584 | 0.74518 | 2.2355 | 252.2203 | 2.2355 | -0.44711 | -1.7884 | 0 | 0 | -4.4409e-16 | 60.0911 | 168.7967 | 25.0724 | 4.4711 | 5.9614 | 264.3928 | 2.2355 | -0.44711 | -1.7884 | 0 | 0 | -4.4409e-16 | 60.0911 | 147.1866 | 18.3658 | 18.6294 | 20.1198 | 264.3928 |  |  | C1 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C1 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | C1 | 1.5983 | 36.9203 | 128.5019 | 559.3987 | 1552.0917 | C1 | 0 | 8679.2717 | 1819.3778 | 416.8514 | 3469.7521 | 14385.253 |  | 96.0426 | 7277.491 | 540.6664 | 416.8514 | 3469.7521 | 11800.8035 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 99.6156 | 6215.5204 | 2992.0386 | 2501.1085 | 9252.6723 | 21060.9553 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151 |  | 99.6156 | 5417.6668 | 2130.228 | 10421.2854 | 31227.7689 | 49296.5647
|  |  | 0.36021 | 0.36021 | C2 | 0.081868 | 0.26855 | 0.0057322 | 0.0010152 | 0.0030457 | 0.36021 | 0 | 0.32027 | 0.019289 | 0.0010152 | 0.0030457 | 0.34362 | 0.0030457 | -0.00060914 | -0.0024365 | 0 | 0 | -4.3368e-19 | 0.081868 | 0.22997 | 0.034159 | 0.0060914 | 0.0081218 | 0.36021 | 0.0030457 | -0.00060914 | -0.0024365 | 0 | 0 | -4.3368e-19 | 0.081868 | 0.20053 | 0.025022 | 0.025381 | 0.027411 | 0.36021 |  |  | C2 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C2 | 228326 | 228326 | 228326 | 228326 | 228326 | C2 | 2.2833 | 52.7433 | 183.5741 | 799.141 | 2217.2738 | C2 | 0 | 16.8923 | 3.541 | 0.81131 | 6.7531 | 27.9978 |  | 0.18693 | 14.1641 | 1.0523 | 0.81131 | 6.7531 | 22.9677 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.19388 | 12.0972 | 5.8234 | 4.8679 | 18.0083 | 40.9906 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175 |  | 0.19388 | 10.5443 | 4.146 | 20.2828 | 60.7781 | 95.945
|  |  | 2.1612 | 2.1612 | C3 | 0.49121 | 1.6113 | 0.034393 | 0.0060914 | 0.018274 | 2.1612 | 0 | 1.9216 | 0.11574 | 0.0060914 | 0.018274 | 2.0617 | 0.018274 | -0.0036548 | -0.014619 | 0 | 0 | -1.7347e-18 | 0.49121 | 1.3798 | 0.20495 | 0.036548 | 0.048731 | 2.1612 | 0.018274 | -0.0036548 | -0.014619 | 0 | 0 | -1.7347e-18 | 0.49121 | 1.2032 | 0.15013 | 0.15228 | 0.16447 | 2.1612 |  |  | C3 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C3 | 342489 | 342489 | 342489 | 342489 | 342489 | C3 | 3.4249 | 79.115 | 275.3612 | 1198.7115 | 3325.9107 | C3 | 0 | 152.0308 | 31.8692 | 7.3018 | 60.7781 | 251.9799 |  | 1.6823 | 127.4765 | 9.4706 | 7.3018 | 60.7781 | 206.7093 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.7449 | 108.8744 | 52.4102 | 43.8108 | 162.0748 | 368.9151 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576 |  | 1.7449 | 94.8988 | 37.3142 | 182.5449 | 547.0026 | 863.5054
|  |  | 87.8908 | 87.8908 | C4 | 19.9758 | 65.5255 | 1.3987 | 0.24772 | 0.74315 | 87.8908 | 0 | 78.1469 | 4.7066 | 0.24772 | 0.74315 | 83.8443 | 0.74315 | -0.14863 | -0.59452 | 0 | 0 | 0 | 19.9758 | 56.1123 | 8.3347 | 1.4863 | 1.9817 | 87.8908 | 0.74315 | -0.14863 | -0.59452 | 0 | 0 | 0 | 19.9758 | 48.9285 | 6.1053 | 6.1929 | 6.6883 | 87.8908 |  |  | C4 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C4 | 570815 | 570815 | 570815 | 570815 | 570815 | C4 | 5.7082 | 131.8583 | 458.9353 | 1997.8525 | 5543.1845 | C4 | 0 | 10304.3124 | 2160.0242 | 494.8995 | 4119.4021 | 17078.6382 |  | 114.0248 | 8640.0731 | 641.8966 | 494.8995 | 4119.4021 | 14010.2961 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 118.2668 | 7379.2671 | 3552.2451 | 2969.397 | 10985.0722 | 25004.2482 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793 |  | 118.2668 | 6432.0294 | 2529.0757 | 12372.4876 | 37074.6185 | 58526.4781
|  |  | 354.805 | 354.805 |  | 80.64 | 264.5188 | 5.6462 | 1 | 3 |  | 0 | 315.47 | 19 | 1 | 3 |  | 3 | -0.6 | -2.4 | 0 | 0 |  | 80.64 | 226.5188 | 33.6462 | 6 | 8 |  | 3 | -0.6 | -2.4 | 0 | 0 |  | 80.64 | 197.5188 | 24.6462 | 25 | 27 | [22 empty] | 0 | 19152.5073 | 4014.8122 | 919.864 | 7656.6853 | 31743.8689 |  | 211.9367 | 16059.2047 | 1193.0859 | 919.864 | 7656.6853 | 26040.7766 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 219.8212 | 13715.7591 | 6602.5172 | 5519.1842 | 20417.8276 | 46475.1092 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694 |  | 219.8212 | 11955.1393 | 4700.764 | 22996.6007 | 68910.168 | 108782.4932
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 |  | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 |  | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 |  | 119415.9203 | 617009.5815 | 1376024.6812 | 885845.0718 | 909674.305 | 3907969.5599 |  | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 |  | 160462.2081 | 529233.5746 | 1335892.1614 | 747218.2341 | 1531824.1286 | 4304630.3068
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 77 | 76.199 | C1 | 43 | 16 | 2 | 2 | 14 | 77 | 40 | 16 | 2 | 2 | 15 | 75 | 8.0103 | 0 | 0 | 0 | -8.8114 | -0.80103 | 32 | 20 | 4 | 4 | 16 | 76 | 12.416 | 0 | 0 | 0 | -13.2171 | -0.80103 | 29 | 23 | 4 | 5 | 16 | 77 |  |  | C1 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C1 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | C1 | 1145.2464 | 1145.2464 | 2032.8759 | 3954.8992 | 7511.4217 | C1 | 45809.8574 | 18323.943 | 4065.7519 | 7909.7984 | 112671.3259 | 188780.6766 |  | 49245.5968 | 18323.943 | 4065.7519 | 7909.7984 | 105159.9042 | 184704.9942 |  | 36647.886 | 22904.9287 | 8131.5037 | 15819.5969 | 120182.7476 | 203686.6629 |  | 45821.6946 | 22904.9287 | 8131.5037 | 15819.5969 | 53996.8352 | 146674.5592 |  | 33212.1466 | 26340.668 | 8131.5037 | 19774.4961 | 120182.7476 | 207641.5621 |  | 47431.5501 | 26340.668 | 8131.5037 | 19774.4961 | 20903.8791 | 122582.097
|  |  | 27 | 26.7192 | C2 | 15 | 6 | 1 | 0 | 5 | 27 | 14 | 6 | 1 | 0 | 5 | 26 | 2.8079 | 0 | 0 | 0 | -3.0887 | -0.28079 | 12 | 7 | 1 | 2 | 6 | 28 | 4.3523 | 0 | 0 | 0 | -4.6331 | -0.28079 | 10 | 8 | 2 | 2 | 6 | 28 |  |  | C2 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C2 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | C2 | 1636.0663 | 1636.0663 | 2904.1085 | 5649.856 | 10730.6025 | C2 | 22904.9287 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 89278.4475 |  | 24540.9951 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 90914.5139 |  | 19632.796 | 11452.4644 | 2904.1085 | 11299.7121 | 64383.6148 | 109672.6957 |  | 24226.7463 | 11452.4644 | 2904.1085 | 11299.7121 | 31239.8246 | 81122.8558 |  | 16360.6634 | 13088.5307 | 5808.217 | 11299.7121 | 64383.6148 | 110940.7379 |  | 23481.2863 | 13088.5307 | 5808.217 | 11299.7121 | 14667.9295 | 68345.6755
|  |  | 90 | 89.0818 | C3 | 50 | 21 | 3 | 1 | 15 | 90 | 46 | 18 | 3 | 1 | 17 | 85 | 9.1817 | 0 | 0 | 0 | -10.0999 | -0.91817 | 38 | 23 | 5 | 5 | 19 | 90 | 14.2317 | 0 | 0 | 0 | -15.1499 | -0.91817 | 33 | 27 | 5 | 5 | 19 | 89 |  |  | C3 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C3 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | C3 | 2454.0995 | 2454.0995 | 4356.1627 | 8474.784 | 16095.9037 | C3 | 112888.5773 | 44173.7911 | 13068.4881 | 8474.784 | 273630.3629 | 452236.0034 |  | 122704.9753 | 51536.0896 | 13068.4881 | 8474.784 | 241438.5555 | 437222.8926 |  | 93255.7812 | 56444.2886 | 21780.8136 | 42373.9202 | 305822.1703 | 519676.9739 |  | 115788.6845 | 56444.2886 | 21780.8136 | 42373.9202 | 143254.9293 | 379642.6362 |  | 80985.2837 | 66260.6867 | 21780.8136 | 42373.9202 | 305822.1703 | 517222.8744 |  | 115911.2838 | 66260.6867 | 21780.8136 | 42373.9202 | 61971.3088 | 308298.0131
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C4 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | C4 | 4090.1658 | 4090.1658 | 7260.2712 | 14124.6401 | 26826.5062 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 194 | 192 |  | 108 | 43 | 6 | 3 | 34 |  | 100 | 40 | 6 | 3 | 37 |  | 20 | 0 | 0 | 0 | -22 |  | 82 | 50 | 10 | 11 | 41 |  | 31 | 0 | 0 | 0 | -33 |  | 72 | 58 | 11 | 12 | 41 | [22 empty] | 181603.3635 | 72314.1321 | 20038.3485 | 16384.5825 | 439954.7011 | 730295.1276 |  | 196491.5671 | 79676.4306 | 20038.3485 | 16384.5825 | 400251.4719 | 712842.4007 |  | 149536.4632 | 90801.6817 | 32816.4258 | 69493.2291 | 490388.5327 | 833036.3325 |  | 185837.1255 | 90801.6817 | 32816.4258 | 69493.2291 | 228491.5891 | 607440.0512 |  | 130558.0937 | 105689.8854 | 35720.5343 | 73448.1283 | 490388.5327 | 835805.1744 |  | 186824.1202 | 105689.8854 | 35720.5343 | 73448.1283 | 97543.1173 | 499225.7855
| 132kV Transformer |  | 59 | 59 | C1 | 12 | 19 | 15 | 7 | 6 | 59 | 5 | 19 | 15 | 7 | 11 | 57 | 2.1923 | 0 | 0 | 0 | -2.1923 | 0 | 11 | 10 | 16 | 16 | 7 | 60 | 6.2115 | 0 | 0 | 0 | -6.2115 | 0 | 11 | 10 | 6 | 17 | 17 | 61 |  |  | C1 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C1 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | C1 | 1418.2655 | 1418.2655 | 2428.685 | 4604.9455 | 10096.9831 | C1 | 7091.3276 | 26947.0449 | 36430.2757 | 32234.6186 | 111066.8143 | 213770.0812 |  | 17019.1863 | 26947.0449 | 36430.2757 | 32234.6186 | 60581.8987 | 173213.0242 |  | 15600.9207 | 14182.6552 | 38858.9608 | 73679.1283 | 70678.8818 | 213000.5468 |  | 18710.1952 | 14182.6552 | 38858.9608 | 73679.1283 | 48543.1881 | 193974.1275 |  | 15600.9207 | 14182.6552 | 14572.1103 | 78284.0738 | 171648.713 | 294288.473 |  | 24410.5316 | 14182.6552 | 14572.1103 | 78284.0738 | 108930.914 | 240380.2849
|  |  | 51 | 51 | C2 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 1.8462 | 0 | 0 | 0 | -1.8462 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 5.2308 | 0 | 0 | 0 | -5.2308 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C2 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C2 | 858587 | 858587 | 858587 | 858587 | 858587 | C2 | 2026.0936 | 2026.0936 | 3469.5501 | 6578.4936 | 14424.2616 | C2 | 10130.468 | 30391.404 | 48573.7009 | 39470.9616 | 144242.616 | 272809.1506 |  | 20260.936 | 34443.5912 | 48573.7009 | 39470.9616 | 57697.0464 | 200446.2362 |  | 20260.936 | 18234.8424 | 45104.1509 | 85520.4167 | 72121.308 | 241241.654 |  | 24001.4165 | 18234.8424 | 45104.1509 | 85520.4167 | 45491.902 | 218352.7285 |  | 18234.8424 | 14182.6552 | 17347.7503 | 92098.9103 | 216363.924 | 358228.0823 |  | 28832.8705 | 14182.6552 | 17347.7503 | 92098.9103 | 140913.9402 | 293376.1266
|  |  | 51 | 51 | C3 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 1.8462 | 0 | 0 | 0 | -1.8462 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 5.2308 | 0 | 0 | 0 | -5.2308 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C3 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C3 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | C3 | 3039.1404 | 3039.1404 | 5204.3251 | 9867.7404 | 21636.3924 | C3 | 15195.702 | 45587.1061 | 72860.5514 | 59206.4423 | 216363.924 | 409213.7258 |  | 30391.404 | 51665.3869 | 72860.5514 | 59206.4423 | 86545.5696 | 300669.3543 |  | 30391.404 | 27352.2636 | 67656.2263 | 128280.6251 | 108181.962 | 361862.4811 |  | 36002.1248 | 27352.2636 | 67656.2263 | 128280.6251 | 68237.853 | 327529.0928 |  | 27352.2636 | 21273.9828 | 26021.6255 | 138148.3655 | 324545.886 | 537342.1234 |  | 43249.3057 | 21273.9828 | 26021.6255 | 138148.3655 | 211370.9104 | 440064.1899
|  |  | 3 | 3 | C4 | 1 | 1 | 1 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 3 | 0.11538 | 0 | 0 | 0 | -0.11538 | 0 | 1 | 1 | 1 | 1 | 0 | 4 | 0.32692 | 0 | 0 | 0 | -0.32692 | 0 | 1 | 0 | 0 | 1 | 1 | 3 |  |  | C4 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C4 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | C4 | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 36060.654 | C4 | 0 | 5065.234 | 8673.8752 | 0 | 36060.654 | 49799.7632 |  | 5065.234 | 5065.234 | 8673.8752 | 0 | 0 | 18804.3432 |  | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 0 | 35250.5772 |  | 5649.6841 | 5065.234 | 8673.8752 | 16446.234 | -4160.8447 | 31674.1826 |  | 5065.234 | 0 | 0 | 16446.234 | 36060.654 | 57572.122 |  | 6721.1759 | 0 | 0 | 16446.234 | 24271.594 | 47439.0039
|  |  | 164 | 164 |  | 33 | 54 | 44 | 19 | 14 |  | 15 | 50 | 44 | 19 | 32 |  | 6 | 0 | 0 | 0 | -6 |  | 32 | 29 | 43 | 43 | 17 |  | 17 | 0 | 0 | 0 | -17 |  | 30 | 24 | 16 | 46 | 48 | [22 empty] | 32417.4976 | 107990.789 | 166538.4032 | 130912.0225 | 507734.0083 | 945592.7207 |  | 72736.7603 | 118121.257 | 166538.4032 | 130912.0225 | 204824.5147 | 693132.9578 |  | 71318.4948 | 64834.9953 | 160293.2131 | 303926.404 | 250982.1518 | 851355.2591 |  | 84363.4205 | 64834.9953 | 160293.2131 | 303926.404 | 158112.0983 | 771530.1313 |  | 66253.2608 | 49639.2933 | 57941.4861 | 324977.5835 | 748619.177 | 1247430.8008 |  | 103213.8837 | 49639.2933 | 57941.4861 | 324977.5835 | 485487.3587 | 1021259.6053
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 10.9182 | 10.1281 | C1 | 0.069593 | 1.7577 | 3.5512 | 5.0591 | 0.48064 | 10.9182 | 0.068227 | 1.758 | 3.5519 | 5.1278 | 0.48064 | 10.9865 | 0 | 0 | 0 | -0.40769 | 0 | -0.40769 | 0.0009295 | 0.86512 | 2.3839 | 5.9513 | 1.717 | 10.9182 | 0 | 0 | 0 | -0.79012 | 0 | -0.79012 | 0.0009295 | 0.035179 | 2.2525 | 4.4407 | 4.1888 | 10.9182 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | C1 | 89.1849 | 89.1849 | 267.5547 | 624.2943 | 891.849 | C1 | 6.0848 | 156.7859 | 950.3179 | 3201.2465 | 428.6599 | 4743.0951 |  | 6.2066 | 156.7643 | 950.1285 | 3158.3535 | 428.6599 | 4700.1129 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 77.1561 | 637.8191 | 3460.8589 | 1531.2611 | 5707.1781 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239 |  | 0.082898 | 3.1375 | 602.679 | 2279.0617 | 3735.7979 | 6620.759
|  |  | 116.779 | 108.328 | C2 | 0.74435 | 18.8005 | 37.9824 | 54.1109 | 5.1408 | 116.779 | 0.72974 | 18.8031 | 37.99 | 54.8457 | 5.1408 | 117.5094 | 0 | 0 | 0 | -4.3606 | 0 | -4.3606 | 0.0099418 | 9.2532 | 25.4975 | 63.6541 | 18.3642 | 116.779 | 0 | 0 | 0 | -8.4509 | 0 | -8.4509 | 0.0099418 | 0.37627 | 24.0928 | 47.4972 | 44.8028 | 116.779 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 127407 | 127407 | 127407 | 127407 | 127407 | C2 | 127.407 | 127.407 | 382.221 | 891.849 | 1274.07 | C2 | 92.974 | 2395.6419 | 14520.5776 | 48914.1022 | 6549.7974 | 72473.0931 |  | 94.8352 | 2395.3128 | 14517.6837 | 48258.709 | 6549.7974 | 71816.3381 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 1178.9218 | 9745.6884 | 52880.9033 | 23397.2175 | 87203.9977 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186 |  | 1.2667 | 47.9394 | 9208.7573 | 34823.3911 | 57081.89 | 101163.2444
|  |  | 31.9588 | 29.646 | C3 | 0.2037 | 5.1451 | 10.3946 | 14.8085 | 1.4069 | 31.9588 | 0.19971 | 5.1458 | 10.3967 | 15.0096 | 1.4069 | 32.1587 | 0 | 0 | 0 | -1.1934 | 0 | -1.1934 | 0.0027208 | 2.5323 | 6.9779 | 17.4202 | 5.0257 | 31.9588 | 0 | 0 | 0 | -2.3128 | 0 | -2.3128 | 0.0027208 | 0.10297 | 6.5934 | 12.9985 | 12.2611 | 31.9588 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | C3 | 191.1105 | 191.1105 | 573.3315 | 1337.7735 | 1911.105 | C3 | 38.1661 | 983.4189 | 5960.7448 | 20079.3997 | 2688.7134 | 29750.4429 |  | 38.9302 | 983.2838 | 5959.5569 | 19810.3586 | 2688.7134 | 29480.8428 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 483.9513 | 4000.6371 | 21707.7846 | 9604.6347 | 35797.5276 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836 |  | 0.51997 | 19.6793 | 3780.2251 | 14295.1165 | 23432.3034 | 41527.8443
|  |  | 0.22406 | 0.20785 | C4 | 0.0014282 | 0.036072 | 0.072876 | 0.10382 | 0.0098637 | 0.22406 | 0.0014001 | 0.036077 | 0.072891 | 0.10523 | 0.0098637 | 0.22546 | 0 | 0 | 0 | -0.0083666 | 0 | -0.0083666 | 1.9075e-05 | 0.017754 | 0.048922 | 0.12213 | 0.035235 | 0.22406 | 0 | 0 | 0 | -0.016215 | 0 | -0.016215 | 1.9075e-05 | 0.00072194 | 0.046226 | 0.091132 | 0.085962 | 0.22406 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | C4 | 318.5175 | 318.5175 | 955.5525 | 2229.6225 | 3185.175 | C4 | 0.44597 | 11.4912 | 69.6511 | 234.627 | 31.4175 | 347.6328 |  | 0.4549 | 11.4896 | 69.6372 | 231.4833 | 31.4175 | 344.4825 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 5.655 | 46.7473 | 253.6546 | 112.2298 | 418.2927 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038 |  | 0.0060758 | 0.22995 | 44.1718 | 167.0379 | 273.8055 | 485.2512
|  |  | 159.88 | 148.31 |  | 1.0191 | 25.7394 | 52.0011 | 74.0822 | 7.0382 |  | 0.99907 | 25.7429 | 52.0114 | 75.0883 | 7.0382 |  | 0 | 0 | 0 | -5.97 | 0 |  | 0.013611 | 12.6684 | 34.9082 | 87.1478 | 25.142 |  | 0 | 0 | 0 | -11.57 | 0 |  | 0.013611 | 0.51514 | 32.985 | 65.0276 | 61.3387 | [22 empty] | 137.6709 | 3547.3379 | 21501.2914 | 72429.3754 | 9698.5882 | 107314.2638 |  | 140.4269 | 3546.8505 | 21497.0062 | 71458.9044 | 9698.5882 | 106341.7763 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 1745.6842 | 14430.8919 | 78303.2014 | 34645.343 | 129126.9961 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973 |  | 1.8756 | 70.9861 | 13635.8333 | 51564.6071 | 84523.7969 | 149797.0989
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 104 | 104 | C1 | 4 | 74 | 6 | 14 | 6 | 104 | 2 | 55 | 19 | 18 | 10 | 104 | 3.3091 | 0 | 0 | 0 | -3.3091 | 0 | 3 | 32 | 46 | 8 | 15 | 104 | 6.6181 | 0 | 0 | 0 | -6.6181 | 0 | 3 | 13 | 48 | 17 | 22 | 103 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | C1 | 9.0026 | 9.0026 | 18.0052 | 120.0344 | 451.0293 | C1 | 18.0052 | 495.142 | 342.0981 | 2160.6194 | 4510.2931 | 7526.1577 |  | 36.0103 | 666.191 | 108.031 | 1680.4818 | 2706.1758 | 5196.8899 |  | 27.0077 | 288.0826 | 828.2375 | 960.2753 | 6765.4396 | 8869.0427 |  | 56.7979 | 288.0826 | 828.2375 | 960.2753 | 5272.9535 | 7406.3467 |  | 27.0077 | 117.0336 | 864.2478 | 2040.585 | 9922.6448 | 12971.5189 |  | 86.588 | 117.0336 | 864.2478 | 2040.585 | 6937.6725 | 10046.1269
|  |  | 2572 | 2572 | C2 | 102 | 1838 | 141 | 337 | 154 | 2572 | 43 | 1359 | 464 | 456 | 251 | 2573 | 82.3958 | 0 | 0 | 0 | -82.3958 | 0 | 68 | 796 | 1135 | 190 | 384 | 2573 | 164.7915 | 0 | 0 | 0 | -164.7915 | 0 | 68 | 327 | 1202 | 426 | 551 | 2574 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 1286083 | 1286083 | 1286083 | 1286083 | 1286083 | C2 | 12.8608 | 12.8608 | 25.7217 | 171.4777 | 644.3276 | C2 | 553.0157 | 17477.868 | 11934.8502 | 78193.8464 | 161726.2233 | 269885.8036 |  | 1311.8047 | 23638.2055 | 3626.7541 | 57787.9961 | 99226.4478 | 185591.2082 |  | 874.5364 | 10237.2207 | 29194.0841 | 32580.7693 | 247421.7919 | 320308.4024 |  | 1934.2144 | 10237.2207 | 29194.0841 | 32580.7693 | 194331.9282 | 268278.2166 |  | 874.5364 | 4205.4914 | 30917.4353 | 73049.5144 | 355024.4982 | 464071.4758 |  | 2993.8923 | 4205.4914 | 30917.4353 | 73049.5144 | 248844.7708 | 360011.1042
|  |  | 447 | 447 | C3 | 18 | 319 | 24 | 59 | 27 | 447 | 7 | 236 | 80 | 79 | 44 | 446 | 14.2952 | 0 | 0 | 0 | -14.2952 | 0 | 12 | 138 | 197 | 33 | 66 | 446 | 28.5903 | 0 | 0 | 0 | -28.5903 | 0 | 12 | 57 | 208 | 74 | 95 | 446 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | C3 | 19.2912 | 19.2912 | 38.5825 | 257.2166 | 966.4914 | C3 | 135.0387 | 4552.7338 | 3086.5992 | 20320.1114 | 42525.6205 | 70620.1036 |  | 347.2424 | 6153.9072 | 925.9798 | 15175.7794 | 26095.2671 | 48698.1758 |  | 231.4949 | 2662.1918 | 7600.7505 | 8488.1478 | 63788.4307 | 82771.0158 |  | 507.2665 | 2662.1918 | 7600.7505 | 8488.1478 | 49972.2734 | 69230.6301 |  | 231.4949 | 1099.601 | 8025.1579 | 19034.0284 | 91816.6806 | 120206.9628 |  | 783.0381 | 1099.601 | 8025.1579 | 19034.0284 | 64184.366 | 93126.1914
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | C4 | 32.1521 | 32.1521 | 64.3041 | 428.6943 | 1610.819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3123 | 3123 |  | 124 | 2231 | 171 | 410 | 187 |  | 52 | 1650 | 563 | 553 | 305 |  | 100 | 0 | 0 | 0 | -100 |  | 83 | 966 | 1378 | 231 | 465 |  | 200 | 0 | 0 | 0 | -200 |  | 83 | 397 | 1458 | 517 | 668 | [22 empty] | 706.0596 | 22525.7437 | 15363.5475 | 100674.5772 | 208762.1369 | 348032.065 |  | 1695.0574 | 30458.3037 | 4660.7648 | 74644.2573 | 128027.8907 | 239486.2739 |  | 1133.0391 | 13187.4951 | 37623.0721 | 42029.1924 | 317975.6622 | 411948.4609 |  | 2498.2788 | 13187.4951 | 37623.0721 | 42029.1924 | 249577.1551 | 344915.1934 |  | 1133.0391 | 5422.1259 | 39806.841 | 94124.1278 | 456763.8236 | 597249.9575 |  | 3863.5185 | 5422.1259 | 39806.841 | 94124.1278 | 319966.8093 | 463183.4225
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 52.7896 | 52.7896 | C1 | 2.6478 | 46.9644 | 1.6221 | 1.3898 | 0.16545 | 52.7896 | 1 | 47 | 3 | 1 | 0 | 52 | 1.456 | -0.2912 | -1.1648 | 0 | 0 | -2.2204e-16 | 2.6478 | 40.975 | 5.8908 | 1.5884 | 1.6876 | 52.7896 | 2.9782 | -0.59563 | -2.3825 | 0 | 0 | 0 | 2.6478 | 35.9122 | 4.6996 | 3.7062 | 5.824 | 52.7896 |  | 2.317 | C1 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C1 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | C1 | 4.7807 | 45.4166 | 384.3676 | 1185.1335 | 3214.107 | C1 | 4.7807 | 2134.579 | 1153.1029 | 1185.1335 | 0 | 4477.5961 |  | 12.6582 | 2132.9638 | 623.4996 | 1647.1082 | 531.7848 | 4948.0146 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 19.6189 | 1847.7201 | 1816.5401 | 1882.4093 | 5424.2045 | 10990.4929 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418 |  | 26.8959 | 1603.9554 | 890.5982 | 4392.2885 | 18718.8233 | 25632.5612
|  |  | 1314.4617 | 1314.4617 | C2 | 65.9298 | 1169.4145 | 40.3914 | 34.6062 | 4.1198 | 1314.4617 | 26 | 1178 | 70 | 35 | 7 | 1316 | 36.2541 | -7.2508 | -29.0033 | 0 | 0 | 0 | 65.9298 | 1020.2782 | 146.6819 | 39.55 | 42.0218 | 1314.4617 | 74.1562 | -14.8312 | -59.325 | 0 | 0 | 0 | 65.9298 | 894.2126 | 117.0194 | 92.2833 | 145.0165 | 1314.4617 |  |  | C2 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C2 | 682956 | 682956 | 682956 | 682956 | 682956 | C2 | 6.8296 | 64.8808 | 549.0966 | 1693.0479 | 4591.5815 | C2 | 177.5686 | 76429.606 | 38436.7637 | 59256.6773 | 32141.0704 | 206441.6859 |  | 450.2715 | 75872.571 | 22178.7704 | 58589.9907 | 18916.3433 | 176007.9469 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 697.8713 | 65726.0438 | 64616.9258 | 66959.9894 | 192946.7017 | 390947.5319 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601 |  | 956.7256 | 57054.9863 | 31679.8499 | 156239.9752 | 665855.2844 | 911786.8214
|  |  | 228.0512 | 228.0512 | C3 | 11.4384 | 202.8864 | 7.0077 | 6.004 | 0.71476 | 228.0512 | 5 | 204 | 12 | 6 | 1 | 228 | 6.2899 | -1.258 | -5.0319 | 0 | 0 | -1.7764e-15 | 11.4384 | 177.0121 | 25.4484 | 6.8617 | 7.2905 | 228.0512 | 12.8657 | -2.5731 | -10.2925 | 0 | 0 | 0 | 11.4384 | 155.1405 | 20.3022 | 16.0106 | 25.1595 | 228.0512 |  |  | C3 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C3 | 1024434 | 1024434 | 1024434 | 1024434 | 1024434 | C3 | 10.2443 | 97.3212 | 823.6449 | 2539.5719 | 6887.3722 | C3 | 51.2217 | 19853.5309 | 9883.7392 | 15237.4313 | 6887.3722 | 51913.2954 |  | 117.1791 | 19745.151 | 5771.8246 | 15247.5157 | 4922.8074 | 45804.4777 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 181.6147 | 17104.609 | 16815.971 | 17425.7322 | 50212.6356 | 101740.5625 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845 |  | 248.9792 | 14848.0446 | 8244.3947 | 40660.0417 | 173282.821 | 237284.2812
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C4 | 1707390 | 1707390 | 1707390 | 1707390 | 1707390 | C4 | 17.0739 | 162.2021 | 1372.7416 | 4232.6198 | 11478.9537 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1595.3025 | 1595.3025 |  | 80.016 | 1419.2653 | 49.0212 | 42 | 5 |  | 32 | 1429 | 85 | 42 | 8 |  | 44 | -8.8 | -35.2 | 0 | 0 |  | 80.016 | 1238.2653 | 178.0212 | 48 | 51 |  | 90 | -18 | -72 | 0 | 0 |  | 80.016 | 1085.2653 | 142.0212 | 112 | 176 | [22 empty] | 233.571 | 98417.7159 | 49473.6058 | 75679.2422 | 39028.4426 | 262832.5774 |  | 580.1088 | 97750.6859 | 28574.0945 | 75484.6145 | 24370.9355 | 226760.4392 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 899.1049 | 84678.3729 | 83249.4369 | 86268.1309 | 248583.5418 | 503678.5873 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865 |  | 1232.6007 | 73506.9863 | 40814.8428 | 201292.3054 | 857856.9286 | 1174703.6639
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 |  | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 |  | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 |  | 273599.8053 | 255248.2291 | 328413.0398 | 580020.1579 | 919409.7273 | 2356690.9594 |  | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 |  | 295135.9987 | 234329.277 | 187919.5375 | 745406.7522 | 1845378.0108 | 3308169.5761
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 269066.8564 | 267196.2864 |  | 36234.8093 | 102297.8188 | 83782.0698 | 25268.2431 | 21483.9155 |  | 22042.9663 | 103434.5141 | 86548.7282 | 28258.5442 | 28483.6662 |  | 9204 | -272.933 | -739.8523 | -1665.0402 | -7464.7863 |  | 33932.1673 | 90891.2169 | 88029.2386 | 25016.7125 | 31197.5201 |  | 18835 | -697.5749 | -1477.0877 | -3241.9711 | -15288.9363 |  | 29163.1673 | 87383.2531 | 88101.4332 | 24816.473 | 39602.5289 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 |  | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 |  | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 |  | 1276880.0121 | 3849692.1437 | 5907710.7044 | 3645716.801 | 6006394.7373 | 20686394.3984 |  | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 |  | 1472936.545 | 3642282.842 | 5687931.8969 | 3426530.5866 | 7520517.959 | 21750199.8295
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 | LV Network | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 | LV Network | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 | LV Network | 322253.2779 | 290986.5968 | 1004163.994 | 583203.9116 | 1728565.5552 | 3929173.3355 | LV Network | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 | LV Network | 342778.2514 | 281278.7207 | 1024066.3775 | 485284.7807 | 1758269.4843 | 3891677.6147
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 | HV Network | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 | HV Network | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 | HV Network | 561611.0086 | 2686447.7363 | 3199108.9893 | 1596647.6597 | 2448745.1498 | 10492560.5436 | HV Network | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 | HV Network | 674560.0867 | 2597441.2697 | 3140053.8206 | 1448620.8195 | 2385046.3353 | 10245722.3319
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 | EHV Network | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 | EHV Network | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 | EHV Network | 119415.9203 | 617009.5815 | 1376024.6812 | 885845.0718 | 909674.305 | 3907969.5599 | EHV Network | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 | EHV Network | 160462.2081 | 529233.5746 | 1335892.1614 | 747218.2341 | 1531824.1286 | 4304630.3068
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 | 132kV Network | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 | 132kV Network | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 | 132kV Network | 273599.8053 | 255248.2291 | 328413.0398 | 580020.1579 | 919409.7273 | 2356690.9594 | 132kV Network | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 | 132kV Network | 295135.9987 | 234329.277 | 187919.5375 | 745406.7522 | 1845378.0108 | 3308169.5761
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 | Total | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 | Total | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 | Total | 1276880.0121 | 3849692.1437 | 5907710.7044 | 3645716.801 | 6006394.7373 | 20686394.3984 | Total | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 | Total | 1472936.545 | 3642282.842 | 5687931.8969 | 3426530.5866 | 7520517.959 | 21750199.8295
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## ENWL - Refurb
Secondary deliverables RIIO-ED1 - Refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
ENWL | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 3251 | 3251 | C1 | 365 | 1078 | 581 | 295 | 932 | 3251 | 228 | 1082 | 597 | 295 | 1019 | 3221 | 0 | 333.9413 | 0 | 0 | -333.9413 | 0 | 325 | 750 | 949 | 211 | 1017 | 3252 | 0 | 667.8826 | 0 | 0 | -667.8826 | 0 | 216 | 696 | 981 | 132 | 1227 | 3252 | Yes |  | C1 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C1 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | C1 | 10.03 | 17.3692 | 18.0526 | 30.8232 | 94.9612 | C1 | 2286.8431 | 18793.4975 | 10777.4025 | 9092.8586 | 96765.4981 | 137716.0998 |  | 3660.9549 | 18724.0206 | 10488.5609 | 9092.8586 | 88503.8707 | 130470.2657 |  | 3259.7544 | 13026.916 | 17131.9179 | 6503.7056 | 96575.5757 | 136497.8695 |  | 3259.7544 | 18827.2165 | 17131.9179 | 6503.7056 | 64864.0968 | 110586.6912 |  | 2166.4829 | 12088.978 | 17709.6011 | 4068.6689 | 116517.4349 | 152551.1659 |  | 2166.4829 | 23689.579 | 17709.6011 | 4068.6689 | 53094.4772 | 100728.8092
|  |  | 9179 | 9179 | C2 | 1032 | 3044 | 1640 | 833 | 2630 | 9179 | 642 | 3055 | 1684 | 834 | 2878 | 9093 | 0 | 942.7094 | 0 | 0 | -942.7094 | 0 | 918 | 2118 | 2678 | 594 | 2870 | 9178 | 0 | 1885.4188 | 0 | 0 | -1885.4188 | 0 | 610 | 1964 | 2769 | 371 | 3462 | 9176 | No |  | C2 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C2 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | C2 | 14.3286 | 24.8132 | 25.7894 | 44.0332 | 135.6589 | C2 | 9198.9552 | 75804.2445 | 43429.399 | 36723.6999 | 390426.3334 | 555582.632 |  | 14787.1056 | 75531.2996 | 42294.6641 | 36679.6667 | 356782.9245 | 526075.6605 |  | 13153.6462 | 52554.3011 | 69064.0918 | 26155.7287 | 389341.0621 | 550268.83 |  | 13153.6462 | 75945.9127 | 69064.0918 | 26155.7287 | 261454.1363 | 445773.5157 |  | 8740.4403 | 48733.0724 | 71410.9298 | 16336.3221 | 469651.1349 | 614871.8996 |  | 8740.4403 | 95516.2957 | 71410.9298 | 16336.3221 | 213877.2832 | 405881.2711
|  |  | 3561 | 3561 | C3 | 400 | 1181 | 637 | 323 | 1020 | 3561 | 249 | 1185 | 653 | 324 | 1116 | 3527 | 0 | 365.7293 | 0 | 0 | -365.7293 | 0 | 356 | 822 | 1039 | 231 | 1113 | 3561 | 0 | 731.4586 | 0 | 0 | -731.4586 | 0 | 237 | 762 | 1075 | 144 | 1344 | 3562 |  |  | C3 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C3 | 15254 | 15254 | 15254 | 15254 | 15254 | C3 | 21.4929 | 37.2198 | 38.6841 | 66.0498 | 203.4884 | C3 | 5351.7286 | 44105.4156 | 25260.746 | 21400.1417 | 227093.0098 | 323211.0417 |  | 8597.1544 | 43956.5366 | 24641.7997 | 21334.0919 | 207558.1272 | 306087.7097 |  | 7651.4674 | 30594.6427 | 40192.8256 | 15257.5084 | 226482.5447 | 320178.9889 |  | 7651.4674 | 44206.9998 | 40192.8256 | 15257.5084 | 152060.8877 | 259369.6889 |  | 5093.814 | 28361.4571 | 41585.4548 | 9511.1741 | 273488.3558 | 358040.2558 |  | 5093.814 | 55586.1712 | 41585.4548 | 9511.1741 | 124645.0419 | 236421.6559
|  |  | 781 | 781 | C4 | 88 | 258 | 140 | 71 | 224 | 781 | 55 | 260 | 143 | 71 | 245 | 774 | 0 | 80.195 | 0 | 0 | -80.195 | 0 | 78 | 180 | 228 | 51 | 244 | 781 | 0 | 160.39 | 0 | 0 | -160.39 | 0 | 52 | 167 | 236 | 32 | 295 | 782 |  |  | C4 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C4 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | C4 | 35.8215 | 62.0329 | 64.4736 | 110.083 | 339.1473 | C4 | 1970.1812 | 16128.5627 | 9219.721 | 7815.8954 | 83091.0803 | 118225.4406 |  | 3152.2899 | 16004.4968 | 9026.3003 | 7815.8954 | 75968.9877 | 111967.9701 |  | 2794.0752 | 11165.928 | 14699.9747 | 5614.2347 | 82751.9331 | 117026.1457 |  | 2794.0752 | 16140.6585 | 14699.9747 | 5614.2347 | 55554.0214 | 94802.9645 |  | 1862.7168 | 10359.4999 | 15215.7633 | 3522.6571 | 100048.4437 | 131009.0807 |  | 1862.7168 | 20308.9608 | 15215.7633 | 3522.6571 | 45652.6204 | 86562.7183
|  |  | 16772 | 16772 |  | 1885 | 5561 | 2998 | 1522 | 4806 |  | 1174 | 5582 | 3077 | 1524 | 5258 |  | 0 | 1722.575 | 0 | 0 | -1722.575 |  | 1677 | 3870 | 4894 | 1087 | 5244 |  | 0 | 3445.15 | 0 | 0 | -3445.15 |  | 1115 | 3589 | 5061 | 679 | 6328 | [22 empty] | 18807.7081 | 154831.7203 | 88687.2685 | 75032.5955 | 797375.9216 | 1134735.2141 |  | 30197.5048 | 154216.3536 | 86451.325 | 74922.5125 | 728813.9102 | 1074601.6061 |  | 26858.9432 | 107341.7878 | 141088.81 | 53531.1774 | 795151.1155 | 1123971.834 |  | 26858.9432 | 155120.7875 | 141088.81 | 53531.1774 | 533933.1422 | 910532.8603 |  | 17863.454 | 99543.0075 | 145921.7491 | 33438.8222 | 959705.3693 | 1256472.402 |  | 17863.454 | 195101.0067 | 145921.7491 | 33438.8222 | 437269.4226 | 829594.4546
| LV UGB |  | 1539 | 1539 | C1 | 860 | 217 | 86 | 115 | 261 | 1539 | 817 | 217 | 86 | 115 | 302 | 1537 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 188 | 111 | 35 | 345 | 1539 | 0 | 0 | 0 | 0 | 0 | 0 | 658 | 379 | 44 | 77 | 380 | 1538 |  |  | C1 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C1 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | C1 | 5.8409 | 5.8409 | 10.1144 | 21.2659 | 48.5832 | C1 | 4772.0163 | 1267.4756 | 869.8342 | 2445.5752 | 14672.1255 | 24027.0268 |  | 5023.1751 | 1267.4756 | 869.8342 | 2445.5752 | 12680.2145 | 22286.2745 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133
|  |  | 10442 | 10442 | C2 | 5837 | 1470 | 580 | 784 | 1771 | 10442 | 5541 | 1470 | 580 | 784 | 2051 | 10426 | 0 | 0 | 0 | 0 | 0 | 0 | 5837 | 1273 | 749 | 237 | 2344 | 10440 | 0 | 0 | 0 | 0 | 0 | 0 | 4465 | 2572 | 299 | 524 | 2580 | 10440 |  |  | C2 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C2 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | C2 | 8.3441 | 8.3441 | 14.4491 | 30.3798 | 69.4046 | C2 | 46234.9053 | 12265.8926 | 8380.4623 | 23817.7759 | 142348.7677 | 233047.8039 |  | 48704.7721 | 12265.8926 | 8380.4623 | 23817.7759 | 122915.4889 | 216084.3918 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261
|  |  | 8109 | 8109 | C3 | 4534 | 1142 | 451 | 608 | 1374 | 8109 | 4305 | 1142 | 451 | 608 | 1593 | 8099 | 0 | 0 | 0 | 0 | 0 | 0 | 4534 | 990 | 583 | 184 | 1820 | 8111 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 1998 | 233 | 407 | 2005 | 8112 |  |  | C3 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C3 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | C3 | 12.5162 | 12.5162 | 21.6736 | 45.5697 | 104.1069 | C3 | 53882.3139 | 14293.5197 | 9774.7978 | 27706.3924 | 165842.2138 | 271499.2376 |  | 56748.5276 | 14293.5197 | 9774.7978 | 27706.3924 | 143042.8134 | 251566.0509 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C4 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | C4 | 20.8604 | 20.8604 | 36.1227 | 75.9495 | 173.5114 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20090 | 20090 |  | 11231 | 2829 | 1117 | 1507 | 3406 |  | 10663 | 2829 | 1117 | 1507 | 3946 |  | 0 | 0 | 0 | 0 | 0 |  | 11231 | 2451 | 1443 | 456 | 4509 |  | 0 | 0 | 0 | 0 | 0 |  | 8592 | 4949 | 576 | 1008 | 4965 | [22 empty] | 104889.2355 | 27826.8879 | 19025.0942 | 53969.7436 | 322863.1071 | 528574.0683 |  | 110476.4748 | 27826.8879 | 19025.0942 | 53969.7436 | 278638.5167 | 489936.7172 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823
| LV OHL Support |  | 28539 | 28539 | C1 | 3308 | 4632 | 13014 | 4744 | 2841 | 28539 | 657 | 4886 | 13689 | 5431 | 3966 | 28629 | 0 | 0 | 0 | 0 | 0 | 0 | 3150 | 4107 | 12747 | 4305 | 4229 | 28538 | 0 | 0 | 0 | 0 | 0 | 0 | 3052 | 3425 | 13256 | 3830 | 4976 | 28539 |  |  | C1 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C1 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | C1 | 12.4899 | 12.6968 | 21.5987 | 42.1194 | 71.1283 | C1 | 8205.8724 | 62036.6 | 295664.9903 | 228750.6004 | 282094.657 | 876752.7201 |  | 41316.6302 | 58811.611 | 281085.8488 | 199814.555 | 202075.3708 | 783104.0158 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123
|  |  | 9423 | 9423 | C2 | 1092 | 1530 | 4297 | 1566 | 938 | 9423 | 216 | 1613 | 4520 | 1794 | 1309 | 9452 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 1356 | 4209 | 1422 | 1397 | 9424 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1131 | 4377 | 1264 | 1643 | 9423 |  |  | C2 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C2 | 7778 | 7778 | 7778 | 7778 | 7778 | C2 | 17.8427 | 18.1383 | 30.8553 | 60.1706 | 101.6118 | C2 | 3854.0301 | 29257.0714 | 139466.0735 | 107946.0708 | 133009.8357 | 413533.0816 |  | 19484.2633 | 27751.5929 | 132585.3358 | 94227.1721 | 95311.8609 | 369360.2251 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713
|  |  | 21147 | 21147 | C3 | 2451 | 3433 | 9643 | 3515 | 2105 | 21147 | 487 | 3621 | 10144 | 4025 | 2939 | 21216 | 0 | 0 | 0 | 0 | 0 | 0 | 2334 | 3043 | 9445 | 3191 | 3134 | 21147 | 0 | 0 | 0 | 0 | 0 | 0 | 2262 | 2538 | 9823 | 2837 | 3687 | 21147 |  |  | C3 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C3 | 11667 | 11667 | 11667 | 11667 | 11667 | C3 | 26.7641 | 27.2074 | 46.283 | 90.2559 | 152.4177 | C3 | 13034.1157 | 98518.1547 | 469494.6404 | 363280.0458 | 447955.585 | 1392282.5417 |  | 65598.8042 | 93403.1553 | 446306.8629 | 317249.5307 | 320839.2332 | 1243397.5863 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C4 | 19445 | 19445 | 19445 | 19445 | 19445 | C4 | 44.6068 | 45.3457 | 77.1383 | 150.4265 | 254.0295 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 59109 | 59109 |  | 6851 | 9595 | 26954 | 9825 | 5884 |  | 1360 | 10120 | 28353 | 11250 | 8214 |  | 0 | 0 | 0 | 0 | 0 |  | 6524 | 8506 | 26401 | 8918 | 8760 |  | 0 | 0 | 0 | 0 | 0 |  | 6322 | 7094 | 27456 | 7931 | 10306 | [22 empty] | 25094.0183 | 189811.8262 | 904625.7043 | 699976.717 | 863060.0777 | 2682568.3434 |  | 126399.6978 | 179966.3591 | 859978.0475 | 611291.2579 | 618226.4649 | 2395861.8271 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 |  | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 |  | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 |  | 257702.488 | 338765.5964 | 1008001.4594 | 624753.6757 | 1823283.2157 | 4052506.4351 |  | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 |  | 219027.2054 | 376836.72 | 1031741.3081 | 562971.2668 | 1926375.4417 | 4116951.942
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1899 | 1899 | C1 | 312 | 461 | 253 | 229 | 644 | 1899 | 239 | 463 | 254 | 233 | 678 | 1867 | 0 | 33.8348 | 0 | 0 | -33.8348 | 0 | 161 | 561 | 185 | 129 | 864 | 1900 | 0 | 67.6695 | 0 | 0 | -67.6695 | 0 | 106 | 578 | 142 | 93 | 981 | 1900 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C1 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | C1 | 6.1027 | 79.5042 | 139.3443 | 269.1109 | 467.1086 | C1 | 1458.5385 | 36810.4663 | 35393.4599 | 62702.8297 | 316699.658 | 453064.9523 |  | 1904.0335 | 36651.4578 | 35254.1156 | 61626.3862 | 300817.9642 | 436253.9573 |  | 982.5301 | 44601.8825 | 25778.7011 | 34715.3005 | 403581.865 | 509660.2792 |  | 982.5301 | 47291.8905 | 25778.7011 | 34715.3005 | 387777.3509 | 496545.7732 |  | 646.8832 | 45953.4547 | 19786.8949 | 25027.3097 | 458233.5759 | 549648.1184 |  | 646.8832 | 51333.4707 | 19786.8949 | 25027.3097 | 426624.5477 | 523419.1062
|  |  | 451 | 451 | C2 | 74 | 110 | 60 | 54 | 153 | 451 | 57 | 110 | 60 | 55 | 161 | 443 | 0 | 15.6779 | 0 | 0 | -15.6779 | 0 | 38 | 133 | 44 | 31 | 205 | 451 | 0 | 31.3558 | 0 | 0 | -31.3558 | 0 | 25 | 137 | 34 | 22 | 233 | 451 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C2 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | C2 | 8.7181 | 113.5775 | 199.0633 | 384.4441 | 667.2981 | C2 | 496.9318 | 12493.5245 | 11943.7997 | 21144.4245 | 107434.9872 | 153513.6677 |  | 645.1395 | 12493.5245 | 11943.7997 | 20759.9804 | 102096.6028 | 147939.0469 |  | 331.2879 | 15105.8069 | 8758.7865 | 11917.7665 | 136796.1017 | 172909.7495 |  | 331.2879 | 16886.464 | 8758.7865 | 11917.7665 | 126334.2667 | 164228.5715 |  | 217.9526 | 15560.1169 | 6768.1532 | 8457.7698 | 155480.4473 | 186484.4397 |  | 217.9526 | 19121.4311 | 6768.1532 | 8457.7698 | 134556.7772 | 169122.0838
|  |  | 2347 | 2347 | C3 | 386 | 569 | 313 | 283 | 796 | 2347 | 295 | 572 | 315 | 288 | 838 | 2308 | 0 | 81.4873 | 0 | 0 | -81.4873 | 0 | 200 | 692 | 228 | 160 | 1066 | 2346 | 0 | 162.9746 | 0 | 0 | -162.9746 | 0 | 132 | 713 | 174 | 116 | 1211 | 2346 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C3 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | C3 | 13.0772 | 170.3662 | 298.595 | 576.6661 | 1000.9471 | C3 | 3857.7601 | 97449.4911 | 94057.423 | 166079.8431 | 838793.658 | 1200238.1753 |  | 5047.7811 | 96938.3924 | 93460.233 | 163196.5125 | 796753.8804 | 1155396.7993 |  | 2615.4306 | 117893.4403 | 68079.6585 | 92266.5795 | 1067009.5935 | 1347864.7025 |  | 2615.4306 | 131776.1296 | 68079.6585 | 92266.5795 | 985445.0938 | 1280182.8921 |  | 1726.1842 | 121471.1314 | 51955.5289 | 66893.2701 | 1212146.921 | 1454193.0356 |  | 1726.1842 | 149236.51 | 51955.5289 | 66893.2701 | 1049017.9215 | 1318829.4148
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C4 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | C4 | 21.7953 | 283.9437 | 497.6583 | 961.1102 | 1668.2451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4697 | 4697 |  | 772 | 1140 | 626 | 566 | 1593 |  | 591 | 1145 | 629 | 576 | 1677 |  | 0 | 131 | 0 | 0 | -131 |  | 399 | 1386 | 457 | 320 | 2135 |  | 0 | 262 | 0 | 0 | -262 |  | 263 | 1428 | 350 | 231 | 2425 | [22 empty] | 5813.2304 | 146753.4819 | 141394.6826 | 249927.0972 | 1262928.3032 | 1806816.7953 |  | 7596.9541 | 146083.3747 | 140658.1483 | 245582.8791 | 1199668.4473 | 1739589.8035 |  | 3929.2486 | 177601.1297 | 102617.1461 | 138899.6466 | 1607387.5603 | 2030434.7312 |  | 3929.2486 | 195954.4841 | 102617.1461 | 138899.6466 | 1499556.7114 | 1940957.2368 |  | 2591.0199 | 182984.703 | 78510.577 | 100378.3496 | 1825860.9442 | 2190325.5937 |  | 2591.0199 | 219691.4119 | 78510.577 | 100378.3496 | 1610199.2465 | 2011370.6048
| HV Switchgear (GM) - Distribution |  | 12 | 12 | C1 | 1 | 6 | 3 | 1 | 1 | 12 | 1 | 6 | 3 | 1 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 3 | 1 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2 | 1 | 3 | 12 |  |  | C1 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C1 | 22715 | 22715 | 22715 | 22715 | 22715 | C1 | 19.285 | 19.285 | 33.3683 | 65.6463 | 121.5252 | C1 | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669
|  |  | 28964 | 28964 | C2 | 2639 | 14945 | 6789 | 1775 | 2816 | 28964 | 1310 | 15230 | 7011 | 1941 | 3415 | 28907 | 0 | 0 | 0 | 0 | 0 | 0 | 2555 | 13020 | 6152 | 2634 | 4601 | 28962 | 0 | 0 | 0 | 0 | 0 | 0 | 2437 | 11427 | 5340 | 2529 | 7229 | 28962 |  |  | C2 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C2 | 32450 | 32450 | 32450 | 32450 | 32450 | C2 | 27.55 | 27.55 | 47.669 | 93.7805 | 173.6075 | C2 | 36090.5655 | 419587.2615 | 334207.7095 | 182027.9505 | 592869.6125 | 1564783.0995 |  | 72704.5819 | 411735.4972 | 323625.1804 | 166460.3875 | 488878.72 | 1463404.3671 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222
|  |  | 1505 | 1505 | C3 | 137 | 777 | 353 | 92 | 146 | 1505 | 68 | 792 | 364 | 101 | 177 | 1502 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 677 | 320 | 137 | 239 | 1506 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 594 | 278 | 131 | 376 | 1506 |  |  | C3 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C3 | 48675 | 48675 | 48675 | 48675 | 48675 | C3 | 41.3251 | 41.3251 | 71.5036 | 140.6707 | 260.4112 | C3 | 2810.1051 | 32729.4594 | 26027.3013 | 14207.7458 | 46092.7912 | 121867.4028 |  | 5661.5353 | 32109.5833 | 25240.762 | 12941.709 | 38020.0425 | 113973.632 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712
|  |  | 34 | 34 | C4 | 3 | 18 | 8 | 2 | 3 | 34 | 2 | 18 | 9 | 2 | 4 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 16 | 7 | 3 | 6 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 6 | 3 | 9 | 35 |  |  | C4 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C4 | 81125 | 81125 | 81125 | 81125 | 81125 | C4 | 68.8751 | 68.8751 | 119.1726 | 234.4512 | 434.0187 | C4 | 137.7502 | 1239.7523 | 1072.5536 | 468.9025 | 1736.075 | 4655.0336 |  | 206.6254 | 1239.7523 | 953.381 | 468.9025 | 1302.0562 | 4170.7174 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354
|  |  | 30515 | 30515 |  | 2780 | 15746 | 7153 | 1870 | 2966 |  | 1381 | 16046 | 7387 | 2045 | 3597 |  | 0 | 0 | 0 | 0 | 0 |  | 2692 | 13718 | 6482 | 2775 | 4848 |  | 0 | 0 | 0 | 0 | 0 |  | 2568 | 12040 | 5626 | 2664 | 7617 | [22 empty] | 39057.7059 | 453672.1834 | 361407.6695 | 196770.2451 | 640820.004 | 1691727.8078 |  | 78592.0276 | 445200.543 | 349919.4284 | 179936.6453 | 528322.344 | 1581970.9884 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977
| HV Transformer (GM) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C1 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | C1 | 17.5777 | 17.5777 | 30.3869 | 59.8934 | 168.7346 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14545 | 14545 | C2 | 4823 | 6506 | 2560 | 334 | 322 | 14545 | 4284 | 6630 | 2571 | 336 | 588 | 14409 | 0 | 0 | 0 | 0 | 0 | 0 | 4178 | 6111 | 3001 | 644 | 613 | 14547 | 0 | 0 | 0 | 0 | 0 | 0 | 3436 | 5557 | 3195 | 1197 | 1161 | 14546 |  |  | C2 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C2 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | C2 | 25.1111 | 25.1111 | 43.4099 | 85.5621 | 241.0494 | C2 | 107575.7912 | 166486.3434 | 111606.7455 | 28748.8546 | 141737.0648 | 556154.7995 |  | 121110.6538 | 163372.5717 | 111129.237 | 28577.7305 | 77617.9165 | 501808.1094 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635
|  |  | 2292 | 2292 | C3 | 760 | 1025 | 403 | 53 | 51 | 2292 | 675 | 1044 | 405 | 53 | 93 | 2270 | 0 | 0 | 0 | 0 | 0 | 0 | 658 | 962 | 473 | 101 | 96 | 2290 | 0 | 0 | 0 | 0 | 0 | 0 | 541 | 875 | 503 | 189 | 183 | 2291 |  |  | C3 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C3 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | C3 | 37.6666 | 37.6666 | 65.1148 | 128.3431 | 361.5741 | C3 | 25424.9506 | 39323.9237 | 26371.4889 | 6802.1843 | 33626.3955 | 131548.943 |  | 28626.6111 | 38608.2584 | 26241.2593 | 6802.1843 | 18440.2814 | 118718.5945 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C4 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | C4 | 62.7777 | 62.7777 | 108.5246 | 213.9052 | 602.6236 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 16837 | 16837 |  | 5583 | 7531 | 2963 | 387 | 373 |  | 4959 | 7674 | 2976 | 389 | 681 |  | 0 | 0 | 0 | 0 | 0 |  | 4836 | 7073 | 3474 | 745 | 709 |  | 0 | 0 | 0 | 0 | 0 |  | 3977 | 6432 | 3698 | 1386 | 1344 | [22 empty] | 133000.7418 | 205810.2671 | 137978.2344 | 35551.0389 | 175363.4603 | 687703.7425 |  | 149737.2649 | 201980.8301 | 137370.4963 | 35379.9148 | 96058.1979 | 620526.7039 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 3628 | 3628 | C1 | 204 | 1790 | 1305 | 281 | 48 | 3628 | 44 | 1814 | 1321 | 320 | 128 | 3627 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 1677 | 1326 | 316 | 117 | 3628 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 1663 | 1340 | 304 | 137 | 3629 |  |  | C1 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C1 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | C1 | 27.1392 | 27.1879 | 46.931 | 91.5265 | 143.007 | C1 | 1194.1258 | 49318.8161 | 61995.8864 | 29288.4641 | 18304.9008 | 160102.1933 |  | 5536.4014 | 48666.307 | 61244.99 | 25718.9326 | 6864.3378 | 148030.9687 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833
|  |  | 75099 | 75099 | C2 | 4224 | 37056 | 27000 | 5822 | 997 | 75099 | 902 | 37540 | 27350 | 6618 | 2653 | 75063 | 0 | 0 | 0 | 0 | 0 | 0 | 3970 | 34721 | 27449 | 6541 | 2419 | 75100 | 0 | 0 | 0 | 0 | 0 | 0 | 3829 | 34431 | 27726 | 6284 | 2830 | 75100 |  |  | C2 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C2 | 17378 | 17378 | 17378 | 17378 | 17378 | C2 | 38.7703 | 38.8398 | 67.0443 | 130.7521 | 204.2958 | C2 | 34970.8268 | 1458047.2182 | 1833662.2614 | 865317.2125 | 541996.6725 | 4733994.1914 |  | 163765.8232 | 1439248.7405 | 1810196.748 | 761238.5632 | 203682.8807 | 4378132.7556 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055
|  |  | 20166 | 20166 | C3 | 1134 | 9950 | 7251 | 1563 | 268 | 20166 | 242 | 10080 | 7344 | 1777 | 712 | 20155 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 9323 | 7371 | 1757 | 649 | 20166 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 9245 | 7445 | 1687 | 760 | 20165 |  |  | C3 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C3 | 26067 | 26067 | 26067 | 26067 | 26067 | C3 | 58.1555 | 58.2597 | 100.5665 | 196.1281 | 306.4437 | C3 | 14073.6254 | 587258.2296 | 738560.2732 | 348519.6479 | 218187.8802 | 1906599.6564 |  | 65948.3109 | 579684.4628 | 729207.59 | 306548.2328 | 82126.8987 | 1763515.4952 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549
|  |  | 77 | 77 | C4 | 4 | 38 | 28 | 6 | 1 | 77 | 1 | 38 | 28 | 7 | 3 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 28 | 7 | 2 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 28 | 6 | 3 | 76 |  |  | C4 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C4 | 43445 | 43445 | 43445 | 43445 | 43445 | C4 | 96.9258 | 97.0996 | 167.6108 | 326.8802 | 510.7394 | C4 | 96.9258 | 3689.7839 | 4693.1027 | 2288.1613 | 1532.2183 | 12300.1918 |  | 387.7032 | 3689.7839 | 4693.1027 | 1961.2811 | 510.7394 | 11242.6102 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903
|  |  | 98970 | 98970 |  | 5566 | 48834 | 35584 | 7672 | 1314 |  | 1189 | 49472 | 36043 | 8722 | 3496 |  | 0 | 0 | 0 | 0 | 0 |  | 5232 | 45756 | 36174 | 8621 | 3187 |  | 0 | 0 | 0 | 0 | 0 |  | 5046 | 45374 | 36539 | 8281 | 3730 | [22 empty] | 50335.5039 | 2098314.0478 | 2638911.5237 | 1245413.4858 | 780021.6718 | 6812996.2329 |  | 235638.2387 | 2071289.2941 | 2605342.4306 | 1095467.0096 | 293184.8567 | 6300921.8297 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 |  | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 |  | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 |  | 431250.7437 | 2714226.5048 | 3229263.74 | 1705079.9092 | 3256711.3844 | 11336532.282 |  | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 |  | 395507.7614 | 2657131.508 | 3200339.3994 | 1665720.2037 | 4145598.0766 | 12064296.9491
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 937 | 937 | C1 | 215 | 458 | 214 | 23 | 27 | 937 | 174 | 460 | 214 | 24 | 45 | 917 | 0 | 23.1285 | 0 | 0 | -23.1285 | 0 | 184 | 319 | 345 | 45 | 41 | 934 | 0 | 46.257 | 0 | 0 | -46.257 | 0 | 170 | 231 | 377 | 75 | 83 | 936 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C1 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | C1 | 4.7176 | 61.4602 | 105.2948 | 208.0341 | 361.0949 | C1 | 820.8667 | 28271.6771 | 22533.0796 | 4992.8196 | 16249.2689 | 72867.7119 |  | 1014.2893 | 28148.7567 | 22533.0796 | 4784.7854 | 9749.5614 | 66230.4725 |  | 868.043 | 19605.7934 | 36326.6938 | 9361.5367 | 14804.8895 | 80966.9564 |  | 868.043 | 21027.2759 | 36326.6938 | 9361.5367 | 6453.301 | 74036.8504 |  | 801.9962 | 14197.2987 | 39696.1263 | 15602.5612 | 29970.8738 | 100268.8562 |  | 801.9962 | 17040.2637 | 39696.1263 | 15602.5612 | 13267.6969 | 86408.6442
|  |  | 333 | 333 | C2 | 77 | 163 | 76 | 8 | 9 | 333 | 62 | 164 | 77 | 9 | 16 | 328 | 0 | 8.2515 | 0 | 0 | -8.2515 | 0 | 66 | 114 | 123 | 17 | 15 | 335 | 0 | 16.503 | 0 | 0 | -16.503 | 0 | 60 | 82 | 135 | 27 | 30 | 334 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C2 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | C2 | 6.7395 | 87.8002 | 150.4211 | 297.1916 | 515.8498 | C2 | 417.8468 | 14399.2393 | 11582.4241 | 2674.7248 | 8253.5969 | 37327.8318 |  | 518.9387 | 14311.439 | 11432.003 | 2377.5331 | 4642.6483 | 33282.5622 |  | 444.8046 | 10009.2273 | 18501.7944 | 5052.2579 | 7737.7471 | 41745.8313 |  | 444.8046 | 10733.7124 | 18501.7944 | 5052.2579 | 3481.2037 | 38213.7731 |  | 404.3678 | 7199.6196 | 20306.8475 | 8024.1743 | 15475.4942 | 51410.5035 |  | 404.3678 | 8648.5899 | 20306.8475 | 8024.1743 | 6962.4075 | 44346.387
|  |  | 294 | 294 | C3 | 68 | 144 | 67 | 7 | 8 | 294 | 55 | 144 | 67 | 8 | 14 | 288 | 0 | 7.2565 | 0 | 0 | -7.2565 | 0 | 58 | 100 | 108 | 15 | 13 | 294 | 0 | 14.513 | 0 | 0 | -14.513 | 0 | 53 | 72 | 119 | 24 | 26 | 294 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C3 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | C3 | 10.1092 | 131.7004 | 225.6316 | 445.7875 | 773.7747 | C3 | 556.0058 | 18964.8517 | 15117.3198 | 3566.2997 | 10832.8459 | 49037.3229 |  | 687.4253 | 18964.8517 | 15117.3198 | 3120.5122 | 6190.1977 | 44080.3067 |  | 586.3334 | 13170.0359 | 24368.217 | 6686.8119 | 10059.0712 | 54870.4694 |  | 586.3334 | 14125.717 | 24368.217 | 6686.8119 | 4444.1898 | 50211.2691 |  | 535.7874 | 9482.4258 | 26850.165 | 10698.8991 | 20118.1425 | 67685.4198 |  | 535.7874 | 11393.7881 | 26850.165 | 10698.8991 | 8888.3795 | 58367.0192
|  |  | 217 | 217 | C4 | 50 | 106 | 50 | 5 | 6 | 217 | 40 | 107 | 50 | 6 | 10 | 213 | 0 | 5.3635 | 0 | 0 | -5.3635 | 0 | 43 | 74 | 80 | 11 | 10 | 218 | 0 | 10.727 | 0 | 0 | -10.727 | 0 | 39 | 53 | 88 | 18 | 19 | 217 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C4 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | C4 | 16.8487 | 219.5006 | 376.0527 | 742.9791 | 1289.6245 | C4 | 673.9464 | 23486.564 | 18802.6365 | 4457.8746 | 12896.2452 | 60317.2668 |  | 842.433 | 23267.0634 | 18802.6365 | 3714.8955 | 7737.7471 | 54364.7756 |  | 724.4924 | 16243.0443 | 30084.2185 | 8172.7701 | 12896.2452 | 68120.7704 |  | 724.4924 | 17420.3326 | 30084.2185 | 8172.7701 | 5979.3622 | 62381.1759 |  | 657.0977 | 11633.5317 | 33092.6403 | 13373.6239 | 24502.8658 | 83259.7595 |  | 657.0977 | 13988.1085 | 33092.6403 | 13373.6239 | 10669.0999 | 71780.5703
|  |  | 1781 | 1781 |  | 410 | 871 | 407 | 43 | 50 |  | 331 | 875 | 408 | 47 | 85 |  | 0 | 44 | 0 | 0 | -44 |  | 351 | 607 | 656 | 88 | 79 |  | 0 | 88 | 0 | 0 | -88 |  | 322 | 438 | 719 | 144 | 158 | [22 empty] | 2468.6657 | 85122.332 | 68035.4601 | 15691.7187 | 48231.957 | 219550.1334 |  | 3063.0864 | 84692.1109 | 67885.039 | 13997.7263 | 28320.1544 | 197958.1169 |  | 2623.6733 | 59028.1009 | 109280.9236 | 29273.3767 | 45497.953 | 245704.0275 |  | 2623.6733 | 63307.0381 | 109280.9236 | 29273.3767 | 20358.0567 | 224843.0684 |  | 2399.2492 | 42512.8759 | 119945.779 | 47699.2585 | 90067.3763 | 302624.5389 |  | 2399.2492 | 51070.7502 | 119945.779 | 47699.2585 | 39787.5838 | 260902.6207
| EHV Transformer |  | 439 | 439 | C1 | 45 | 96 | 206 | 43 | 49 | 439 | 35 | 95 | 206 | 43 | 59 | 438 | 0 | 16.6336 | 16.6336 | 0 | -33.2672 | 0 | 29 | 75 | 143 | 90 | 102 | 439 | 0 | 33.2672 | 33.2672 | 0 | -66.5345 | 0 | 20 | 76 | 45 | 88 | 210 | 439 |  |  | C1 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C1 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | C1 | 267.4477 | 270.1797 | 467.4393 | 909.7131 | 1679.1834 | C1 | 9360.6698 | 25667.0727 | 96292.5028 | 39117.6645 | 99071.8178 | 269509.7276 |  | 12035.1469 | 25937.2524 | 96292.5028 | 39117.6645 | 82279.9842 | 255662.5509 |  | 7755.9835 | 20263.4785 | 66843.8247 | 81874.1816 | 171276.7019 | 348014.1703 |  | 7755.9835 | 24757.5437 | 74619.0305 | 81874.1816 | 115414.9244 | 304421.6637 |  | 5348.9542 | 20533.6582 | 21034.77 | 80054.7553 | 352628.5039 | 479600.6416 |  | 5348.9542 | 29521.7886 | 36585.1815 | 80054.7553 | 240904.9489 | 392415.6285
|  |  | 192 | 192 | C2 | 19 | 42 | 90 | 19 | 22 | 192 | 15 | 42 | 90 | 19 | 25 | 191 | 0 | 7.2437 | 7.2437 | 0 | -14.4873 | 0 | 13 | 33 | 62 | 39 | 45 | 192 | 0 | 14.4873 | 14.4873 | 0 | -28.9747 | 0 | 9 | 33 | 19 | 39 | 92 | 192 |  |  | C2 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C2 | 317306 | 317306 | 317306 | 317306 | 317306 | C2 | 382.0682 | 385.971 | 667.7705 | 1299.5902 | 2398.8334 | C2 | 5731.0223 | 16210.7828 | 60099.3429 | 24692.2135 | 59970.834 | 166704.1955 |  | 7259.2949 | 16210.7828 | 60099.3429 | 24692.2135 | 52774.3339 | 161035.9681 |  | 4966.886 | 12737.0436 | 41401.7696 | 50684.0172 | 107947.5012 | 217737.2176 |  | 4966.886 | 15532.8906 | 46238.8791 | 50684.0172 | 73194.7825 | 190617.4554 |  | 3438.6134 | 12737.0436 | 12687.6391 | 50684.0172 | 220692.6691 | 300239.9824 |  | 3438.6134 | 18328.7377 | 22361.8582 | 50684.0172 | 151187.2316 | 246000.4581
|  |  | 53 | 53 | C3 | 5 | 12 | 25 | 5 | 6 | 53 | 4 | 12 | 25 | 5 | 7 | 53 | 0 | 2.0313 | 2.0313 | 0 | -4.0626 | 0 | 4 | 9 | 17 | 11 | 13 | 54 | 0 | 4.0626 | 4.0626 | 0 | -8.1252 | 0 | 2 | 9 | 5 | 11 | 26 | 53 |  |  | C3 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C3 | 475959 | 475959 | 475959 | 475959 | 475959 | C3 | 573.1022 | 578.9565 | 1001.6557 | 1949.3853 | 3598.25 | C3 | 2292.4089 | 6947.4783 | 25041.3929 | 9746.9264 | 25187.7503 | 69215.9568 |  | 2865.5112 | 6947.4783 | 25041.3929 | 9746.9264 | 21589.5002 | 66190.809 |  | 2292.4089 | 5210.6087 | 17028.1472 | 21443.238 | 46777.2505 | 92751.6534 |  | 2292.4089 | 6386.6396 | 19062.8044 | 21443.238 | 32159.0434 | 81344.1344 |  | 1146.2045 | 5210.6087 | 5008.2786 | 21443.238 | 93554.501 | 126362.8309 |  | 1146.2045 | 7562.6705 | 9077.593 | 21443.238 | 64318.0869 | 103547.7929
|  |  | 36 | 36 | C4 | 4 | 8 | 17 | 3 | 4 | 36 | 3 | 8 | 17 | 3 | 5 | 36 | 0 | 1.3414 | 1.3414 | 0 | -2.6828 | 0 | 2 | 6 | 12 | 7 | 8 | 35 | 0 | 2.6828 | 2.6828 | 0 | -5.3657 | 0 | 2 | 6 | 4 | 7 | 17 | 36 |  |  | C4 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C4 | 793265 | 793265 | 793265 | 793265 | 793265 | C4 | 955.1704 | 964.9275 | 1669.4262 | 3248.9755 | 5997.0834 | C4 | 2865.5112 | 7719.4204 | 28380.2453 | 9746.9264 | 29985.417 | 78697.5202 |  | 3820.6815 | 7719.4204 | 28380.2453 | 9746.9264 | 23988.3336 | 73655.6072 |  | 1910.3408 | 5789.5653 | 20033.1143 | 22742.8282 | 47976.6672 | 98452.5158 |  | 1910.3408 | 7083.9389 | 22272.5169 | 22742.8282 | 31887.4456 | 85897.0703 |  | 1910.3408 | 5789.5653 | 6677.7048 | 22742.8282 | 101950.4178 | 139070.8568 |  | 1910.3408 | 8378.3125 | 11156.5099 | 22742.8282 | 69771.9745 | 113959.966
|  |  | 720 | 720 |  | 73 | 158 | 338 | 70 | 81 |  | 57 | 157 | 338 | 70 | 96 |  | 0 | 27.25 | 27.25 | 0 | -54.5 |  | 48 | 123 | 234 | 147 | 168 |  | 0 | 54.5 | 54.5 | 0 | -109 |  | 33 | 124 | 73 | 145 | 345 | [22 empty] | 20249.6122 | 56544.7542 | 209813.4839 | 83303.7308 | 214215.819 | 584127.4001 |  | 25980.6345 | 56814.9339 | 209813.4839 | 83303.7308 | 180632.152 | 556544.9351 |  | 16925.6192 | 44000.6961 | 145306.8558 | 176744.2651 | 373978.1208 | 756955.557 |  | 16925.6192 | 53761.0129 | 162193.2309 | 176744.2651 | 252656.1958 | 662280.3239 |  | 11844.1128 | 44270.8758 | 45408.3924 | 174924.8388 | 768826.0919 | 1045274.3117 |  | 11844.1128 | 63791.5094 | 79181.1426 | 174924.8388 | 526182.2419 | 855923.8454
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | C1 | 87.4881 | 87.4881 | 262.4643 | 612.4167 | 874.881 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 227.0678 | C2 | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 | 227.0678 | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 | 234.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 | 227.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | 227.0675 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 124983 | 124983 | 124983 | 124983 | 124983 | C2 | 124.983 | 124.983 | 374.949 | 874.881 | 1249.83 | C2 | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | C3 | 187.4745 | 187.4745 | 562.4235 | 1312.3215 | 1874.745 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | C4 | 312.4575 | 312.4575 | 937.3725 | 2187.2025 | 3124.575 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 227.0678 |  | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 |  | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 |  | 0 | 0 | 0 | 0 | 0 |  | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 |  | 0 | 0 | 0 | 0 | 0 |  | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | [22 empty] | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744
| EHV UG Cable (Oil) |  | 17.0815 | 17.0815 | C1 | 1.6369 | 2.5218 | 2.8663 | 6.9395 | 3.1171 | 17.0815 | 1.63 | 2.5796 | 3.0569 | 8.8085 | 4.8454 | 20.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090919 | 3.5395 | 2.8444 | 5.6227 | 5.0659 | 17.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090919 | 2.2753 | 3.4238 | 1.729 | 9.6443 | 17.0815 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | C1 | 194.5762 | 194.5762 | 583.7286 | 1362.0334 | 1945.762 | C1 | 317.1507 | 501.9325 | 1784.4163 | 11997.4175 | 9428.0449 | 24028.9618 |  | 318.5082 | 490.6886 | 1673.1151 | 9451.7929 | 6065.0403 | 17999.1451 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996
|  |  | 246.8 | 246.8 | C2 | 23.651 | 36.4363 | 41.4126 | 100.2639 | 45.0362 | 246.8 | 23.5502 | 37.2712 | 44.1675 | 127.2676 | 70.0084 | 302.2649 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13136 | 51.1394 | 41.0967 | 81.2383 | 73.1937 | 246.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13136 | 32.875 | 49.4679 | 24.9812 | 139.3439 | 246.7995 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 277966 | 277966 | 277966 | 277966 | 277966 | C2 | 277.966 | 277.966 | 833.898 | 1945.762 | 2779.66 | C2 | 6546.1447 | 10360.1311 | 36831.2217 | 247632.544 | 194599.4408 | 495969.4824 |  | 6574.1645 | 10128.0511 | 34533.9105 | 195089.612 | 125185.3879 | 371511.126 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146
|  |  | 29.9197 | 29.9197 | C3 | 2.8672 | 4.4172 | 5.0205 | 12.155 | 5.4598 | 29.9197 | 2.855 | 4.5184 | 5.3544 | 15.4287 | 8.4871 | 36.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015925 | 6.1996 | 4.9822 | 9.8485 | 8.8733 | 29.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015925 | 3.9855 | 5.997 | 3.0285 | 16.8927 | 29.9196 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 416949 | 416949 | 416949 | 416949 | 416949 | C3 | 416.949 | 416.949 | 1250.847 | 2918.643 | 4169.49 | C3 | 1190.3873 | 1883.9438 | 6697.5938 | 45030.8766 | 35387.0427 | 90189.8443 |  | 1195.4826 | 1841.741 | 6279.838 | 35476.1782 | 22764.406 | 67557.6458 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 694915 | 694915 | 694915 | 694915 | 694915 | C4 | 694.915 | 694.915 | 2084.745 | 4864.405 | 6949.15 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293.8012 | 293.8012 |  | 28.1551 | 43.3753 | 49.2994 | 119.3584 | 53.613 |  | 28.0351 | 44.3692 | 52.5789 | 151.5048 | 83.3409 |  | 0 | 0 | 0 | 0 | 0 |  | 0.15638 | 60.8785 | 48.9233 | 96.7095 | 87.1329 |  | 0 | 0 | 0 | 0 | 0 |  | 0.15638 | 39.1358 | 58.8887 | 29.7387 | 165.8809 | [22 empty] | 8053.6827 | 12746.0073 | 45313.2319 | 304660.8381 | 239414.5284 | 610188.2884 |  | 8088.1553 | 12460.4808 | 42486.8636 | 240017.583 | 154014.8342 | 457067.9168 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 693 | 693 | C1 | 26 | 441 | 68 | 24 | 134 | 693 | 26 | 395 | 94 | 40 | 140 | 695 | 0 | 101.6361 | -47.9834 | -40.2396 | -13.4132 | 0 | 0 | 261 | 208 | 52 | 171 | 692 | 0 | 205.3753 | -96.8774 | -81.3734 | -27.1245 | 0 | 0 | 170 | 162 | 127 | 233 | 692 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | C1 | 3.0023 | 3.0023 | 6.0045 | 40.0303 | 150.4138 | C1 | 78.0591 | 1185.8974 | 564.4271 | 1601.2117 | 21057.9358 | 24487.5312 |  | 78.0591 | 1324.002 | 408.309 | 960.727 | 20155.4528 | 22926.5499 |  | 0 | 783.593 | 1248.9452 | 2081.5753 | 25720.7645 | 29834.8778 |  | 0 | 1088.7323 | 960.827 | 470.7725 | 23703.234 | 26223.5659 |  | 0 | 510.3862 | 972.7361 | 5083.8473 | 35046.4217 | 41613.3914 |  | 0 | 1126.9788 | 391.0313 | 1826.4461 | 30966.5268 | 34310.983
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 428896 | 428896 | 428896 | 428896 | 428896 | C2 | 4.289 | 4.289 | 8.5779 | 57.1861 | 214.8769 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6 | 6 | C3 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 1.1257 | -0.61401 | -0.38376 | -0.12792 | 0 | 0 | 2 | 2 | 1 | 2 | 7 | 0 | 2.2764 | -1.2417 | -0.77604 | -0.25868 | 0 | 0 | 2 | 2 | 1 | 2 | 7 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 643344 | 643344 | 643344 | 643344 | 643344 | C3 | 6.4334 | 6.4334 | 12.8669 | 85.7792 | 322.3153 | C3 | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 0 | 20.1089 | 17.8334 | 52.8609 | 603.4005 | 694.2037 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 0 | 27.5119 | 9.7574 | 19.2111 | 561.2541 | 617.7344
|  |  | 231 | 231 | C4 | 8 | 147 | 23 | 8 | 45 | 231 | 8 | 131 | 31 | 13 | 46 | 229 | 0 | 39.2382 | -21.4026 | -13.3766 | -4.4589 | 0 | 0 | 87 | 69 | 18 | 57 | 231 | 0 | 79.3483 | -43.2809 | -27.0506 | -9.0169 | 0 | 0 | 57 | 54 | 42 | 78 | 231 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 1072240 | 1072240 | 1072240 | 1072240 | 1072240 | C4 | 10.7224 | 10.7224 | 21.4448 | 142.9653 | 537.1922 | C4 | 85.7792 | 1404.6344 | 664.7888 | 1858.5493 | 24710.843 | 28724.5948 |  | 85.7792 | 1576.1928 | 493.2304 | 1143.7227 | 24173.6508 | 27472.5759 |  | 0 | 932.8488 | 1479.6912 | 2573.376 | 30619.9577 | 35605.8737 |  | 0 | 1353.5762 | 1020.7159 | 660.9788 | 28224.6802 | 31259.9511 |  | 0 | 611.1768 | 1158.0192 | 6004.544 | 41900.9947 | 49674.7347 |  | 0 | 1461.9811 | 229.8691 | 2137.2519 | 37057.2114 | 40886.3134
|  |  | 930 | 930 |  | 34 | 592 | 92 | 32 | 180 |  | 34 | 530 | 126 | 53 | 187 |  | 0 | 142 | -70 | -54 | -18 |  | 0 | 350 | 279 | 71 | 230 |  | 0 | 287 | -141.4 | -109.2 | -36.4 |  | 0 | 229 | 218 | 170 | 313 | [22 empty] | 163.8383 | 2616.2656 | 1242.0828 | 3459.7611 | 46091.0942 | 53573.0419 |  | 163.8383 | 2925.9285 | 914.4063 | 2104.4497 | 44651.419 | 50760.0418 |  | 0 | 1729.3087 | 2754.3701 | 4740.7305 | 56985.3528 | 66209.7621 |  | 0 | 2462.4174 | 1999.3763 | 1184.6122 | 52531.3147 | 58177.7206 |  | 0 | 1134.4299 | 2156.4891 | 11174.1705 | 77592.0471 | 92057.1366 |  | 0 | 2616.4717 | 630.6578 | 3982.9091 | 68584.9923 | 75815.0309
| EHV OHL Support - Poles |  | 263 | 263 | C1 | 12 | 112 | 108 | 21 | 10 | 263 | 2 | 114 | 110 | 24 | 15 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 122 | 25 | 12 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 82 | 127 | 28 | 16 | 265 |  |  | C1 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C1 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | C1 | 65.7424 | 66.812 | 113.6298 | 243.7157 | 330.7688 | C1 | 131.4847 | 7616.5691 | 12499.2763 | 5849.1775 | 4961.5322 | 31058.0399 |  | 788.9083 | 7482.9451 | 12272.0168 | 5118.0303 | 3307.6882 | 28969.5886 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173
|  |  | 8940 | 8940 | C2 | 423 | 3799 | 3664 | 722 | 332 | 8940 | 52 | 3863 | 3736 | 805 | 507 | 8963 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 3167 | 4116 | 846 | 393 | 8939 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 2761 | 4281 | 959 | 525 | 8939 |  |  | C2 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C2 | 117544 | 117544 | 117544 | 117544 | 117544 | C2 | 93.9177 | 95.4457 | 162.3283 | 348.1653 | 472.5269 | C2 | 4883.7181 | 368706.8473 | 606458.3943 | 280273.089 | 239571.1282 | 1499893.1769 |  | 39727.1685 | 362598.3207 | 594770.7593 | 251375.3668 | 156878.9242 | 1405350.5394 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067
|  |  | 3324 | 3324 | C3 | 157 | 1412 | 1363 | 268 | 124 | 3324 | 19 | 1436 | 1389 | 300 | 188 | 3332 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 1178 | 1530 | 315 | 146 | 3324 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 1027 | 1591 | 357 | 195 | 3324 |  |  | C3 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C3 | 176316 | 176316 | 176316 | 176316 | 176316 | C3 | 140.8765 | 143.1686 | 243.4924 | 522.248 | 708.7903 | C3 | 2676.6532 | 205590.0981 | 338210.938 | 156674.3976 | 133252.5802 | 836404.6671 |  | 22117.608 | 202154.0519 | 331880.1357 | 139962.4619 | 87889.9997 | 784004.2572 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701
|  |  | 7 | 7 | C4 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 6 |  |  | C4 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C4 | 293860 | 293860 | 293860 | 293860 | 293860 | C4 | 234.7941 | 238.6143 | 405.8207 | 870.4133 | 1181.3172 | C4 | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039
|  |  | 12534 | 12534 |  | 592 | 5326 | 5138 | 1012 | 466 |  | 73 | 5416 | 5238 | 1130 | 710 |  | 0 | 0 | 0 | 0 | 0 |  | 584 | 4441 | 5771 | 1187 | 551 |  | 0 | 0 | 0 | 0 | 0 |  | 579 | 3872 | 6002 | 1345 | 736 | [22 empty] | 7691.856 | 582629.3574 | 958386.0707 | 443667.0775 | 377785.2406 | 2370159.6021 |  | 62633.6848 | 572951.1606 | 940140.3738 | 397326.2723 | 248076.612 | 2221128.1035 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198
| EHV OHL Fittings and Conductors (Tower Lines) |  | 264.3928 | 264.3928 | C1 | 60.0911 | 197.1135 | 4.2075 | 0.74518 | 2.2355 | 264.3928 | 0 | 235.0812 | 14.1584 | 0.74518 | 2.2355 | 252.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0911 | 168.7967 | 25.0724 | 4.4711 | 5.9614 | 264.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0911 | 147.1866 | 18.3658 | 18.6294 | 20.1198 | 264.3928 |  |  | C1 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C1 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | C1 | 1.5983 | 36.9203 | 128.5019 | 559.3987 | 1552.0917 | C1 | 0 | 8679.2717 | 1819.3778 | 416.8514 | 3469.7521 | 14385.253 |  | 96.0426 | 7277.491 | 540.6664 | 416.8514 | 3469.7521 | 11800.8035 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151
|  |  | 0.36021 | 0.36021 | C2 | 0.081868 | 0.26855 | 0.0057322 | 0.0010152 | 0.0030457 | 0.36021 | 0 | 0.32027 | 0.019289 | 0.0010152 | 0.0030457 | 0.34362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081868 | 0.22997 | 0.034159 | 0.0060914 | 0.0081218 | 0.36021 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081868 | 0.20053 | 0.025022 | 0.025381 | 0.027411 | 0.36021 |  |  | C2 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C2 | 228326 | 228326 | 228326 | 228326 | 228326 | C2 | 2.2833 | 52.7433 | 183.5741 | 799.141 | 2217.2738 | C2 | 0 | 16.8923 | 3.541 | 0.81131 | 6.7531 | 27.9978 |  | 0.18693 | 14.1641 | 1.0523 | 0.81131 | 6.7531 | 22.9677 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175
|  |  | 2.1612 | 2.1612 | C3 | 0.49121 | 1.6113 | 0.034393 | 0.0060914 | 0.018274 | 2.1612 | 0 | 1.9216 | 0.11574 | 0.0060914 | 0.018274 | 2.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49121 | 1.3798 | 0.20495 | 0.036548 | 0.048731 | 2.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49121 | 1.2032 | 0.15013 | 0.15228 | 0.16447 | 2.1612 |  |  | C3 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C3 | 342489 | 342489 | 342489 | 342489 | 342489 | C3 | 3.4249 | 79.115 | 275.3612 | 1198.7115 | 3325.9107 | C3 | 0 | 152.0308 | 31.8692 | 7.3018 | 60.7781 | 251.9799 |  | 1.6823 | 127.4765 | 9.4706 | 7.3018 | 60.7781 | 206.7093 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576
|  |  | 87.8908 | 87.8908 | C4 | 19.9758 | 65.5255 | 1.3987 | 0.24772 | 0.74315 | 87.8908 | 0 | 78.1469 | 4.7066 | 0.24772 | 0.74315 | 83.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9758 | 56.1123 | 8.3347 | 1.4863 | 1.9817 | 87.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9758 | 48.9285 | 6.1053 | 6.1929 | 6.6883 | 87.8908 |  |  | C4 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C4 | 570815 | 570815 | 570815 | 570815 | 570815 | C4 | 5.7082 | 131.8583 | 458.9353 | 1997.8525 | 5543.1845 | C4 | 0 | 10304.3124 | 2160.0242 | 494.8995 | 4119.4021 | 17078.6382 |  | 114.0248 | 8640.0731 | 641.8966 | 494.8995 | 4119.4021 | 14010.2961 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793
|  |  | 354.805 | 354.805 |  | 80.64 | 264.5188 | 5.6462 | 1 | 3 |  | 0 | 315.47 | 19 | 1 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 80.64 | 226.5188 | 33.6462 | 6 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 80.64 | 197.5188 | 24.6462 | 25 | 27 | [22 empty] | 0 | 19152.5073 | 4014.8122 | 919.864 | 7656.6853 | 31743.8689 |  | 211.9367 | 16059.2047 | 1193.0859 | 919.864 | 7656.6853 | 26040.7766 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 |  | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 |  | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 |  | 81637.2401 | 631818.3708 | 1392663.1966 | 942202.6952 | 993469.1711 | 4041790.6739 |  | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 |  | 75814.7624 | 558830.5508 | 1368646.2144 | 859922.9752 | 1756937.6373 | 4620152.1401
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 77 | 77 | C1 | 43 | 16 | 2 | 2 | 14 | 77 | 40 | 16 | 2 | 2 | 15 | 75 | 0 | 1.6021 | 0 | -1.6021 | 0 | 0 | 32 | 20 | 4 | 4 | 16 | 76 | 0 | 3.2041 | 0 | -3.2041 | 0 | 0 | 29 | 23 | 4 | 5 | 16 | 77 |  |  | C1 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C1 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | C1 | 1145.2464 | 1145.2464 | 2032.8759 | 3954.8992 | 7511.4217 | C1 | 45809.8574 | 18323.943 | 4065.7519 | 7909.7984 | 112671.3259 | 188780.6766 |  | 49245.5968 | 18323.943 | 4065.7519 | 7909.7984 | 105159.9042 | 184704.9942 |  | 36647.886 | 22904.9287 | 8131.5037 | 15819.5969 | 120182.7476 | 203686.6629 |  | 36647.886 | 24739.6905 | 8131.5037 | 9483.5826 | 120182.7476 | 199185.4104 |  | 33212.1466 | 26340.668 | 8131.5037 | 19774.4961 | 120182.7476 | 207641.5621 |  | 33212.1466 | 30010.1915 | 8131.5037 | 7102.4676 | 120182.7476 | 198639.0571
|  |  | 27 | 27 | C2 | 15 | 6 | 1 | 0 | 5 | 27 | 14 | 6 | 1 | 0 | 5 | 26 | 0 | 0.56158 | 0 | -0.56158 | 0 | 0 | 12 | 7 | 1 | 2 | 6 | 28 | 0 | 1.1232 | 0 | -1.1232 | 0 | 0 | 10 | 8 | 2 | 2 | 6 | 28 |  |  | C2 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C2 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | C2 | 1636.0663 | 1636.0663 | 2904.1085 | 5649.856 | 10730.6025 | C2 | 22904.9287 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 89278.4475 |  | 24540.9951 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 90914.5139 |  | 19632.796 | 11452.4644 | 2904.1085 | 11299.7121 | 64383.6148 | 109672.6957 |  | 19632.796 | 12371.2544 | 2904.1085 | 8126.8386 | 64383.6148 | 107418.6123 |  | 16360.6634 | 13088.5307 | 5808.217 | 11299.7121 | 64383.6148 | 110940.7379 |  | 16360.6634 | 14926.1108 | 5808.217 | 4953.9651 | 64383.6148 | 106432.571
|  |  | 90 | 90 | C3 | 50 | 21 | 3 | 1 | 15 | 90 | 46 | 18 | 3 | 1 | 17 | 85 | 0 | 1.8363 | 0 | -1.8363 | 0 | 0 | 38 | 23 | 5 | 5 | 19 | 90 | 0 | 3.6727 | 0 | -3.6727 | 0 | 0 | 33 | 27 | 5 | 5 | 19 | 89 |  |  | C3 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C3 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | C3 | 2454.0995 | 2454.0995 | 4356.1627 | 8474.784 | 16095.9037 | C3 | 112888.5773 | 44173.7911 | 13068.4881 | 8474.784 | 273630.3629 | 452236.0034 |  | 122704.9753 | 51536.0896 | 13068.4881 | 8474.784 | 241438.5555 | 437222.8926 |  | 93255.7812 | 56444.2886 | 21780.8136 | 42373.9202 | 305822.1703 | 519676.9739 |  | 93255.7812 | 60950.8693 | 21780.8136 | 26811.2677 | 305822.1703 | 508620.902 |  | 80985.2837 | 66260.6867 | 21780.8136 | 42373.9202 | 305822.1703 | 517222.8744 |  | 80985.2837 | 75273.848 | 21780.8136 | 11248.6152 | 305822.1703 | 495110.7307
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C4 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | C4 | 4090.1658 | 4090.1658 | 7260.2712 | 14124.6401 | 26826.5062 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 194 | 194 |  | 108 | 43 | 6 | 3 | 34 |  | 100 | 40 | 6 | 3 | 37 |  | 0 | 4 | 0 | -4 | 0 |  | 82 | 50 | 10 | 11 | 41 |  | 0 | 8 | 0 | -8 | 0 |  | 72 | 58 | 11 | 12 | 41 | [22 empty] | 181603.3635 | 72314.1321 | 20038.3485 | 16384.5825 | 439954.7011 | 730295.1276 |  | 196491.5671 | 79676.4306 | 20038.3485 | 16384.5825 | 400251.4719 | 712842.4007 |  | 149536.4632 | 90801.6817 | 32816.4258 | 69493.2291 | 490388.5327 | 833036.3325 |  | 149536.4632 | 98061.8142 | 32816.4258 | 44421.6888 | 490388.5327 | 815224.9247 |  | 130558.0937 | 105689.8854 | 35720.5343 | 73448.1283 | 490388.5327 | 835805.1744 |  | 130558.0937 | 120210.1503 | 35720.5343 | 23305.0478 | 490388.5327 | 800182.3587
| 132kV Transformer |  | 59 | 59 | C1 | 12 | 19 | 15 | 7 | 6 | 59 | 5 | 19 | 15 | 7 | 11 | 57 | 0 | 2.5577 | 0 | 0 | -2.5577 | 0 | 11 | 10 | 16 | 16 | 7 | 60 | 0 | 5.1154 | 0 | 0 | -5.1154 | 0 | 11 | 10 | 6 | 17 | 17 | 61 |  |  | C1 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C1 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | C1 | 1418.2655 | 1418.2655 | 2428.685 | 4604.9455 | 10096.9831 | C1 | 7091.3276 | 26947.0449 | 36430.2757 | 32234.6186 | 111066.8143 | 213770.0812 |  | 17019.1863 | 26947.0449 | 36430.2757 | 32234.6186 | 60581.8987 | 173213.0242 |  | 15600.9207 | 14182.6552 | 38858.9608 | 73679.1283 | 70678.8818 | 213000.5468 |  | 15600.9207 | 17810.142 | 38858.9608 | 73679.1283 | 44853.9058 | 190803.0576 |  | 15600.9207 | 14182.6552 | 14572.1103 | 78284.0738 | 171648.713 | 294288.473 |  | 15600.9207 | 21437.6288 | 14572.1103 | 78284.0738 | 119998.7609 | 249893.4946
|  |  | 51 | 51 | C2 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 0 | 2.1538 | 0 | 0 | -2.1538 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 0 | 4.3077 | 0 | 0 | -4.3077 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C2 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C2 | 858587 | 858587 | 858587 | 858587 | 858587 | C2 | 2026.0936 | 2026.0936 | 3469.5501 | 6578.4936 | 14424.2616 | C2 | 10130.468 | 30391.404 | 48573.7009 | 39470.9616 | 144242.616 | 272809.1506 |  | 20260.936 | 34443.5912 | 48573.7009 | 39470.9616 | 57697.0464 | 200446.2362 |  | 20260.936 | 18234.8424 | 45104.1509 | 85520.4167 | 72121.308 | 241241.654 |  | 20260.936 | 22598.7363 | 45104.1509 | 85520.4167 | 41053.6676 | 214537.9076 |  | 18234.8424 | 14182.6552 | 17347.7503 | 92098.9103 | 216363.924 | 358228.0823 |  | 18234.8424 | 22910.443 | 17347.7503 | 92098.9103 | 154228.6433 | 304820.5894
|  |  | 51 | 51 | C3 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 0 | 2.1538 | 0 | 0 | -2.1538 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 0 | 4.3077 | 0 | 0 | -4.3077 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C3 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C3 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | C3 | 3039.1404 | 3039.1404 | 5204.3251 | 9867.7404 | 21636.3924 | C3 | 15195.702 | 45587.1061 | 72860.5514 | 59206.4423 | 216363.924 | 409213.7258 |  | 30391.404 | 51665.3869 | 72860.5514 | 59206.4423 | 86545.5696 | 300669.3543 |  | 30391.404 | 27352.2636 | 67656.2263 | 128280.6251 | 108181.962 | 361862.4811 |  | 30391.404 | 33898.1045 | 67656.2263 | 128280.6251 | 61580.5014 | 321806.8614 |  | 27352.2636 | 21273.9828 | 26021.6255 | 138148.3655 | 324545.886 | 537342.1234 |  | 27352.2636 | 34365.6646 | 26021.6255 | 138148.3655 | 231342.9649 | 457230.8841
|  |  | 3 | 3 | C4 | 1 | 1 | 1 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 3 | 0 | 0.13462 | 0 | 0 | -0.13462 | 0 | 1 | 1 | 1 | 1 | 0 | 4 | 0 | 0.26923 | 0 | 0 | -0.26923 | 0 | 1 | 0 | 0 | 1 | 1 | 3 |  |  | C4 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C4 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | C4 | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 36060.654 | C4 | 0 | 5065.234 | 8673.8752 | 0 | 36060.654 | 49799.7632 |  | 5065.234 | 5065.234 | 8673.8752 | 0 | 0 | 18804.3432 |  | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 0 | 35250.5772 |  | 5065.234 | 5747.0924 | 8673.8752 | 16446.234 | -4854.3188 | 31078.1168 |  | 5065.234 | 0 | 0 | 16446.234 | 36060.654 | 57572.122 |  | 5065.234 | 1363.7168 | 0 | 16446.234 | 26352.0164 | 49227.2012
|  |  | 164 | 164 |  | 33 | 54 | 44 | 19 | 14 |  | 15 | 50 | 44 | 19 | 32 |  | 0 | 7 | 0 | 0 | -7 |  | 32 | 29 | 43 | 43 | 17 |  | 0 | 14 | 0 | 0 | -14 |  | 30 | 24 | 16 | 46 | 48 | [22 empty] | 32417.4976 | 107990.789 | 166538.4032 | 130912.0225 | 507734.0083 | 945592.7207 |  | 72736.7603 | 118121.257 | 166538.4032 | 130912.0225 | 204824.5147 | 693132.9578 |  | 71318.4948 | 64834.9953 | 160293.2131 | 303926.404 | 250982.1518 | 851355.2591 |  | 71318.4948 | 80054.0753 | 160293.2131 | 303926.404 | 142633.7561 | 758225.9433 |  | 66253.2608 | 49639.2933 | 57941.4861 | 324977.5835 | 748619.177 | 1247430.8008 |  | 66253.2608 | 80077.4533 | 57941.4861 | 324977.5835 | 531922.3855 | 1061172.1692
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 10.9182 | 10.9182 | C1 | 0.069593 | 1.7577 | 3.5512 | 5.0591 | 0.48064 | 10.9182 | 0.068227 | 1.758 | 3.5519 | 5.1278 | 0.48064 | 10.9865 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009295 | 0.86512 | 2.3839 | 5.9513 | 1.717 | 10.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009295 | 0.035179 | 2.2525 | 4.4407 | 4.1888 | 10.9182 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | C1 | 89.1849 | 89.1849 | 267.5547 | 624.2943 | 891.849 | C1 | 6.0848 | 156.7859 | 950.3179 | 3201.2465 | 428.6599 | 4743.0951 |  | 6.2066 | 156.7643 | 950.1285 | 3158.3535 | 428.6599 | 4700.1129 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239
|  |  | 116.779 | 116.779 | C2 | 0.74435 | 18.8005 | 37.9824 | 54.1109 | 5.1408 | 116.779 | 0.72974 | 18.8031 | 37.99 | 54.8457 | 5.1408 | 117.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099418 | 9.2532 | 25.4975 | 63.6541 | 18.3642 | 116.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099418 | 0.37627 | 24.0928 | 47.4972 | 44.8028 | 116.779 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 127407 | 127407 | 127407 | 127407 | 127407 | C2 | 127.407 | 127.407 | 382.221 | 891.849 | 1274.07 | C2 | 92.974 | 2395.6419 | 14520.5776 | 48914.1022 | 6549.7974 | 72473.0931 |  | 94.8352 | 2395.3128 | 14517.6837 | 48258.709 | 6549.7974 | 71816.3381 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186
|  |  | 31.9588 | 31.9588 | C3 | 0.2037 | 5.1451 | 10.3946 | 14.8085 | 1.4069 | 31.9588 | 0.19971 | 5.1458 | 10.3967 | 15.0096 | 1.4069 | 32.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027208 | 2.5323 | 6.9779 | 17.4202 | 5.0257 | 31.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027208 | 0.10297 | 6.5934 | 12.9985 | 12.2611 | 31.9588 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | C3 | 191.1105 | 191.1105 | 573.3315 | 1337.7735 | 1911.105 | C3 | 38.1661 | 983.4189 | 5960.7448 | 20079.3997 | 2688.7134 | 29750.4429 |  | 38.9302 | 983.2838 | 5959.5569 | 19810.3586 | 2688.7134 | 29480.8428 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836
|  |  | 0.22406 | 0.22406 | C4 | 0.0014282 | 0.036072 | 0.072876 | 0.10382 | 0.0098637 | 0.22406 | 0.0014001 | 0.036077 | 0.072891 | 0.10523 | 0.0098637 | 0.22546 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9075e-05 | 0.017754 | 0.048922 | 0.12213 | 0.035235 | 0.22406 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9075e-05 | 0.00072194 | 0.046226 | 0.091132 | 0.085962 | 0.22406 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | C4 | 318.5175 | 318.5175 | 955.5525 | 2229.6225 | 3185.175 | C4 | 0.44597 | 11.4912 | 69.6511 | 234.627 | 31.4175 | 347.6328 |  | 0.4549 | 11.4896 | 69.6372 | 231.4833 | 31.4175 | 344.4825 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038
|  |  | 159.88 | 159.88 |  | 1.0191 | 25.7394 | 52.0011 | 74.0822 | 7.0382 |  | 0.99907 | 25.7429 | 52.0114 | 75.0883 | 7.0382 |  | 0 | 0 | 0 | 0 | 0 |  | 0.013611 | 12.6684 | 34.9082 | 87.1478 | 25.142 |  | 0 | 0 | 0 | 0 | 0 |  | 0.013611 | 0.51514 | 32.985 | 65.0276 | 61.3387 | [22 empty] | 137.6709 | 3547.3379 | 21501.2914 | 72429.3754 | 9698.5882 | 107314.2638 |  | 140.4269 | 3546.8505 | 21497.0062 | 71458.9044 | 9698.5882 | 106341.7763 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 104 | 104 | C1 | 4 | 74 | 6 | 14 | 6 | 104 | 2 | 55 | 19 | 18 | 10 | 104 | 0 | 8.7465 | 0 | -6.5599 | -2.1866 | 0 | 3 | 32 | 46 | 8 | 15 | 104 | 0 | 17.5301 | 0 | -13.1476 | -4.3825 | 0 | 3 | 13 | 48 | 17 | 22 | 103 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | C1 | 9.0026 | 9.0026 | 18.0052 | 120.0344 | 451.0293 | C1 | 18.0052 | 495.142 | 342.0981 | 2160.6194 | 4510.2931 | 7526.1577 |  | 36.0103 | 666.191 | 108.031 | 1680.4818 | 2706.1758 | 5196.8899 |  | 27.0077 | 288.0826 | 828.2375 | 960.2753 | 6765.4396 | 8869.0427 |  | 27.0077 | 366.8239 | 828.2375 | 172.8623 | 5779.2048 | 7174.1361 |  | 27.0077 | 117.0336 | 864.2478 | 2040.585 | 9922.6448 | 12971.5189 |  | 27.0077 | 274.8498 | 864.2478 | 462.4224 | 7945.9961 | 9574.5239
|  |  | 2572 | 2572 | C2 | 102 | 1838 | 141 | 337 | 154 | 2572 | 43 | 1359 | 464 | 456 | 251 | 2573 | 0 | 528.7394 | -310.9509 | -163.3414 | -54.4471 | 0 | 68 | 796 | 1135 | 190 | 384 | 2573 | 0 | 1056.9522 | -620.4524 | -327.3749 | -109.125 | 0 | 68 | 327 | 1202 | 426 | 551 | 2574 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 1286083 | 1286083 | 1286083 | 1286083 | 1286083 | C2 | 12.8608 | 12.8608 | 25.7217 | 171.4777 | 644.3276 | C2 | 553.0157 | 17477.868 | 11934.8502 | 78193.8464 | 161726.2233 | 269885.8036 |  | 1311.8047 | 23638.2055 | 3626.7541 | 57787.9961 | 99226.4478 | 185591.2082 |  | 874.5364 | 10237.2207 | 29194.0841 | 32580.7693 | 247421.7919 | 320308.4024 |  | 874.5364 | 17037.2477 | 21195.9114 | 4571.3626 | 212340.0099 | 256019.068 |  | 874.5364 | 4205.4914 | 30917.4353 | 73049.5144 | 355024.4982 | 464071.4758 |  | 874.5364 | 17798.7739 | 14958.3698 | 16912.017 | 284712.2827 | 335255.9798
|  |  | 447 | 447 | C3 | 18 | 319 | 24 | 59 | 27 | 447 | 7 | 236 | 80 | 79 | 44 | 446 | 0 | 115.5141 | -77.7291 | -28.3387 | -9.4462 | 0 | 12 | 138 | 197 | 33 | 66 | 446 | 0 | 231.5177 | -155.7876 | -56.7976 | -18.9325 | 0 | 12 | 57 | 208 | 74 | 95 | 446 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | C3 | 19.2912 | 19.2912 | 38.5825 | 257.2166 | 966.4914 | C3 | 135.0387 | 4552.7338 | 3086.5992 | 20320.1114 | 42525.6205 | 70620.1036 |  | 347.2424 | 6153.9072 | 925.9798 | 15175.7794 | 26095.2671 | 48698.1758 |  | 231.4949 | 2662.1918 | 7600.7505 | 8488.1478 | 63788.4307 | 82771.0158 |  | 231.4949 | 4890.6029 | 4601.7674 | 1198.9528 | 54658.714 | 65581.532 |  | 231.4949 | 1099.601 | 8025.1579 | 19034.0284 | 91816.6806 | 120206.9628 |  | 231.4949 | 5565.8655 | 2014.4842 | 4424.752 | 73518.5618 | 85755.1584
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | C4 | 32.1521 | 32.1521 | 64.3041 | 428.6943 | 1610.819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3123 | 3123 |  | 124 | 2231 | 171 | 410 | 187 |  | 52 | 1650 | 563 | 553 | 305 |  | 0 | 653 | -388.68 | -198.24 | -66.08 |  | 83 | 966 | 1378 | 231 | 465 |  | 0 | 1306 | -776.24 | -397.32 | -132.44 |  | 83 | 397 | 1458 | 517 | 668 | [22 empty] | 706.0596 | 22525.7437 | 15363.5475 | 100674.5772 | 208762.1369 | 348032.065 |  | 1695.0574 | 30458.3037 | 4660.7648 | 74644.2573 | 128027.8907 | 239486.2739 |  | 1133.0391 | 13187.4951 | 37623.0721 | 42029.1924 | 317975.6622 | 411948.4609 |  | 1133.0391 | 22294.6745 | 26625.9162 | 5943.1776 | 272777.9287 | 328774.7362 |  | 1133.0391 | 5422.1259 | 39806.841 | 94124.1278 | 456763.8236 | 597249.9575 |  | 1133.0391 | 23639.4892 | 17837.1017 | 21799.1914 | 366176.8407 | 430585.6622
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 52.7896 | 52.7896 | C1 | 2.6478 | 46.9644 | 1.6221 | 1.3898 | 0.16545 | 52.7896 | 1 | 47 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6478 | 40.975 | 5.8908 | 1.5884 | 1.6876 | 52.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6478 | 35.9122 | 4.6996 | 3.7062 | 5.824 | 52.7896 |  | 4.6996 | C1 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C1 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | C1 | 4.7807 | 45.4166 | 384.3676 | 1185.1335 | 3214.107 | C1 | 4.7807 | 2134.579 | 1153.1029 | 1185.1335 | 0 | 4477.5961 |  | 12.6582 | 2132.9638 | 623.4996 | 1647.1082 | 531.7848 | 4948.0146 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418
|  |  | 1314.4617 | 1314.4617 | C2 | 65.9298 | 1169.4145 | 40.3914 | 34.6062 | 4.1198 | 1314.4617 | 26 | 1178 | 70 | 35 | 7 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9298 | 1020.2782 | 146.6819 | 39.55 | 42.0218 | 1314.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9298 | 894.2126 | 117.0194 | 92.2833 | 145.0165 | 1314.4617 |  |  | C2 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C2 | 682956 | 682956 | 682956 | 682956 | 682956 | C2 | 6.8296 | 64.8808 | 549.0966 | 1693.0479 | 4591.5815 | C2 | 177.5686 | 76429.606 | 38436.7637 | 59256.6773 | 32141.0704 | 206441.6859 |  | 450.2715 | 75872.571 | 22178.7704 | 58589.9907 | 18916.3433 | 176007.9469 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601
|  |  | 228.0512 | 228.0512 | C3 | 11.4384 | 202.8864 | 7.0077 | 6.004 | 0.71476 | 228.0512 | 5 | 204 | 12 | 6 | 1 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4384 | 177.0121 | 25.4484 | 6.8617 | 7.2905 | 228.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4384 | 155.1405 | 20.3022 | 16.0106 | 25.1595 | 228.0512 |  |  | C3 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C3 | 1024434 | 1024434 | 1024434 | 1024434 | 1024434 | C3 | 10.2443 | 97.3212 | 823.6449 | 2539.5719 | 6887.3722 | C3 | 51.2217 | 19853.5309 | 9883.7392 | 15237.4313 | 6887.3722 | 51913.2954 |  | 117.1791 | 19745.151 | 5771.8246 | 15247.5157 | 4922.8074 | 45804.4777 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C4 | 1707390 | 1707390 | 1707390 | 1707390 | 1707390 | C4 | 17.0739 | 162.2021 | 1372.7416 | 4232.6198 | 11478.9537 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1595.3025 | 1595.3025 |  | 80.016 | 1419.2653 | 49.0212 | 42 | 5 |  | 32 | 1429 | 85 | 42 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 80.016 | 1238.2653 | 178.0212 | 48 | 51 |  | 0 | 0 | 0 | 0 | 0 |  | 80.016 | 1085.2653 | 142.0212 | 112 | 176 | [22 empty] | 233.571 | 98417.7159 | 49473.6058 | 75679.2422 | 39028.4426 | 262832.5774 |  | 580.1088 | 97750.6859 | 28574.0945 | 75484.6145 | 24370.9355 | 226760.4392 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 |  | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 |  | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 |  | 222569.9816 | 287440.7135 | 337933.7097 | 524621.201 | 1189029.1022 | 2561594.708 |  | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 |  | 198526.3781 | 298744.7998 | 207918.0781 | 634099.0336 | 2330868.4843 | 3670156.7739
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 269066.8564 | 269066.8564 |  | 36234.8093 | 102297.8188 | 83782.0698 | 25268.2431 | 21483.9155 |  | 22042.9663 | 103434.5141 | 86548.7282 | 28258.5442 | 28483.6662 |  | 0 | 2730.825 | -431.43 | -256.24 | -2043.155 |  | 33932.1673 | 90891.2169 | 88029.2386 | 25016.7125 | 31197.5201 |  | 0 | 5464.65 | -863.14 | -514.52 | -4086.99 |  | 29163.1673 | 87383.2531 | 88101.4332 | 24816.473 | 39602.5289 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 |  | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 |  | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 |  | 993160.4534 | 3972251.1855 | 5967862.1057 | 3796657.4811 | 7262492.8734 | 21992424.0991 |  | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 |  | 888876.1073 | 3891543.5787 | 5808645 | 3722713.4792 | 10159779.6399 | 24471557.8051
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 | LV Network | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 | LV Network | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 | LV Network | 257702.488 | 338765.5964 | 1008001.4594 | 624753.6757 | 1823283.2157 | 4052506.4351 | LV Network | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 | LV Network | 219027.2054 | 376836.72 | 1031741.3081 | 562971.2668 | 1926375.4417 | 4116951.942
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 | HV Network | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 | HV Network | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 | HV Network | 431250.7437 | 2714226.5048 | 3229263.74 | 1705079.9092 | 3256711.3844 | 11336532.282 | HV Network | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 | HV Network | 395507.7614 | 2657131.508 | 3200339.3994 | 1665720.2037 | 4145598.0766 | 12064296.9491
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 | EHV Network | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 | EHV Network | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 | EHV Network | 81637.2401 | 631818.3708 | 1392663.1966 | 942202.6952 | 993469.1711 | 4041790.6739 | EHV Network | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 | EHV Network | 75814.7624 | 558830.5508 | 1368646.2144 | 859922.9752 | 1756937.6373 | 4620152.1401
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 | 132kV Network | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 | 132kV Network | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 | 132kV Network | 222569.9816 | 287440.7135 | 337933.7097 | 524621.201 | 1189029.1022 | 2561594.708 | 132kV Network | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 | 132kV Network | 198526.3781 | 298744.7998 | 207918.0781 | 634099.0336 | 2330868.4843 | 3670156.7739
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 | Total | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 | Total | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 | Total | 993160.4534 | 3972251.1855 | 5967862.1057 | 3796657.4811 | 7262492.8734 | 21992424.0991 | Total | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 | Total | 888876.1073 | 3891543.5787 | 5808645 | 3722713.4792 | 10159779.6399 | 24471557.8051
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## ENWL - HVP
Secondary deliverables RIIO-ED1 - HVP - Asset Replacement and Refurbishment driven | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
ENWL | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 3251 | 3251 | C1 | 365 | 1078 | 581 | 295 | 932 | 3251 | 228 | 1082 | 597 | 295 | 1019 | 3221 | 0 | 0 | 0 | 0 | 0 | 0 | 325 | 750 | 949 | 211 | 1017 | 3252 | 0 | 0 | 0 | 0 | 0 | 0 | 216 | 696 | 981 | 132 | 1227 | 3252 | Yes |  | C1 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C1 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | 7118.5333 | C1 | 10.03 | 17.3692 | 18.0526 | 30.8232 | 94.9612 | C1 | 2286.8431 | 18793.4975 | 10777.4025 | 9092.8586 | 96765.4981 | 137716.0998 |  | 3660.9549 | 18724.0206 | 10488.5609 | 9092.8586 | 88503.8707 | 130470.2657 |  | 3259.7544 | 13026.916 | 17131.9179 | 6503.7056 | 96575.5757 | 136497.8695 |  | 3259.7544 | 13026.916 | 17131.9179 | 6503.7056 | 96575.5757 | 136497.8695 |  | 2166.4829 | 12088.978 | 17709.6011 | 4068.6689 | 116517.4349 | 152551.1659 |  | 2166.4829 | 12088.978 | 17709.6011 | 4068.6689 | 116517.4349 | 152551.1659
|  |  | 9179 | 9179 | C2 | 1032 | 3044 | 1640 | 833 | 2630 | 9179 | 642 | 3055 | 1684 | 834 | 2878 | 9093 | 0 | 0 | 0 | 0 | 0 | 0 | 918 | 2118 | 2678 | 594 | 2870 | 9178 | 0 | 0 | 0 | 0 | 0 | 0 | 610 | 1964 | 2769 | 371 | 3462 | 9176 | No |  | C2 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C2 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | 10169.3333 | C2 | 14.3286 | 24.8132 | 25.7894 | 44.0332 | 135.6589 | C2 | 9198.9552 | 75804.2445 | 43429.399 | 36723.6999 | 390426.3334 | 555582.632 |  | 14787.1056 | 75531.2996 | 42294.6641 | 36679.6667 | 356782.9245 | 526075.6605 |  | 13153.6462 | 52554.3011 | 69064.0918 | 26155.7287 | 389341.0621 | 550268.83 |  | 13153.6462 | 52554.3011 | 69064.0918 | 26155.7287 | 389341.0621 | 550268.83 |  | 8740.4403 | 48733.0724 | 71410.9298 | 16336.3221 | 469651.1349 | 614871.8996 |  | 8740.4403 | 48733.0724 | 71410.9298 | 16336.3221 | 469651.1349 | 614871.8996
|  |  | 3561 | 3561 | C3 | 400 | 1181 | 637 | 323 | 1020 | 3561 | 249 | 1185 | 653 | 324 | 1116 | 3527 | 0 | 0 | 0 | 0 | 0 | 0 | 356 | 822 | 1039 | 231 | 1113 | 3561 | 0 | 0 | 0 | 0 | 0 | 0 | 237 | 762 | 1075 | 144 | 1344 | 3562 |  |  | C3 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C3 | 15254 | 15254 | 15254 | 15254 | 15254 | C3 | 21.4929 | 37.2198 | 38.6841 | 66.0498 | 203.4884 | C3 | 5351.7286 | 44105.4156 | 25260.746 | 21400.1417 | 227093.0098 | 323211.0417 |  | 8597.1544 | 43956.5366 | 24641.7997 | 21334.0919 | 207558.1272 | 306087.7097 |  | 7651.4674 | 30594.6427 | 40192.8256 | 15257.5084 | 226482.5447 | 320178.9889 |  | 7651.4674 | 30594.6427 | 40192.8256 | 15257.5084 | 226482.5447 | 320178.9889 |  | 5093.814 | 28361.4571 | 41585.4548 | 9511.1741 | 273488.3558 | 358040.2558 |  | 5093.814 | 28361.4571 | 41585.4548 | 9511.1741 | 273488.3558 | 358040.2558
|  |  | 781 | 781 | C4 | 88 | 258 | 140 | 71 | 224 | 781 | 55 | 260 | 143 | 71 | 245 | 774 | 0 | 0 | 0 | 0 | 0 | 0 | 78 | 180 | 228 | 51 | 244 | 781 | 0 | 0 | 0 | 0 | 0 | 0 | 52 | 167 | 236 | 32 | 295 | 782 |  |  | C4 | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334 | C4 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | 25423.3333 | C4 | 35.8215 | 62.0329 | 64.4736 | 110.083 | 339.1473 | C4 | 1970.1812 | 16128.5627 | 9219.721 | 7815.8954 | 83091.0803 | 118225.4406 |  | 3152.2899 | 16004.4968 | 9026.3003 | 7815.8954 | 75968.9877 | 111967.9701 |  | 2794.0752 | 11165.928 | 14699.9747 | 5614.2347 | 82751.9331 | 117026.1457 |  | 2794.0752 | 11165.928 | 14699.9747 | 5614.2347 | 82751.9331 | 117026.1457 |  | 1862.7168 | 10359.4999 | 15215.7633 | 3522.6571 | 100048.4437 | 131009.0807 |  | 1862.7168 | 10359.4999 | 15215.7633 | 3522.6571 | 100048.4437 | 131009.0807
|  |  | 16772 | 16772 |  | 1885 | 5561 | 2998 | 1522 | 4806 |  | 1174 | 5582 | 3077 | 1524 | 5258 |  | 0 | 0 | 0 | 0 | 0 |  | 1677 | 3870 | 4894 | 1087 | 5244 |  | 0 | 0 | 0 | 0 | 0 |  | 1115 | 3589 | 5061 | 679 | 6328 | [22 empty] | 18807.7081 | 154831.7203 | 88687.2685 | 75032.5955 | 797375.9216 | 1134735.2141 |  | 30197.5048 | 154216.3536 | 86451.325 | 74922.5125 | 728813.9102 | 1074601.6061 |  | 26858.9432 | 107341.7878 | 141088.81 | 53531.1774 | 795151.1155 | 1123971.834 |  | 26858.9432 | 107341.7878 | 141088.81 | 53531.1774 | 795151.1155 | 1123971.834 |  | 17863.454 | 99543.0075 | 145921.7491 | 33438.8222 | 959705.3693 | 1256472.402 |  | 17863.454 | 99543.0075 | 145921.7491 | 33438.8222 | 959705.3693 | 1256472.402
| LV UGB |  | 1539 | 1539 | C1 | 860 | 217 | 86 | 115 | 261 | 1539 | 817 | 217 | 86 | 115 | 302 | 1537 | 0 | 0 | 0 | 0 | 0 | 0 | 860 | 188 | 111 | 35 | 345 | 1539 | 0 | 0 | 0 | 0 | 0 | 0 | 658 | 379 | 44 | 77 | 380 | 1538 |  |  | C1 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C1 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | 7798.266 | C1 | 5.8409 | 5.8409 | 10.1144 | 21.2659 | 48.5832 | C1 | 4772.0163 | 1267.4756 | 869.8342 | 2445.5752 | 14672.1255 | 24027.0268 |  | 5023.1751 | 1267.4756 | 869.8342 | 2445.5752 | 12680.2145 | 22286.2745 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 5023.1751 | 1098.0894 | 1122.693 | 744.3055 | 16761.203 | 24749.466 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133 |  | 3843.313 | 2213.7016 | 445.0314 | 1637.4721 | 18461.6149 | 26601.133
|  |  | 10442 | 10442 | C2 | 5837 | 1470 | 580 | 784 | 1771 | 10442 | 5541 | 1470 | 580 | 784 | 2051 | 10426 | 0 | 0 | 0 | 0 | 0 | 0 | 5837 | 1273 | 749 | 237 | 2344 | 10440 | 0 | 0 | 0 | 0 | 0 | 0 | 4465 | 2572 | 299 | 524 | 2580 | 10440 |  |  | C2 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C2 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | 11140.38 | C2 | 8.3441 | 8.3441 | 14.4491 | 30.3798 | 69.4046 | C2 | 46234.9053 | 12265.8926 | 8380.4623 | 23817.7759 | 142348.7677 | 233047.8039 |  | 48704.7721 | 12265.8926 | 8380.4623 | 23817.7759 | 122915.4889 | 216084.3918 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 48704.7721 | 10622.0961 | 10822.3556 | 7200.0165 | 162684.306 | 240033.5463 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261 |  | 37256.6057 | 21461.14 | 4320.2728 | 15919.0237 | 179063.7839 | 258020.8261
|  |  | 8109 | 8109 | C3 | 4534 | 1142 | 451 | 608 | 1374 | 8109 | 4305 | 1142 | 451 | 608 | 1593 | 8099 | 0 | 0 | 0 | 0 | 0 | 0 | 4534 | 990 | 583 | 184 | 1820 | 8111 | 0 | 0 | 0 | 0 | 0 | 0 | 3469 | 1998 | 233 | 407 | 2005 | 8112 |  |  | C3 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C3 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | 16710.57 | C3 | 12.5162 | 12.5162 | 21.6736 | 45.5697 | 104.1069 | C3 | 53882.3139 | 14293.5197 | 9774.7978 | 27706.3924 | 165842.2138 | 271499.2376 |  | 56748.5276 | 14293.5197 | 9774.7978 | 27706.3924 | 143042.8134 | 251566.0509 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 56748.5276 | 12391.0548 | 12635.7142 | 8384.8293 | 189474.469 | 279634.5948 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232 |  | 43418.7565 | 25007.4014 | 5049.951 | 18546.8778 | 208734.2365 | 300757.2232
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623 | C4 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | 27850.95 | C4 | 20.8604 | 20.8604 | 36.1227 | 75.9495 | 173.5114 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20090 | 20090 |  | 11231 | 2829 | 1117 | 1507 | 3406 |  | 10663 | 2829 | 1117 | 1507 | 3946 |  | 0 | 0 | 0 | 0 | 0 |  | 11231 | 2451 | 1443 | 456 | 4509 |  | 0 | 0 | 0 | 0 | 0 |  | 8592 | 4949 | 576 | 1008 | 4965 | [22 empty] | 104889.2355 | 27826.8879 | 19025.0942 | 53969.7436 | 322863.1071 | 528574.0683 |  | 110476.4748 | 27826.8879 | 19025.0942 | 53969.7436 | 278638.5167 | 489936.7172 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 110476.4748 | 24111.2403 | 24580.7627 | 16329.1512 | 368919.978 | 544417.6071 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823 |  | 84518.6753 | 48682.243 | 9815.2552 | 36103.3736 | 406259.6353 | 585379.1823
| LV OHL Support |  | 28539 | 28539 | C1 | 3308 | 4632 | 13014 | 4744 | 2841 | 28539 | 657 | 4886 | 13689 | 5431 | 3966 | 28629 | 0 | 0 | 0 | 0 | 0 | 0 | 3150 | 4107 | 12747 | 4305 | 4229 | 28538 | 0 | 0 | 0 | 0 | 0 | 0 | 3052 | 3425 | 13256 | 3830 | 4976 | 28539 |  |  | C1 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C1 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | 5444.6 | C1 | 12.4899 | 12.6968 | 21.5987 | 42.1194 | 71.1283 | C1 | 8205.8724 | 62036.6 | 295664.9903 | 228750.6004 | 282094.657 | 876752.7201 |  | 41316.6302 | 58811.611 | 281085.8488 | 199814.555 | 202075.3708 | 783104.0158 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 39343.2241 | 52145.7872 | 275318.9884 | 181324.1272 | 300801.3879 | 848933.5147 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123 |  | 38119.2126 | 43486.5647 | 286312.741 | 161317.4 | 353934.1939 | 883170.1123
|  |  | 9423 | 9423 | C2 | 1092 | 1530 | 4297 | 1566 | 938 | 9423 | 216 | 1613 | 4520 | 1794 | 1309 | 9452 | 0 | 0 | 0 | 0 | 0 | 0 | 1040 | 1356 | 4209 | 1422 | 1397 | 9424 | 0 | 0 | 0 | 0 | 0 | 0 | 1008 | 1131 | 4377 | 1264 | 1643 | 9423 |  |  | C2 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C2 | 7778 | 7778 | 7778 | 7778 | 7778 | C2 | 17.8427 | 18.1383 | 30.8553 | 60.1706 | 101.6118 | C2 | 3854.0301 | 29257.0714 | 139466.0735 | 107946.0708 | 133009.8357 | 413533.0816 |  | 19484.2633 | 27751.5929 | 132585.3358 | 94227.1721 | 95311.8609 | 369360.2251 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 18556.4413 | 24595.5294 | 129870.0671 | 85562.6046 | 141951.6734 | 400536.3158 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713 |  | 17985.4739 | 20514.4128 | 135053.7619 | 76055.6485 | 166948.1743 | 416557.4713
|  |  | 21147 | 21147 | C3 | 2451 | 3433 | 9643 | 3515 | 2105 | 21147 | 487 | 3621 | 10144 | 4025 | 2939 | 21216 | 0 | 0 | 0 | 0 | 0 | 0 | 2334 | 3043 | 9445 | 3191 | 3134 | 21147 | 0 | 0 | 0 | 0 | 0 | 0 | 2262 | 2538 | 9823 | 2837 | 3687 | 21147 |  |  | C3 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C3 | 11667 | 11667 | 11667 | 11667 | 11667 | C3 | 26.7641 | 27.2074 | 46.283 | 90.2559 | 152.4177 | C3 | 13034.1157 | 98518.1547 | 469494.6404 | 363280.0458 | 447955.585 | 1392282.5417 |  | 65598.8042 | 93403.1553 | 446306.8629 | 317249.5307 | 320839.2332 | 1243397.5863 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 62467.4047 | 82792.2521 | 437142.8311 | 288006.6152 | 477677.0342 | 1348086.1373 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215 |  | 60540.3897 | 69052.4929 | 454637.8009 | 256056.0223 | 561964.0157 | 1402250.7215
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064 | C4 | 19445 | 19445 | 19445 | 19445 | 19445 | C4 | 44.6068 | 45.3457 | 77.1383 | 150.4265 | 254.0295 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 59109 | 59109 |  | 6851 | 9595 | 26954 | 9825 | 5884 |  | 1360 | 10120 | 28353 | 11250 | 8214 |  | 0 | 0 | 0 | 0 | 0 |  | 6524 | 8506 | 26401 | 8918 | 8760 |  | 0 | 0 | 0 | 0 | 0 |  | 6322 | 7094 | 27456 | 7931 | 10306 | [22 empty] | 25094.0183 | 189811.8262 | 904625.7043 | 699976.717 | 863060.0777 | 2682568.3434 |  | 126399.6978 | 179966.3591 | 859978.0475 | 611291.2579 | 618226.4649 | 2395861.8271 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 120367.0701 | 159533.5686 | 842331.8866 | 554893.347 | 920430.0955 | 2597555.9678 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051 |  | 116645.0762 | 133053.4703 | 876004.3039 | 493429.0709 | 1082846.3838 | 2701978.3051
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 |  | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 |  | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 |  | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 |  | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 |  | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1899 | 1899 | C1 | 312 | 461 | 253 | 229 | 644 | 1899 | 239 | 463 | 254 | 233 | 678 | 1867 | 0 | 0 | 0 | 0 | 0 | 0 | 161 | 561 | 185 | 129 | 864 | 1900 | 0 | 0 | 0 | 0 | 0 | 0 | 106 | 578 | 142 | 93 | 981 | 1900 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C1 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | 84759.325 | C1 | 6.1027 | 79.5042 | 139.3443 | 269.1109 | 467.1086 | C1 | 1458.5385 | 36810.4663 | 35393.4599 | 62702.8297 | 316699.658 | 453064.9523 |  | 1904.0335 | 36651.4578 | 35254.1156 | 61626.3862 | 300817.9642 | 436253.9573 |  | 982.5301 | 44601.8825 | 25778.7011 | 34715.3005 | 403581.865 | 509660.2792 |  | 982.5301 | 44601.8825 | 25778.7011 | 34715.3005 | 403581.865 | 509660.2792 |  | 646.8832 | 45953.4547 | 19786.8949 | 25027.3097 | 458233.5759 | 549648.1184 |  | 646.8832 | 45953.4547 | 19786.8949 | 25027.3097 | 458233.5759 | 549648.1184
|  |  | 451 | 451 | C2 | 74 | 110 | 60 | 54 | 153 | 451 | 57 | 110 | 60 | 55 | 161 | 443 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 133 | 44 | 31 | 205 | 451 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 137 | 34 | 22 | 233 | 451 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C2 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | 121084.75 | C2 | 8.7181 | 113.5775 | 199.0633 | 384.4441 | 667.2981 | C2 | 496.9318 | 12493.5245 | 11943.7997 | 21144.4245 | 107434.9872 | 153513.6677 |  | 645.1395 | 12493.5245 | 11943.7997 | 20759.9804 | 102096.6028 | 147939.0469 |  | 331.2879 | 15105.8069 | 8758.7865 | 11917.7665 | 136796.1017 | 172909.7495 |  | 331.2879 | 15105.8069 | 8758.7865 | 11917.7665 | 136796.1017 | 172909.7495 |  | 217.9526 | 15560.1169 | 6768.1532 | 8457.7698 | 155480.4473 | 186484.4397 |  | 217.9526 | 15560.1169 | 6768.1532 | 8457.7698 | 155480.4473 | 186484.4397
|  |  | 2347 | 2347 | C3 | 386 | 569 | 313 | 283 | 796 | 2347 | 295 | 572 | 315 | 288 | 838 | 2308 | 0 | 0 | 0 | 0 | 0 | 0 | 200 | 692 | 228 | 160 | 1066 | 2346 | 0 | 0 | 0 | 0 | 0 | 0 | 132 | 713 | 174 | 116 | 1211 | 2346 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C3 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | 181627.125 | C3 | 13.0772 | 170.3662 | 298.595 | 576.6661 | 1000.9471 | C3 | 3857.7601 | 97449.4911 | 94057.423 | 166079.8431 | 838793.658 | 1200238.1753 |  | 5047.7811 | 96938.3924 | 93460.233 | 163196.5125 | 796753.8804 | 1155396.7993 |  | 2615.4306 | 117893.4403 | 68079.6585 | 92266.5795 | 1067009.5935 | 1347864.7025 |  | 2615.4306 | 117893.4403 | 68079.6585 | 92266.5795 | 1067009.5935 | 1347864.7025 |  | 1726.1842 | 121471.1314 | 51955.5289 | 66893.2701 | 1212146.921 | 1454193.0356 |  | 1726.1842 | 121471.1314 | 51955.5289 | 66893.2701 | 1212146.921 | 1454193.0356
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511 | C4 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | 302711.875 | C4 | 21.7953 | 283.9437 | 497.6583 | 961.1102 | 1668.2451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4697 | 4697 |  | 772 | 1140 | 626 | 566 | 1593 |  | 591 | 1145 | 629 | 576 | 1677 |  | 0 | 0 | 0 | 0 | 0 |  | 399 | 1386 | 457 | 320 | 2135 |  | 0 | 0 | 0 | 0 | 0 |  | 263 | 1428 | 350 | 231 | 2425 | [22 empty] | 5813.2304 | 146753.4819 | 141394.6826 | 249927.0972 | 1262928.3032 | 1806816.7953 |  | 7596.9541 | 146083.3747 | 140658.1483 | 245582.8791 | 1199668.4473 | 1739589.8035 |  | 3929.2486 | 177601.1297 | 102617.1461 | 138899.6466 | 1607387.5603 | 2030434.7312 |  | 3929.2486 | 177601.1297 | 102617.1461 | 138899.6466 | 1607387.5603 | 2030434.7312 |  | 2591.0199 | 182984.703 | 78510.577 | 100378.3496 | 1825860.9442 | 2190325.5937 |  | 2591.0199 | 182984.703 | 78510.577 | 100378.3496 | 1825860.9442 | 2190325.5937
| HV Switchgear (GM) - Distribution |  | 12 | 12 | C1 | 1 | 6 | 3 | 1 | 1 | 12 | 1 | 6 | 3 | 1 | 1 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 3 | 1 | 2 | 12 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 5 | 2 | 1 | 3 | 12 |  |  | C1 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C1 | 22715 | 22715 | 22715 | 22715 | 22715 | C1 | 19.285 | 19.285 | 33.3683 | 65.6463 | 121.5252 | C1 | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 115.7102 | 100.105 | 65.6463 | 121.5252 | 422.2718 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 19.285 | 96.4252 | 100.105 | 65.6463 | 243.0505 | 524.5121 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669 |  | 19.285 | 96.4252 | 66.7367 | 65.6463 | 364.5757 | 612.669
|  |  | 28964 | 28964 | C2 | 2639 | 14945 | 6789 | 1775 | 2816 | 28964 | 1310 | 15230 | 7011 | 1941 | 3415 | 28907 | 0 | 0 | 0 | 0 | 0 | 0 | 2555 | 13020 | 6152 | 2634 | 4601 | 28962 | 0 | 0 | 0 | 0 | 0 | 0 | 2437 | 11427 | 5340 | 2529 | 7229 | 28962 |  |  | C2 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C2 | 32450 | 32450 | 32450 | 32450 | 32450 | C2 | 27.55 | 27.55 | 47.669 | 93.7805 | 173.6075 | C2 | 36090.5655 | 419587.2615 | 334207.7095 | 182027.9505 | 592869.6125 | 1564783.0995 |  | 72704.5819 | 411735.4972 | 323625.1804 | 166460.3875 | 488878.72 | 1463404.3671 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 70390.3777 | 358701.651 | 293259.9956 | 247017.837 | 798768.1075 | 1768137.9688 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222 |  | 67139.4719 | 314814.4213 | 254552.727 | 237170.8845 | 1255008.6175 | 2128686.1222
|  |  | 1505 | 1505 | C3 | 137 | 777 | 353 | 92 | 146 | 1505 | 68 | 792 | 364 | 101 | 177 | 1502 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 677 | 320 | 137 | 239 | 1506 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 594 | 278 | 131 | 376 | 1506 |  |  | C3 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C3 | 48675 | 48675 | 48675 | 48675 | 48675 | C3 | 41.3251 | 41.3251 | 71.5036 | 140.6707 | 260.4112 | C3 | 2810.1051 | 32729.4594 | 26027.3013 | 14207.7458 | 46092.7912 | 121867.4028 |  | 5661.5353 | 32109.5833 | 25240.762 | 12941.709 | 38020.0425 | 113973.632 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 5496.235 | 27977.0758 | 22881.144 | 19271.8927 | 62238.2887 | 137864.6362 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712 |  | 5248.2845 | 24547.0945 | 19877.9938 | 18427.8682 | 97914.63 | 166015.8712
|  |  | 34 | 34 | C4 | 3 | 18 | 8 | 2 | 3 | 34 | 2 | 18 | 9 | 2 | 4 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 16 | 7 | 3 | 6 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 14 | 6 | 3 | 9 | 35 |  |  | C4 | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535 | C4 | 81125 | 81125 | 81125 | 81125 | 81125 | C4 | 68.8751 | 68.8751 | 119.1726 | 234.4512 | 434.0187 | C4 | 137.7502 | 1239.7523 | 1072.5536 | 468.9025 | 1736.075 | 4655.0336 |  | 206.6254 | 1239.7523 | 953.381 | 468.9025 | 1302.0562 | 4170.7174 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 206.6254 | 1102.002 | 834.2084 | 703.3537 | 2604.1125 | 5450.302 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354 |  | 206.6254 | 964.2517 | 715.0357 | 703.3537 | 3906.1687 | 6495.4354
|  |  | 30515 | 30515 |  | 2780 | 15746 | 7153 | 1870 | 2966 |  | 1381 | 16046 | 7387 | 2045 | 3597 |  | 0 | 0 | 0 | 0 | 0 |  | 2692 | 13718 | 6482 | 2775 | 4848 |  | 0 | 0 | 0 | 0 | 0 |  | 2568 | 12040 | 5626 | 2664 | 7617 | [22 empty] | 39057.7059 | 453672.1834 | 361407.6695 | 196770.2451 | 640820.004 | 1691727.8078 |  | 78592.0276 | 445200.543 | 349919.4284 | 179936.6453 | 528322.344 | 1581970.9884 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 76112.5231 | 387877.1539 | 317075.453 | 267058.7299 | 863853.5592 | 1911977.4192 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977 |  | 72613.6668 | 340422.1928 | 275212.4933 | 256367.7528 | 1357193.992 | 2301810.0977
| HV Transformer (GM) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C1 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | 14672.574 | C1 | 17.5777 | 17.5777 | 30.3869 | 59.8934 | 168.7346 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14545 | 14545 | C2 | 4823 | 6506 | 2560 | 334 | 322 | 14545 | 4284 | 6630 | 2571 | 336 | 588 | 14409 | 0 | 0 | 0 | 0 | 0 | 0 | 4178 | 6111 | 3001 | 644 | 613 | 14547 | 0 | 0 | 0 | 0 | 0 | 0 | 3436 | 5557 | 3195 | 1197 | 1161 | 14546 |  |  | C2 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C2 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | 20960.82 | C2 | 25.1111 | 25.1111 | 43.4099 | 85.5621 | 241.0494 | C2 | 107575.7912 | 166486.3434 | 111606.7455 | 28748.8546 | 141737.0648 | 556154.7995 |  | 121110.6538 | 163372.5717 | 111129.237 | 28577.7305 | 77617.9165 | 501808.1094 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 104914.0185 | 153453.7021 | 130272.9845 | 55101.9713 | 147763.3006 | 591505.977 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635 |  | 86281.6103 | 139542.1735 | 138694.497 | 102417.7945 | 279858.3882 | 746794.4635
|  |  | 2292 | 2292 | C3 | 760 | 1025 | 403 | 53 | 51 | 2292 | 675 | 1044 | 405 | 53 | 93 | 2270 | 0 | 0 | 0 | 0 | 0 | 0 | 658 | 962 | 473 | 101 | 96 | 2290 | 0 | 0 | 0 | 0 | 0 | 0 | 541 | 875 | 503 | 189 | 183 | 2291 |  |  | C3 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C3 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | 31441.23 | C3 | 37.6666 | 37.6666 | 65.1148 | 128.3431 | 361.5741 | C3 | 25424.9506 | 39323.9237 | 26371.4889 | 6802.1843 | 33626.3955 | 131548.943 |  | 28626.6111 | 38608.2584 | 26241.2593 | 6802.1843 | 18440.2814 | 118718.5945 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 24784.6185 | 36235.263 | 30799.2944 | 12962.6532 | 34711.1179 | 139492.947 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491 |  | 20377.6271 | 32958.2693 | 32752.738 | 24256.8461 | 66168.0685 | 176513.5491
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115 | C4 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | 52402.05 | C4 | 62.7777 | 62.7777 | 108.5246 | 213.9052 | 602.6236 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 16837 | 16837 |  | 5583 | 7531 | 2963 | 387 | 373 |  | 4959 | 7674 | 2976 | 389 | 681 |  | 0 | 0 | 0 | 0 | 0 |  | 4836 | 7073 | 3474 | 745 | 709 |  | 0 | 0 | 0 | 0 | 0 |  | 3977 | 6432 | 3698 | 1386 | 1344 | [22 empty] | 133000.7418 | 205810.2671 | 137978.2344 | 35551.0389 | 175363.4603 | 687703.7425 |  | 149737.2649 | 201980.8301 | 137370.4963 | 35379.9148 | 96058.1979 | 620526.7039 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 129698.6371 | 189688.9651 | 161072.2789 | 68064.6245 | 182474.4185 | 730998.9241 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126 |  | 106659.2374 | 172500.4429 | 171447.235 | 126674.6405 | 346026.4568 | 923308.0126
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 3628 | 3628 | C1 | 204 | 1790 | 1305 | 281 | 48 | 3628 | 44 | 1814 | 1321 | 320 | 128 | 3627 | 0 | 0 | 0 | 0 | 0 | 0 | 192 | 1677 | 1326 | 316 | 117 | 3628 | 0 | 0 | 0 | 0 | 0 | 0 | 185 | 1663 | 1340 | 304 | 137 | 3629 |  |  | C1 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C1 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | 12164.6 | C1 | 27.1392 | 27.1879 | 46.931 | 91.5265 | 143.007 | C1 | 1194.1258 | 49318.8161 | 61995.8864 | 29288.4641 | 18304.9008 | 160102.1933 |  | 5536.4014 | 48666.307 | 61244.99 | 25718.9326 | 6864.3378 | 148030.9687 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5210.7307 | 45594.0764 | 62230.5415 | 28922.3583 | 16731.8234 | 158689.5304 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833 |  | 5020.7562 | 45213.4461 | 62887.5759 | 27824.0409 | 19591.9642 | 160537.7833
|  |  | 75099 | 75099 | C2 | 4224 | 37056 | 27000 | 5822 | 997 | 75099 | 902 | 37540 | 27350 | 6618 | 2653 | 75063 | 0 | 0 | 0 | 0 | 0 | 0 | 3970 | 34721 | 27449 | 6541 | 2419 | 75100 | 0 | 0 | 0 | 0 | 0 | 0 | 3829 | 34431 | 27726 | 6284 | 2830 | 75100 |  |  | C2 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C2 | 17378 | 17378 | 17378 | 17378 | 17378 | C2 | 38.7703 | 38.8398 | 67.0443 | 130.7521 | 204.2958 | C2 | 34970.8268 | 1458047.2182 | 1833662.2614 | 865317.2125 | 541996.6725 | 4733994.1914 |  | 163765.8232 | 1439248.7405 | 1810196.748 | 761238.5632 | 203682.8807 | 4378132.7556 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 153918.1625 | 1348557.7374 | 1840299.6495 | 855249.303 | 494191.4628 | 4692216.3151 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055 |  | 148451.5476 | 1337294.1867 | 1858870.9272 | 821646.0204 | 578157.0234 | 4744419.7055
|  |  | 20166 | 20166 | C3 | 1134 | 9950 | 7251 | 1563 | 268 | 20166 | 242 | 10080 | 7344 | 1777 | 712 | 20155 | 0 | 0 | 0 | 0 | 0 | 0 | 1066 | 9323 | 7371 | 1757 | 649 | 20166 | 0 | 0 | 0 | 0 | 0 | 0 | 1028 | 9245 | 7445 | 1687 | 760 | 20165 |  |  | C3 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C3 | 26067 | 26067 | 26067 | 26067 | 26067 | C3 | 58.1555 | 58.2597 | 100.5665 | 196.1281 | 306.4437 | C3 | 14073.6254 | 587258.2296 | 738560.2732 | 348519.6479 | 218187.8802 | 1906599.6564 |  | 65948.3109 | 579684.4628 | 729207.59 | 306548.2328 | 82126.8987 | 1763515.4952 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 61993.7385 | 543155.6026 | 741275.5683 | 344597.0858 | 198881.9301 | 1889903.9253 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549 |  | 59783.8304 | 538611.3425 | 748717.4883 | 330868.1182 | 232897.1755 | 1910877.9549
|  |  | 77 | 77 | C4 | 4 | 38 | 28 | 6 | 1 | 77 | 1 | 38 | 28 | 7 | 3 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 28 | 7 | 2 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 35 | 28 | 6 | 3 | 76 |  |  | C4 | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756 | C4 | 43445 | 43445 | 43445 | 43445 | 43445 | C4 | 96.9258 | 97.0996 | 167.6108 | 326.8802 | 510.7394 | C4 | 96.9258 | 3689.7839 | 4693.1027 | 2288.1613 | 1532.2183 | 12300.1918 |  | 387.7032 | 3689.7839 | 4693.1027 | 1961.2811 | 510.7394 | 11242.6102 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 387.7032 | 3398.4851 | 4693.1027 | 2288.1613 | 1021.4788 | 11788.9311 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903 |  | 387.7032 | 3398.4851 | 4693.1027 | 1961.2811 | 1532.2183 | 11972.7903
|  |  | 98970 | 98970 |  | 5566 | 48834 | 35584 | 7672 | 1314 |  | 1189 | 49472 | 36043 | 8722 | 3496 |  | 0 | 0 | 0 | 0 | 0 |  | 5232 | 45756 | 36174 | 8621 | 3187 |  | 0 | 0 | 0 | 0 | 0 |  | 5046 | 45374 | 36539 | 8281 | 3730 | [22 empty] | 50335.5039 | 2098314.0478 | 2638911.5237 | 1245413.4858 | 780021.6718 | 6812996.2329 |  | 235638.2387 | 2071289.2941 | 2605342.4306 | 1095467.0096 | 293184.8567 | 6300921.8297 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 221510.3349 | 1940705.9016 | 2648498.862 | 1231056.9083 | 710826.6952 | 6752598.702 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339 |  | 213643.8373 | 1924517.4605 | 2675169.0941 | 1182299.4606 | 832178.3814 | 6827808.2339
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 |  | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 |  | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 |  | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 |  | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 |  | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 937 | 937 | C1 | 215 | 458 | 214 | 23 | 27 | 937 | 174 | 460 | 214 | 24 | 45 | 917 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 319 | 345 | 45 | 41 | 934 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 231 | 377 | 75 | 83 | 936 |  |  | C1 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C1 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | 65522.5667 | C1 | 4.7176 | 61.4602 | 105.2948 | 208.0341 | 361.0949 | C1 | 820.8667 | 28271.6771 | 22533.0796 | 4992.8196 | 16249.2689 | 72867.7119 |  | 1014.2893 | 28148.7567 | 22533.0796 | 4784.7854 | 9749.5614 | 66230.4725 |  | 868.043 | 19605.7934 | 36326.6938 | 9361.5367 | 14804.8895 | 80966.9564 |  | 868.043 | 19605.7934 | 36326.6938 | 9361.5367 | 14804.8895 | 80966.9564 |  | 801.9962 | 14197.2987 | 39696.1263 | 15602.5612 | 29970.8738 | 100268.8562 |  | 801.9962 | 14197.2987 | 39696.1263 | 15602.5612 | 29970.8738 | 100268.8562
|  |  | 333 | 333 | C2 | 77 | 163 | 76 | 8 | 9 | 333 | 62 | 164 | 77 | 9 | 16 | 328 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 114 | 123 | 17 | 15 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 82 | 135 | 27 | 30 | 334 |  |  | C2 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C2 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | 93603.6667 | C2 | 6.7395 | 87.8002 | 150.4211 | 297.1916 | 515.8498 | C2 | 417.8468 | 14399.2393 | 11582.4241 | 2674.7248 | 8253.5969 | 37327.8318 |  | 518.9387 | 14311.439 | 11432.003 | 2377.5331 | 4642.6483 | 33282.5622 |  | 444.8046 | 10009.2273 | 18501.7944 | 5052.2579 | 7737.7471 | 41745.8313 |  | 444.8046 | 10009.2273 | 18501.7944 | 5052.2579 | 7737.7471 | 41745.8313 |  | 404.3678 | 7199.6196 | 20306.8475 | 8024.1743 | 15475.4942 | 51410.5035 |  | 404.3678 | 7199.6196 | 20306.8475 | 8024.1743 | 15475.4942 | 51410.5035
|  |  | 294 | 294 | C3 | 68 | 144 | 67 | 7 | 8 | 294 | 55 | 144 | 67 | 8 | 14 | 288 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 100 | 108 | 15 | 13 | 294 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 72 | 119 | 24 | 26 | 294 |  |  | C3 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C3 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | 140405.5 | C3 | 10.1092 | 131.7004 | 225.6316 | 445.7875 | 773.7747 | C3 | 556.0058 | 18964.8517 | 15117.3198 | 3566.2997 | 10832.8459 | 49037.3229 |  | 687.4253 | 18964.8517 | 15117.3198 | 3120.5122 | 6190.1977 | 44080.3067 |  | 586.3334 | 13170.0359 | 24368.217 | 6686.8119 | 10059.0712 | 54870.4694 |  | 586.3334 | 13170.0359 | 24368.217 | 6686.8119 | 10059.0712 | 54870.4694 |  | 535.7874 | 9482.4258 | 26850.165 | 10698.8991 | 20118.1425 | 67685.4198 |  | 535.7874 | 9482.4258 | 26850.165 | 10698.8991 | 20118.1425 | 67685.4198
|  |  | 217 | 217 | C4 | 50 | 106 | 50 | 5 | 6 | 217 | 40 | 107 | 50 | 6 | 10 | 213 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 74 | 80 | 11 | 10 | 218 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 53 | 88 | 18 | 19 | 217 |  |  | C4 | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511 | C4 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | 234009.1667 | C4 | 16.8487 | 219.5006 | 376.0527 | 742.9791 | 1289.6245 | C4 | 673.9464 | 23486.564 | 18802.6365 | 4457.8746 | 12896.2452 | 60317.2668 |  | 842.433 | 23267.0634 | 18802.6365 | 3714.8955 | 7737.7471 | 54364.7756 |  | 724.4924 | 16243.0443 | 30084.2185 | 8172.7701 | 12896.2452 | 68120.7704 |  | 724.4924 | 16243.0443 | 30084.2185 | 8172.7701 | 12896.2452 | 68120.7704 |  | 657.0977 | 11633.5317 | 33092.6403 | 13373.6239 | 24502.8658 | 83259.7595 |  | 657.0977 | 11633.5317 | 33092.6403 | 13373.6239 | 24502.8658 | 83259.7595
|  |  | 1781 | 1781 |  | 410 | 871 | 407 | 43 | 50 |  | 331 | 875 | 408 | 47 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 351 | 607 | 656 | 88 | 79 |  | 0 | 0 | 0 | 0 | 0 |  | 322 | 438 | 719 | 144 | 158 | [22 empty] | 2468.6657 | 85122.332 | 68035.4601 | 15691.7187 | 48231.957 | 219550.1334 |  | 3063.0864 | 84692.1109 | 67885.039 | 13997.7263 | 28320.1544 | 197958.1169 |  | 2623.6733 | 59028.1009 | 109280.9236 | 29273.3767 | 45497.953 | 245704.0275 |  | 2623.6733 | 59028.1009 | 109280.9236 | 29273.3767 | 45497.953 | 245704.0275 |  | 2399.2492 | 42512.8759 | 119945.779 | 47699.2585 | 90067.3763 | 302624.5389 |  | 2399.2492 | 42512.8759 | 119945.779 | 47699.2585 | 90067.3763 | 302624.5389
| EHV Transformer |  | 439 | 439 | C1 | 45 | 96 | 206 | 43 | 49 | 439 | 35 | 95 | 206 | 43 | 59 | 438 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 75 | 143 | 90 | 102 | 439 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 76 | 45 | 88 | 210 | 439 |  |  | C1 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C1 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | 222114.2 | C1 | 267.4477 | 270.1797 | 467.4393 | 909.7131 | 1679.1834 | C1 | 9360.6698 | 25667.0727 | 96292.5028 | 39117.6645 | 99071.8178 | 269509.7276 |  | 12035.1469 | 25937.2524 | 96292.5028 | 39117.6645 | 82279.9842 | 255662.5509 |  | 7755.9835 | 20263.4785 | 66843.8247 | 81874.1816 | 171276.7019 | 348014.1703 |  | 7755.9835 | 20263.4785 | 66843.8247 | 81874.1816 | 171276.7019 | 348014.1703 |  | 5348.9542 | 20533.6582 | 21034.77 | 80054.7553 | 352628.5039 | 479600.6416 |  | 5348.9542 | 20533.6582 | 21034.77 | 80054.7553 | 352628.5039 | 479600.6416
|  |  | 192 | 192 | C2 | 19 | 42 | 90 | 19 | 22 | 192 | 15 | 42 | 90 | 19 | 25 | 191 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 33 | 62 | 39 | 45 | 192 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 33 | 19 | 39 | 92 | 192 |  |  | C2 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C2 | 317306 | 317306 | 317306 | 317306 | 317306 | C2 | 382.0682 | 385.971 | 667.7705 | 1299.5902 | 2398.8334 | C2 | 5731.0223 | 16210.7828 | 60099.3429 | 24692.2135 | 59970.834 | 166704.1955 |  | 7259.2949 | 16210.7828 | 60099.3429 | 24692.2135 | 52774.3339 | 161035.9681 |  | 4966.886 | 12737.0436 | 41401.7696 | 50684.0172 | 107947.5012 | 217737.2176 |  | 4966.886 | 12737.0436 | 41401.7696 | 50684.0172 | 107947.5012 | 217737.2176 |  | 3438.6134 | 12737.0436 | 12687.6391 | 50684.0172 | 220692.6691 | 300239.9824 |  | 3438.6134 | 12737.0436 | 12687.6391 | 50684.0172 | 220692.6691 | 300239.9824
|  |  | 53 | 53 | C3 | 5 | 12 | 25 | 5 | 6 | 53 | 4 | 12 | 25 | 5 | 7 | 53 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 17 | 11 | 13 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 9 | 5 | 11 | 26 | 53 |  |  | C3 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C3 | 475959 | 475959 | 475959 | 475959 | 475959 | C3 | 573.1022 | 578.9565 | 1001.6557 | 1949.3853 | 3598.25 | C3 | 2292.4089 | 6947.4783 | 25041.3929 | 9746.9264 | 25187.7503 | 69215.9568 |  | 2865.5112 | 6947.4783 | 25041.3929 | 9746.9264 | 21589.5002 | 66190.809 |  | 2292.4089 | 5210.6087 | 17028.1472 | 21443.238 | 46777.2505 | 92751.6534 |  | 2292.4089 | 5210.6087 | 17028.1472 | 21443.238 | 46777.2505 | 92751.6534 |  | 1146.2045 | 5210.6087 | 5008.2786 | 21443.238 | 93554.501 | 126362.8309 |  | 1146.2045 | 5210.6087 | 5008.2786 | 21443.238 | 93554.501 | 126362.8309
|  |  | 36 | 36 | C4 | 4 | 8 | 17 | 3 | 4 | 36 | 3 | 8 | 17 | 3 | 5 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 12 | 7 | 8 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 6 | 4 | 7 | 17 | 36 |  |  | C4 | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756 | C4 | 793265 | 793265 | 793265 | 793265 | 793265 | C4 | 955.1704 | 964.9275 | 1669.4262 | 3248.9755 | 5997.0834 | C4 | 2865.5112 | 7719.4204 | 28380.2453 | 9746.9264 | 29985.417 | 78697.5202 |  | 3820.6815 | 7719.4204 | 28380.2453 | 9746.9264 | 23988.3336 | 73655.6072 |  | 1910.3408 | 5789.5653 | 20033.1143 | 22742.8282 | 47976.6672 | 98452.5158 |  | 1910.3408 | 5789.5653 | 20033.1143 | 22742.8282 | 47976.6672 | 98452.5158 |  | 1910.3408 | 5789.5653 | 6677.7048 | 22742.8282 | 101950.4178 | 139070.8568 |  | 1910.3408 | 5789.5653 | 6677.7048 | 22742.8282 | 101950.4178 | 139070.8568
|  |  | 720 | 720 |  | 73 | 158 | 338 | 70 | 81 |  | 57 | 157 | 338 | 70 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 48 | 123 | 234 | 147 | 168 |  | 0 | 0 | 0 | 0 | 0 |  | 33 | 124 | 73 | 145 | 345 | [22 empty] | 20249.6122 | 56544.7542 | 209813.4839 | 83303.7308 | 214215.819 | 584127.4001 |  | 25980.6345 | 56814.9339 | 209813.4839 | 83303.7308 | 180632.152 | 556544.9351 |  | 16925.6192 | 44000.6961 | 145306.8558 | 176744.2651 | 373978.1208 | 756955.557 |  | 16925.6192 | 44000.6961 | 145306.8558 | 176744.2651 | 373978.1208 | 756955.557 |  | 11844.1128 | 44270.8758 | 45408.3924 | 174924.8388 | 768826.0919 | 1045274.3117 |  | 11844.1128 | 44270.8758 | 45408.3924 | 174924.8388 | 768826.0919 | 1045274.3117
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | 87488.1 | C1 | 87.4881 | 87.4881 | 262.4643 | 612.4167 | 874.881 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 227.0678 | C2 | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 | 227.0678 | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 | 234.2399 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 | 227.0675 | 0 | 0 | 0 | 0 | 0 | 0 | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | 227.0675 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 124983 | 124983 | 124983 | 124983 | 124983 | C2 | 124.983 | 124.983 | 374.949 | 874.881 | 1249.83 | C2 | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | 187474.5 | C3 | 187.4745 | 187.4745 | 562.4235 | 1312.3215 | 1874.745 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | 312457.5 | C4 | 312.4575 | 312.4575 | 937.3725 | 2187.2025 | 3124.575 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 227.0678 | 227.0678 |  | 2.9791 | 33.92 | 35.102 | 93.8026 | 61.2642 |  | 2.9321 | 33.932 | 35.1378 | 100.9511 | 61.287 |  | 0 | 0 | 0 | 0 | 0 |  | 0.34134 | 26.886 | 37.7396 | 78.8553 | 83.2452 |  | 0 | 0 | 0 | 0 | 0 |  | 0.34134 | 12.8181 | 39.8921 | 25.7067 | 148.3093 | [22 empty] | 366.4596 | 4240.917 | 13174.8835 | 88320.213 | 76598.3384 | 182700.8115 |  | 372.3338 | 4239.4236 | 13161.4432 | 82066.0731 | 76569.8285 | 176409.1022 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 3360.2935 | 14150.4409 | 68988.987 | 104042.3694 | 190584.7524 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744 |  | 42.6616 | 1602.0444 | 14957.4999 | 22490.2788 | 185361.3897 | 224453.8744
| EHV UG Cable (Oil) |  | 17.0815 | 17.0815 | C1 | 1.6369 | 2.5218 | 2.8663 | 6.9395 | 3.1171 | 17.0815 | 1.63 | 2.5796 | 3.0569 | 8.8085 | 4.8454 | 20.9204 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090919 | 3.5395 | 2.8444 | 5.6227 | 5.0659 | 17.0815 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0090919 | 2.2753 | 3.4238 | 1.729 | 9.6443 | 17.0815 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | 194576.2 | C1 | 194.5762 | 194.5762 | 583.7286 | 1362.0334 | 1945.762 | C1 | 317.1507 | 501.9325 | 1784.4163 | 11997.4175 | 9428.0449 | 24028.9618 |  | 318.5082 | 490.6886 | 1673.1151 | 9451.7929 | 6065.0403 | 17999.1451 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 688.6955 | 1660.3527 | 7658.2653 | 9857.0146 | 19866.0972 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996 |  | 1.7691 | 442.7288 | 1998.557 | 2354.9604 | 18765.4844 | 23563.4996
|  |  | 246.8 | 246.8 | C2 | 23.651 | 36.4363 | 41.4126 | 100.2639 | 45.0362 | 246.8 | 23.5502 | 37.2712 | 44.1675 | 127.2676 | 70.0084 | 302.2649 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13136 | 51.1394 | 41.0967 | 81.2383 | 73.1937 | 246.7995 | 0 | 0 | 0 | 0 | 0 | 0 | 0.13136 | 32.875 | 49.4679 | 24.9812 | 139.3439 | 246.7995 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 277966 | 277966 | 277966 | 277966 | 277966 | C2 | 277.966 | 277.966 | 833.898 | 1945.762 | 2779.66 | C2 | 6546.1447 | 10360.1311 | 36831.2217 | 247632.544 | 194599.4408 | 495969.4824 |  | 6574.1645 | 10128.0511 | 34533.9105 | 195089.612 | 125185.3879 | 371511.126 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 14215.0116 | 34270.4888 | 158070.3273 | 203453.5862 | 410045.9284 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146 |  | 36.5144 | 9138.1382 | 41251.1898 | 48607.5295 | 387328.7427 | 486362.1146
|  |  | 29.9197 | 29.9197 | C3 | 2.8672 | 4.4172 | 5.0205 | 12.155 | 5.4598 | 29.9197 | 2.855 | 4.5184 | 5.3544 | 15.4287 | 8.4871 | 36.6437 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015925 | 6.1996 | 4.9822 | 9.8485 | 8.8733 | 29.9196 | 0 | 0 | 0 | 0 | 0 | 0 | 0.015925 | 3.9855 | 5.997 | 3.0285 | 16.8927 | 29.9196 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 416949 | 416949 | 416949 | 416949 | 416949 | C3 | 416.949 | 416.949 | 1250.847 | 2918.643 | 4169.49 | C3 | 1190.3873 | 1883.9438 | 6697.5938 | 45030.8766 | 35387.0427 | 90189.8443 |  | 1195.4826 | 1841.741 | 6279.838 | 35476.1782 | 22764.406 | 67557.6458 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 2584.9366 | 6231.936 | 28744.3859 | 36997.1297 | 74565.0282 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872 |  | 6.64 | 1661.7298 | 7501.3454 | 8839.063 | 70434.009 | 88442.7872
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 694915 | 694915 | 694915 | 694915 | 694915 | C4 | 694.915 | 694.915 | 2084.745 | 4864.405 | 6949.15 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 293.8012 | 293.8012 |  | 28.1551 | 43.3753 | 49.2994 | 119.3584 | 53.613 |  | 28.0351 | 44.3692 | 52.5789 | 151.5048 | 83.3409 |  | 0 | 0 | 0 | 0 | 0 |  | 0.15638 | 60.8785 | 48.9233 | 96.7095 | 87.1329 |  | 0 | 0 | 0 | 0 | 0 |  | 0.15638 | 39.1358 | 58.8887 | 29.7387 | 165.8809 | [22 empty] | 8053.6827 | 12746.0073 | 45313.2319 | 304660.8381 | 239414.5284 | 610188.2884 |  | 8088.1553 | 12460.4808 | 42486.8636 | 240017.583 | 154014.8342 | 457067.9168 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 17488.6438 | 42162.7775 | 194472.9785 | 250307.7305 | 504477.0538 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013 |  | 44.9234 | 11242.5968 | 50751.0921 | 59801.5529 | 476528.2361 | 598368.4013
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 693 | 693 | C1 | 26 | 441 | 68 | 24 | 134 | 693 | 26 | 395 | 94 | 40 | 140 | 695 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 261 | 208 | 52 | 171 | 692 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 170 | 162 | 127 | 233 | 692 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | 300227.2 | C1 | 3.0023 | 3.0023 | 6.0045 | 40.0303 | 150.4138 | C1 | 78.0591 | 1185.8974 | 564.4271 | 1601.2117 | 21057.9358 | 24487.5312 |  | 78.0591 | 1324.002 | 408.309 | 960.727 | 20155.4528 | 22926.5499 |  | 0 | 783.593 | 1248.9452 | 2081.5753 | 25720.7645 | 29834.8778 |  | 0 | 783.593 | 1248.9452 | 2081.5753 | 25720.7645 | 29834.8778 |  | 0 | 510.3862 | 972.7361 | 5083.8473 | 35046.4217 | 41613.3914 |  | 0 | 510.3862 | 972.7361 | 5083.8473 | 35046.4217 | 41613.3914
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 428896 | 428896 | 428896 | 428896 | 428896 | C2 | 4.289 | 4.289 | 8.5779 | 57.1861 | 214.8769 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6 | 6 | C3 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 4 | 1 | 0 | 1 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 2 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 2 | 7 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 643344 | 643344 | 643344 | 643344 | 643344 | C3 | 6.4334 | 6.4334 | 12.8669 | 85.7792 | 322.3153 | C3 | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 25.7338 | 12.8669 | 0 | 322.3153 | 360.916 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105 |  | 0 | 12.8669 | 25.7338 | 85.7792 | 644.6307 | 769.0105
|  |  | 231 | 231 | C4 | 8 | 147 | 23 | 8 | 45 | 231 | 8 | 131 | 31 | 13 | 46 | 229 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 87 | 69 | 18 | 57 | 231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 54 | 42 | 78 | 231 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 1072240 | 1072240 | 1072240 | 1072240 | 1072240 | C4 | 10.7224 | 10.7224 | 21.4448 | 142.9653 | 537.1922 | C4 | 85.7792 | 1404.6344 | 664.7888 | 1858.5493 | 24710.843 | 28724.5948 |  | 85.7792 | 1576.1928 | 493.2304 | 1143.7227 | 24173.6508 | 27472.5759 |  | 0 | 932.8488 | 1479.6912 | 2573.376 | 30619.9577 | 35605.8737 |  | 0 | 932.8488 | 1479.6912 | 2573.376 | 30619.9577 | 35605.8737 |  | 0 | 611.1768 | 1158.0192 | 6004.544 | 41900.9947 | 49674.7347 |  | 0 | 611.1768 | 1158.0192 | 6004.544 | 41900.9947 | 49674.7347
|  |  | 930 | 930 |  | 34 | 592 | 92 | 32 | 180 |  | 34 | 530 | 126 | 53 | 187 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 350 | 279 | 71 | 230 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 229 | 218 | 170 | 313 | [22 empty] | 163.8383 | 2616.2656 | 1242.0828 | 3459.7611 | 46091.0942 | 53573.0419 |  | 163.8383 | 2925.9285 | 914.4063 | 2104.4497 | 44651.419 | 50760.0418 |  | 0 | 1729.3087 | 2754.3701 | 4740.7305 | 56985.3528 | 66209.7621 |  | 0 | 1729.3087 | 2754.3701 | 4740.7305 | 56985.3528 | 66209.7621 |  | 0 | 1134.4299 | 2156.4891 | 11174.1705 | 77592.0471 | 92057.1366 |  | 0 | 1134.4299 | 2156.4891 | 11174.1705 | 77592.0471 | 92057.1366
| EHV OHL Support - Poles |  | 263 | 263 | C1 | 12 | 112 | 108 | 21 | 10 | 263 | 2 | 114 | 110 | 24 | 15 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 94 | 122 | 25 | 12 | 265 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 82 | 127 | 28 | 16 | 265 |  |  | C1 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C1 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | 82280.8 | C1 | 65.7424 | 66.812 | 113.6298 | 243.7157 | 330.7688 | C1 | 131.4847 | 7616.5691 | 12499.2763 | 5849.1775 | 4961.5322 | 31058.0399 |  | 788.9083 | 7482.9451 | 12272.0168 | 5118.0303 | 3307.6882 | 28969.5886 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 788.9083 | 6280.3289 | 13862.8337 | 6092.8932 | 3969.2258 | 30994.19 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173 |  | 788.9083 | 5478.5848 | 14430.9827 | 6824.0404 | 5292.3011 | 32814.8173
|  |  | 8940 | 8940 | C2 | 423 | 3799 | 3664 | 722 | 332 | 8940 | 52 | 3863 | 3736 | 805 | 507 | 8963 | 0 | 0 | 0 | 0 | 0 | 0 | 417 | 3167 | 4116 | 846 | 393 | 8939 | 0 | 0 | 0 | 0 | 0 | 0 | 413 | 2761 | 4281 | 959 | 525 | 8939 |  |  | C2 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C2 | 117544 | 117544 | 117544 | 117544 | 117544 | C2 | 93.9177 | 95.4457 | 162.3283 | 348.1653 | 472.5269 | C2 | 4883.7181 | 368706.8473 | 606458.3943 | 280273.089 | 239571.1282 | 1499893.1769 |  | 39727.1685 | 362598.3207 | 594770.7593 | 251375.3668 | 156878.9242 | 1405350.5394 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 39163.6626 | 302276.6206 | 668143.1346 | 294547.8675 | 185703.0638 | 1489834.3491 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067 |  | 38787.9919 | 263525.655 | 694927.2982 | 333890.5496 | 248076.612 | 1579208.1067
|  |  | 3324 | 3324 | C3 | 157 | 1412 | 1363 | 268 | 124 | 3324 | 19 | 1436 | 1389 | 300 | 188 | 3332 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 1178 | 1530 | 315 | 146 | 3324 | 0 | 0 | 0 | 0 | 0 | 0 | 154 | 1027 | 1591 | 357 | 195 | 3324 |  |  | C3 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C3 | 176316 | 176316 | 176316 | 176316 | 176316 | C3 | 140.8765 | 143.1686 | 243.4924 | 522.248 | 708.7903 | C3 | 2676.6532 | 205590.0981 | 338210.938 | 156674.3976 | 133252.5802 | 836404.6671 |  | 22117.608 | 202154.0519 | 331880.1357 | 139962.4619 | 87889.9997 | 784004.2572 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 21835.855 | 168652.6014 | 372543.3659 | 164508.1175 | 103483.3867 | 831023.3265 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701 |  | 21694.9785 | 147034.144 | 387396.402 | 186442.5331 | 138214.1124 | 880782.1701
|  |  | 7 | 7 | C4 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 3 | 3 | 1 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 1 | 0 | 6 |  |  | C4 | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402 | C4 | 293860 | 293860 | 293860 | 293860 | 293860 | C4 | 234.7941 | 238.6143 | 405.8207 | 870.4133 | 1181.3172 | C4 | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 715.843 | 1217.462 | 870.4133 | 0 | 2803.7183 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039 |  | 0 | 477.2286 | 1217.462 | 870.4133 | 0 | 2565.1039
|  |  | 12534 | 12534 |  | 592 | 5326 | 5138 | 1012 | 466 |  | 73 | 5416 | 5238 | 1130 | 710 |  | 0 | 0 | 0 | 0 | 0 |  | 584 | 4441 | 5771 | 1187 | 551 |  | 0 | 0 | 0 | 0 | 0 |  | 579 | 3872 | 6002 | 1345 | 736 | [22 empty] | 7691.856 | 582629.3574 | 958386.0707 | 443667.0775 | 377785.2406 | 2370159.6021 |  | 62633.6848 | 572951.1606 | 940140.3738 | 397326.2723 | 248076.612 | 2221128.1035 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 61788.4259 | 477686.7795 | 1055766.7962 | 466019.2915 | 293155.6764 | 2354416.9695 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198 |  | 61271.8788 | 416515.6124 | 1097972.1449 | 528027.5364 | 391583.0255 | 2495370.198
| EHV OHL Fittings and Conductors (Tower Lines) |  | 264.3928 | 264.3928 | C1 | 60.0911 | 197.1135 | 4.2075 | 0.74518 | 2.2355 | 264.3928 | 0 | 235.0812 | 14.1584 | 0.74518 | 2.2355 | 252.2203 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0911 | 168.7967 | 25.0724 | 4.4711 | 5.9614 | 264.3928 | 0 | 0 | 0 | 0 | 0 | 0 | 60.0911 | 147.1866 | 18.3658 | 18.6294 | 20.1198 | 264.3928 |  |  | C1 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C1 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | 159828.2 | C1 | 1.5983 | 36.9203 | 128.5019 | 559.3987 | 1552.0917 | C1 | 0 | 8679.2717 | 1819.3778 | 416.8514 | 3469.7521 | 14385.253 |  | 96.0426 | 7277.491 | 540.6664 | 416.8514 | 3469.7521 | 11800.8035 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 96.0426 | 6232.0277 | 3221.8547 | 2501.1085 | 9252.6723 | 21303.7057 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151 |  | 96.0426 | 5434.1741 | 2360.0442 | 10421.2854 | 31227.7689 | 49539.3151
|  |  | 0.36021 | 0.36021 | C2 | 0.081868 | 0.26855 | 0.0057322 | 0.0010152 | 0.0030457 | 0.36021 | 0 | 0.32027 | 0.019289 | 0.0010152 | 0.0030457 | 0.34362 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081868 | 0.22997 | 0.034159 | 0.0060914 | 0.0081218 | 0.36021 | 0 | 0 | 0 | 0 | 0 | 0 | 0.081868 | 0.20053 | 0.025022 | 0.025381 | 0.027411 | 0.36021 |  |  | C2 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C2 | 228326 | 228326 | 228326 | 228326 | 228326 | C2 | 2.2833 | 52.7433 | 183.5741 | 799.141 | 2217.2738 | C2 | 0 | 16.8923 | 3.541 | 0.81131 | 6.7531 | 27.9978 |  | 0.18693 | 14.1641 | 1.0523 | 0.81131 | 6.7531 | 22.9677 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.18693 | 12.1293 | 6.2706 | 4.8679 | 18.0083 | 41.463 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175 |  | 0.18693 | 10.5764 | 4.5933 | 20.2828 | 60.7781 | 96.4175
|  |  | 2.1612 | 2.1612 | C3 | 0.49121 | 1.6113 | 0.034393 | 0.0060914 | 0.018274 | 2.1612 | 0 | 1.9216 | 0.11574 | 0.0060914 | 0.018274 | 2.0617 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49121 | 1.3798 | 0.20495 | 0.036548 | 0.048731 | 2.1612 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49121 | 1.2032 | 0.15013 | 0.15228 | 0.16447 | 2.1612 |  |  | C3 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C3 | 342489 | 342489 | 342489 | 342489 | 342489 | C3 | 3.4249 | 79.115 | 275.3612 | 1198.7115 | 3325.9107 | C3 | 0 | 152.0308 | 31.8692 | 7.3018 | 60.7781 | 251.9799 |  | 1.6823 | 127.4765 | 9.4706 | 7.3018 | 60.7781 | 206.7093 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.6823 | 109.1636 | 56.4358 | 43.8108 | 162.0748 | 373.1673 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576 |  | 1.6823 | 95.1879 | 41.3398 | 182.5449 | 547.0026 | 867.7576
|  |  | 87.8908 | 87.8908 | C4 | 19.9758 | 65.5255 | 1.3987 | 0.24772 | 0.74315 | 87.8908 | 0 | 78.1469 | 4.7066 | 0.24772 | 0.74315 | 83.8443 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9758 | 56.1123 | 8.3347 | 1.4863 | 1.9817 | 87.8908 | 0 | 0 | 0 | 0 | 0 | 0 | 19.9758 | 48.9285 | 6.1053 | 6.1929 | 6.6883 | 87.8908 |  |  | C4 | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711 | C4 | 570815 | 570815 | 570815 | 570815 | 570815 | C4 | 5.7082 | 131.8583 | 458.9353 | 1997.8525 | 5543.1845 | C4 | 0 | 10304.3124 | 2160.0242 | 494.8995 | 4119.4021 | 17078.6382 |  | 114.0248 | 8640.0731 | 641.8966 | 494.8995 | 4119.4021 | 14010.2961 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 114.0248 | 7398.8651 | 3825.0902 | 2969.397 | 10985.0722 | 25292.4494 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793 |  | 114.0248 | 6451.6275 | 2801.9209 | 12372.4876 | 37074.6185 | 58814.6793
|  |  | 354.805 | 354.805 |  | 80.64 | 264.5188 | 5.6462 | 1 | 3 |  | 0 | 315.47 | 19 | 1 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 80.64 | 226.5188 | 33.6462 | 6 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 80.64 | 197.5188 | 24.6462 | 25 | 27 | [22 empty] | 0 | 19152.5073 | 4014.8122 | 919.864 | 7656.6853 | 31743.8689 |  | 211.9367 | 16059.2047 | 1193.0859 | 919.864 | 7656.6853 | 26040.7766 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 211.9367 | 13752.1857 | 7109.6513 | 5519.1842 | 20417.8276 | 47010.7854 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694 |  | 211.9367 | 11991.5659 | 5207.8982 | 22996.6007 | 68910.168 | 109318.1694
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 |  | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 |  | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 |  | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 |  | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 |  | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 77 | 77 | C1 | 43 | 16 | 2 | 2 | 14 | 77 | 40 | 16 | 2 | 2 | 15 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 20 | 4 | 4 | 16 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 23 | 4 | 5 | 16 | 77 |  |  | C1 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C1 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | 577357.55 | C1 | 1145.2464 | 1145.2464 | 2032.8759 | 3954.8992 | 7511.4217 | C1 | 45809.8574 | 18323.943 | 4065.7519 | 7909.7984 | 112671.3259 | 188780.6766 |  | 49245.5968 | 18323.943 | 4065.7519 | 7909.7984 | 105159.9042 | 184704.9942 |  | 36647.886 | 22904.9287 | 8131.5037 | 15819.5969 | 120182.7476 | 203686.6629 |  | 36647.886 | 22904.9287 | 8131.5037 | 15819.5969 | 120182.7476 | 203686.6629 |  | 33212.1466 | 26340.668 | 8131.5037 | 19774.4961 | 120182.7476 | 207641.5621 |  | 33212.1466 | 26340.668 | 8131.5037 | 19774.4961 | 120182.7476 | 207641.5621
|  |  | 27 | 27 | C2 | 15 | 6 | 1 | 0 | 5 | 27 | 14 | 6 | 1 | 0 | 5 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 7 | 1 | 2 | 6 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 2 | 2 | 6 | 28 |  |  | C2 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C2 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | 824796.5 | C2 | 1636.0663 | 1636.0663 | 2904.1085 | 5649.856 | 10730.6025 | C2 | 22904.9287 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 89278.4475 |  | 24540.9951 | 9816.398 | 2904.1085 | 0 | 53653.0123 | 90914.5139 |  | 19632.796 | 11452.4644 | 2904.1085 | 11299.7121 | 64383.6148 | 109672.6957 |  | 19632.796 | 11452.4644 | 2904.1085 | 11299.7121 | 64383.6148 | 109672.6957 |  | 16360.6634 | 13088.5307 | 5808.217 | 11299.7121 | 64383.6148 | 110940.7379 |  | 16360.6634 | 13088.5307 | 5808.217 | 11299.7121 | 64383.6148 | 110940.7379
|  |  | 90 | 90 | C3 | 50 | 21 | 3 | 1 | 15 | 90 | 46 | 18 | 3 | 1 | 17 | 85 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 23 | 5 | 5 | 19 | 90 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 27 | 5 | 5 | 19 | 89 |  |  | C3 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C3 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | 1237194.75 | C3 | 2454.0995 | 2454.0995 | 4356.1627 | 8474.784 | 16095.9037 | C3 | 112888.5773 | 44173.7911 | 13068.4881 | 8474.784 | 273630.3629 | 452236.0034 |  | 122704.9753 | 51536.0896 | 13068.4881 | 8474.784 | 241438.5555 | 437222.8926 |  | 93255.7812 | 56444.2886 | 21780.8136 | 42373.9202 | 305822.1703 | 519676.9739 |  | 93255.7812 | 56444.2886 | 21780.8136 | 42373.9202 | 305822.1703 | 519676.9739 |  | 80985.2837 | 66260.6867 | 21780.8136 | 42373.9202 | 305822.1703 | 517222.8744 |  | 80985.2837 | 66260.6867 | 21780.8136 | 42373.9202 | 305822.1703 | 517222.8744
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301 | C4 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | 2061991.25 | C4 | 4090.1658 | 4090.1658 | 7260.2712 | 14124.6401 | 26826.5062 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 194 | 194 |  | 108 | 43 | 6 | 3 | 34 |  | 100 | 40 | 6 | 3 | 37 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 50 | 10 | 11 | 41 |  | 0 | 0 | 0 | 0 | 0 |  | 72 | 58 | 11 | 12 | 41 | [22 empty] | 181603.3635 | 72314.1321 | 20038.3485 | 16384.5825 | 439954.7011 | 730295.1276 |  | 196491.5671 | 79676.4306 | 20038.3485 | 16384.5825 | 400251.4719 | 712842.4007 |  | 149536.4632 | 90801.6817 | 32816.4258 | 69493.2291 | 490388.5327 | 833036.3325 |  | 149536.4632 | 90801.6817 | 32816.4258 | 69493.2291 | 490388.5327 | 833036.3325 |  | 130558.0937 | 105689.8854 | 35720.5343 | 73448.1283 | 490388.5327 | 835805.1744 |  | 130558.0937 | 105689.8854 | 35720.5343 | 73448.1283 | 490388.5327 | 835805.1744
| 132kV Transformer |  | 59 | 59 | C1 | 12 | 19 | 15 | 7 | 6 | 59 | 5 | 19 | 15 | 7 | 11 | 57 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 16 | 16 | 7 | 60 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 10 | 6 | 17 | 17 | 61 |  |  | C1 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C1 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | 601010.9 | C1 | 1418.2655 | 1418.2655 | 2428.685 | 4604.9455 | 10096.9831 | C1 | 7091.3276 | 26947.0449 | 36430.2757 | 32234.6186 | 111066.8143 | 213770.0812 |  | 17019.1863 | 26947.0449 | 36430.2757 | 32234.6186 | 60581.8987 | 173213.0242 |  | 15600.9207 | 14182.6552 | 38858.9608 | 73679.1283 | 70678.8818 | 213000.5468 |  | 15600.9207 | 14182.6552 | 38858.9608 | 73679.1283 | 70678.8818 | 213000.5468 |  | 15600.9207 | 14182.6552 | 14572.1103 | 78284.0738 | 171648.713 | 294288.473 |  | 15600.9207 | 14182.6552 | 14572.1103 | 78284.0738 | 171648.713 | 294288.473
|  |  | 51 | 51 | C2 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C2 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C2 | 858587 | 858587 | 858587 | 858587 | 858587 | C2 | 2026.0936 | 2026.0936 | 3469.5501 | 6578.4936 | 14424.2616 | C2 | 10130.468 | 30391.404 | 48573.7009 | 39470.9616 | 144242.616 | 272809.1506 |  | 20260.936 | 34443.5912 | 48573.7009 | 39470.9616 | 57697.0464 | 200446.2362 |  | 20260.936 | 18234.8424 | 45104.1509 | 85520.4167 | 72121.308 | 241241.654 |  | 20260.936 | 18234.8424 | 45104.1509 | 85520.4167 | 72121.308 | 241241.654 |  | 18234.8424 | 14182.6552 | 17347.7503 | 92098.9103 | 216363.924 | 358228.0823 |  | 18234.8424 | 14182.6552 | 17347.7503 | 92098.9103 | 216363.924 | 358228.0823
|  |  | 51 | 51 | C3 | 10 | 17 | 14 | 6 | 4 | 51 | 5 | 15 | 14 | 6 | 10 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 9 | 13 | 13 | 5 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 7 | 5 | 14 | 15 | 50 |  |  | C3 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C3 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | 1287880.5 | C3 | 3039.1404 | 3039.1404 | 5204.3251 | 9867.7404 | 21636.3924 | C3 | 15195.702 | 45587.1061 | 72860.5514 | 59206.4423 | 216363.924 | 409213.7258 |  | 30391.404 | 51665.3869 | 72860.5514 | 59206.4423 | 86545.5696 | 300669.3543 |  | 30391.404 | 27352.2636 | 67656.2263 | 128280.6251 | 108181.962 | 361862.4811 |  | 30391.404 | 27352.2636 | 67656.2263 | 128280.6251 | 108181.962 | 361862.4811 |  | 27352.2636 | 21273.9828 | 26021.6255 | 138148.3655 | 324545.886 | 537342.1234 |  | 27352.2636 | 21273.9828 | 26021.6255 | 138148.3655 | 324545.886 | 537342.1234
|  |  | 3 | 3 | C4 | 1 | 1 | 1 | 0 | 0 | 3 | 0 | 1 | 1 | 0 | 1 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 3 |  |  | C4 | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168 | C4 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | 2146467.5 | C4 | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 36060.654 | C4 | 0 | 5065.234 | 8673.8752 | 0 | 36060.654 | 49799.7632 |  | 5065.234 | 5065.234 | 8673.8752 | 0 | 0 | 18804.3432 |  | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 0 | 35250.5772 |  | 5065.234 | 5065.234 | 8673.8752 | 16446.234 | 0 | 35250.5772 |  | 5065.234 | 0 | 0 | 16446.234 | 36060.654 | 57572.122 |  | 5065.234 | 0 | 0 | 16446.234 | 36060.654 | 57572.122
|  |  | 164 | 164 |  | 33 | 54 | 44 | 19 | 14 |  | 15 | 50 | 44 | 19 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 29 | 43 | 43 | 17 |  | 0 | 0 | 0 | 0 | 0 |  | 30 | 24 | 16 | 46 | 48 | [22 empty] | 32417.4976 | 107990.789 | 166538.4032 | 130912.0225 | 507734.0083 | 945592.7207 |  | 72736.7603 | 118121.257 | 166538.4032 | 130912.0225 | 204824.5147 | 693132.9578 |  | 71318.4948 | 64834.9953 | 160293.2131 | 303926.404 | 250982.1518 | 851355.2591 |  | 71318.4948 | 64834.9953 | 160293.2131 | 303926.404 | 250982.1518 | 851355.2591 |  | 66253.2608 | 49639.2933 | 57941.4861 | 324977.5835 | 748619.177 | 1247430.8008 |  | 66253.2608 | 49639.2933 | 57941.4861 | 324977.5835 | 748619.177 | 1247430.8008
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 10.9182 | 10.9182 | C1 | 0.069593 | 1.7577 | 3.5512 | 5.0591 | 0.48064 | 10.9182 | 0.068227 | 1.758 | 3.5519 | 5.1278 | 0.48064 | 10.9865 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009295 | 0.86512 | 2.3839 | 5.9513 | 1.717 | 10.9182 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0009295 | 0.035179 | 2.2525 | 4.4407 | 4.1888 | 10.9182 |  |  | C1 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C1 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | 89184.9 | C1 | 89.1849 | 89.1849 | 267.5547 | 624.2943 | 891.849 | C1 | 6.0848 | 156.7859 | 950.3179 | 3201.2465 | 428.6599 | 4743.0951 |  | 6.2066 | 156.7643 | 950.1285 | 3158.3535 | 428.6599 | 4700.1129 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 77.1561 | 637.8191 | 3715.3785 | 1531.2611 | 5961.6977 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239 |  | 0.082898 | 3.1375 | 602.679 | 2772.3266 | 3735.7979 | 7114.0239
|  |  | 116.779 | 116.779 | C2 | 0.74435 | 18.8005 | 37.9824 | 54.1109 | 5.1408 | 116.779 | 0.72974 | 18.8031 | 37.99 | 54.8457 | 5.1408 | 117.5094 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099418 | 9.2532 | 25.4975 | 63.6541 | 18.3642 | 116.779 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0099418 | 0.37627 | 24.0928 | 47.4972 | 44.8028 | 116.779 |  |  | C2 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C2 | 127407 | 127407 | 127407 | 127407 | 127407 | C2 | 127.407 | 127.407 | 382.221 | 891.849 | 1274.07 | C2 | 92.974 | 2395.6419 | 14520.5776 | 48914.1022 | 6549.7974 | 72473.0931 |  | 94.8352 | 2395.3128 | 14517.6837 | 48258.709 | 6549.7974 | 71816.3381 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 1178.9218 | 9745.6884 | 56769.887 | 23397.2175 | 91092.9814 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186 |  | 1.2667 | 47.9394 | 9208.7573 | 42360.3327 | 57081.89 | 108700.186
|  |  | 31.9588 | 31.9588 | C3 | 0.2037 | 5.1451 | 10.3946 | 14.8085 | 1.4069 | 31.9588 | 0.19971 | 5.1458 | 10.3967 | 15.0096 | 1.4069 | 32.1587 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027208 | 2.5323 | 6.9779 | 17.4202 | 5.0257 | 31.9588 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0027208 | 0.10297 | 6.5934 | 12.9985 | 12.2611 | 31.9588 |  |  | C3 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C3 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | 191110.5 | C3 | 191.1105 | 191.1105 | 573.3315 | 1337.7735 | 1911.105 | C3 | 38.1661 | 983.4189 | 5960.7448 | 20079.3997 | 2688.7134 | 29750.4429 |  | 38.9302 | 983.2838 | 5959.5569 | 19810.3586 | 2688.7134 | 29480.8428 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 483.9513 | 4000.6371 | 23304.2252 | 9604.6347 | 37393.9682 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836 |  | 0.51997 | 19.6793 | 3780.2251 | 17389.0558 | 23432.3034 | 44621.7836
|  |  | 0.22406 | 0.22406 | C4 | 0.0014282 | 0.036072 | 0.072876 | 0.10382 | 0.0098637 | 0.22406 | 0.0014001 | 0.036077 | 0.072891 | 0.10523 | 0.0098637 | 0.22546 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9075e-05 | 0.017754 | 0.048922 | 0.12213 | 0.035235 | 0.22406 | 0 | 0 | 0 | 0 | 0 | 0 | 1.9075e-05 | 0.00072194 | 0.046226 | 0.091132 | 0.085962 | 0.22406 |  |  | C4 | 0.001 | 0.001 | 0.003 | 0.007 | 0.01 | C4 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | 318517.5 | C4 | 318.5175 | 318.5175 | 955.5525 | 2229.6225 | 3185.175 | C4 | 0.44597 | 11.4912 | 69.6511 | 234.627 | 31.4175 | 347.6328 |  | 0.4549 | 11.4896 | 69.6372 | 231.4833 | 31.4175 | 344.4825 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 5.655 | 46.7473 | 272.309 | 112.2298 | 436.9471 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038 |  | 0.0060758 | 0.22995 | 44.1718 | 203.1904 | 273.8055 | 521.4038
|  |  | 159.88 | 159.88 |  | 1.0191 | 25.7394 | 52.0011 | 74.0822 | 7.0382 |  | 0.99907 | 25.7429 | 52.0114 | 75.0883 | 7.0382 |  | 0 | 0 | 0 | 0 | 0 |  | 0.013611 | 12.6684 | 34.9082 | 87.1478 | 25.142 |  | 0 | 0 | 0 | 0 | 0 |  | 0.013611 | 0.51514 | 32.985 | 65.0276 | 61.3387 | [22 empty] | 137.6709 | 3547.3379 | 21501.2914 | 72429.3754 | 9698.5882 | 107314.2638 |  | 140.4269 | 3546.8505 | 21497.0062 | 71458.9044 | 9698.5882 | 106341.7763 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 1745.6842 | 14430.8919 | 84061.7996 | 34645.343 | 134885.5943 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973 |  | 1.8756 | 70.9861 | 13635.8333 | 62724.9055 | 84523.7969 | 160957.3973
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 104 | 104 | C1 | 4 | 74 | 6 | 14 | 6 | 104 | 2 | 55 | 19 | 18 | 10 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 32 | 46 | 8 | 15 | 104 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 13 | 48 | 17 | 22 | 103 |  |  | C1 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | 900258.1 | C1 | 9.0026 | 9.0026 | 18.0052 | 120.0344 | 451.0293 | C1 | 18.0052 | 495.142 | 342.0981 | 2160.6194 | 4510.2931 | 7526.1577 |  | 36.0103 | 666.191 | 108.031 | 1680.4818 | 2706.1758 | 5196.8899 |  | 27.0077 | 288.0826 | 828.2375 | 960.2753 | 6765.4396 | 8869.0427 |  | 27.0077 | 288.0826 | 828.2375 | 960.2753 | 6765.4396 | 8869.0427 |  | 27.0077 | 117.0336 | 864.2478 | 2040.585 | 9922.6448 | 12971.5189 |  | 27.0077 | 117.0336 | 864.2478 | 2040.585 | 9922.6448 | 12971.5189
|  |  | 2572 | 2572 | C2 | 102 | 1838 | 141 | 337 | 154 | 2572 | 43 | 1359 | 464 | 456 | 251 | 2573 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 796 | 1135 | 190 | 384 | 2573 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 327 | 1202 | 426 | 551 | 2574 |  |  | C2 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C2 | 1286083 | 1286083 | 1286083 | 1286083 | 1286083 | C2 | 12.8608 | 12.8608 | 25.7217 | 171.4777 | 644.3276 | C2 | 553.0157 | 17477.868 | 11934.8502 | 78193.8464 | 161726.2233 | 269885.8036 |  | 1311.8047 | 23638.2055 | 3626.7541 | 57787.9961 | 99226.4478 | 185591.2082 |  | 874.5364 | 10237.2207 | 29194.0841 | 32580.7693 | 247421.7919 | 320308.4024 |  | 874.5364 | 10237.2207 | 29194.0841 | 32580.7693 | 247421.7919 | 320308.4024 |  | 874.5364 | 4205.4914 | 30917.4353 | 73049.5144 | 355024.4982 | 464071.4758 |  | 874.5364 | 4205.4914 | 30917.4353 | 73049.5144 | 355024.4982 | 464071.4758
|  |  | 447 | 447 | C3 | 18 | 319 | 24 | 59 | 27 | 447 | 7 | 236 | 80 | 79 | 44 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 138 | 197 | 33 | 66 | 446 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 57 | 208 | 74 | 95 | 446 |  |  | C3 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C3 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | 1929124.5 | C3 | 19.2912 | 19.2912 | 38.5825 | 257.2166 | 966.4914 | C3 | 135.0387 | 4552.7338 | 3086.5992 | 20320.1114 | 42525.6205 | 70620.1036 |  | 347.2424 | 6153.9072 | 925.9798 | 15175.7794 | 26095.2671 | 48698.1758 |  | 231.4949 | 2662.1918 | 7600.7505 | 8488.1478 | 63788.4307 | 82771.0158 |  | 231.4949 | 2662.1918 | 7600.7505 | 8488.1478 | 63788.4307 | 82771.0158 |  | 231.4949 | 1099.601 | 8025.1579 | 19034.0284 | 91816.6806 | 120206.9628 |  | 231.4949 | 1099.601 | 8025.1579 | 19034.0284 | 91816.6806 | 120206.9628
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501 | C4 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | 3215207.5 | C4 | 32.1521 | 32.1521 | 64.3041 | 428.6943 | 1610.819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3123 | 3123 |  | 124 | 2231 | 171 | 410 | 187 |  | 52 | 1650 | 563 | 553 | 305 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 966 | 1378 | 231 | 465 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 397 | 1458 | 517 | 668 | [22 empty] | 706.0596 | 22525.7437 | 15363.5475 | 100674.5772 | 208762.1369 | 348032.065 |  | 1695.0574 | 30458.3037 | 4660.7648 | 74644.2573 | 128027.8907 | 239486.2739 |  | 1133.0391 | 13187.4951 | 37623.0721 | 42029.1924 | 317975.6622 | 411948.4609 |  | 1133.0391 | 13187.4951 | 37623.0721 | 42029.1924 | 317975.6622 | 411948.4609 |  | 1133.0391 | 5422.1259 | 39806.841 | 94124.1278 | 456763.8236 | 597249.9575 |  | 1133.0391 | 5422.1259 | 39806.841 | 94124.1278 | 456763.8236 | 597249.9575
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 52.7896 | 52.7896 | C1 | 2.6478 | 46.9644 | 1.6221 | 1.3898 | 0.16545 | 52.7896 | 1 | 47 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6478 | 40.975 | 5.8908 | 1.5884 | 1.6876 | 52.7896 | 0 | 0 | 0 | 0 | 0 | 0 | 2.6478 | 35.9122 | 4.6996 | 3.7062 | 5.824 | 52.7896 |  | 4.6996 | C1 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C1 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | 478069.2 | C1 | 4.7807 | 45.4166 | 384.3676 | 1185.1335 | 3214.107 | C1 | 4.7807 | 2134.579 | 1153.1029 | 1185.1335 | 0 | 4477.5961 |  | 12.6582 | 2132.9638 | 623.4996 | 1647.1082 | 531.7848 | 4948.0146 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 12.6582 | 1860.9453 | 2264.2482 | 1882.4093 | 5424.2045 | 11444.4656 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418 |  | 12.6582 | 1631.007 | 1806.3649 | 4392.2885 | 18718.8233 | 26561.1418
|  |  | 1314.4617 | 1314.4617 | C2 | 65.9298 | 1169.4145 | 40.3914 | 34.6062 | 4.1198 | 1314.4617 | 26 | 1178 | 70 | 35 | 7 | 1316 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9298 | 1020.2782 | 146.6819 | 39.55 | 42.0218 | 1314.4617 | 0 | 0 | 0 | 0 | 0 | 0 | 65.9298 | 894.2126 | 117.0194 | 92.2833 | 145.0165 | 1314.4617 |  |  | C2 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C2 | 682956 | 682956 | 682956 | 682956 | 682956 | C2 | 6.8296 | 64.8808 | 549.0966 | 1693.0479 | 4591.5815 | C2 | 177.5686 | 76429.606 | 38436.7637 | 59256.6773 | 32141.0704 | 206441.6859 |  | 450.2715 | 75872.571 | 22178.7704 | 58589.9907 | 18916.3433 | 176007.9469 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 450.2715 | 66196.4834 | 80542.5449 | 66959.9894 | 192946.7017 | 407095.9909 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601 |  | 450.2715 | 58017.2491 | 64254.9799 | 156239.9752 | 665855.2844 | 944817.7601
|  |  | 228.0512 | 228.0512 | C3 | 11.4384 | 202.8864 | 7.0077 | 6.004 | 0.71476 | 228.0512 | 5 | 204 | 12 | 6 | 1 | 228 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4384 | 177.0121 | 25.4484 | 6.8617 | 7.2905 | 228.0512 | 0 | 0 | 0 | 0 | 0 | 0 | 11.4384 | 155.1405 | 20.3022 | 16.0106 | 25.1595 | 228.0512 |  |  | C3 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C3 | 1024434 | 1024434 | 1024434 | 1024434 | 1024434 | C3 | 10.2443 | 97.3212 | 823.6449 | 2539.5719 | 6887.3722 | C3 | 51.2217 | 19853.5309 | 9883.7392 | 15237.4313 | 6887.3722 | 51913.2954 |  | 117.1791 | 19745.151 | 5771.8246 | 15247.5157 | 4922.8074 | 45804.4777 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 117.1791 | 17227.0366 | 20960.4695 | 17425.7322 | 50212.6356 | 105943.053 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845 |  | 117.1791 | 15098.4648 | 16721.7779 | 40660.0417 | 173282.821 | 245880.2845
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231 | C4 | 1707390 | 1707390 | 1707390 | 1707390 | 1707390 | C4 | 17.0739 | 162.2021 | 1372.7416 | 4232.6198 | 11478.9537 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1595.3025 | 1595.3025 |  | 80.016 | 1419.2653 | 49.0212 | 42 | 5 |  | 32 | 1429 | 85 | 42 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 80.016 | 1238.2653 | 178.0212 | 48 | 51 |  | 0 | 0 | 0 | 0 | 0 |  | 80.016 | 1085.2653 | 142.0212 | 112 | 176 | [22 empty] | 233.571 | 98417.7159 | 49473.6058 | 75679.2422 | 39028.4426 | 262832.5774 |  | 580.1088 | 97750.6859 | 28574.0945 | 75484.6145 | 24370.9355 | 226760.4392 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 580.1088 | 85284.4653 | 103767.2626 | 86268.1309 | 248583.5418 | 524483.5095 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865 |  | 580.1088 | 74746.7209 | 82783.1227 | 201292.3054 | 857856.9286 | 1217259.1865
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 |  | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 |  | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 |  | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 |  | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 |  | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 269066.8564 | 269066.8564 |  | 36234.8093 | 102297.8188 | 83782.0698 | 25268.2431 | 21483.9155 |  | 22042.9663 | 103434.5141 | 86548.7282 | 28258.5442 | 28483.6662 |  | 0 | 0 | 0 | 0 | 0 |  | 33932.1673 | 90891.2169 | 88029.2386 | 25016.7125 | 31197.5201 |  | 0 | 0 | 0 | 0 | 0 |  | 29163.1673 | 87383.2531 | 88101.4332 | 24816.473 | 39602.5289 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 |  | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 |  | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 |  | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 |  | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 |  | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 148790.9619 | 372470.4343 | 1012338.067 | 828979.0561 | 1983299.1064 | 4345877.6258 | LV Network | 267073.6774 | 362009.6006 | 965454.4668 | 740183.5139 | 1625678.8918 | 3960400.1504 | LV Network | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 | LV Network | 257702.488 | 290986.5968 | 1008001.4594 | 624753.6757 | 2084501.189 | 4265945.4089 | LV Network | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894 | LV Network | 219027.2054 | 281278.7207 | 1031741.3081 | 562971.2668 | 2448811.3884 | 4543829.8894
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 228207.1819 | 2904549.9802 | 3279692.1101 | 1727661.8671 | 2859133.4393 | 10999244.5786 | HV Network | 471564.4853 | 2864554.0419 | 3233290.5037 | 1556366.4489 | 2117233.8458 | 10243009.3256 | HV Network | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 | HV Network | 431250.7437 | 2695873.1504 | 3229263.74 | 1705079.9092 | 3364542.2332 | 11426009.7765 | HV Network | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938 | HV Network | 395507.7614 | 2620424.7992 | 3200339.3994 | 1665720.2037 | 4361259.7744 | 12243251.938
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 38994.1145 | 763052.1409 | 1299980.025 | 940023.2032 | 1009993.6628 | 4052043.1464 | EHV Network | 100513.6697 | 750143.2429 | 1275594.6956 | 819735.6993 | 739921.6854 | 3685908.9929 | EHV Network | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 | EHV Network | 81637.2401 | 617046.0082 | 1376531.8154 | 945758.8134 | 1144385.0305 | 4165358.9076 | EHV Network | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303 | EHV Network | 75814.7624 | 529270.0012 | 1336399.2956 | 867114.2365 | 2058868.3346 | 4867466.6303
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 215098.1625 | 304795.7186 | 272915.1965 | 396079.7998 | 1205177.8771 | 2394066.7545 | 132kV Network | 271643.9205 | 329553.5278 | 241308.6172 | 368884.3812 | 767173.4011 | 1978563.8479 | 132kV Network | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 | 132kV Network | 222569.9816 | 255854.3216 | 348930.8655 | 585778.7561 | 1342575.2315 | 2755709.1564 | 132kV Network | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163 | 132kV Network | 198526.3781 | 235569.0116 | 229887.8173 | 756567.0506 | 2638152.2588 | 4058702.5163
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 631090.4208 | 4344868.274 | 5864925.3986 | 3892743.9261 | 7057604.0856 | 21791232.1052 | Total | 1110795.7529 | 4306260.4131 | 5715648.2833 | 3485170.0433 | 5250007.8242 | 19867882.3168 | Total | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 | Total | 993160.4534 | 3859760.0769 | 5962727.8803 | 3861371.1544 | 7936003.6843 | 22613023.2493 | Total | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741 | Total | 888876.1073 | 3666542.5327 | 5798367.8204 | 3852372.7575 | 11507091.7561 | 25713250.9741
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## ENWL - Average Cons. of Failure
Secondary deliverables RIIO-ED1 - Average Consequence of Asset Failure
ENWL
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period |  |  |  |  | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure
| LV Network | [5 empty] | LV Network
| LV Switchgear and Other | 3024 | 2745.3333 | 1120 | 3280 | 10169.3333 | LV Switchgear and Other | 3024 | 2745.3333 | 1120 | 3280 | 10169.3333
| LV UGB | 3563.77 | 1996.61 | 1120 | 4460 | 11140.38 | LV UGB | 3563.77 | 1996.61 | 1120 | 4460 | 11140.38
| LV OHL Support | 3508 | 1120 | 1950 | 1200 | 7778 | LV OHL Support | 3508 | 1120 | 1950 | 1200 | 7778
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| HV Network | [5 empty] | HV Network
| HV Switchgear (GM) - Primary | 87236 | 3200 | 1443.75 | 29205 | 121084.75 | HV Switchgear (GM) - Primary | 87236 | 3200 | 1443.75 | 29205 | 121084.75
| HV Switchgear (GM) - Distribution | 21401.3333 | 3202.3333 | 1453.3333 | 6393 | 32450 | HV Switchgear (GM) - Distribution | 21401.3333 | 3202.3333 | 1453.3333 | 6393 | 32450
| HV Transformer (GM) | 7190.82 | 1120 | 3000 | 9650 | 20960.82 | HV Transformer (GM) | 7190.82 | 1120 | 3000 | 9650 | 20960.82
| HV UG Cable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | HV UG Cable | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
| HV OHL Support - Poles | 11058 | 1120 | 1950 | 3250 | 17378 | HV OHL Support - Poles | 11058 | 1120 | 1950 | 3250 | 17378
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| EHV Network | [5 empty] | EHV Network
| EHV Switchgear (GM) | 61123.8333 | 2054.5 | 1799.6667 | 28625.6667 | 93603.6667 | EHV Switchgear (GM) | 61123.8333 | 2054.5 | 1799.6667 | 28625.6667 | 93603.6667
| EHV Transformer | 266806 | 1120 | 5200 | 44180 | 317306 | EHV Transformer | 266806 | 1120 | 5200 | 44180 | 317306
| EHV UG Cable (Gas) | 110138 | 1470 | 1267 | 12108 | 124983 | EHV UG Cable (Gas) | 110138 | 1470 | 1267 | 12108 | 124983
| EHV UG Cable (Oil) | 166876 | 1050 | 59730 | 50310 | 277966 | EHV UG Cable (Oil) | 166876 | 1050 | 59730 | 50310 | 277966
| EHV UG Cable (Non Pressurised) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | EHV UG Cable (Non Pressurised) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
| EHV OHL Support - Towers | 409510 | 1122 | 6542 | 11722 | 428896 | EHV OHL Support - Towers | 409510 | 1122 | 6542 | 11722 | 428896
| EHV OHL Support - Poles | 110624 | 1120 | 2150 | 3650 | 117544 | EHV OHL Support - Poles | 110624 | 1120 | 2150 | 3650 | 117544
| EHV OHL Fittings and Conductors (Tower Lines) | 217194 | 1120 | 2114 | 7898 | 228326 | EHV OHL Fittings and Conductors (Tower Lines) | 217194 | 1120 | 2114 | 7898 | 228326
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| 132kV Network | [5 empty] | 132kV Network
| 132kV CBs | 767310 | 3842 | 8294.5 | 45350 | 824796.5 | 132kV CBs | 767310 | 3842 | 8294.5 | 45350 | 824796.5
| 132kV Transformer | 778857 | 16960 | 12150 | 50620 | 858587 | 132kV Transformer | 778857 | 16960 | 12150 | 50620 | 858587
| 132kV UG Cable (Gas) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | 132kV UG Cable (Gas) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
| 132kV UG Cable (Oil) | 41280 | 1050 | 59922 | 25155 | 127407 | 132kV UG Cable (Oil) | 41280 | 1050 | 59922 | 25155 | 127407
| 132kV UG Cable (Non Pressurised) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | 132kV UG Cable (Non Pressurised) | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
| 132kV OHL Support - Tower | 1266350 | 1122 | 6688 | 11923 | 1286083 | 132kV OHL Support - Tower | 1266350 | 1122 | 6688 | 11923 | 1286083
| 132kV OHL Fittings and Conductors (Tower Lines) | 671641 | 1120 | 2162 | 8033 | 682956 | 132kV OHL Fittings and Conductors (Tower Lines) | 671641 | 1120 | 2162 | 8033 | 682956
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
|  | 0 | 0 | 0 | 0 | 0
| Other | 0 | 0 | 0 | 0 | 0 | Other
| Submarine Cables | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable | Submarine Cables | Not applicable | Not applicable | Not applicable | Not applicable | Not applicable
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]

## ENWL - Probs. of Failure
Probabilities of Asset Failure
ENWL
Price base (2012/13)
Average Probabilities of Asset Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0.0019245 | 0.0019245 | 0.002488 | 0.002488 | 0.003433 | 0.003433 | 0.008835 | 0.008835 | 1 | LV Switchgear and Other | 0.001409 | 0.00244 | 0.002536 | 0.00433 | 0.01334
| LV UGB | 0 | 0.000749 | 0.000749 | 0.001023 | 0.001023 | 0.002012 | 0.002012 | 0.0044785 | 0.0044785 | 1 | LV UGB | 0.000749 | 0.000749 | 0.001297 | 0.002727 | 0.00623
| LV OHL Support | 0 | 0.002313 | 0.002313 | 0.0031495 | 0.0031495 | 0.0058515 | 0.0058515 | 0.0104 | 0.0104 | 1 | LV OHL Support | 0.002294 | 0.002332 | 0.003967 | 0.007736 | 0.013064
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear (at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB and LV Pillar OD (not at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | [10 empty] | HV Network
| HV Switchgear (GM) - Primary | 0 | 0.000505 | 0.000505 | 0.001291 | 0.001291 | 0.0024095 | 0.0024095 | 0.004343 | 0.004343 | 1 | HV Switchgear (GM) - Primary | 7.2e-05 | 0.000938 | 0.001644 | 0.003175 | 0.005511
| HV Switchgear (GM) - Distribution | 0 | 0.000849 | 0.000849 | 0.001159 | 0.001159 | 0.0021795 | 0.0021795 | 0.00412 | 0.00412 | 1 | HV Switchgear (GM) - Distribution | 0.000849 | 0.000849 | 0.001469 | 0.00289 | 0.00535
| HV Transformer (GM) | 0 | 0.001198 | 0.001198 | 0.0016345 | 0.0016345 | 0.0030765 | 0.0030765 | 0.007791 | 0.007791 | 1 | HV Transformer (GM) | 0.001198 | 0.001198 | 0.002071 | 0.004082 | 0.0115
| HV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV UG Cable | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles | 0 | 0.002233 | 0.002233 | 0.0030465 | 0.0030465 | 0.005691 | 0.005691 | 0.00964 | 0.00964 | 1 | HV OHL Support - Poles | 0.002231 | 0.002235 | 0.003858 | 0.007524 | 0.011756
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | [10 empty] | EHV Network
| EHV Switchgear (GM) | 0 | 0.000505 | 0.000505 | 0.0012725 | 0.0012725 | 0.002391 | 0.002391 | 0.004343 | 0.004343 | 1 | EHV Switchgear (GM) | 7.2e-05 | 0.000938 | 0.001607 | 0.003175 | 0.005511
| EHV Transformer | 0 | 0.0012102 | 0.0012102 | 0.0016604 | 0.0016604 | 0.0031001 | 0.0031001 | 0.0058278 | 0.0058278 | 1 | EHV Transformer | 0.0012041 | 0.0012164 | 0.0021045 | 0.0040957 | 0.00756
| EHV UG Cable (Gas) | 0 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.005 | 0.0085 | 0.0085 | 1 | EHV UG Cable (Gas) | 0.001 | 0.001 | 0.003 | 0.007 | 0.01
| EHV UG Cable (Oil) | 0 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.005 | 0.0085 | 0.0085 | 1 | EHV UG Cable (Oil) | 0.001 | 0.001 | 0.003 | 0.007 | 0.01
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers | 0 | 1e-05 | 1e-05 | 1.5e-05 | 1.5e-05 | 7.6667e-05 | 7.6667e-05 | 0.00031717 | 0.00031717 | 1 | EHV OHL Support - Towers | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501
| EHV OHL Support - Poles | 0 | 0.0008055 | 0.0008055 | 0.0010965 | 0.0010965 | 0.0021715 | 0.0021715 | 0.003491 | 0.003491 | 1 | EHV OHL Support - Poles | 0.000799 | 0.000812 | 0.001381 | 0.002962 | 0.00402
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0.0001205 | 0.0001205 | 0.0005175 | 0.0005175 | 0.002152 | 0.002152 | 0.0066055 | 0.0066055 | 1 | EHV OHL Fittings and Conductors (Tower Lines) | 1e-05 | 0.000231 | 0.000804 | 0.0035 | 0.009711
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | [10 empty] | 132kV Network
| 132kV CBs | 0 | 0.0019836 | 0.0019836 | 0.0027523 | 0.0027523 | 0.0051855 | 0.0051855 | 0.00993 | 0.00993 | 1 | 132kV CBs | 0.0019836 | 0.0019836 | 0.003521 | 0.00685 | 0.01301
| 132kV Transformer | 0 | 0.0023598 | 0.0023598 | 0.0032004 | 0.0032004 | 0.0058515 | 0.0058515 | 0.012231 | 0.012231 | 1 | 132kV Transformer | 0.0023598 | 0.0023598 | 0.004041 | 0.007662 | 0.0168
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) | 0 | 0.001 | 0.001 | 0.002 | 0.002 | 0.005 | 0.005 | 0.0085 | 0.0085 | 1 | 132kV UG Cable (Oil) | 0.001 | 0.001 | 0.003 | 0.007 | 0.01
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower | 0 | 1e-05 | 1e-05 | 1.5e-05 | 1.5e-05 | 7.6667e-05 | 7.6667e-05 | 0.00031717 | 0.00031717 | 1 | 132kV OHL Support - Tower | 1e-05 | 1e-05 | 2e-05 | 0.00013333 | 0.000501
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 5.25e-05 | 5.25e-05 | 0.0004495 | 0.0004495 | 0.0016415 | 0.0016415 | 0.004601 | 0.004601 | 1 | 132kV OHL Fittings and Conductors (Tower Lines) | 1e-05 | 9.5e-05 | 0.000804 | 0.002479 | 0.0067231
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Other | [10 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 3960400.1504 | 4265945.4089 | 3715734.3618 | 4543829.8894 | 3464799.6673
HV Network | 10243009.3256 | 11426009.7765 | 10403083.0492 | 12243251.938 | 10066767.3429
EHV Network | 3685908.9929 | 4165358.9076 | 3784401.3262 | 4867466.6303 | 4057315.8166
132kV Network | 1978563.8479 | 2755709.1564 | 2162576.5111 | 4058702.5163 | 2919623.8337
Other | 0 | 0 | 0 | 0 | 0
Total | 19867882.3168 | 22613023.2493 | 20065795.2482 | 25713250.9741 | 20508506.6605
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment
LV Network |  | 305545.2584 | -550211.047 | 583429.739 | -1079030.2222
HV Network |  | 1183000.4509 | -1022926.7273 | 2000242.6124 | -2176484.5951
EHV Network |  | 479449.9147 | -380957.5815 | 1181557.6374 | -810150.8137
132kV Network |  | 777145.3085 | -593132.6453 | 2080138.6685 | -1139078.6827
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 2745140.9325 | -2547228.0011 | 5845368.6572 | -5204744.3136