## SPN - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 1 | 1 | C1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | C1 | 8.3151 | 19.0395 | 58.9198 | 96.0302 | 154.2283 | C1 | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198
|  |  | 13779 | 13779 | C2 | 1531 | 1533 | 9111 | 1558 | 46 | 13779 | 1486 | 1347 | 9111 | 1558 | 91 | 13593 | 363 | 0 | 0 | -287 | -76 | 0 | 961 | 1371 | 9146 | 2111 | 190 | 13779 | 695 | 0 | 0 | -559 | -136 | 0 | 45 | 1480 | 8545 | 3378 | 331 | 13779 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10983 | 10983 | 10983 | 10983 | 10983 | C2 | 11.8787 | 27.1994 | 84.1712 | 137.186 | 220.3262 | C2 | 17651.8005 | 36637.5281 | 766883.8029 | 213735.7565 | 20049.6801 | 1054958.5681 |  | 18186.3436 | 41696.6077 | 766883.8029 | 213735.7565 | 10135.0031 | 1050637.5138 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 15727.4454 | 37290.3125 | 769829.7949 | 250227.2272 | 25117.1816 | 1098191.9616 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857 |  | 8790.2641 | 40255.042 | 719242.9037 | 386727.2771 | 42963.6001 | 1197979.0869
|  |  | 6600 | 6600 | C3 | 644 | 1451 | 3831 | 655 | 19 | 6600 | 590 | 1451 | 3831 | 655 | 73 | 6600 | 252 | 0 | 0 | -246 | -6 | 0 | 434 | 1445 | 3801 | 877 | 43 | 6600 | 503 | 0 | 0 | -479 | -24 | 0 | 54 | 1489 | 3551 | 1404 | 102 | 6600 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | C3 | 17.8181 | 40.799 | 126.2568 | 205.779 | 330.4892 | C3 | 10512.6807 | 59199.3911 | 483689.8006 | 134785.2252 | 24125.7139 | 712312.8115 |  | 11474.8582 | 59199.3911 | 483689.8006 | 134785.2252 | 6279.2954 | 695428.5705 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 12223.2185 | 58954.597 | 479902.0966 | 129846.5299 | 12228.1016 | 693154.5436 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035 |  | 9924.6833 | 60749.7542 | 448337.8966 | 190345.547 | 25778.1601 | 735136.0412
|  |  | 606 | 606 | C4 | 59 | 133 | 352 | 60 | 2 | 606 | 54 | 133 | 352 | 60 | 7 | 606 | 12 | 0 | 0 | -12 | 0 | 0 | 40 | 132 | 349 | 81 | 4 | 606 | 24 | 0 | 0 | -22 | -2 | 0 | 5 | 137 | 326 | 129 | 9 | 606 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | C4 | 29.6968 | 67.9984 | 210.428 | 342.9649 | 550.8154 | C4 | 1603.6293 | 9043.7848 | 74070.656 | 20577.897 | 3855.7077 | 109151.6747 |  | 1752.1134 | 9043.7848 | 74070.656 | 20577.897 | 1101.6308 | 106546.0819 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 1544.2356 | 8975.7864 | 73439.372 | 23664.5815 | 2203.2615 | 109827.237 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074 |  | 861.2083 | 9315.7783 | 68599.528 | 36697.2496 | 3855.7077 | 119329.4719
|  |  | 20986 | 20986 |  | 2234 | 3117 | 13295 | 2273 | 67 |  | 2130 | 2931 | 13295 | 2273 | 171 |  | 627 | 0 | 0 | -545 | -82 |  | 1435 | 2948 | 13297 | 3069 | 237 |  | 1222 | 0 | 0 | -1060 | -162 |  | 104 | 3106 | 12423 | 4911 | 442 | [22 empty] | 29768.1104 | 104880.704 | 1324703.1793 | 369098.8787 | 48031.1017 | 1876481.9741 |  | 31413.3153 | 109939.7836 | 1324703.1793 | 369098.8787 | 17515.9293 | 1852671.0861 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 29494.8995 | 105220.6959 | 1323230.1833 | 403738.3386 | 39548.5447 | 1901232.662 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165 |  | 19576.1556 | 110320.5745 | 1236239.2482 | 613770.0737 | 72597.4679 | 2052503.5198
| LV UGB |  | 677 | 677 | C1 | 91 | 126 | 187 | 258 | 15 | 677 | 86 | 126 | 187 | 258 | 20 | 677 | 13 | 0 | 0 | 0 | -13 | 0 | 55 | 73 | 135 | 384 | 30 | 677 | 29 | 0 | 0 | 0 | -29 | 0 | 46 | 33 | 66 | 485 | 46 | 676 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | C1 | 11.0956 | 16.6433 | 55.4778 | 122.0512 | 238.5547 | C1 | 954.2186 | 2097.0618 | 10374.3535 | 31489.2142 | 4771.0931 | 49685.9412 |  | 1009.6964 | 2097.0618 | 10374.3535 | 31489.2142 | 3578.3198 | 48548.6457 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 754.4984 | 1214.9644 | 7489.5065 | 46867.6676 | 4055.4291 | 60382.066 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176 |  | 832.1674 | 549.2305 | 3661.5365 | 59194.8406 | 4055.4291 | 68293.2041
|  |  | 19687 | 19687 | C2 | 2638 | 3677 | 5444 | 7503 | 425 | 19687 | 2493 | 3677 | 5444 | 7503 | 569 | 19686 | 2284 | 0 | 0 | -1898 | -386 | 0 | 1594 | 2136 | 3923 | 11170 | 863 | 19686 | 2738 | 0 | 0 | -1898 | -840 | 0 | 1334 | 963 | 1930 | 14111 | 1350 | 19688 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11057 | 11057 | 11057 | 11057 | 11057 | C2 | 15.8508 | 23.7762 | 79.254 | 174.3589 | 340.7924 | C2 | 39516.0631 | 87425.1287 | 431458.9798 | 1308214.6945 | 193910.8534 | 2060525.7195 |  | 41814.4302 | 87425.1287 | 431458.9798 | 1308214.6945 | 144836.7534 | 2013749.9866 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 61469.4314 | 50785.9872 | 310913.5889 | 1616655.5574 | 162557.9562 | 2202382.5211 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375 |  | 64544.4881 | 22896.4914 | 152960.2923 | 2129445.0305 | 173804.1041 | 2543650.4064
|  |  | 4474 | 4474 | C3 | 599 | 836 | 1237 | 1705 | 97 | 4474 | 567 | 836 | 1237 | 1705 | 129 | 4474 | 828 | 0 | 0 | -740 | -88 | 0 | 362 | 486 | 892 | 2539 | 196 | 4475 | 931 | 0 | 0 | -740 | -191 | 0 | 303 | 219 | 439 | 3207 | 307 | 4475 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | C3 | 23.7762 | 35.6643 | 118.8811 | 261.5383 | 511.1885 | C3 | 13481.1118 | 29815.3689 | 147055.8665 | 445922.8417 | 65943.3219 | 702218.5107 |  | 14241.9505 | 29815.3689 | 147055.8665 | 445922.8417 | 49585.2885 | 686621.3161 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 28293.6914 | 17332.858 | 106041.9021 | 470507.4441 | 55208.3625 | 677384.258 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747 |  | 29339.8447 | 7810.4854 | 52188.7837 | 645215.0442 | 59297.8708 | 793852.0288
|  |  | 3369 | 3369 | C4 | 451 | 629 | 932 | 1284 | 73 | 3369 | 427 | 629 | 932 | 1284 | 97 | 3369 | 623 | 0 | 0 | -557 | -66 | 0 | 273 | 366 | 671 | 1912 | 148 | 3370 | 1226 | 0 | 0 | -1082 | -144 | 0 | 228 | 165 | 330 | 2415 | 231 | 3369 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | C4 | 39.627 | 59.4405 | 198.1351 | 435.8972 | 851.9809 | C4 | 16920.737 | 37388.0922 | 184661.9072 | 559692.0124 | 82642.1475 | 881304.8964 |  | 17871.7854 | 37388.0922 | 184661.9072 | 559692.0124 | 62194.6059 | 861808.4032 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 35505.8088 | 21755.2333 | 132948.6478 | 590640.7141 | 69862.434 | 850712.8379 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691 |  | 57617.6852 | 9807.6871 | 65384.5809 | 581050.9755 | 74122.3385 | 787983.2673
|  |  | 28207 | 28207 |  | 3779 | 5268 | 7800 | 10750 | 610 |  | 3573 | 5268 | 7800 | 10750 | 815 |  | 3748 | 0 | 0 | -3195 | -553 |  | 2284 | 3061 | 5621 | 16005 | 1237 |  | 4924 | 0 | 0 | -3720 | -1204 |  | 1911 | 1380 | 2765 | 20218 | 1934 | [22 empty] | 70872.1304 | 156725.6516 | 773551.1071 | 2345318.7627 | 347267.4159 | 3693735.0677 |  | 74937.8626 | 156725.6516 | 773551.1071 | 2345318.7627 | 260194.9676 | 3610728.3516 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 126023.43 | 91089.0429 | 557393.6453 | 2724671.3831 | 291684.1818 | 3790861.6831 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711 |  | 152334.1854 | 41063.8944 | 274195.1933 | 3414905.8908 | 311279.7425 | 4193778.9065
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | C1 | 14.8033 | 14.8033 | 29.7404 | 81.901 | 162.3867 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 124969 | 124969 | C2 | 21863 | 72930 | 26079 | 4097 | 0 | 124969 | 19674 | 73119 | 26079 | 4097 | 2189 | 125158 | 4322 | 0 | 0 | -1366 | -2956 | 0 | 16316 | 54726 | 37003 | 13968 | 2956 | 124969 | 8656 | 0 | 0 | -1366 | -7290 | 0 | 13510 | 48074 | 35619 | 19954 | 7812 | 124969 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13911 | 13911 | 13911 | 13911 | 13911 | C2 | 21.1475 | 21.1475 | 42.4864 | 117.0014 | 231.981 | C2 | 416056.8929 | 1546287.6868 | 1108001.6864 | 479354.7947 | 507806.3433 | 4057507.4041 |  | 462348.8792 | 1542290.7999 | 1108001.6864 | 479354.7947 | 0 | 3591996.1602 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 436443.1308 | 1157320.8051 | 1572122.6429 | 1474451.8239 | 0 | 4640338.4027 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865 |  | 468756.5867 | 1016647.3045 | 1513321.5257 | 2174822.2903 | 121094.0663 | 5294641.7736
|  |  | 1184 | 1184 | C3 | 143 | 852 | 189 | 0 | 0 | 1184 | 124 | 852 | 189 | 0 | 19 | 1184 | 58 | 0 | 0 | -28 | -30 | 0 | 143 | 529 | 350 | 132 | 30 | 1184 | 104 | 0 | 0 | -28 | -76 | 0 | 126 | 456 | 337 | 189 | 76 | 1184 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | C3 | 31.7213 | 31.7213 | 63.7295 | 175.5021 | 347.9715 | C3 | 3933.4442 | 27026.5685 | 12044.882 | 0 | 6611.4576 | 49616.3524 |  | 4536.1494 | 27026.5685 | 12044.882 | 0 | 0 | 43607.6 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 6375.9862 | 16780.5807 | 22305.3371 | 18252.2206 | 0 | 63714.1246 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956 |  | 7295.9046 | 14464.924 | 21476.8531 | 28255.8416 | 0 | 71493.5233
|  |  | 2 | 2 | C4 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | C4 | 52.8689 | 52.8689 | 106.2159 | 292.5035 | 579.9524 | C4 | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848
|  |  | 126155 | 126155 |  | 22006 | 73783 | 26269 | 4097 | 0 |  | 19798 | 73972 | 26269 | 4097 | 2208 |  | 4380 | 0 | 0 | -1394 | -2986 |  | 16459 | 55256 | 37354 | 14100 | 2986 |  | 8760 | 0 | 0 | -1394 | -7366 |  | 13636 | 48531 | 35957 | 20143 | 7888 | [22 empty] | 419990.3371 | 1573367.1242 | 1120152.7843 | 479354.7947 | 514417.8009 | 4107282.8413 |  | 466885.0286 | 1569370.2373 | 1120152.7843 | 479354.7947 | 0 | 3635762.845 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 442819.117 | 1174154.2547 | 1594534.1958 | 1492704.0445 | 0 | 4704211.6121 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669 |  | 476052.4914 | 1031165.0974 | 1534904.5947 | 2203078.1319 | 121094.0663 | 5366294.3817
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 |  | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 598337.4466 | 1370463.9934 | 3475158.0245 | 4621113.7662 | 331232.7265 | 10396305.9572 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 |  | 647962.8324 | 1182549.5663 | 3045339.0362 | 6231754.0963 | 504971.2768 | 11612576.808
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1843 | 1843 | C1 | 494 | 947 | 398 | 4 | 0 | 1843 | 477 | 947 | 398 | 20 | 1 | 1843 | 87 | 33 | 0 | -117 | -3 | 0 | 437 | 678 | 538 | 183 | 7 | 1843 | 179 | 180 | 0 | -325 | -34 | 0 | 211 | 638 | 620 | 336 | 38 | 1843 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | C1 | 58.7072 | 58.7072 | 219.7445 | 403.678 | 555.67 | C1 | 28003.3423 | 55595.734 | 87458.3248 | 8073.5593 | 555.67 | 179686.6303 |  | 29001.3649 | 55595.734 | 87458.3248 | 1614.7119 | 0 | 173670.1356 |  | 25655.0536 | 39803.4928 | 118222.5596 | 73873.068 | 3889.6899 | 261443.8638 |  | 30762.5814 | 41740.8309 | 118222.5596 | 26642.7458 | 2222.6799 | 219591.3977 |  | 12387.2227 | 37455.2041 | 136241.6114 | 135635.7969 | 21115.4594 | 342835.2945 |  | 22895.8144 | 48022.5031 | 136241.6114 | 4440.4576 | 2222.6799 | 213823.0665
|  |  | 829 | 836 | C2 | 99 | 627 | 103 | 0 | 0 | 829 | 98 | 533 | 103 | 11 | 1 | 746 | 54 | 8 | 0 | -55 | 0 | 7 | 74 | 427 | 222 | 106 | 0 | 829 | 89 | 78 | 0 | -148 | -12 | 7 | 40 | 270 | 358 | 149 | 12 | 829 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | C2 | 83.8675 | 83.8675 | 313.9208 | 576.6828 | 793.8143 | C2 | 8219.0103 | 44701.352 | 32333.8387 | 6343.5109 | 793.8143 | 92391.5261 |  | 8302.8778 | 52584.8925 | 32333.8387 | 0 | 0 | 93221.6089 |  | 6206.1915 | 35811.402 | 69690.4095 | 61128.3779 | 0 | 172836.3809 |  | 10735.0339 | 36482.3417 | 69690.4095 | 29410.8233 | 0 | 146318.6084 |  | 3354.6981 | 22644.2121 | 112383.6334 | 85925.7387 | 9525.7711 | 233834.0534 |  | 10818.9013 | 29185.8733 | 112383.6334 | 576.6828 | 0 | 152965.0908
|  |  | 317 | 317 | C3 | 44 | 244 | 29 | 0 | 0 | 317 | 44 | 244 | 29 | 0 | 0 | 317 | 14 | 8 | 0 | -22 | 0 | 0 | 38 | 181 | 50 | 48 | 0 | 317 | 28 | 31 | 0 | -56 | -3 | 0 | 20 | 102 | 135 | 57 | 3 | 317 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | C3 | 125.8012 | 125.8012 | 470.8811 | 865.0242 | 1190.7214 | C3 | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 4780.4448 | 22770.0132 | 23544.0573 | 41521.1623 | 0 | 92615.6776 |  | 6541.6613 | 23776.4227 | 23544.0573 | 22490.6296 | 0 | 76352.7708 |  | 2516.0236 | 12831.7202 | 63568.9546 | 49306.3803 | 3572.1642 | 131795.2428 |  | 6038.4566 | 16731.5567 | 63568.9546 | 865.0242 | 0 | 87203.9921
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | C4 | 209.6686 | 209.6686 | 784.8019 | 1441.707 | 1984.5357 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2989 | 2996 |  | 637 | 1818 | 530 | 4 | 0 |  | 619 | 1724 | 530 | 31 | 2 |  | 155 | 49 | 0 | -194 | -3 |  | 549 | 1286 | 810 | 337 | 7 |  | 296 | 289 | 0 | -529 | -49 |  | 271 | 1010 | 1113 | 542 | 53 | [22 empty] | 41757.6044 | 130992.5734 | 133447.7166 | 14417.0703 | 1349.4842 | 321964.449 |  | 42839.4945 | 138876.1139 | 133447.7166 | 1614.7119 | 0 | 316778.037 |  | 36641.6898 | 98384.9081 | 211457.0264 | 176522.6082 | 3889.6899 | 526895.9223 |  | 48039.2766 | 101999.5952 | 211457.0264 | 78544.1987 | 2222.6799 | 442262.7769 |  | 18257.9443 | 72931.1363 | 312194.1994 | 270867.9159 | 34213.3947 | 708464.5907 |  | 39753.1723 | 93939.9331 | 312194.1994 | 5882.1647 | 2222.6799 | 453992.1494
| HV Switchgear (GM) - Distribution |  | 4606 | 4592 | C1 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 1477 | 2931 | 42 | 88 | 68 | 4606 | 0 | 0 | 0 | 0 | -14 | -14 | 268 | 4101 | 52 | 28 | 157 | 4606 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | C1 | 13.6425 | 13.6425 | 51.2806 | 94.0237 | 160.8309 | C1 | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 22998.8235 | 87902.1128
|  |  | 22477 | 19345 | C2 | 5578 | 7761 | 6551 | 2065 | 522 | 22477 | 4662 | 7508 | 6551 | 2291 | 2419 | 23431 | 1343 | 0 | -91 | -571 | -2251 | -1570 | 4507 | 8127 | 1170 | 6052 | 2621 | 22477 | 2681 | 0 | -91 | -571 | -5151 | -3132 | 2324 | 9700 | 1039 | 1616 | 7798 | 22477 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | C2 | 19.4893 | 19.4893 | 73.2581 | 134.3195 | 229.7585 | C2 | 90858.975 | 146325.4364 | 479913.5676 | 307726.0048 | 555785.7551 | 1580609.7388 |  | 108711.146 | 151256.2216 | 479913.5676 | 277369.7948 | 119933.9248 | 1137184.6548 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 114012.2273 | 158389.2943 | 79045.4495 | 736205.252 | 85010.6364 | 1172662.8594 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394 |  | 97543.7945 | 189045.9154 | 69448.6433 | 140363.8913 | 608170.6877 | 1104572.9322
|  |  | 585 | 389 | C3 | 91 | 195 | 229 | 49 | 21 | 585 | 91 | 195 | 229 | 49 | 21 | 585 | 80 | 0 | 0 | -15 | -163 | -98 | 2 | 137 | 98 | 175 | 173 | 585 | 161 | 0 | 0 | -15 | -342 | -196 | 0 | 105 | 74 | 44 | 362 | 585 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | C3 | 29.2339 | 29.2339 | 109.8871 | 201.4793 | 344.6377 | C3 | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 2397.1802 | 4005.0449 | 10768.9352 | 32236.6832 | 3446.3772 | 52854.2206 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456 |  | 4706.6586 | 3069.56 | 8131.6449 | 5842.8988 | 6892.7543 | 28643.5166
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | C4 | 48.7232 | 48.7232 | 183.1452 | 335.7988 | 574.3962 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27668 | 24326 |  | 8838 | 9250 | 6897 | 2136 | 547 |  | 7922 | 8997 | 6897 | 2362 | 2444 |  | 1423 | 0 | -91 | -586 | -2414 |  | 5986 | 11195 | 1310 | 6315 | 2862 |  | 2842 | 0 | -91 | -586 | -5507 |  | 2592 | 13906 | 1165 | 1688 | 8317 | [22 empty] | 136752.3071 | 169679.4282 | 511077.5474 | 319667.0095 | 563666.4708 | 1700842.763 |  | 154604.4781 | 174610.2134 | 511077.5474 | 289310.7995 | 127814.6406 | 1257417.679 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 136559.3634 | 202380.4737 | 91968.1717 | 776716.0171 | 99393.517 | 1307017.5429 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309 |  | 105906.6401 | 248063.3217 | 80246.8817 | 148839.4526 | 638062.2656 | 1221118.5616
| HV Transformer (GM) |  | 9731 | 9731 | C1 | 1332 | 2840 | 5559 | 0 | 0 | 9731 | 1259 | 2840 | 5559 | 62 | 11 | 9731 | 169 | 0 | 0 | -169 | 0 | 0 | 730 | 3228 | 5574 | 199 | 0 | 9731 | 338 | 0 | 0 | -338 | 0 | 0 | 139 | 3457 | 5717 | 418 | 0 | 9731 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | C1 | 45.0878 | 54.95 | 154.9879 | 295.6111 | 498.624 | C1 | 56765.5022 | 156058.1406 | 861577.5631 | 18327.889 | 5484.864 | 1098213.959 |  | 60056.9094 | 156058.1406 | 861577.5631 | 0 | 0 | 1077692.6132 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 40533.9051 | 177378.7598 | 863902.3812 | 8868.3334 | 0 | 1090683.3795 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129 |  | 21506.8662 | 189962.3212 | 886065.6464 | 23648.889 | 0 | 1121183.7229
|  |  | 5287 | 5287 | C2 | 651 | 1916 | 2720 | 0 | 0 | 5287 | 595 | 1714 | 2720 | 50 | 6 | 5085 | 91 | 0 | 0 | -91 | 0 | 0 | 382 | 1888 | 2913 | 104 | 0 | 5287 | 182 | 0 | 0 | -182 | 0 | 0 | 72 | 2009 | 2988 | 218 | 0 | 5287 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | C2 | 64.4111 | 78.5001 | 221.4112 | 422.3016 | 712.32 | C2 | 38324.6044 | 134549.1212 | 602238.5762 | 21115.0795 | 4273.92 | 800501.3013 |  | 41931.626 | 150406.1355 | 602238.5762 | 0 | 0 | 794576.3377 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 30466.4502 | 148208.1336 | 644970.9458 | 5489.9207 | 0 | 829135.4502 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768 |  | 16360.4193 | 157706.6421 | 661576.7889 | 15202.8572 | 0 | 850846.7076
|  |  | 4141 | 4141 | C3 | 566 | 1209 | 2366 | 0 | 0 | 4141 | 518 | 1209 | 2366 | 43 | 5 | 4141 | 74 | 0 | 0 | -74 | 0 | 0 | 311 | 1374 | 2370 | 86 | 0 | 4141 | 148 | 0 | 0 | -148 | 0 | 0 | 59 | 1471 | 2433 | 178 | 0 | 4141 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | C3 | 96.6166 | 117.7501 | 332.1169 | 633.4524 | 1068.48 | C3 | 50047.4245 | 142359.8783 | 785788.4953 | 27238.4526 | 5342.4 | 1010776.6506 |  | 54685.0237 | 142359.8783 | 785788.4953 | 0 | 0 | 982833.3973 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 37197.4101 | 161788.6458 | 787116.9627 | 7601.4286 | 0 | 993704.4472 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638 |  | 19999.6465 | 173210.4061 | 808040.325 | 19003.5716 | 0 | 1020253.9491
|  |  | 2071 | 2071 | C4 | 283 | 605 | 1183 | 0 | 0 | 2071 | 260 | 605 | 1183 | 21 | 2 | 2071 | 37 | 0 | 0 | -37 | 0 | 0 | 155 | 687 | 1186 | 43 | 0 | 2071 | 74 | 0 | 0 | -74 | 0 | 0 | 30 | 736 | 1216 | 89 | 0 | 2071 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | C4 | 161.0277 | 196.2502 | 553.5281 | 1055.754 | 1780.8 | C4 | 41867.2149 | 118731.357 | 654823.746 | 22170.8335 | 3561.6 | 841154.7514 |  | 45570.8531 | 118731.357 | 654823.746 | 0 | 0 | 819125.9561 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 30917.3279 | 134823.8715 | 656484.3304 | 6334.5239 | 0 | 828560.0536 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399 |  | 16746.8859 | 144440.1302 | 673090.1735 | 15836.3096 | 0 | 850113.4992
|  |  | 21230 | 21230 |  | 2832 | 6570 | 11828 | 0 | 0 |  | 2632 | 6368 | 11828 | 176 | 24 |  | 371 | 0 | 0 | -371 | 0 |  | 1578 | 7177 | 12043 | 432 | 0 |  | 742 | 0 | 0 | -742 | 0 |  | 300 | 7673 | 12354 | 903 | 0 | [22 empty] | 187004.746 | 551698.4971 | 2904428.3807 | 88852.2546 | 18662.7838 | 3750646.6623 |  | 202244.4122 | 567555.5114 | 2904428.3807 | 0 | 0 | 3674228.3044 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 139115.0933 | 622199.4107 | 2952474.6201 | 28294.2065 | 0 | 3742083.3306 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676 |  | 74613.818 | 665319.4995 | 3028772.9338 | 73691.6275 | 0 | 3842397.8788
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 9772 | 9772 | C1 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 393 | 0 | 0 | 0 | -393 | 0 | 558 | 5094 | 2706 | 1021 | 393 | 9772 | 514 | 0 | 0 | 0 | -514 | 0 | 382 | 4298 | 2825 | 1534 | 733 | 9772 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | C1 | 19.1659 | 19.1659 | 72.1182 | 151.5867 | 233.6923 | C1 | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 18226.7282 | 97630.8658 | 195151.8933 | 154770.0352 | 0 | 465779.5225 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464 |  | 17172.6062 | 82374.8452 | 203733.9611 | 232534.0195 | 51178.6161 | 586994.0481
|  |  | 39560 | 39560 | C2 | 4761 | 27072 | 6789 | 938 | 0 | 39560 | 3776 | 27093 | 6789 | 938 | 985 | 39581 | 605 | 0 | 0 | 0 | -605 | 0 | 3243 | 20614 | 10962 | 4136 | 605 | 39560 | 1983 | 0 | 0 | 0 | -1983 | 0 | 2533 | 17389 | 11440 | 6215 | 1983 | 39560 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | C2 | 27.3798 | 27.3798 | 103.026 | 216.5524 | 333.8462 | C2 | 103386.0983 | 741800.7314 | 699443.6721 | 203126.197 | 328838.4663 | 2076595.1651 |  | 130355.1944 | 741225.7558 | 699443.6721 | 203126.197 | 0 | 1774150.8193 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 105357.4434 | 564407.0527 | 1129371.2673 | 895660.9283 | 0 | 2694796.6917 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443 |  | 123647.1451 | 476107.2203 | 1178617.7065 | 1345873.4694 | 0 | 3124245.5412
|  |  | 18629 | 18629 | C3 | 2618 | 12458 | 3162 | 391 | 0 | 18629 | 2100 | 12458 | 3162 | 391 | 518 | 18629 | 1148 | 0 | 0 | -917 | -231 | 0 | 1581 | 9711 | 5159 | 1947 | 231 | 18629 | 1796 | 0 | 0 | -917 | -879 | 0 | 1246 | 8194 | 5385 | 2925 | 879 | 18629 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | C3 | 41.0697 | 41.0697 | 154.539 | 324.8287 | 500.7692 | C3 | 86246.3479 | 511646.1916 | 488652.4285 | 127008.0112 | 259398.4653 | 1472951.4445 |  | 107520.4471 | 511646.1916 | 488652.4285 | 127008.0112 | 0 | 1234827.0783 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 112079.1826 | 398827.7546 | 797266.8812 | 334573.5334 | 0 | 1642747.3518 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012 |  | 124933.9954 | 336525.0356 | 832192.7031 | 652255.9758 | 0 | 1945907.71
|  |  | 41 | 41 | C4 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 0 | 0 | 0 | -2 | 0 | 2 | 22 | 11 | 4 | 2 | 41 | 3 | 0 | 0 | 0 | -3 | 0 | 2 | 18 | 12 | 6 | 3 | 41 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | C4 | 68.4495 | 68.4495 | 257.5651 | 541.3811 | 834.6154 | C4 | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 273.7979 | 1505.8886 | 2833.2156 | 2165.5245 | 0 | 6778.4267 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033 |  | 342.2474 | 1232.0907 | 3090.7807 | 3248.2867 | 0 | 7913.4055
|  |  | 68002 | 68002 |  | 8123 | 46800 | 11571 | 1508 | 0 |  | 6620 | 46821 | 11571 | 1508 | 1503 |  | 2148 | 0 | 0 | -917 | -1231 |  | 5384 | 35441 | 18838 | 7108 | 1231 |  | 4296 | 0 | 0 | -917 | -3379 |  | 4163 | 29899 | 19662 | 10680 | 3598 | [22 empty] | 203990.4097 | 1394704.751 | 1304927.611 | 357268.2301 | 588236.9315 | 3849127.9333 |  | 252233.6049 | 1394129.7753 | 1304927.611 | 357268.2301 | 0 | 3308559.2213 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 235937.1521 | 1062371.5617 | 2124623.2575 | 1387170.0214 | 0 | 4810101.9927 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952 |  | 266095.9941 | 896239.1918 | 2217635.1514 | 2233911.7515 | 51178.6161 | 5665060.7048
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 |  | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 |  | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 |  | 559650.8854 | 1988951.0413 | 5380523.0757 | 2270724.4438 | 101616.1969 | 10301465.643 |  | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 |  | 486369.6245 | 1903561.9461 | 5638849.1663 | 2462324.9962 | 691463.5616 | 11182569.2947
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 217 | 217 | C1 | 136 | 76 | 5 | 0 | 0 | 217 | 136 | 76 | 5 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 71 | 13 | 2 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 117 | 18 | 2 | 0 | 217 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | C1 | 165.6424 | 165.6424 | 625.0091 | 1143.9769 | 1952.7416 | C1 | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772
|  |  | 505 | 505 | C2 | 153 | 280 | 69 | 3 | 0 | 505 | 153 | 271 | 69 | 3 | 0 | 496 | 12 | 5 | 0 | -5 | -12 | 0 | 112 | 227 | 143 | 11 | 12 | 505 | 12 | 8 | 0 | -5 | -15 | 0 | 74 | 190 | 207 | 17 | 17 | 505 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | C2 | 236.6321 | 236.6321 | 892.8701 | 1634.2527 | 2789.6309 | C2 | 36204.7037 | 64127.2857 | 61608.0394 | 4902.758 | 0 | 166842.7867 |  | 36204.7037 | 66256.9741 | 61608.0394 | 4902.758 | 0 | 168972.4752 |  | 26502.7897 | 53715.4755 | 127680.4294 | 17976.7792 | 33475.5706 | 259351.0444 |  | 29342.3743 | 54898.6357 | 127680.4294 | 9805.516 | 0 | 221726.9553 |  | 17510.7717 | 44960.0896 | 184824.1181 | 27782.2952 | 47423.725 | 322500.9996 |  | 20350.3563 | 46853.146 | 184824.1181 | 19611.0319 | 5579.2618 | 277217.9141
|  |  | 70 | 70 | C3 | 8 | 54 | 8 | 0 | 0 | 70 | 8 | 54 | 8 | 0 | 0 | 70 | 5 | 0 | 0 | 0 | -5 | 0 | 8 | 41 | 16 | 0 | 5 | 70 | 5 | 0 | 0 | 0 | -5 | 0 | 5 | 32 | 26 | 2 | 5 | 70 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | C3 | 354.9481 | 354.9481 | 1339.3052 | 2451.379 | 4184.4463 | C3 | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 4614.325 | 14552.8711 | 21428.8833 | 0 | 0 | 40596.0793 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037 |  | 3549.4808 | 11358.3384 | 34821.9353 | 4902.758 | 0 | 54632.5125
|  |  | 6 | 6 | C4 | 2 | 3 | 1 | 0 | 0 | 6 | 2 | 3 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 6 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | C4 | 591.5801 | 591.5801 | 2232.1753 | 4085.6316 | 6974.0772 | C4 | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616
|  |  | 798 | 798 |  | 299 | 413 | 83 | 3 | 0 |  | 299 | 404 | 83 | 3 | 0 |  | 17 | 5 | 0 | -5 | -17 |  | 253 | 341 | 174 | 13 | 17 |  | 17 | 8 | 0 | -5 | -20 |  | 159 | 341 | 255 | 21 | 22 | [22 empty] | 62754.8198 | 97658.0472 | 77679.7018 | 4902.758 | 0 | 242995.3268 |  | 62754.8198 | 99787.7357 | 77679.7018 | 4902.758 | 0 | 245125.0153 |  | 52224.6935 | 81212.1197 | 161698.7816 | 20264.733 | 54397.8022 | 369798.13 |  | 56839.0185 | 82395.28 | 161698.7816 | 12093.4697 | 0 | 313026.5498 |  | 32536.9069 | 76881.7532 | 239824.9185 | 34973.0069 | 68345.9566 | 452562.5421 |  | 37151.2319 | 78774.8096 | 239824.9185 | 26801.7436 | 5579.2618 | 388131.9654
| EHV Transformer |  | 194 | 194 | C1 | 21 | 140 | 22 | 8 | 3 | 194 | 21 | 140 | 22 | 8 | 3 | 194 | 4 | 2 | 0 | -3 | -3 | 0 | 11 | 109 | 52 | 14 | 8 | 194 | 12 | 6 | 0 | -15 | -3 | 0 | 5 | 86 | 78 | 16 | 9 | 194 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | C1 | 890.0227 | 890.0227 | 3333.6634 | 6914.518 | 14150.0662 | C1 | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 9790.2493 | 97012.4705 | 173350.4943 | 96803.2517 | 113200.5292 | 490156.995 |  | 13350.34 | 98792.5158 | 173350.4943 | 76059.6977 | 70750.3308 | 432303.3786 |  | 4450.1133 | 76541.9492 | 260025.7415 | 110632.2876 | 127350.5954 | 579000.687 |  | 15130.3853 | 81882.0852 | 260025.7415 | 6914.518 | 84900.3969 | 448853.1268
|  |  | 259 | 259 | C2 | 29 | 154 | 59 | 11 | 6 | 259 | 26 | 143 | 59 | 11 | 9 | 248 | 11 | 9 | 0 | -11 | -9 | 0 | 22 | 120 | 84 | 23 | 10 | 259 | 23 | 20 | 0 | -31 | -12 | 0 | 12 | 89 | 96 | 46 | 16 | 259 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | C2 | 1271.461 | 1271.461 | 4762.3762 | 9877.8828 | 20214.3802 | C2 | 33057.9847 | 181818.9159 | 280980.1968 | 108656.711 | 181929.422 | 786443.2304 |  | 36872.3676 | 195804.9863 | 280980.1968 | 108656.711 | 121286.2813 | 743600.5431 |  | 27972.1409 | 152575.314 | 400039.6022 | 227191.3049 | 202143.8022 | 1009922.1643 |  | 41958.2114 | 164018.4626 | 400039.6022 | 118534.5939 | 20214.3802 | 744765.2503 |  | 15257.5314 | 113160.0246 | 457188.1168 | 454382.6098 | 323430.0835 | 1363418.3661 |  | 44501.1333 | 138589.2436 | 457188.1168 | 148168.2423 | 80857.5209 | 869304.2569
|  |  | 42 | 42 | C3 | 4 | 29 | 7 | 0 | 2 | 42 | 3 | 29 | 7 | 0 | 3 | 42 | 2 | 1 | 0 | -1 | -2 | 0 | 4 | 17 | 18 | 1 | 2 | 42 | 2 | 5 | 0 | -5 | -2 | 0 | 2 | 9 | 23 | 5 | 3 | 42 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | C3 | 1907.1914 | 1907.1914 | 7143.5643 | 14816.8242 | 30321.5703 | C3 | 5721.5743 | 55308.5513 | 50004.9503 | 0 | 90964.711 | 201999.7869 |  | 7628.7657 | 55308.5513 | 50004.9503 | 0 | 60643.1407 | 173585.408 |  | 7628.7657 | 32422.2542 | 128584.1579 | 14816.8242 | 60643.1407 | 244095.1427 |  | 11443.1486 | 34329.4457 | 128584.1579 | 0 | 0 | 174356.7521 |  | 3814.3829 | 17164.7228 | 164301.9795 | 74084.1212 | 90964.711 | 350329.9173 |  | 7628.7657 | 26700.68 | 164301.9795 | 0 | 30321.5703 | 228952.9955
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | C4 | 3178.6524 | 3178.6524 | 11905.9405 | 24694.7071 | 50535.9505 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 495 | 495 |  | 54 | 323 | 88 | 19 | 11 |  | 50 | 312 | 88 | 19 | 15 |  | 17 | 12 | 0 | -15 | -14 |  | 37 | 246 | 154 | 38 | 20 |  | 37 | 31 | 0 | -51 | -17 |  | 19 | 184 | 197 | 67 | 28 | [22 empty] | 57470.035 | 361730.6403 | 404325.7408 | 163972.8548 | 315344.3314 | 1302843.6024 |  | 63191.6092 | 375716.7108 | 404325.7408 | 163972.8548 | 224379.6204 | 1231586.5361 |  | 45391.1559 | 282010.0388 | 701974.2544 | 338811.3808 | 375987.4721 | 1744174.3019 |  | 66751.6999 | 297140.4241 | 701974.2544 | 194594.2916 | 90964.711 | 1351425.3809 |  | 23522.0276 | 206866.6966 | 881515.8378 | 639099.0186 | 541745.3899 | 2292748.9704 |  | 67260.2843 | 247172.0087 | 881515.8378 | 155082.7603 | 196079.4881 | 1547110.3792
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | C1 | 74.7619 | 74.7619 | 280.2348 | 577.8137 | 1188.9171 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 199818 | 199818 | 199818 | 199818 | 199818 | C2 | 106.8027 | 106.8027 | 400.3354 | 825.4482 | 1698.453 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 0 | C3 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | -7 | -7 | 0 | 0 | 0 | 0 | 7 | 7 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 299727 | 299727 | 299727 | 299727 | 299727 | C3 | 160.2041 | 160.2041 | 600.503 | 1238.1722 | 2547.6795 | C3 | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 499545 | 499545 | 499545 | 499545 | 499545 | C4 | 267.0068 | 267.0068 | 1000.8384 | 2063.6204 | 4246.1325 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | -7 |  | 0 | 0 | 0 | 0 | 7 | [22 empty] | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 126 | 126 | C1 | 2 | 69 | 41 | 3 | 11 | 126 | 2 | 84 | 38 | 0 | 2 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 59 | 2 | 17 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 80 | 5 | 18 | 126 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | C1 | 116.2368 | 116.2368 | 435.6977 | 898.3615 | 1848.4805 | C1 | 232.4736 | 9763.8917 | 16556.5141 | 0 | 3696.9611 | 30249.8405 |  | 232.4736 | 8020.3396 | 17863.6073 | 2695.0846 | 20333.286 | 49144.7912 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233
|  |  | 175 | 166.5 | C2 | 3 | 96 | 56 | 5 | 15 | 175 | 3 | 117 | 51 | 5 | 5 | 181 | 0 | 0 | 0 | 0 | -5 | -5 | 0 | 67 | 82 | 3 | 23 | 175 | 0 | 0 | 0 | 0 | -8.5 | -8.5 | 0 | 34 | 111 | 6 | 24 | 175 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 310669 | 310669 | 310669 | 310669 | 310669 | C2 | 166.0526 | 166.0526 | 622.4253 | 1283.3736 | 2640.6865 | C2 | 498.1577 | 19428.1519 | 31743.6924 | 6416.8682 | 13203.4325 | 71290.3028 |  | 498.1577 | 15941.0477 | 34855.8191 | 6416.8682 | 39610.2975 | 97322.1903 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 47532.357 | 113546.8788 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 40930.6408 | 123365.8832
|  |  | 145 | 132 | C3 | 2 | 80 | 47 | 3 | 13 | 145 | 2 | 90 | 42 | 11 | 0 | 145 | 0 | 0 | -3.45 | 0 | -0.55 | -4 | 0 | 55 | 68 | 3 | 19 | 145 | 0 | 0 | -3.45 | 0 | -9.55 | -13 | 0 | 26 | 92 | 6 | 21 | 145 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | C3 | 249.0789 | 249.0789 | 933.638 | 1925.0605 | 3961.0298 | C3 | 498.1577 | 22417.0984 | 39212.7965 | 21175.665 | 0 | 83303.7177 |  | 498.1577 | 19926.3097 | 43880.9866 | 5775.1814 | 51493.3868 | 121574.0221 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 13699.3379 | 60266.3337 | 5775.1814 | 73080.9989 | 152821.8518 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353 |  | 0 | 6476.0506 | 82673.646 | 11550.3628 | 45353.7906 | 146053.85
|  |  | 13 | 11.3 | C4 | 0 | 8 | 4 | 0 | 1 | 13 | 0 | 9 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | -1.7 | -1.7 | 0 | 2 | 8 | 1 | 2 | 13 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | C4 | 415.1315 | 415.1315 | 1556.0634 | 3208.4341 | 6601.7163 | C4 | 0 | 3736.1831 | 6224.2534 | 0 | 0 | 9960.4365 |  | 0 | 3321.0516 | 6224.2534 | 0 | 6601.7163 | 16147.0213 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 1980.5149 | 18467.7187
|  |  | 459 | 435.8 |  | 7 | 253 | 148 | 11 | 40 |  | 7 | 300 | 135 | 16 | 7 |  | 0 | 0 | -3.45 | 0 | -5.55 |  | 0 | 175 | 215 | 8 | 61 |  | 0 | 0 | -3.45 | 0 | -19.75 |  | 0 | 85 | 291 | 18 | 65 | [22 empty] | 1228.7891 | 55345.3251 | 93737.2564 | 27592.5332 | 16900.3936 | 194804.2974 |  | 1228.7891 | 47208.7486 | 102824.6664 | 14887.1342 | 118038.6865 | 284188.0249 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 32479.8847 | 146347.7584 | 11422.0254 | 165240.9577 | 355490.6263 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134 |  | 0 | 15625.5478 | 199067.1848 | 26950.8464 | 121537.5962 | 363181.1753
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 338 | 338 | C1 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 208 | 16 | 12 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 189 | 25 | 22 | 338 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | C1 | 0 | 0 | 12.1985 | 42.3409 | 98.717 | C1 | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812
|  |  | 166 | 166 | C2 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 103 | 7 | 5 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 94 | 11 | 10 | 166 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 215767 | 215767 | 215767 | 215767 | 215767 | C2 | 0 | 0 | 17.4264 | 60.487 | 141.0242 | C2 | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834
|  |  | 15 | 15 | C3 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | C3 | 0 | 0 | 26.1396 | 90.7306 | 211.5363 | C3 | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236
|  |  | 56 | 56 | C4 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 3 | 2 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 5 | 4 | 56 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | C4 | 0 | 0 | 43.5661 | 151.2176 | 352.5606 | C4 | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312
|  |  | 575 | 575 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 354 | 27 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 322 | 42 | 37 | [22 empty] | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331
| EHV OHL Support - Poles |  | 673 | 673 | C1 | 61 | 499 | 96 | 11 | 6 | 673 | 61 | 499 | 96 | 11 | 6 | 673 | 20 | 0 | 0 | 0 | -20 | 0 | 27 | 355 | 210 | 61 | 20 | 673 | 45 | 0 | 0 | 0 | -45 | 0 | 24 | 279 | 245 | 80 | 45 | 673 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | C1 | 15.4993 | 15.4993 | 58.3259 | 122.6046 | 189.0162 | C1 | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 728.4661 | 5502.2441 | 12248.4379 | 7478.8805 | 0 | 25958.0286 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224 |  | 1069.4503 | 4324.2989 | 14289.8442 | 9808.3679 | 0 | 29491.9612
|  |  | 43 | 43 | C2 | 3 | 37 | 3 | 0 | 0 | 43 | 3 | 37 | 3 | 0 | 0 | 43 | 2 | 0 | 0 | 0 | -2 | 0 | 2 | 21 | 14 | 4 | 2 | 43 | 2 | 0 | 0 | 0 | -2 | 0 | 1 | 19 | 16 | 5 | 2 | 43 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 64595 | 64595 | 64595 | 64595 | 64595 | C2 | 22.1418 | 22.1418 | 83.3227 | 175.1494 | 270.0232 | C2 | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 88.5673 | 464.9784 | 1166.5179 | 700.5977 | 0 | 2420.6613 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934 |  | 66.4255 | 420.6947 | 1333.1633 | 875.7471 | 0 | 2696.0306
|  |  | 10397 | 10397 | C3 | 952 | 7695 | 1492 | 161 | 97 | 10397 | 847 | 7695 | 1492 | 161 | 202 | 10397 | 388 | 0 | 0 | -181 | -207 | 0 | 517 | 5488 | 3249 | 936 | 207 | 10397 | 769 | 0 | 0 | -181 | -588 | 0 | 472 | 4313 | 3785 | 1239 | 588 | 10397 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | C3 | 33.2127 | 33.2127 | 124.9841 | 262.7241 | 405.0348 | C3 | 28131.1917 | 255572.0426 | 186476.2173 | 42298.5864 | 81817.0254 | 594295.0634 |  | 31618.5295 | 255572.0426 | 186476.2173 | 42298.5864 | 39288.3736 | 555253.7494 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 30057.5307 | 182271.5231 | 406073.2105 | 198356.725 | 0 | 816758.9893 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911 |  | 41217.0117 | 143246.5523 | 473064.6666 | 277962.1392 | 0 | 935490.3697
|  |  | 638 | 638 | C4 | 58 | 473 | 91 | 10 | 6 | 638 | 58 | 473 | 91 | 10 | 6 | 638 | 20 | 0 | 0 | -1 | -19 | 0 | 25 | 338 | 199 | 57 | 19 | 638 | 44 | 0 | 0 | -1 | -43 | 0 | 23 | 264 | 232 | 76 | 43 | 638 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | C4 | 55.3546 | 55.3546 | 208.3068 | 437.8736 | 675.058 | C4 | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 2490.9556 | 18709.8441 | 41453.0465 | 24520.9197 | 0 | 87174.7659 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144 |  | 3708.7561 | 14613.6061 | 48327.1698 | 32840.5174 | 0 | 99490.0494
|  |  | 11751 | 11751 |  | 1074 | 8704 | 1682 | 182 | 109 |  | 969 | 8704 | 1682 | 182 | 214 |  | 430 | 0 | 0 | -182 | -248 |  | 571 | 6202 | 3672 | 1058 | 248 |  | 860 | 0 | 0 | -182 | -678 |  | 520 | 4875 | 4278 | 1400 | 678 | [22 empty] | 32353.6382 | 290308.1414 | 211281.3871 | 48025.9726 | 87001.4705 | 668970.6099 |  | 35840.976 | 290308.1414 | 211281.3871 | 48025.9726 | 44472.8187 | 629929.2959 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 33365.5197 | 206948.5897 | 460941.2128 | 231057.1229 | 0 | 932312.445 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229 |  | 46061.6435 | 162605.152 | 537014.8439 | 321486.7716 | 0 | 1067168.4109
| EHV OHL Fittings and Conductors (Tower Lines) |  | 64 | 64 | C1 | 1 | 0 | 8 | 42 | 13 | 64 | 0 | 0 | 8 | 42 | 14 | 64 | 2.9421 | 0 | 0 | 0 | -2.9421 | 0 | 1 | 0 | 8 | 33 | 22 | 64 | 5.8842 | 0 | 0 | 0 | -5.8842 | 0 | 1 | 0 | 2 | 12 | 49 | 64 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | C1 | 0 | 0 | 12.2256 | 39.8434 | 77.3125 | C1 | 0 | 0 | 97.8044 | 1673.4214 | 1082.3745 | 2853.6003 |  | 0 | 0 | 97.8044 | 1673.4214 | 1005.062 | 2776.2878 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 97.8044 | 1314.8311 | 1473.4136 | 2886.0491 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822 |  | 0 | 0 | 24.4511 | 478.1204 | 3333.3895 | 3835.961
|  |  | 18 | 18 | C2 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 3 | 11 | 4 | 18 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 3 | 8 | 7 | 18 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 0 | 0 | 4 | 14 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | C2 | 0 | 0 | 17.4651 | 56.9191 | 110.4464 | C2 | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 52.3952 | 455.3528 | 662.6783 | 1170.4262 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256 |  | 0 | 0 | 0 | 227.6764 | 1325.3565 | 1553.0329
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | C3 | 0 | 0 | 26.1976 | 85.3786 | 165.6696 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | C4 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | C4 | 0 | 0 | 43.6627 | 142.2977 | 276.1159 | C4 | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159
|  |  | 83 | 83 |  | 1 | 0 | 11 | 54 | 17 |  | 0 | 0 | 11 | 54 | 18 |  | 3.9421 | 0 | 0 | 0 | -3.9421 |  | 1 | 0 | 11 | 42 | 29 |  | 7.8842 | 0 | 0 | 0 | -7.8842 |  | 1 | 0 | 2 | 16 | 64 | [22 empty] | 0 | 0 | 150.1997 | 2441.8291 | 1524.16 | 4116.1888 |  | 0 | 0 | 150.1997 | 2441.8291 | 1446.8475 | 4038.8763 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 150.1997 | 1912.4816 | 2136.0918 | 4198.7731 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237 |  | 0 | 0 | 24.4511 | 705.7968 | 4934.8619 | 5665.1098
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 |  | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 |  | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 |  | 156956.2381 | 618964.1785 | 1477160.9178 | 461391.8443 | 261148.1428 | 2975621.3215 |  | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 |  | 150473.1597 | 504177.5181 | 1862933.0736 | 533598.6179 | 333335.0021 | 3384517.3715
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 128 | 128 | C1 | 56 | 56 | 9 | 7 | 0 | 128 | 56 | 53 | 9 | 10 | 0 | 128 | 3 | 0 | 0 | 0 | -3 | 0 | 29 | 76 | 5 | 8 | 10 | 128 | 11 | 0 | 0 | 0 | -11 | 0 | 2 | 99 | 6 | 1 | 20 | 128 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | C1 | 566.8931 | 566.8931 | 2163.712 | 3830.461 | 5875.081 | C1 | 31746.0137 | 30045.3344 | 19473.4083 | 38304.6103 | 0 | 119569.3666 |  | 31746.0137 | 31746.0137 | 19473.4083 | 26813.2272 | 0 | 109778.6628 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 18140.5792 | 43083.8757 | 10818.5601 | 30643.6882 | 41125.5673 | 143812.2706 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572 |  | 7369.6103 | 56122.4171 | 12982.2722 | 3830.461 | 52875.7293 | 133180.4899
|  |  | 91 | 92 | C2 | 14 | 52 | 9 | 15 | 1 | 91 | 7 | 29 | 9 | 23 | 4 | 72 | 8 | 0 | 0 | 0 | -8 | 0 | 9 | 55 | 5 | 2 | 20 | 91 | 13 | 0 | 0 | 0 | -12 | 1 | 9 | 51 | 1 | 0 | 30 | 91 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | C2 | 809.8473 | 809.8473 | 3091.0172 | 5472.0872 | 8392.9729 | C2 | 5668.931 | 23485.5714 | 27819.1546 | 125858.0053 | 33571.8916 | 216403.5539 |  | 11337.862 | 42112.059 | 27819.1546 | 82081.3078 | 8392.9729 | 171743.3563 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 13767.4039 | 44541.6008 | 15455.0859 | 10944.1744 | 100715.6749 | 185423.9399 |  | 7288.6256 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 303471.0417 |  | 17816.6403 | 41302.2117 | 3091.0172 | 0 | 151073.5124 | 213283.3816
|  |  | 13 | 13 | C3 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 9 | 1 | 3 | 0 | 13 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 9 | 0 | 1 | 3 | 13 | 3 | 0 | 0 | 0 | -3 | 0 | 0 | 9 | 0 | 0 | 4 | 13 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | C3 | 1214.7709 | 1214.7709 | 4636.5258 | 8208.1308 | 12589.4594 | C3 | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 1214.7709 | 10932.9384 | 0 | 8208.1308 | 25178.9187 | 45534.7588 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758 |  | 3644.3128 | 10932.9384 | 0 | 0 | 12589.4594 | 27166.7105
|  |  | 2 | 2 | C4 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | C4 | 2024.6182 | 2024.6182 | 7727.543 | 13680.218 | 20982.4323 | C4 | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362
|  |  | 234 | 235 |  | 71 | 117 | 20 | 25 | 1 |  | 64 | 91 | 20 | 36 | 4 |  | 12 | 0 | 0 | 0 | -12 |  | 39 | 140 | 11 | 11 | 33 |  | 27 | 0 | 0 | 0 | -26 |  | 11 | 160 | 7 | 2 | 54 | [22 empty] | 39439.5629 | 64463.8441 | 59656.6316 | 188787.0079 | 33571.8916 | 385918.9382 |  | 45108.4939 | 84791.011 | 59656.6316 | 133518.9273 | 8392.9729 | 331468.0368 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 35147.3723 | 98558.4149 | 34001.189 | 49795.9934 | 167020.1609 | 384523.1305 |  | 8422.4118 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572037.2109 |  | 28830.5635 | 110382.1853 | 16073.2893 | 17510.679 | 216538.7011 | 389335.4182
| 132kV Transformer |  | 41 | 40 | C1 | 6 | 26 | 5 | 3 | 1 | 41 | 5 | 25 | 5 | 4 | 2 | 41 | 2 | 0 | 0 | -1 | -2 | -1 | 4 | 26 | 6 | 3 | 2 | 41 | 4 | 0 | 0 | -3 | -2 | -1 | 2 | 18 | 15 | 3 | 3 | 41 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | C1 | 2793.658 | 2793.658 | 10463.908 | 21703.7153 | 44415.0999 | C1 | 13968.29 | 69841.4502 | 52319.5402 | 86814.8611 | 88830.1998 | 311774.3413 |  | 16761.948 | 72635.1082 | 52319.5402 | 65111.1458 | 44415.0999 | 251242.8421 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 16761.948 | 72635.1082 | 62783.4482 | 43407.4305 | 0 | 195587.935 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262 |  | 16761.948 | 50285.8441 | 156958.6205 | 0 | 44415.0999 | 268421.5126
|  |  | 125 | 125 | C2 | 19 | 79 | 24 | 1 | 2 | 125 | 18 | 75 | 24 | 3 | 3 | 123 | 3 | 0 | 0 | -3 | 0 | 0 | 12 | 70 | 35 | 6 | 2 | 125 | 5 | 7 | 0 | -12 | 0 | 0 | 7 | 67 | 34 | 15 | 2 | 125 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469152 | 469152 | 469152 | 469152 | 469152 | C2 | 3990.94 | 3990.94 | 14948.44 | 31005.3075 | 63450.1427 | C2 | 71836.9202 | 299320.5007 | 358762.5611 | 93015.9226 | 190350.4282 | 1013286.3329 |  | 75827.8602 | 315284.2608 | 358762.5611 | 31005.3075 | 126900.2855 | 907780.2751 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 59864.1001 | 279365.8007 | 523195.4017 | 93015.9226 | 126900.2855 | 1082341.5106 |  | 27936.5801 | 267392.9807 | 508246.9616 | 465079.6129 | 126900.2855 | 1395556.4207 |  | 47891.2801 | 295329.5607 | 508246.9616 | 93015.9226 | 126900.2855 | 1071384.0105
|  |  | 17 | 17 | C3 | 3 | 9 | 4 | 1 | 0 | 17 | 2 | 9 | 4 | 1 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 5 | 3 | 0 | 17 | 0 | 2 | 0 | -2 | 0 | 0 | 1 | 6 | 6 | 4 | 0 | 17 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 703728 | 703728 | 703728 | 703728 | 703728 | C3 | 5986.41 | 5986.41 | 22422.6601 | 46507.9613 | 95175.2141 | C3 | 11972.82 | 53877.6901 | 89690.6403 | 46507.9613 | 95175.2141 | 297224.3259 |  | 17959.23 | 53877.6901 | 89690.6403 | 46507.9613 | 0 | 208035.5217 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757 |  | 5986.41 | 47891.2801 | 134535.9604 | 93015.9226 | 0 | 281429.5731
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1172880 | 1172880 | 1172880 | 1172880 | 1172880 | C4 | 9977.35 | 9977.35 | 37371.1001 | 77513.2688 | 158625.3569 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 183 | 182 |  | 28 | 114 | 33 | 5 | 3 |  | 25 | 109 | 33 | 8 | 6 |  | 5 | 0 | 0 | -4 | -2 |  | 19 | 102 | 46 | 12 | 4 |  | 9 | 9 | 0 | -17 | -2 |  | 10 | 91 | 55 | 22 | 5 | [22 empty] | 97778.0302 | 423039.6411 | 500772.7416 | 226338.7449 | 374355.8422 | 1622285 |  | 110549.0383 | 441797.0591 | 500772.7416 | 142624.4146 | 171315.3854 | 1367058.639 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 94585.2782 | 387919.369 | 698092.1502 | 275947.237 | 126900.2855 | 1583444.3199 |  | 39510.3061 | 353597.2849 | 799741.5425 | 716222.6038 | 260145.5853 | 2169217.3226 |  | 70639.6382 | 393506.685 | 799741.5425 | 186031.8451 | 171315.3854 | 1621235.0962
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | C1 | 262.0625 | 262.0625 | 982.3054 | 2025.4074 | 4167.5049 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 700421 | 700421 | 700421 | 700421 | 700421 | C2 | 374.375 | 374.375 | 1403.2935 | 2893.4392 | 5953.5785 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 14.2 | C3 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 16 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | -10.8 | -10.8 | 0 | 0 | 0 | 0 | 25 | 25 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | C3 | 561.5625 | 561.5625 | 2104.9402 | 4340.1587 | 8930.3678 | C3 | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 126811.2221 | 126811.2221
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | C4 | 935.9376 | 935.9376 | 3508.2337 | 7233.5979 | 14883.9463 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 14.2 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 16 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 0 | -10.8 |  | 0 | 0 | 0 | 0 | 25 | [22 empty] | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 126811.2221 | 126811.2221
| 132kV UG Cable (Oil) |  | 34 | 34 | C1 | 11 | 11 | 9 | 1 | 2 | 34 | 10 | 16 | 7 | 1 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 8 | 3 | 3 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 11 | 3 | 3 | 34 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | C1 | 306.3424 | 306.3424 | 1148.2826 | 2367.6343 | 4871.6755 | C1 | 3063.4242 | 4901.4787 | 8037.9781 | 2367.6343 | 0 | 18370.5154 |  | 3369.7666 | 3369.7666 | 10334.5433 | 2367.6343 | 9743.3511 | 29185.0619 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592
|  |  | 30 | 29.9 | C2 | 9 | 11 | 8 | 0 | 2 | 30 | 9 | 15 | 7 | 1 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 8 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | -0.1 | -0.1 | 9 | 5 | 10 | 3 | 3 | 30 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 818769 | 818769 | 818769 | 818769 | 818769 | C2 | 437.632 | 437.632 | 1640.4037 | 3382.3347 | 6959.5365 | C2 | 3938.6883 | 6564.4805 | 11482.8258 | 3382.3347 | 6959.5365 | 32327.8658 |  | 3938.6883 | 4813.9523 | 13123.2295 | 0 | 13919.073 | 35794.9431 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20182.6558 | 52860.5454
|  |  | 36 | 36 | C3 | 12 | 11 | 9 | 1 | 3 | 36 | 11 | 17 | 7 | 1 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 9 | 3 | 3 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 11 | 4 | 3 | 36 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | C3 | 656.448 | 656.448 | 2460.6055 | 5073.5021 | 10439.3048 | C3 | 7220.9285 | 11159.6168 | 17224.2388 | 5073.5021 | 0 | 40678.2862 |  | 7877.3765 | 7220.9285 | 22145.4498 | 5073.5021 | 31317.9143 | 73635.1712 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484
|  |  | 134 | 123.6 | C4 | 43 | 45 | 34 | 2 | 10 | 134 | 40 | 62 | 28 | 3 | 1 | 134 | 0 | 0 | 0 | 0 | -8 | -8 | 39 | 39 | 33 | 13 | 10 | 134 | 0 | 0 | 0 | -2.4 | -8 | -10.4 | 39 | 27 | 42 | 13 | 13 | 134 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | C4 | 1094.0801 | 1094.0801 | 4101.0092 | 8455.8368 | 17398.8413 | C4 | 43763.2031 | 67832.9647 | 114828.2584 | 25367.5105 | 17398.8413 | 269190.778 |  | 47045.4433 | 49233.6034 | 139434.3138 | 16911.6737 | 173988.4125 | 426613.4467 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 34797.6825 | 365395.112 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879 |  | 42669.123 | 29540.1621 | 172242.3876 | 89631.8706 | 86994.2063 | 421077.7495
|  |  | 234 | 223.5 |  | 75 | 78 | 60 | 4 | 17 |  | 70 | 110 | 49 | 6 | 2 |  | 0 | 0 | 0 | 0 | -8 |  | 68 | 68 | 58 | 22 | 18 |  | 0 | 0 | 0 | -2.4 | -8.1 |  | 68 | 47 | 74 | 23 | 22 | [22 empty] | 57986.244 | 90458.5407 | 151573.3011 | 36190.9817 | 24358.3777 | 360567.4453 |  | 62231.2747 | 64638.2509 | 185037.5364 | 24352.8101 | 228968.7509 | 565228.623 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 94649.6964 | 529524.4814 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946 |  | 56235.7159 | 39124.3035 | 228344.1939 | 127175.7862 | 153109.803 | 603989.8025
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 51.5767 | 120.25 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2258 | 2188 | C2 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 790 | 994 | 456 | 18 | 2258 | 8 | 0 | 0 | 0 | -8 | 0 | 0 | 790 | 964 | 486 | 18 | 2258 | 16 | 0 | 0 | -70 | -16 | -70 | 0 | 789 | 962 | 465 | 42 | 2258 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 73.681 | 171.7857 | C2 | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20463.4319 | 35808.9702 | 1717.8568 | 57990.259 |  | 0 | 0 | 20420.9767 | 34261.6691 | 7214.9986 | 61897.6443 |  | 0 | 0 | 20420.9767 | 29103.9984 | 4466.4277 | 53991.4028
|  |  | 312 | 312 | C3 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 67 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 64 | 6 | 312 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 110.5215 | 257.6785 | C3 | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594
|  |  | 5 | 5 | C4 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 184.2025 | 429.4642 | C4 | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407
|  |  | 2575 | 2505 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 901 | 1133 | 520 | 21 |  | 8 | 0 | 0 | 0 | -8 |  | 0 | 901 | 1099 | 554 | 21 |  | 16 | 0 | 0 | -70 | -16 |  | 0 | 900 | 1097 | 530 | 48 | [22 empty] | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24804.4815 | 43398.1141 | 2490.8924 | 70693.4881 |  | 0 | 0 | 24762.0263 | 41519.2484 | 8761.0697 | 75042.3444 |  | 0 | 0 | 24762.0263 | 36361.5778 | 6012.4988 | 67136.1029
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 48.4269 | 93.9681 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1003 | 981 | C2 | 215 | 464 | 324 | 0 | 0 | 1003 | 189 | 464 | 350 | 0 | 0 | 1003 | 109.1199 | 0 | 0 | -109.1199 | 0 | 0 | 178 | 420 | 280 | 125 | 0 | 1003 | 235.1191 | 0 | -22 | -235.1191 | 0 | -22 | 26 | 494 | 244 | 239 | 0 | 1003 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 69.1813 | 134.2401 | C2 | 0 | 0 | 7429.6693 | 0 | 0 | 7429.6693 |  | 0 | 0 | 6877.751 | 0 | 0 | 6877.751 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5943.7354 | 1098.6086 | 0 | 7042.344 |  | 0 | 0 | 5179.5409 | 16534.3366 | 0 | 21713.8775 |  | 0 | 0 | 4712.5331 | 268.4854 | 0 | 4981.0184
|  |  | 147 | 147 | C3 | 31 | 68 | 48 | 0 | 0 | 147 | 31 | 68 | 48 | 0 | 0 | 147 | 18 | 0 | 0 | -18 | 0 | 0 | 22 | 62 | 45 | 18 | 0 | 147 | 28 | 0 | 0 | -28 | 0 | 0 | 0 | 72 | 39 | 36 | 0 | 147 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 103.772 | 201.3602 | C3 | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1432.8648 | 0 | 0 | 1432.8648 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077 |  | 0 | 0 | 1241.8161 | 830.1759 | 0 | 2071.992
|  |  | 1 | 1 | C4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 172.9533 | 335.6003 | C4 | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1151 | 1129 |  | 246 | 532 | 373 | 0 | 0 |  | 220 | 532 | 399 | 0 | 0 |  | 128.1199 | 0 | 0 | -128.1199 | 0 |  | 200 | 482 | 325 | 144 | 0 |  | 264.1191 | 0 | -22 | -264.1191 | 0 |  | 26 | 566 | 283 | 276 | 0 | [22 empty] | 0 | 0 | 9011.1274 | 0 | 0 | 9011.1274 |  | 0 | 0 | 8459.2092 | 0 | 0 | 8459.2092 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 7376.6002 | 1098.6086 | 0 | 8475.2088 |  | 0 | 0 | 6421.357 | 20443.0815 | 0 | 26864.4385 |  | 0 | 0 | 5954.3492 | 1098.6613 | 0 | 7053.0105
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 |  | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 185968.3665 | 542932.3158 | 944062.6656 | 621140.2138 | 391061.0352 | 2685164.5968 |  | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 |  | 155705.9175 | 543013.1739 | 1074875.4013 | 368178.5494 | 673787.6104 | 2815560.6524
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 313807 | 310328.5 |  | 50304 | 158234 | 82171 | 21650 | 1448 |  | 44998 | 157737 | 82173 | 22091 | 7478 |  | 13473.062 | 66 | -94.45 | -7536.1199 | -7587.4921 |  | 34863 | 125195 | 95392 | 49327 | 9031 |  | 24320.0033 | 337 | -116.45 | -9539.5191 | -18479.5342 |  | 23791 | 112928 | 92300 | 61502 | 23287 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 |  | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 |  | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 |  | 1500912.9365 | 4521311.529 | 11276904.6835 | 7974370.2681 | 1085058.1014 | 26358557.5185 |  | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 |  | 1440511.5341 | 4133302.2044 | 11621996.6774 | 9595856.2598 | 2203557.4509 | 28995224.1266
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 | LV Network | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 598337.4466 | 1370463.9934 | 3475158.0245 | 4621113.7662 | 331232.7265 | 10396305.9572 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 | LV Network | 647962.8324 | 1182549.5663 | 3045339.0362 | 6231754.0963 | 504971.2768 | 11612576.808
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 | HV Network | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 | HV Network | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 | HV Network | 559650.8854 | 1988951.0413 | 5380523.0757 | 2270724.4438 | 101616.1969 | 10301465.643 | HV Network | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 | HV Network | 486369.6245 | 1903561.9461 | 5638849.1663 | 2462324.9962 | 691463.5616 | 11182569.2947
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 | EHV Network | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 | EHV Network | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 | EHV Network | 156956.2381 | 618964.1785 | 1477160.9178 | 461391.8443 | 261148.1428 | 2975621.3215 | EHV Network | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 | EHV Network | 150473.1597 | 504177.5181 | 1862933.0736 | 533598.6179 | 333335.0021 | 3384517.3715
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 | 132kV Network | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 185968.3665 | 542932.3158 | 944062.6656 | 621140.2138 | 391061.0352 | 2685164.5968 | 132kV Network | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 | 132kV Network | 155705.9175 | 543013.1739 | 1074875.4013 | 368178.5494 | 673787.6104 | 2815560.6524
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 | Total | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 | Total | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 | Total | 1500912.9365 | 4521311.529 | 11276904.6835 | 7974370.2681 | 1085058.1014 | 26358557.5185 | Total | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 | Total | 1440511.5341 | 4133302.2044 | 11621996.6774 | 9595856.2598 | 2203557.4509 | 28995224.1266
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SPN - Asset Rep
Secondary deliverables RIIO-ED1 - Asset Replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 1 | 1 | C1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | C1 | 8.3151 | 19.0395 | 58.9198 | 96.0302 | 154.2283 | C1 | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198
|  |  | 13779 | 13779 | C2 | 1531 | 1533 | 9111 | 1558 | 46 | 13779 | 1486 | 1347 | 9111 | 1558 | 91 | 13593 | 363 | 0 | 0 | -287 | -76 | 0 | 961 | 1371 | 9146 | 2111 | 190 | 13779 | 695 | 0 | 0 | -559 | -136 | 0 | 45 | 1480 | 8545 | 3378 | 331 | 13779 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10983 | 10983 | 10983 | 10983 | 10983 | C2 | 11.8787 | 27.1994 | 84.1712 | 137.186 | 220.3262 | C2 | 17651.8005 | 36637.5281 | 766883.8029 | 213735.7565 | 20049.6801 | 1054958.5681 |  | 18186.3436 | 41696.6077 | 766883.8029 | 213735.7565 | 10135.0031 | 1050637.5138 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 15727.4454 | 37290.3125 | 769829.7949 | 250227.2272 | 25117.1816 | 1098191.9616 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857 |  | 8790.2641 | 40255.042 | 719242.9037 | 386727.2771 | 42963.6001 | 1197979.0869
|  |  | 6600 | 6600 | C3 | 644 | 1451 | 3831 | 655 | 19 | 6600 | 590 | 1451 | 3831 | 655 | 73 | 6600 | 252 | 0 | 0 | -246 | -6 | 0 | 434 | 1445 | 3801 | 877 | 43 | 6600 | 503 | 0 | 0 | -479 | -24 | 0 | 54 | 1489 | 3551 | 1404 | 102 | 6600 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | C3 | 17.8181 | 40.799 | 126.2568 | 205.779 | 330.4892 | C3 | 10512.6807 | 59199.3911 | 483689.8006 | 134785.2252 | 24125.7139 | 712312.8115 |  | 11474.8582 | 59199.3911 | 483689.8006 | 134785.2252 | 6279.2954 | 695428.5705 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 12223.2185 | 58954.597 | 479902.0966 | 129846.5299 | 12228.1016 | 693154.5436 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035 |  | 9924.6833 | 60749.7542 | 448337.8966 | 190345.547 | 25778.1601 | 735136.0412
|  |  | 606 | 606 | C4 | 59 | 133 | 352 | 60 | 2 | 606 | 54 | 133 | 352 | 60 | 7 | 606 | 12 | 0 | 0 | -12 | 0 | 0 | 40 | 132 | 349 | 81 | 4 | 606 | 24 | 0 | 0 | -22 | -2 | 0 | 5 | 137 | 326 | 129 | 9 | 606 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | C4 | 29.6968 | 67.9984 | 210.428 | 342.9649 | 550.8154 | C4 | 1603.6293 | 9043.7848 | 74070.656 | 20577.897 | 3855.7077 | 109151.6747 |  | 1752.1134 | 9043.7848 | 74070.656 | 20577.897 | 1101.6308 | 106546.0819 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 1544.2356 | 8975.7864 | 73439.372 | 23664.5815 | 2203.2615 | 109827.237 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074 |  | 861.2083 | 9315.7783 | 68599.528 | 36697.2496 | 3855.7077 | 119329.4719
|  |  | 20986 | 20986 |  | 2234 | 3117 | 13295 | 2273 | 67 |  | 2130 | 2931 | 13295 | 2273 | 171 |  | 627 | 0 | 0 | -545 | -82 |  | 1435 | 2948 | 13297 | 3069 | 237 |  | 1222 | 0 | 0 | -1060 | -162 |  | 104 | 3106 | 12423 | 4911 | 442 | [22 empty] | 29768.1104 | 104880.704 | 1324703.1793 | 369098.8787 | 48031.1017 | 1876481.9741 |  | 31413.3153 | 109939.7836 | 1324703.1793 | 369098.8787 | 17515.9293 | 1852671.0861 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 29494.8995 | 105220.6959 | 1323230.1833 | 403738.3386 | 39548.5447 | 1901232.662 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165 |  | 19576.1556 | 110320.5745 | 1236239.2482 | 613770.0737 | 72597.4679 | 2052503.5198
| LV UGB |  | 677 | 677 | C1 | 91 | 126 | 187 | 258 | 15 | 677 | 86 | 126 | 187 | 258 | 20 | 677 | 13 | 0 | 0 | 0 | -13 | 0 | 55 | 73 | 135 | 384 | 30 | 677 | 29 | 0 | 0 | 0 | -29 | 0 | 46 | 33 | 66 | 485 | 46 | 676 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | C1 | 11.0956 | 16.6433 | 55.4778 | 122.0512 | 238.5547 | C1 | 954.2186 | 2097.0618 | 10374.3535 | 31489.2142 | 4771.0931 | 49685.9412 |  | 1009.6964 | 2097.0618 | 10374.3535 | 31489.2142 | 3578.3198 | 48548.6457 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 754.4984 | 1214.9644 | 7489.5065 | 46867.6676 | 4055.4291 | 60382.066 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176 |  | 832.1674 | 549.2305 | 3661.5365 | 59194.8406 | 4055.4291 | 68293.2041
|  |  | 19687 | 19687 | C2 | 2638 | 3677 | 5444 | 7503 | 425 | 19687 | 2493 | 3677 | 5444 | 7503 | 569 | 19686 | 2284 | 0 | 0 | -1898 | -386 | 0 | 1594 | 2136 | 3923 | 11170 | 863 | 19686 | 2738 | 0 | 0 | -1898 | -840 | 0 | 1334 | 963 | 1930 | 14111 | 1350 | 19688 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11057 | 11057 | 11057 | 11057 | 11057 | C2 | 15.8508 | 23.7762 | 79.254 | 174.3589 | 340.7924 | C2 | 39516.0631 | 87425.1287 | 431458.9798 | 1308214.6945 | 193910.8534 | 2060525.7195 |  | 41814.4302 | 87425.1287 | 431458.9798 | 1308214.6945 | 144836.7534 | 2013749.9866 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 61469.4314 | 50785.9872 | 310913.5889 | 1616655.5574 | 162557.9562 | 2202382.5211 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375 |  | 64544.4881 | 22896.4914 | 152960.2923 | 2129445.0305 | 173804.1041 | 2543650.4064
|  |  | 4474 | 4474 | C3 | 599 | 836 | 1237 | 1705 | 97 | 4474 | 567 | 836 | 1237 | 1705 | 129 | 4474 | 828 | 0 | 0 | -740 | -88 | 0 | 362 | 486 | 892 | 2539 | 196 | 4475 | 931 | 0 | 0 | -740 | -191 | 0 | 303 | 219 | 439 | 3207 | 307 | 4475 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | C3 | 23.7762 | 35.6643 | 118.8811 | 261.5383 | 511.1885 | C3 | 13481.1118 | 29815.3689 | 147055.8665 | 445922.8417 | 65943.3219 | 702218.5107 |  | 14241.9505 | 29815.3689 | 147055.8665 | 445922.8417 | 49585.2885 | 686621.3161 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 28293.6914 | 17332.858 | 106041.9021 | 470507.4441 | 55208.3625 | 677384.258 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747 |  | 29339.8447 | 7810.4854 | 52188.7837 | 645215.0442 | 59297.8708 | 793852.0288
|  |  | 3369 | 3369 | C4 | 451 | 629 | 932 | 1284 | 73 | 3369 | 427 | 629 | 932 | 1284 | 97 | 3369 | 623 | 0 | 0 | -557 | -66 | 0 | 273 | 366 | 671 | 1912 | 148 | 3370 | 1226 | 0 | 0 | -1082 | -144 | 0 | 228 | 165 | 330 | 2415 | 231 | 3369 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | C4 | 39.627 | 59.4405 | 198.1351 | 435.8972 | 851.9809 | C4 | 16920.737 | 37388.0922 | 184661.9072 | 559692.0124 | 82642.1475 | 881304.8964 |  | 17871.7854 | 37388.0922 | 184661.9072 | 559692.0124 | 62194.6059 | 861808.4032 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 35505.8088 | 21755.2333 | 132948.6478 | 590640.7141 | 69862.434 | 850712.8379 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691 |  | 57617.6852 | 9807.6871 | 65384.5809 | 581050.9755 | 74122.3385 | 787983.2673
|  |  | 28207 | 28207 |  | 3779 | 5268 | 7800 | 10750 | 610 |  | 3573 | 5268 | 7800 | 10750 | 815 |  | 3748 | 0 | 0 | -3195 | -553 |  | 2284 | 3061 | 5621 | 16005 | 1237 |  | 4924 | 0 | 0 | -3720 | -1204 |  | 1911 | 1380 | 2765 | 20218 | 1934 | [22 empty] | 70872.1304 | 156725.6516 | 773551.1071 | 2345318.7627 | 347267.4159 | 3693735.0677 |  | 74937.8626 | 156725.6516 | 773551.1071 | 2345318.7627 | 260194.9676 | 3610728.3516 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 126023.43 | 91089.0429 | 557393.6453 | 2724671.3831 | 291684.1818 | 3790861.6831 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711 |  | 152334.1854 | 41063.8944 | 274195.1933 | 3414905.8908 | 311279.7425 | 4193778.9065
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | C1 | 14.8033 | 14.8033 | 29.7404 | 81.901 | 162.3867 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 124969 | 124969 | C2 | 21863 | 72930 | 26079 | 4097 | 0 | 124969 | 19674 | 73119 | 26079 | 4097 | 2189 | 125158 | 4322 | 0 | 0 | -1366 | -2956 | 0 | 16316 | 54726 | 37003 | 13968 | 2956 | 124969 | 8656 | 0 | 0 | -1366 | -7290 | 0 | 13510 | 48074 | 35619 | 19954 | 7812 | 124969 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13911 | 13911 | 13911 | 13911 | 13911 | C2 | 21.1475 | 21.1475 | 42.4864 | 117.0014 | 231.981 | C2 | 416056.8929 | 1546287.6868 | 1108001.6864 | 479354.7947 | 507806.3433 | 4057507.4041 |  | 462348.8792 | 1542290.7999 | 1108001.6864 | 479354.7947 | 0 | 3591996.1602 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 436443.1308 | 1157320.8051 | 1572122.6429 | 1474451.8239 | 0 | 4640338.4027 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865 |  | 468756.5867 | 1016647.3045 | 1513321.5257 | 2174822.2903 | 121094.0663 | 5294641.7736
|  |  | 1184 | 1184 | C3 | 143 | 852 | 189 | 0 | 0 | 1184 | 124 | 852 | 189 | 0 | 19 | 1184 | 58 | 0 | 0 | -28 | -30 | 0 | 143 | 529 | 350 | 132 | 30 | 1184 | 104 | 0 | 0 | -28 | -76 | 0 | 126 | 456 | 337 | 189 | 76 | 1184 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | C3 | 31.7213 | 31.7213 | 63.7295 | 175.5021 | 347.9715 | C3 | 3933.4442 | 27026.5685 | 12044.882 | 0 | 6611.4576 | 49616.3524 |  | 4536.1494 | 27026.5685 | 12044.882 | 0 | 0 | 43607.6 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 6375.9862 | 16780.5807 | 22305.3371 | 18252.2206 | 0 | 63714.1246 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956 |  | 7295.9046 | 14464.924 | 21476.8531 | 28255.8416 | 0 | 71493.5233
|  |  | 2 | 2 | C4 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | C4 | 52.8689 | 52.8689 | 106.2159 | 292.5035 | 579.9524 | C4 | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848
|  |  | 126155 | 126155 |  | 22006 | 73783 | 26269 | 4097 | 0 |  | 19798 | 73972 | 26269 | 4097 | 2208 |  | 4380 | 0 | 0 | -1394 | -2986 |  | 16459 | 55256 | 37354 | 14100 | 2986 |  | 8760 | 0 | 0 | -1394 | -7366 |  | 13636 | 48531 | 35957 | 20143 | 7888 | [22 empty] | 419990.3371 | 1573367.1242 | 1120152.7843 | 479354.7947 | 514417.8009 | 4107282.8413 |  | 466885.0286 | 1569370.2373 | 1120152.7843 | 479354.7947 | 0 | 3635762.845 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 442819.117 | 1174154.2547 | 1594534.1958 | 1492704.0445 | 0 | 4704211.6121 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669 |  | 476052.4914 | 1031165.0974 | 1534904.5947 | 2203078.1319 | 121094.0663 | 5366294.3817
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 |  | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 598337.4466 | 1370463.9934 | 3475158.0245 | 4621113.7662 | 331232.7265 | 10396305.9572 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 |  | 647962.8324 | 1182549.5663 | 3045339.0362 | 6231754.0963 | 504971.2768 | 11612576.808
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1843 | 1843 | C1 | 494 | 947 | 398 | 4 | 0 | 1843 | 477 | 947 | 398 | 20 | 1 | 1843 | 87 | 0 | 0 | -84 | -3 | 0 | 437 | 678 | 538 | 183 | 7 | 1843 | 179 | 0 | 0 | -145 | -34 | 0 | 211 | 638 | 620 | 336 | 38 | 1843 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | C1 | 58.7072 | 58.7072 | 219.7445 | 403.678 | 555.67 | C1 | 28003.3423 | 55595.734 | 87458.3248 | 8073.5593 | 555.67 | 179686.6303 |  | 29001.3649 | 55595.734 | 87458.3248 | 1614.7119 | 0 | 173670.1356 |  | 25655.0536 | 39803.4928 | 118222.5596 | 73873.068 | 3889.6899 | 261443.8638 |  | 30762.5814 | 39803.4928 | 118222.5596 | 39964.1187 | 2222.6799 | 230975.4325 |  | 12387.2227 | 37455.2041 | 136241.6114 | 135635.7969 | 21115.4594 | 342835.2945 |  | 22895.8144 | 37455.2041 | 136241.6114 | 77102.4917 | 2222.6799 | 275917.8016
|  |  | 829 | 836 | C2 | 99 | 627 | 103 | 0 | 0 | 829 | 98 | 533 | 103 | 11 | 1 | 746 | 54 | 0 | 0 | -47 | 0 | 7 | 74 | 427 | 222 | 106 | 0 | 829 | 89 | 0 | 0 | -70 | -12 | 7 | 40 | 270 | 358 | 149 | 12 | 829 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | C2 | 83.8675 | 83.8675 | 313.9208 | 576.6828 | 793.8143 | C2 | 8219.0103 | 44701.352 | 32333.8387 | 6343.5109 | 793.8143 | 92391.5261 |  | 8302.8778 | 52584.8925 | 32333.8387 | 0 | 0 | 93221.6089 |  | 6206.1915 | 35811.402 | 69690.4095 | 61128.3779 | 0 | 172836.3809 |  | 10735.0339 | 35811.402 | 69690.4095 | 34024.2858 | 0 | 150261.1312 |  | 3354.6981 | 22644.2121 | 112383.6334 | 85925.7387 | 9525.7711 | 233834.0534 |  | 10818.9013 | 22644.2121 | 112383.6334 | 45557.942 | 0 | 191404.6888
|  |  | 317 | 317 | C3 | 44 | 244 | 29 | 0 | 0 | 317 | 44 | 244 | 29 | 0 | 0 | 317 | 14 | 0 | 0 | -14 | 0 | 0 | 38 | 181 | 50 | 48 | 0 | 317 | 28 | 0 | 0 | -25 | -3 | 0 | 20 | 102 | 135 | 57 | 3 | 317 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | C3 | 125.8012 | 125.8012 | 470.8811 | 865.0242 | 1190.7214 | C3 | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 4780.4448 | 22770.0132 | 23544.0573 | 41521.1623 | 0 | 92615.6776 |  | 6541.6613 | 22770.0132 | 23544.0573 | 29410.8233 | 0 | 82266.5551 |  | 2516.0236 | 12831.7202 | 63568.9546 | 49306.3803 | 3572.1642 | 131795.2428 |  | 6038.4566 | 12831.7202 | 63568.9546 | 27680.7749 | 0 | 110119.9062
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | C4 | 209.6686 | 209.6686 | 784.8019 | 1441.707 | 1984.5357 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2989 | 2996 |  | 637 | 1818 | 530 | 4 | 0 |  | 619 | 1724 | 530 | 31 | 2 |  | 155 | 0 | 0 | -145 | -3 |  | 549 | 1286 | 810 | 337 | 7 |  | 296 | 0 | 0 | -240 | -49 |  | 271 | 1010 | 1113 | 542 | 53 | [22 empty] | 41757.6044 | 130992.5734 | 133447.7166 | 14417.0703 | 1349.4842 | 321964.449 |  | 42839.4945 | 138876.1139 | 133447.7166 | 1614.7119 | 0 | 316778.037 |  | 36641.6898 | 98384.9081 | 211457.0264 | 176522.6082 | 3889.6899 | 526895.9223 |  | 48039.2766 | 98384.9081 | 211457.0264 | 103399.2279 | 2222.6799 | 463503.1188 |  | 18257.9443 | 72931.1363 | 312194.1994 | 270867.9159 | 34213.3947 | 708464.5907 |  | 39753.1723 | 72931.1363 | 312194.1994 | 150341.2086 | 2222.6799 | 577442.3966
| HV Switchgear (GM) - Distribution |  | 4606 | 4592 | C1 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 1477 | 2931 | 42 | 88 | 68 | 4606 | 0 | 0 | 0 | 0 | -14 | -14 | 268 | 4101 | 52 | 28 | 157 | 4606 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | C1 | 13.6425 | 13.6425 | 51.2806 | 94.0237 | 160.8309 | C1 | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 22998.8235 | 87902.1128
|  |  | 22477 | 19345 | C2 | 5578 | 7761 | 6551 | 2065 | 522 | 22477 | 4662 | 7508 | 6551 | 2291 | 2419 | 23431 | 1343 | 0 | -91 | -571 | -2251 | -1570 | 4507 | 8127 | 1170 | 6052 | 2621 | 22477 | 2681 | 0 | -91 | -571 | -5151 | -3132 | 2324 | 9700 | 1039 | 1616 | 7798 | 22477 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | C2 | 19.4893 | 19.4893 | 73.2581 | 134.3195 | 229.7585 | C2 | 90858.975 | 146325.4364 | 479913.5676 | 307726.0048 | 555785.7551 | 1580609.7388 |  | 108711.146 | 151256.2216 | 479913.5676 | 277369.7948 | 119933.9248 | 1137184.6548 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 114012.2273 | 158389.2943 | 79045.4495 | 736205.252 | 85010.6364 | 1172662.8594 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394 |  | 97543.7945 | 189045.9154 | 69448.6433 | 140363.8913 | 608170.6877 | 1104572.9322
|  |  | 585 | 389 | C3 | 91 | 195 | 229 | 49 | 21 | 585 | 91 | 195 | 229 | 49 | 21 | 585 | 80 | 0 | 0 | -15 | -163 | -98 | 2 | 137 | 98 | 175 | 173 | 585 | 161 | 0 | 0 | -15 | -342 | -196 | 0 | 105 | 74 | 44 | 362 | 585 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | C3 | 29.2339 | 29.2339 | 109.8871 | 201.4793 | 344.6377 | C3 | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 2397.1802 | 4005.0449 | 10768.9352 | 32236.6832 | 3446.3772 | 52854.2206 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456 |  | 4706.6586 | 3069.56 | 8131.6449 | 5842.8988 | 6892.7543 | 28643.5166
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | C4 | 48.7232 | 48.7232 | 183.1452 | 335.7988 | 574.3962 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27668 | 24326 |  | 8838 | 9250 | 6897 | 2136 | 547 |  | 7922 | 8997 | 6897 | 2362 | 2444 |  | 1423 | 0 | -91 | -586 | -2414 |  | 5986 | 11195 | 1310 | 6315 | 2862 |  | 2842 | 0 | -91 | -586 | -5507 |  | 2592 | 13906 | 1165 | 1688 | 8317 | [22 empty] | 136752.3071 | 169679.4282 | 511077.5474 | 319667.0095 | 563666.4708 | 1700842.763 |  | 154604.4781 | 174610.2134 | 511077.5474 | 289310.7995 | 127814.6406 | 1257417.679 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 136559.3634 | 202380.4737 | 91968.1717 | 776716.0171 | 99393.517 | 1307017.5429 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309 |  | 105906.6401 | 248063.3217 | 80246.8817 | 148839.4526 | 638062.2656 | 1221118.5616
| HV Transformer (GM) |  | 9731 | 9731 | C1 | 1332 | 2840 | 5559 | 0 | 0 | 9731 | 1259 | 2840 | 5559 | 62 | 11 | 9731 | 169 | 0 | 0 | -169 | 0 | 0 | 730 | 3228 | 5574 | 199 | 0 | 9731 | 338 | 0 | 0 | -338 | 0 | 0 | 139 | 3457 | 5717 | 418 | 0 | 9731 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | C1 | 45.0878 | 54.95 | 154.9879 | 295.6111 | 498.624 | C1 | 56765.5022 | 156058.1406 | 861577.5631 | 18327.889 | 5484.864 | 1098213.959 |  | 60056.9094 | 156058.1406 | 861577.5631 | 0 | 0 | 1077692.6132 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 40533.9051 | 177378.7598 | 863902.3812 | 8868.3334 | 0 | 1090683.3795 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129 |  | 21506.8662 | 189962.3212 | 886065.6464 | 23648.889 | 0 | 1121183.7229
|  |  | 5287 | 5287 | C2 | 651 | 1916 | 2720 | 0 | 0 | 5287 | 595 | 1714 | 2720 | 50 | 6 | 5085 | 91 | 0 | 0 | -91 | 0 | 0 | 382 | 1888 | 2913 | 104 | 0 | 5287 | 182 | 0 | 0 | -182 | 0 | 0 | 72 | 2009 | 2988 | 218 | 0 | 5287 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | C2 | 64.4111 | 78.5001 | 221.4112 | 422.3016 | 712.32 | C2 | 38324.6044 | 134549.1212 | 602238.5762 | 21115.0795 | 4273.92 | 800501.3013 |  | 41931.626 | 150406.1355 | 602238.5762 | 0 | 0 | 794576.3377 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 30466.4502 | 148208.1336 | 644970.9458 | 5489.9207 | 0 | 829135.4502 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768 |  | 16360.4193 | 157706.6421 | 661576.7889 | 15202.8572 | 0 | 850846.7076
|  |  | 4141 | 4141 | C3 | 566 | 1209 | 2366 | 0 | 0 | 4141 | 518 | 1209 | 2366 | 43 | 5 | 4141 | 74 | 0 | 0 | -74 | 0 | 0 | 311 | 1374 | 2370 | 86 | 0 | 4141 | 148 | 0 | 0 | -148 | 0 | 0 | 59 | 1471 | 2433 | 178 | 0 | 4141 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | C3 | 96.6166 | 117.7501 | 332.1169 | 633.4524 | 1068.48 | C3 | 50047.4245 | 142359.8783 | 785788.4953 | 27238.4526 | 5342.4 | 1010776.6506 |  | 54685.0237 | 142359.8783 | 785788.4953 | 0 | 0 | 982833.3973 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 37197.4101 | 161788.6458 | 787116.9627 | 7601.4286 | 0 | 993704.4472 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638 |  | 19999.6465 | 173210.4061 | 808040.325 | 19003.5716 | 0 | 1020253.9491
|  |  | 2071 | 2071 | C4 | 283 | 605 | 1183 | 0 | 0 | 2071 | 260 | 605 | 1183 | 21 | 2 | 2071 | 37 | 0 | 0 | -37 | 0 | 0 | 155 | 687 | 1186 | 43 | 0 | 2071 | 74 | 0 | 0 | -74 | 0 | 0 | 30 | 736 | 1216 | 89 | 0 | 2071 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | C4 | 161.0277 | 196.2502 | 553.5281 | 1055.754 | 1780.8 | C4 | 41867.2149 | 118731.357 | 654823.746 | 22170.8335 | 3561.6 | 841154.7514 |  | 45570.8531 | 118731.357 | 654823.746 | 0 | 0 | 819125.9561 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 30917.3279 | 134823.8715 | 656484.3304 | 6334.5239 | 0 | 828560.0536 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399 |  | 16746.8859 | 144440.1302 | 673090.1735 | 15836.3096 | 0 | 850113.4992
|  |  | 21230 | 21230 |  | 2832 | 6570 | 11828 | 0 | 0 |  | 2632 | 6368 | 11828 | 176 | 24 |  | 371 | 0 | 0 | -371 | 0 |  | 1578 | 7177 | 12043 | 432 | 0 |  | 742 | 0 | 0 | -742 | 0 |  | 300 | 7673 | 12354 | 903 | 0 | [22 empty] | 187004.746 | 551698.4971 | 2904428.3807 | 88852.2546 | 18662.7838 | 3750646.6623 |  | 202244.4122 | 567555.5114 | 2904428.3807 | 0 | 0 | 3674228.3044 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 139115.0933 | 622199.4107 | 2952474.6201 | 28294.2065 | 0 | 3742083.3306 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676 |  | 74613.818 | 665319.4995 | 3028772.9338 | 73691.6275 | 0 | 3842397.8788
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 9772 | 9772 | C1 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 393 | 0 | 0 | 0 | -393 | 0 | 558 | 5094 | 2706 | 1021 | 393 | 9772 | 514 | 0 | 0 | 0 | -514 | 0 | 382 | 4298 | 2825 | 1534 | 733 | 9772 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | C1 | 19.1659 | 19.1659 | 72.1182 | 151.5867 | 233.6923 | C1 | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 18226.7282 | 97630.8658 | 195151.8933 | 154770.0352 | 0 | 465779.5225 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464 |  | 17172.6062 | 82374.8452 | 203733.9611 | 232534.0195 | 51178.6161 | 586994.0481
|  |  | 39560 | 39560 | C2 | 4761 | 27072 | 6789 | 938 | 0 | 39560 | 3776 | 27093 | 6789 | 938 | 985 | 39581 | 605 | 0 | 0 | 0 | -605 | 0 | 3243 | 20614 | 10962 | 4136 | 605 | 39560 | 1983 | 0 | 0 | 0 | -1983 | 0 | 2533 | 17389 | 11440 | 6215 | 1983 | 39560 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | C2 | 27.3798 | 27.3798 | 103.026 | 216.5524 | 333.8462 | C2 | 103386.0983 | 741800.7314 | 699443.6721 | 203126.197 | 328838.4663 | 2076595.1651 |  | 130355.1944 | 741225.7558 | 699443.6721 | 203126.197 | 0 | 1774150.8193 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 105357.4434 | 564407.0527 | 1129371.2673 | 895660.9283 | 0 | 2694796.6917 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443 |  | 123647.1451 | 476107.2203 | 1178617.7065 | 1345873.4694 | 0 | 3124245.5412
|  |  | 18629 | 18629 | C3 | 2618 | 12458 | 3162 | 391 | 0 | 18629 | 2100 | 12458 | 3162 | 391 | 518 | 18629 | 1148 | 0 | 0 | -917 | -231 | 0 | 1581 | 9711 | 5159 | 1947 | 231 | 18629 | 1796 | 0 | 0 | -917 | -879 | 0 | 1246 | 8194 | 5385 | 2925 | 879 | 18629 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | C3 | 41.0697 | 41.0697 | 154.539 | 324.8287 | 500.7692 | C3 | 86246.3479 | 511646.1916 | 488652.4285 | 127008.0112 | 259398.4653 | 1472951.4445 |  | 107520.4471 | 511646.1916 | 488652.4285 | 127008.0112 | 0 | 1234827.0783 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 112079.1826 | 398827.7546 | 797266.8812 | 334573.5334 | 0 | 1642747.3518 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012 |  | 124933.9954 | 336525.0356 | 832192.7031 | 652255.9758 | 0 | 1945907.71
|  |  | 41 | 41 | C4 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 0 | 0 | 0 | -2 | 0 | 2 | 22 | 11 | 4 | 2 | 41 | 3 | 0 | 0 | 0 | -3 | 0 | 2 | 18 | 12 | 6 | 3 | 41 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | C4 | 68.4495 | 68.4495 | 257.5651 | 541.3811 | 834.6154 | C4 | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 273.7979 | 1505.8886 | 2833.2156 | 2165.5245 | 0 | 6778.4267 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033 |  | 342.2474 | 1232.0907 | 3090.7807 | 3248.2867 | 0 | 7913.4055
|  |  | 68002 | 68002 |  | 8123 | 46800 | 11571 | 1508 | 0 |  | 6620 | 46821 | 11571 | 1508 | 1503 |  | 2148 | 0 | 0 | -917 | -1231 |  | 5384 | 35441 | 18838 | 7108 | 1231 |  | 4296 | 0 | 0 | -917 | -3379 |  | 4163 | 29899 | 19662 | 10680 | 3598 | [22 empty] | 203990.4097 | 1394704.751 | 1304927.611 | 357268.2301 | 588236.9315 | 3849127.9333 |  | 252233.6049 | 1394129.7753 | 1304927.611 | 357268.2301 | 0 | 3308559.2213 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 235937.1521 | 1062371.5617 | 2124623.2575 | 1387170.0214 | 0 | 4810101.9927 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952 |  | 266095.9941 | 896239.1918 | 2217635.1514 | 2233911.7515 | 51178.6161 | 5665060.7048
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 |  | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 |  | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 |  | 559650.8854 | 1985336.3541 | 5380523.0757 | 2295579.4729 | 101616.1969 | 10322705.985 |  | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 |  | 486369.6245 | 1882553.1493 | 5638849.1663 | 2606784.0401 | 691463.5616 | 11306019.5418
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 217 | 217 | C1 | 136 | 76 | 5 | 0 | 0 | 217 | 136 | 76 | 5 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 71 | 13 | 2 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 117 | 18 | 2 | 0 | 217 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | C1 | 165.6424 | 165.6424 | 625.0091 | 1143.9769 | 1952.7416 | C1 | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772
|  |  | 505 | 505 | C2 | 153 | 280 | 69 | 3 | 0 | 505 | 153 | 271 | 69 | 3 | 0 | 496 | 12 | 0 | 0 | 0 | -12 | 0 | 112 | 227 | 143 | 11 | 12 | 505 | 12 | 0 | 0 | 0 | -12 | 0 | 74 | 190 | 207 | 17 | 17 | 505 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | C2 | 236.6321 | 236.6321 | 892.8701 | 1634.2527 | 2789.6309 | C2 | 36204.7037 | 64127.2857 | 61608.0394 | 4902.758 | 0 | 166842.7867 |  | 36204.7037 | 66256.9741 | 61608.0394 | 4902.758 | 0 | 168972.4752 |  | 26502.7897 | 53715.4755 | 127680.4294 | 17976.7792 | 33475.5706 | 259351.0444 |  | 29342.3743 | 53715.4755 | 127680.4294 | 17976.7792 | 0 | 228715.0584 |  | 17510.7717 | 44960.0896 | 184824.1181 | 27782.2952 | 47423.725 | 322500.9996 |  | 20350.3563 | 44960.0896 | 184824.1181 | 27782.2952 | 13948.1544 | 291865.0136
|  |  | 70 | 70 | C3 | 8 | 54 | 8 | 0 | 0 | 70 | 8 | 54 | 8 | 0 | 0 | 70 | 5 | 0 | 0 | 0 | -5 | 0 | 8 | 41 | 16 | 0 | 5 | 70 | 5 | 0 | 0 | 0 | -5 | 0 | 5 | 32 | 26 | 2 | 5 | 70 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | C3 | 354.9481 | 354.9481 | 1339.3052 | 2451.379 | 4184.4463 | C3 | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 4614.325 | 14552.8711 | 21428.8833 | 0 | 0 | 40596.0793 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037 |  | 3549.4808 | 11358.3384 | 34821.9353 | 4902.758 | 0 | 54632.5125
|  |  | 6 | 6 | C4 | 2 | 3 | 1 | 0 | 0 | 6 | 2 | 3 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 6 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | C4 | 591.5801 | 591.5801 | 2232.1753 | 4085.6316 | 6974.0772 | C4 | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616
|  |  | 798 | 798 |  | 299 | 413 | 83 | 3 | 0 |  | 299 | 404 | 83 | 3 | 0 |  | 17 | 0 | 0 | 0 | -17 |  | 253 | 341 | 174 | 13 | 17 |  | 17 | 0 | 0 | 0 | -17 |  | 159 | 341 | 255 | 21 | 22 | [22 empty] | 62754.8198 | 97658.0472 | 77679.7018 | 4902.758 | 0 | 242995.3268 |  | 62754.8198 | 99787.7357 | 77679.7018 | 4902.758 | 0 | 245125.0153 |  | 52224.6935 | 81212.1197 | 161698.7816 | 20264.733 | 54397.8022 | 369798.13 |  | 56839.0185 | 81212.1197 | 161698.7816 | 20264.733 | 0 | 320014.6528 |  | 32536.9069 | 76881.7532 | 239824.9185 | 34973.0069 | 68345.9566 | 452562.5421 |  | 37151.2319 | 76881.7532 | 239824.9185 | 34973.0069 | 13948.1544 | 402779.0649
| EHV Transformer |  | 194 | 194 | C1 | 21 | 140 | 22 | 8 | 3 | 194 | 21 | 140 | 22 | 8 | 3 | 194 | 4 | 0 | 0 | -1 | -3 | 0 | 11 | 109 | 52 | 14 | 8 | 194 | 12 | 0 | 0 | -9 | -3 | 0 | 5 | 86 | 78 | 16 | 9 | 194 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | C1 | 890.0227 | 890.0227 | 3333.6634 | 6914.518 | 14150.0662 | C1 | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 9790.2493 | 97012.4705 | 173350.4943 | 96803.2517 | 113200.5292 | 490156.995 |  | 13350.34 | 97012.4705 | 173350.4943 | 89888.7337 | 70750.3308 | 444352.3692 |  | 4450.1133 | 76541.9492 | 260025.7415 | 110632.2876 | 127350.5954 | 579000.687 |  | 15130.3853 | 76541.9492 | 260025.7415 | 48401.6258 | 84900.3969 | 485000.0987
|  |  | 259 | 259 | C2 | 29 | 154 | 59 | 11 | 6 | 259 | 26 | 143 | 59 | 11 | 9 | 248 | 11 | 0 | 0 | -7 | -4 | 0 | 22 | 120 | 84 | 23 | 10 | 259 | 23 | 0 | 0 | -16 | -7 | 0 | 12 | 89 | 96 | 46 | 16 | 259 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | C2 | 1271.461 | 1271.461 | 4762.3762 | 9877.8828 | 20214.3802 | C2 | 33057.9847 | 181818.9159 | 280980.1968 | 108656.711 | 181929.422 | 786443.2304 |  | 36872.3676 | 195804.9863 | 280980.1968 | 108656.711 | 121286.2813 | 743600.5431 |  | 27972.1409 | 152575.314 | 400039.6022 | 227191.3049 | 202143.8022 | 1009922.1643 |  | 41958.2114 | 152575.314 | 400039.6022 | 158046.1251 | 121286.2813 | 873905.5341 |  | 15257.5314 | 113160.0246 | 457188.1168 | 454382.6098 | 323430.0835 | 1363418.3661 |  | 44501.1333 | 113160.0246 | 457188.1168 | 296336.4847 | 181929.422 | 1093115.1813
|  |  | 42 | 42 | C3 | 4 | 29 | 7 | 0 | 2 | 42 | 3 | 29 | 7 | 0 | 3 | 42 | 2 | 0 | 0 | -1 | -1 | 0 | 4 | 17 | 18 | 1 | 2 | 42 | 2 | 0 | 0 | -1 | -1 | 0 | 2 | 9 | 23 | 5 | 3 | 42 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | C3 | 1907.1914 | 1907.1914 | 7143.5643 | 14816.8242 | 30321.5703 | C3 | 5721.5743 | 55308.5513 | 50004.9503 | 0 | 90964.711 | 201999.7869 |  | 7628.7657 | 55308.5513 | 50004.9503 | 0 | 60643.1407 | 173585.408 |  | 7628.7657 | 32422.2542 | 128584.1579 | 14816.8242 | 60643.1407 | 244095.1427 |  | 11443.1486 | 32422.2542 | 128584.1579 | 0 | 30321.5703 | 202771.131 |  | 3814.3829 | 17164.7228 | 164301.9795 | 74084.1212 | 90964.711 | 350329.9173 |  | 7628.7657 | 17164.7228 | 164301.9795 | 59267.2969 | 60643.1407 | 309005.9056
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | C4 | 3178.6524 | 3178.6524 | 11905.9405 | 24694.7071 | 50535.9505 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 495 | 495 |  | 54 | 323 | 88 | 19 | 11 |  | 50 | 312 | 88 | 19 | 15 |  | 17 | 0 | 0 | -9 | -8 |  | 37 | 246 | 154 | 38 | 20 |  | 37 | 0 | 0 | -26 | -11 |  | 19 | 184 | 197 | 67 | 28 | [22 empty] | 57470.035 | 361730.6403 | 404325.7408 | 163972.8548 | 315344.3314 | 1302843.6024 |  | 63191.6092 | 375716.7108 | 404325.7408 | 163972.8548 | 224379.6204 | 1231586.5361 |  | 45391.1559 | 282010.0388 | 701974.2544 | 338811.3808 | 375987.4721 | 1744174.3019 |  | 66751.6999 | 282010.0388 | 701974.2544 | 247934.8588 | 222358.1824 | 1521029.0343 |  | 23522.0276 | 206866.6966 | 881515.8378 | 639099.0186 | 541745.3899 | 2292748.9704 |  | 67260.2843 | 206866.6966 | 881515.8378 | 404005.4074 | 327472.9595 | 1887121.1856
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | C1 | 74.7619 | 74.7619 | 280.2348 | 577.8137 | 1188.9171 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 199818 | 199818 | 199818 | 199818 | 199818 | C2 | 106.8027 | 106.8027 | 400.3354 | 825.4482 | 1698.453 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 0 | C3 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | -7 | -7 | 0 | 0 | 0 | 0 | 7 | 7 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 299727 | 299727 | 299727 | 299727 | 299727 | C3 | 160.2041 | 160.2041 | 600.503 | 1238.1722 | 2547.6795 | C3 | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 499545 | 499545 | 499545 | 499545 | 499545 | C4 | 267.0068 | 267.0068 | 1000.8384 | 2063.6204 | 4246.1325 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | -7 |  | 0 | 0 | 0 | 0 | 7 | [22 empty] | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 126 | 126 | C1 | 2 | 69 | 41 | 3 | 11 | 126 | 2 | 84 | 38 | 0 | 2 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 59 | 2 | 17 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 80 | 5 | 18 | 126 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | C1 | 116.2368 | 116.2368 | 435.6977 | 898.3615 | 1848.4805 | C1 | 232.4736 | 9763.8917 | 16556.5141 | 0 | 3696.9611 | 30249.8405 |  | 232.4736 | 8020.3396 | 17863.6073 | 2695.0846 | 20333.286 | 49144.7912 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233
|  |  | 175 | 166.5 | C2 | 3 | 96 | 56 | 5 | 15 | 175 | 3 | 117 | 51 | 5 | 5 | 181 | 0 | 0 | 0 | 0 | -5 | -5 | 0 | 67 | 82 | 3 | 23 | 175 | 0 | 0 | 0 | 0 | -8.5 | -8.5 | 0 | 34 | 111 | 6 | 24 | 175 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 310669 | 310669 | 310669 | 310669 | 310669 | C2 | 166.0526 | 166.0526 | 622.4253 | 1283.3736 | 2640.6865 | C2 | 498.1577 | 19428.1519 | 31743.6924 | 6416.8682 | 13203.4325 | 71290.3028 |  | 498.1577 | 15941.0477 | 34855.8191 | 6416.8682 | 39610.2975 | 97322.1903 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 47532.357 | 113546.8788 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 40930.6408 | 123365.8832
|  |  | 145 | 132 | C3 | 2 | 80 | 47 | 3 | 13 | 145 | 2 | 90 | 42 | 11 | 0 | 145 | 0 | 0 | -3.45 | 0 | -0.55 | -4 | 0 | 55 | 68 | 3 | 19 | 145 | 0 | 0 | -3.45 | 0 | -9.55 | -13 | 0 | 26 | 92 | 6 | 21 | 145 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | C3 | 249.0789 | 249.0789 | 933.638 | 1925.0605 | 3961.0298 | C3 | 498.1577 | 22417.0984 | 39212.7965 | 21175.665 | 0 | 83303.7177 |  | 498.1577 | 19926.3097 | 43880.9866 | 5775.1814 | 51493.3868 | 121574.0221 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 13699.3379 | 60266.3337 | 5775.1814 | 73080.9989 | 152821.8518 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353 |  | 0 | 6476.0506 | 82673.646 | 11550.3628 | 45353.7906 | 146053.85
|  |  | 13 | 11.3 | C4 | 0 | 8 | 4 | 0 | 1 | 13 | 0 | 9 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | -1.7 | -1.7 | 0 | 2 | 8 | 1 | 2 | 13 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | C4 | 415.1315 | 415.1315 | 1556.0634 | 3208.4341 | 6601.7163 | C4 | 0 | 3736.1831 | 6224.2534 | 0 | 0 | 9960.4365 |  | 0 | 3321.0516 | 6224.2534 | 0 | 6601.7163 | 16147.0213 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 1980.5149 | 18467.7187
|  |  | 459 | 435.8 |  | 7 | 253 | 148 | 11 | 40 |  | 7 | 300 | 135 | 16 | 7 |  | 0 | 0 | -3.45 | 0 | -5.55 |  | 0 | 175 | 215 | 8 | 61 |  | 0 | 0 | -3.45 | 0 | -19.75 |  | 0 | 85 | 291 | 18 | 65 | [22 empty] | 1228.7891 | 55345.3251 | 93737.2564 | 27592.5332 | 16900.3936 | 194804.2974 |  | 1228.7891 | 47208.7486 | 102824.6664 | 14887.1342 | 118038.6865 | 284188.0249 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 32479.8847 | 146347.7584 | 11422.0254 | 165240.9577 | 355490.6263 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134 |  | 0 | 15625.5478 | 199067.1848 | 26950.8464 | 121537.5962 | 363181.1753
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 338 | 338 | C1 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 208 | 16 | 12 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 189 | 25 | 22 | 338 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | C1 | 0 | 0 | 12.1985 | 42.3409 | 98.717 | C1 | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812
|  |  | 166 | 166 | C2 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 103 | 7 | 5 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 94 | 11 | 10 | 166 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 215767 | 215767 | 215767 | 215767 | 215767 | C2 | 0 | 0 | 17.4264 | 60.487 | 141.0242 | C2 | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834
|  |  | 15 | 15 | C3 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | C3 | 0 | 0 | 26.1396 | 90.7306 | 211.5363 | C3 | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236
|  |  | 56 | 56 | C4 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 3 | 2 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 5 | 4 | 56 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | C4 | 0 | 0 | 43.5661 | 151.2176 | 352.5606 | C4 | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312
|  |  | 575 | 575 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 354 | 27 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 322 | 42 | 37 | [22 empty] | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331
| EHV OHL Support - Poles |  | 673 | 673 | C1 | 61 | 499 | 96 | 11 | 6 | 673 | 61 | 499 | 96 | 11 | 6 | 673 | 20 | 0 | 0 | 0 | -20 | 0 | 27 | 355 | 210 | 61 | 20 | 673 | 45 | 0 | 0 | 0 | -45 | 0 | 24 | 279 | 245 | 80 | 45 | 673 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | C1 | 15.4993 | 15.4993 | 58.3259 | 122.6046 | 189.0162 | C1 | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 728.4661 | 5502.2441 | 12248.4379 | 7478.8805 | 0 | 25958.0286 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224 |  | 1069.4503 | 4324.2989 | 14289.8442 | 9808.3679 | 0 | 29491.9612
|  |  | 43 | 43 | C2 | 3 | 37 | 3 | 0 | 0 | 43 | 3 | 37 | 3 | 0 | 0 | 43 | 2 | 0 | 0 | 0 | -2 | 0 | 2 | 21 | 14 | 4 | 2 | 43 | 2 | 0 | 0 | 0 | -2 | 0 | 1 | 19 | 16 | 5 | 2 | 43 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 64595 | 64595 | 64595 | 64595 | 64595 | C2 | 22.1418 | 22.1418 | 83.3227 | 175.1494 | 270.0232 | C2 | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 88.5673 | 464.9784 | 1166.5179 | 700.5977 | 0 | 2420.6613 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934 |  | 66.4255 | 420.6947 | 1333.1633 | 875.7471 | 0 | 2696.0306
|  |  | 10397 | 10397 | C3 | 952 | 7695 | 1492 | 161 | 97 | 10397 | 847 | 7695 | 1492 | 161 | 202 | 10397 | 388 | 0 | 0 | -181 | -207 | 0 | 517 | 5488 | 3249 | 936 | 207 | 10397 | 769 | 0 | 0 | -181 | -588 | 0 | 472 | 4313 | 3785 | 1239 | 588 | 10397 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | C3 | 33.2127 | 33.2127 | 124.9841 | 262.7241 | 405.0348 | C3 | 28131.1917 | 255572.0426 | 186476.2173 | 42298.5864 | 81817.0254 | 594295.0634 |  | 31618.5295 | 255572.0426 | 186476.2173 | 42298.5864 | 39288.3736 | 555253.7494 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 30057.5307 | 182271.5231 | 406073.2105 | 198356.725 | 0 | 816758.9893 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911 |  | 41217.0117 | 143246.5523 | 473064.6666 | 277962.1392 | 0 | 935490.3697
|  |  | 638 | 638 | C4 | 58 | 473 | 91 | 10 | 6 | 638 | 58 | 473 | 91 | 10 | 6 | 638 | 20 | 0 | 0 | -1 | -19 | 0 | 25 | 338 | 199 | 57 | 19 | 638 | 44 | 0 | 0 | -1 | -43 | 0 | 23 | 264 | 232 | 76 | 43 | 638 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | C4 | 55.3546 | 55.3546 | 208.3068 | 437.8736 | 675.058 | C4 | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 2490.9556 | 18709.8441 | 41453.0465 | 24520.9197 | 0 | 87174.7659 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144 |  | 3708.7561 | 14613.6061 | 48327.1698 | 32840.5174 | 0 | 99490.0494
|  |  | 11751 | 11751 |  | 1074 | 8704 | 1682 | 182 | 109 |  | 969 | 8704 | 1682 | 182 | 214 |  | 430 | 0 | 0 | -182 | -248 |  | 571 | 6202 | 3672 | 1058 | 248 |  | 860 | 0 | 0 | -182 | -678 |  | 520 | 4875 | 4278 | 1400 | 678 | [22 empty] | 32353.6382 | 290308.1414 | 211281.3871 | 48025.9726 | 87001.4705 | 668970.6099 |  | 35840.976 | 290308.1414 | 211281.3871 | 48025.9726 | 44472.8187 | 629929.2959 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 33365.5197 | 206948.5897 | 460941.2128 | 231057.1229 | 0 | 932312.445 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229 |  | 46061.6435 | 162605.152 | 537014.8439 | 321486.7716 | 0 | 1067168.4109
| EHV OHL Fittings and Conductors (Tower Lines) |  | 64 | 64 | C1 | 1 | 0 | 8 | 42 | 13 | 64 | 0 | 0 | 8 | 42 | 14 | 64 | 2.9421 | 0 | 0 | 0 | -2.9421 | 0 | 1 | 0 | 8 | 33 | 22 | 64 | 5.8842 | 0 | 0 | 0 | -5.8842 | 0 | 1 | 0 | 2 | 12 | 49 | 64 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | C1 | 0 | 0 | 12.2256 | 39.8434 | 77.3125 | C1 | 0 | 0 | 97.8044 | 1673.4214 | 1082.3745 | 2853.6003 |  | 0 | 0 | 97.8044 | 1673.4214 | 1005.062 | 2776.2878 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 97.8044 | 1314.8311 | 1473.4136 | 2886.0491 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822 |  | 0 | 0 | 24.4511 | 478.1204 | 3333.3895 | 3835.961
|  |  | 18 | 18 | C2 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 3 | 11 | 4 | 18 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 0 | 3 | 8 | 7 | 18 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 0 | 0 | 4 | 14 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | C2 | 0 | 0 | 17.4651 | 56.9191 | 110.4464 | C2 | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 52.3952 | 455.3528 | 662.6783 | 1170.4262 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256 |  | 0 | 0 | 0 | 227.6764 | 1325.3565 | 1553.0329
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | C3 | 0 | 0 | 26.1976 | 85.3786 | 165.6696 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | C4 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | C4 | 0 | 0 | 43.6627 | 142.2977 | 276.1159 | C4 | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159
|  |  | 83 | 83 |  | 1 | 0 | 11 | 54 | 17 |  | 0 | 0 | 11 | 54 | 18 |  | 3.9421 | 0 | 0 | 0 | -3.9421 |  | 1 | 0 | 11 | 42 | 29 |  | 7.8842 | 0 | 0 | 0 | -7.8842 |  | 1 | 0 | 2 | 16 | 64 | [22 empty] | 0 | 0 | 150.1997 | 2441.8291 | 1524.16 | 4116.1888 |  | 0 | 0 | 150.1997 | 2441.8291 | 1446.8475 | 4038.8763 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 150.1997 | 1912.4816 | 2136.0918 | 4198.7731 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237 |  | 0 | 0 | 24.4511 | 705.7968 | 4934.8619 | 5665.1098
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 |  | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 |  | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 |  | 156956.2381 | 602650.6329 | 1477160.9178 | 522903.6748 | 392541.6142 | 3152213.0779 |  | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 |  | 150473.1597 | 461979.1496 | 1862933.0736 | 790692.5283 | 473097.3662 | 3739175.2775
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 128 | 128 | C1 | 56 | 56 | 9 | 7 | 0 | 128 | 56 | 53 | 9 | 10 | 0 | 128 | 3 | 0 | 0 | 0 | -3 | 0 | 29 | 76 | 5 | 8 | 10 | 128 | 11 | 0 | 0 | 0 | -11 | 0 | 2 | 99 | 6 | 1 | 20 | 128 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | C1 | 566.8931 | 566.8931 | 2163.712 | 3830.461 | 5875.081 | C1 | 31746.0137 | 30045.3344 | 19473.4083 | 38304.6103 | 0 | 119569.3666 |  | 31746.0137 | 31746.0137 | 19473.4083 | 26813.2272 | 0 | 109778.6628 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 18140.5792 | 43083.8757 | 10818.5601 | 30643.6882 | 41125.5673 | 143812.2706 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572 |  | 7369.6103 | 56122.4171 | 12982.2722 | 3830.461 | 52875.7293 | 133180.4899
|  |  | 91 | 91 | C2 | 14 | 52 | 9 | 15 | 1 | 91 | 7 | 29 | 9 | 23 | 4 | 72 | 8 | 0 | 0 | 0 | -8 | 0 | 9 | 55 | 5 | 2 | 20 | 91 | 12 | 0 | 0 | 0 | -12 | 0 | 9 | 51 | 1 | 0 | 30 | 91 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | C2 | 809.8473 | 809.8473 | 3091.0172 | 5472.0872 | 8392.9729 | C2 | 5668.931 | 23485.5714 | 27819.1546 | 125858.0053 | 33571.8916 | 216403.5539 |  | 11337.862 | 42112.059 | 27819.1546 | 82081.3078 | 8392.9729 | 171743.3563 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 13767.4039 | 44541.6008 | 15455.0859 | 10944.1744 | 100715.6749 | 185423.9399 |  | 7288.6256 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 303471.0417 |  | 17006.793 | 41302.2117 | 3091.0172 | 0 | 151073.5124 | 212473.5343
|  |  | 13 | 13 | C3 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 9 | 1 | 3 | 0 | 13 | 1 | 0 | 0 | 0 | -1 | 0 | 0 | 9 | 0 | 1 | 3 | 13 | 3 | 0 | 0 | 0 | -3 | 0 | 0 | 9 | 0 | 0 | 4 | 13 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | C3 | 1214.7709 | 1214.7709 | 4636.5258 | 8208.1308 | 12589.4594 | C3 | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 1214.7709 | 10932.9384 | 0 | 8208.1308 | 25178.9187 | 45534.7588 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758 |  | 3644.3128 | 10932.9384 | 0 | 0 | 12589.4594 | 27166.7105
|  |  | 2 | 2 | C4 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | C4 | 2024.6182 | 2024.6182 | 7727.543 | 13680.218 | 20982.4323 | C4 | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362
|  |  | 234 | 234 |  | 71 | 117 | 20 | 25 | 1 |  | 64 | 91 | 20 | 36 | 4 |  | 12 | 0 | 0 | 0 | -12 |  | 39 | 140 | 11 | 11 | 33 |  | 26 | 0 | 0 | 0 | -26 |  | 11 | 160 | 7 | 2 | 54 | [22 empty] | 39439.5629 | 64463.8441 | 59656.6316 | 188787.0079 | 33571.8916 | 385918.9382 |  | 45108.4939 | 84791.011 | 59656.6316 | 133518.9273 | 8392.9729 | 331468.0368 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 35147.3723 | 98558.4149 | 34001.189 | 49795.9934 | 167020.1609 | 384523.1305 |  | 8422.4118 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572037.2109 |  | 28020.7162 | 110382.1853 | 16073.2893 | 17510.679 | 216538.7011 | 388525.5709
| 132kV Transformer |  | 41 | 40 | C1 | 6 | 26 | 5 | 3 | 1 | 41 | 5 | 25 | 5 | 4 | 2 | 41 | 2 | 0 | 0 | -1 | -2 | -1 | 4 | 26 | 6 | 3 | 2 | 41 | 4 | 0 | 0 | -3 | -2 | -1 | 2 | 18 | 15 | 3 | 3 | 41 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | C1 | 2793.658 | 2793.658 | 10463.908 | 21703.7153 | 44415.0999 | C1 | 13968.29 | 69841.4502 | 52319.5402 | 86814.8611 | 88830.1998 | 311774.3413 |  | 16761.948 | 72635.1082 | 52319.5402 | 65111.1458 | 44415.0999 | 251242.8421 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 16761.948 | 72635.1082 | 62783.4482 | 43407.4305 | 0 | 195587.935 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262 |  | 16761.948 | 50285.8441 | 156958.6205 | 0 | 44415.0999 | 268421.5126
|  |  | 125 | 125 | C2 | 19 | 79 | 24 | 1 | 2 | 125 | 18 | 75 | 24 | 3 | 3 | 123 | 3 | 0 | 0 | -3 | 0 | 0 | 12 | 70 | 35 | 6 | 2 | 125 | 5 | 0 | 0 | -5 | 0 | 0 | 7 | 67 | 34 | 15 | 2 | 125 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469152 | 469152 | 469152 | 469152 | 469152 | C2 | 3990.94 | 3990.94 | 14948.44 | 31005.3075 | 63450.1427 | C2 | 71836.9202 | 299320.5007 | 358762.5611 | 93015.9226 | 190350.4282 | 1013286.3329 |  | 75827.8602 | 315284.2608 | 358762.5611 | 31005.3075 | 126900.2855 | 907780.2751 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 59864.1001 | 279365.8007 | 523195.4017 | 93015.9226 | 126900.2855 | 1082341.5106 |  | 27936.5801 | 267392.9807 | 508246.9616 | 465079.6129 | 126900.2855 | 1395556.4207 |  | 47891.2801 | 267392.9807 | 508246.9616 | 310053.0752 | 126900.2855 | 1260484.5831
|  |  | 17 | 17 | C3 | 3 | 9 | 4 | 1 | 0 | 17 | 2 | 9 | 4 | 1 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 5 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 6 | 4 | 0 | 17 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 703728 | 703728 | 703728 | 703728 | 703728 | C3 | 5986.41 | 5986.41 | 22422.6601 | 46507.9613 | 95175.2141 | C3 | 11972.82 | 53877.6901 | 89690.6403 | 46507.9613 | 95175.2141 | 297224.3259 |  | 17959.23 | 53877.6901 | 89690.6403 | 46507.9613 | 0 | 208035.5217 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1172880 | 1172880 | 1172880 | 1172880 | 1172880 | C4 | 9977.35 | 9977.35 | 37371.1001 | 77513.2688 | 158625.3569 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 183 | 182 |  | 28 | 114 | 33 | 5 | 3 |  | 25 | 109 | 33 | 8 | 6 |  | 5 | 0 | 0 | -4 | -2 |  | 19 | 102 | 46 | 12 | 4 |  | 9 | 0 | 0 | -8 | -2 |  | 10 | 91 | 55 | 22 | 5 | [22 empty] | 97778.0302 | 423039.6411 | 500772.7416 | 226338.7449 | 374355.8422 | 1622285 |  | 110549.0383 | 441797.0591 | 500772.7416 | 142624.4146 | 171315.3854 | 1367058.639 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 94585.2782 | 387919.369 | 698092.1502 | 275947.237 | 126900.2855 | 1583444.3199 |  | 39510.3061 | 353597.2849 | 799741.5425 | 716222.6038 | 260145.5853 | 2169217.3226 |  | 70639.6382 | 353597.2849 | 799741.5425 | 496084.9204 | 171315.3854 | 1891378.7714
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | C1 | 262.0625 | 262.0625 | 982.3054 | 2025.4074 | 4167.5049 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 700421 | 700421 | 700421 | 700421 | 700421 | C2 | 374.375 | 374.375 | 1403.2935 | 2893.4392 | 5953.5785 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 14.2 | C3 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 16 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | -10.8 | -10.8 | 0 | 0 | 0 | 0 | 25 | 25 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | C3 | 561.5625 | 561.5625 | 2104.9402 | 4340.1587 | 8930.3678 | C3 | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 126811.2221 | 126811.2221
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | C4 | 935.9376 | 935.9376 | 3508.2337 | 7233.5979 | 14883.9463 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 14.2 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 16 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 0 | -10.8 |  | 0 | 0 | 0 | 0 | 25 | [22 empty] | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 126811.2221 | 126811.2221
| 132kV UG Cable (Oil) |  | 34 | 34 | C1 | 11 | 11 | 9 | 1 | 2 | 34 | 10 | 16 | 7 | 1 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 8 | 3 | 3 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 11 | 3 | 3 | 34 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | C1 | 306.3424 | 306.3424 | 1148.2826 | 2367.6343 | 4871.6755 | C1 | 3063.4242 | 4901.4787 | 8037.9781 | 2367.6343 | 0 | 18370.5154 |  | 3369.7666 | 3369.7666 | 10334.5433 | 2367.6343 | 9743.3511 | 29185.0619 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592
|  |  | 30 | 29.9 | C2 | 9 | 11 | 8 | 0 | 2 | 30 | 9 | 15 | 7 | 1 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 8 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | -0.1 | -0.1 | 9 | 5 | 10 | 3 | 3 | 30 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 818769 | 818769 | 818769 | 818769 | 818769 | C2 | 437.632 | 437.632 | 1640.4037 | 3382.3347 | 6959.5365 | C2 | 3938.6883 | 6564.4805 | 11482.8258 | 3382.3347 | 6959.5365 | 32327.8658 |  | 3938.6883 | 4813.9523 | 13123.2295 | 0 | 13919.073 | 35794.9431 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20182.6558 | 52860.5454
|  |  | 36 | 36 | C3 | 12 | 11 | 9 | 1 | 3 | 36 | 11 | 17 | 7 | 1 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 9 | 3 | 3 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 11 | 4 | 3 | 36 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | C3 | 656.448 | 656.448 | 2460.6055 | 5073.5021 | 10439.3048 | C3 | 7220.9285 | 11159.6168 | 17224.2388 | 5073.5021 | 0 | 40678.2862 |  | 7877.3765 | 7220.9285 | 22145.4498 | 5073.5021 | 31317.9143 | 73635.1712 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484
|  |  | 134 | 123.6 | C4 | 43 | 45 | 34 | 2 | 10 | 134 | 40 | 62 | 28 | 3 | 1 | 134 | 0 | 0 | 0 | 0 | -8 | -8 | 39 | 39 | 33 | 13 | 10 | 134 | 0 | 0 | 0 | -2.4 | -8 | -10.4 | 39 | 27 | 42 | 13 | 13 | 134 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | C4 | 1094.0801 | 1094.0801 | 4101.0092 | 8455.8368 | 17398.8413 | C4 | 43763.2031 | 67832.9647 | 114828.2584 | 25367.5105 | 17398.8413 | 269190.778 |  | 47045.4433 | 49233.6034 | 139434.3138 | 16911.6737 | 173988.4125 | 426613.4467 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 34797.6825 | 365395.112 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879 |  | 42669.123 | 29540.1621 | 172242.3876 | 89631.8706 | 86994.2063 | 421077.7495
|  |  | 234 | 223.5 |  | 75 | 78 | 60 | 4 | 17 |  | 70 | 110 | 49 | 6 | 2 |  | 0 | 0 | 0 | 0 | -8 |  | 68 | 68 | 58 | 22 | 18 |  | 0 | 0 | 0 | -2.4 | -8.1 |  | 68 | 47 | 74 | 23 | 22 | [22 empty] | 57986.244 | 90458.5407 | 151573.3011 | 36190.9817 | 24358.3777 | 360567.4453 |  | 62231.2747 | 64638.2509 | 185037.5364 | 24352.8101 | 228968.7509 | 565228.623 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 94649.6964 | 529524.4814 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946 |  | 56235.7159 | 39124.3035 | 228344.1939 | 127175.7862 | 153109.803 | 603989.8025
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 51.5767 | 120.25 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2258 | 2258 | C2 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 790 | 994 | 456 | 18 | 2258 | 8 | 0 | 0 | 0 | -8 | 0 | 0 | 790 | 964 | 486 | 18 | 2258 | 16 | 0 | 0 | 0 | -16 | 0 | 0 | 789 | 962 | 465 | 42 | 2258 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 73.681 | 171.7857 | C2 | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20463.4319 | 35808.9702 | 1717.8568 | 57990.259 |  | 0 | 0 | 20420.9767 | 34261.6691 | 7214.9986 | 61897.6443 |  | 0 | 0 | 20420.9767 | 34261.6691 | 4466.4277 | 59149.0734
|  |  | 312 | 312 | C3 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 67 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 64 | 6 | 312 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 110.5215 | 257.6785 | C3 | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594
|  |  | 5 | 5 | C4 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 184.2025 | 429.4642 | C4 | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407
|  |  | 2575 | 2575 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 901 | 1133 | 520 | 21 |  | 8 | 0 | 0 | 0 | -8 |  | 0 | 901 | 1099 | 554 | 21 |  | 16 | 0 | 0 | 0 | -16 |  | 0 | 900 | 1097 | 530 | 48 | [22 empty] | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24804.4815 | 43398.1141 | 2490.8924 | 70693.4881 |  | 0 | 0 | 24762.0263 | 41519.2484 | 8761.0697 | 75042.3444 |  | 0 | 0 | 24762.0263 | 41519.2484 | 6012.4988 | 72293.7735
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 48.4269 | 93.9681 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1003 | 1003 | C2 | 215 | 464 | 324 | 0 | 0 | 1003 | 189 | 464 | 350 | 0 | 0 | 1003 | 109.1199 | 0 | 0 | -109.1199 | 0 | 0 | 178 | 420 | 280 | 125 | 0 | 1003 | 235.1191 | 0 | 0 | -235.1191 | 0 | 0 | 26 | 494 | 244 | 239 | 0 | 1003 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 69.1813 | 134.2401 | C2 | 0 | 0 | 7429.6693 | 0 | 0 | 7429.6693 |  | 0 | 0 | 6877.751 | 0 | 0 | 6877.751 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5943.7354 | 1098.6086 | 0 | 7042.344 |  | 0 | 0 | 5179.5409 | 16534.3366 | 0 | 21713.8775 |  | 0 | 0 | 5179.5409 | 268.4854 | 0 | 5448.0262
|  |  | 147 | 147 | C3 | 31 | 68 | 48 | 0 | 0 | 147 | 31 | 68 | 48 | 0 | 0 | 147 | 18 | 0 | 0 | -18 | 0 | 0 | 22 | 62 | 45 | 18 | 0 | 147 | 28 | 0 | 0 | -28 | 0 | 0 | 0 | 72 | 39 | 36 | 0 | 147 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 103.772 | 201.3602 | C3 | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1432.8648 | 0 | 0 | 1432.8648 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077 |  | 0 | 0 | 1241.8161 | 830.1759 | 0 | 2071.992
|  |  | 1 | 1 | C4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 1 | 0 | 0 | -1 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 172.9533 | 335.6003 | C4 | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1151 | 1151 |  | 246 | 532 | 373 | 0 | 0 |  | 220 | 532 | 399 | 0 | 0 |  | 128.1199 | 0 | 0 | -128.1199 | 0 |  | 200 | 482 | 325 | 144 | 0 |  | 264.1191 | 0 | 0 | -264.1191 | 0 |  | 26 | 566 | 283 | 276 | 0 | [22 empty] | 0 | 0 | 9011.1274 | 0 | 0 | 9011.1274 |  | 0 | 0 | 8459.2092 | 0 | 0 | 8459.2092 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 7376.6002 | 1098.6086 | 0 | 8475.2088 |  | 0 | 0 | 6421.357 | 20443.0815 | 0 | 26864.4385 |  | 0 | 0 | 6421.357 | 1098.6613 | 0 | 7520.0183
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 |  | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 185968.3665 | 542932.3158 | 944062.6656 | 621140.2138 | 391061.0352 | 2685164.5968 |  | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 |  | 154896.0703 | 503103.7738 | 1075342.409 | 683389.2952 | 673787.6104 | 3090519.1586
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 313807 | 310419.5 |  | 50304 | 158234 | 82171 | 21650 | 1448 |  | 44998 | 157737 | 82173 | 22091 | 7478 |  | 13473.062 | 0 | -94.45 | -7476.1199 | -7581.4921 |  | 34863 | 125195 | 95392 | 49327 | 9031 |  | 24319.0033 | 0 | -94.45 | -9141.5191 | -18470.5342 |  | 23791 | 112928 | 92300 | 61502 | 23287 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 |  | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 |  | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 |  | 1500912.9365 | 4501383.2963 | 11276904.6835 | 8060737.1277 | 1216451.5728 | 26556389.6168 |  | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 |  | 1439701.6869 | 4030185.639 | 11622463.6852 | 10312619.96 | 2343319.8149 | 29748290.786
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 | LV Network | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 598337.4466 | 1370463.9934 | 3475158.0245 | 4621113.7662 | 331232.7265 | 10396305.9572 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 | LV Network | 647962.8324 | 1182549.5663 | 3045339.0362 | 6231754.0963 | 504971.2768 | 11612576.808
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 | HV Network | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 | HV Network | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 | HV Network | 559650.8854 | 1985336.3541 | 5380523.0757 | 2295579.4729 | 101616.1969 | 10322705.985 | HV Network | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 | HV Network | 486369.6245 | 1882553.1493 | 5638849.1663 | 2606784.0401 | 691463.5616 | 11306019.5418
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 | EHV Network | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 | EHV Network | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 | EHV Network | 156956.2381 | 602650.6329 | 1477160.9178 | 522903.6748 | 392541.6142 | 3152213.0779 | EHV Network | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 | EHV Network | 150473.1597 | 461979.1496 | 1862933.0736 | 790692.5283 | 473097.3662 | 3739175.2775
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 | 132kV Network | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 185968.3665 | 542932.3158 | 944062.6656 | 621140.2138 | 391061.0352 | 2685164.5968 | 132kV Network | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 | 132kV Network | 154896.0703 | 503103.7738 | 1075342.409 | 683389.2952 | 673787.6104 | 3090519.1586
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 | Total | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 | Total | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 | Total | 1500912.9365 | 4501383.2963 | 11276904.6835 | 8060737.1277 | 1216451.5728 | 26556389.6168 | Total | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 | Total | 1439701.6869 | 4030185.639 | 11622463.6852 | 10312619.96 | 2343319.8149 | 29748290.786
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SPN - Refurb
Secondary deliverables RIIO-ED1 - Refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 1 | 1 | C1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | C1 | 8.3151 | 19.0395 | 58.9198 | 96.0302 | 154.2283 | C1 | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198
|  |  | 13779 | 13779 | C2 | 1531 | 1533 | 9111 | 1558 | 46 | 13779 | 1486 | 1347 | 9111 | 1558 | 91 | 13593 | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 1371 | 9146 | 2111 | 190 | 13779 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1480 | 8545 | 3378 | 331 | 13779 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10983 | 10983 | 10983 | 10983 | 10983 | C2 | 11.8787 | 27.1994 | 84.1712 | 137.186 | 220.3262 | C2 | 17651.8005 | 36637.5281 | 766883.8029 | 213735.7565 | 20049.6801 | 1054958.5681 |  | 18186.3436 | 41696.6077 | 766883.8029 | 213735.7565 | 10135.0031 | 1050637.5138 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857
|  |  | 6600 | 6600 | C3 | 644 | 1451 | 3831 | 655 | 19 | 6600 | 590 | 1451 | 3831 | 655 | 73 | 6600 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 1445 | 3801 | 877 | 43 | 6600 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1489 | 3551 | 1404 | 102 | 6600 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | C3 | 17.8181 | 40.799 | 126.2568 | 205.779 | 330.4892 | C3 | 10512.6807 | 59199.3911 | 483689.8006 | 134785.2252 | 24125.7139 | 712312.8115 |  | 11474.8582 | 59199.3911 | 483689.8006 | 134785.2252 | 6279.2954 | 695428.5705 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035
|  |  | 606 | 606 | C4 | 59 | 133 | 352 | 60 | 2 | 606 | 54 | 133 | 352 | 60 | 7 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 132 | 349 | 81 | 4 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 137 | 326 | 129 | 9 | 606 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | C4 | 29.6968 | 67.9984 | 210.428 | 342.9649 | 550.8154 | C4 | 1603.6293 | 9043.7848 | 74070.656 | 20577.897 | 3855.7077 | 109151.6747 |  | 1752.1134 | 9043.7848 | 74070.656 | 20577.897 | 1101.6308 | 106546.0819 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074
|  |  | 20986 | 20986 |  | 2234 | 3117 | 13295 | 2273 | 67 |  | 2130 | 2931 | 13295 | 2273 | 171 |  | 0 | 0 | 0 | 0 | 0 |  | 1435 | 2948 | 13297 | 3069 | 237 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 3106 | 12423 | 4911 | 442 | [22 empty] | 29768.1104 | 104880.704 | 1324703.1793 | 369098.8787 | 48031.1017 | 1876481.9741 |  | 31413.3153 | 109939.7836 | 1324703.1793 | 369098.8787 | 17515.9293 | 1852671.0861 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165
| LV UGB |  | 677 | 677 | C1 | 91 | 126 | 187 | 258 | 15 | 677 | 86 | 126 | 187 | 258 | 20 | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 73 | 135 | 384 | 30 | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 66 | 485 | 46 | 676 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | C1 | 11.0956 | 16.6433 | 55.4778 | 122.0512 | 238.5547 | C1 | 954.2186 | 2097.0618 | 10374.3535 | 31489.2142 | 4771.0931 | 49685.9412 |  | 1009.6964 | 2097.0618 | 10374.3535 | 31489.2142 | 3578.3198 | 48548.6457 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176
|  |  | 19687 | 19687 | C2 | 2638 | 3677 | 5444 | 7503 | 425 | 19687 | 2493 | 3677 | 5444 | 7503 | 569 | 19686 | 0 | 0 | 0 | 0 | 0 | 0 | 1594 | 2136 | 3923 | 11170 | 863 | 19686 | 0 | 0 | 0 | 0 | 0 | 0 | 1334 | 963 | 1930 | 14111 | 1350 | 19688 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11057 | 11057 | 11057 | 11057 | 11057 | C2 | 15.8508 | 23.7762 | 79.254 | 174.3589 | 340.7924 | C2 | 39516.0631 | 87425.1287 | 431458.9798 | 1308214.6945 | 193910.8534 | 2060525.7195 |  | 41814.4302 | 87425.1287 | 431458.9798 | 1308214.6945 | 144836.7534 | 2013749.9866 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375
|  |  | 4474 | 4474 | C3 | 599 | 836 | 1237 | 1705 | 97 | 4474 | 567 | 836 | 1237 | 1705 | 129 | 4474 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 486 | 892 | 2539 | 196 | 4475 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 219 | 439 | 3207 | 307 | 4475 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | C3 | 23.7762 | 35.6643 | 118.8811 | 261.5383 | 511.1885 | C3 | 13481.1118 | 29815.3689 | 147055.8665 | 445922.8417 | 65943.3219 | 702218.5107 |  | 14241.9505 | 29815.3689 | 147055.8665 | 445922.8417 | 49585.2885 | 686621.3161 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747
|  |  | 3369 | 3369 | C4 | 451 | 629 | 932 | 1284 | 73 | 3369 | 427 | 629 | 932 | 1284 | 97 | 3369 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 366 | 671 | 1912 | 148 | 3370 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 165 | 330 | 2415 | 231 | 3369 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | C4 | 39.627 | 59.4405 | 198.1351 | 435.8972 | 851.9809 | C4 | 16920.737 | 37388.0922 | 184661.9072 | 559692.0124 | 82642.1475 | 881304.8964 |  | 17871.7854 | 37388.0922 | 184661.9072 | 559692.0124 | 62194.6059 | 861808.4032 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691
|  |  | 28207 | 28207 |  | 3779 | 5268 | 7800 | 10750 | 610 |  | 3573 | 5268 | 7800 | 10750 | 815 |  | 0 | 0 | 0 | 0 | 0 |  | 2284 | 3061 | 5621 | 16005 | 1237 |  | 0 | 0 | 0 | 0 | 0 |  | 1911 | 1380 | 2765 | 20218 | 1934 | [22 empty] | 70872.1304 | 156725.6516 | 773551.1071 | 2345318.7627 | 347267.4159 | 3693735.0677 |  | 74937.8626 | 156725.6516 | 773551.1071 | 2345318.7627 | 260194.9676 | 3610728.3516 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | C1 | 14.8033 | 14.8033 | 29.7404 | 81.901 | 162.3867 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 124969 | 124969 | C2 | 21863 | 72930 | 26079 | 4097 | 0 | 124969 | 19674 | 73119 | 26079 | 4097 | 2189 | 125158 | 0 | 0 | 0 | 0 | 0 | 0 | 16316 | 54726 | 37003 | 13968 | 2956 | 124969 | 0 | 0 | 0 | 0 | 0 | 0 | 13510 | 48074 | 35619 | 19954 | 7812 | 124969 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13911 | 13911 | 13911 | 13911 | 13911 | C2 | 21.1475 | 21.1475 | 42.4864 | 117.0014 | 231.981 | C2 | 416056.8929 | 1546287.6868 | 1108001.6864 | 479354.7947 | 507806.3433 | 4057507.4041 |  | 462348.8792 | 1542290.7999 | 1108001.6864 | 479354.7947 | 0 | 3591996.1602 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865
|  |  | 1184 | 1184 | C3 | 143 | 852 | 189 | 0 | 0 | 1184 | 124 | 852 | 189 | 0 | 19 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 529 | 350 | 132 | 30 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 456 | 337 | 189 | 76 | 1184 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | C3 | 31.7213 | 31.7213 | 63.7295 | 175.5021 | 347.9715 | C3 | 3933.4442 | 27026.5685 | 12044.882 | 0 | 6611.4576 | 49616.3524 |  | 4536.1494 | 27026.5685 | 12044.882 | 0 | 0 | 43607.6 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956
|  |  | 2 | 2 | C4 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | C4 | 52.8689 | 52.8689 | 106.2159 | 292.5035 | 579.9524 | C4 | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848
|  |  | 126155 | 126155 |  | 22006 | 73783 | 26269 | 4097 | 0 |  | 19798 | 73972 | 26269 | 4097 | 2208 |  | 0 | 0 | 0 | 0 | 0 |  | 16459 | 55256 | 37354 | 14100 | 2986 |  | 0 | 0 | 0 | 0 | 0 |  | 13636 | 48531 | 35957 | 20143 | 7888 | [22 empty] | 419990.3371 | 1573367.1242 | 1120152.7843 | 479354.7947 | 514417.8009 | 4107282.8413 |  | 466885.0286 | 1569370.2373 | 1120152.7843 | 479354.7947 | 0 | 3635762.845 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 |  | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1843 | 1843 | C1 | 494 | 947 | 398 | 4 | 0 | 1843 | 477 | 947 | 398 | 20 | 1 | 1843 | 0 | 33 | 0 | -33 | 0 | 0 | 437 | 678 | 538 | 183 | 7 | 1843 | 0 | 180 | 0 | -180 | 0 | 0 | 211 | 638 | 620 | 336 | 38 | 1843 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | C1 | 58.7072 | 58.7072 | 219.7445 | 403.678 | 555.67 | C1 | 28003.3423 | 55595.734 | 87458.3248 | 8073.5593 | 555.67 | 179686.6303 |  | 29001.3649 | 55595.734 | 87458.3248 | 1614.7119 | 0 | 173670.1356 |  | 25655.0536 | 39803.4928 | 118222.5596 | 73873.068 | 3889.6899 | 261443.8638 |  | 25655.0536 | 41740.8309 | 118222.5596 | 60551.6951 | 3889.6899 | 250059.829 |  | 12387.2227 | 37455.2041 | 136241.6114 | 135635.7969 | 21115.4594 | 342835.2945 |  | 12387.2227 | 48022.5031 | 136241.6114 | 62973.7629 | 21115.4594 | 280740.5594
|  |  | 829 | 829 | C2 | 99 | 627 | 103 | 0 | 0 | 829 | 98 | 533 | 103 | 11 | 1 | 746 | 0 | 8 | 0 | -8 | 0 | 0 | 74 | 427 | 222 | 106 | 0 | 829 | 0 | 78 | 0 | -78 | 0 | 0 | 40 | 270 | 358 | 149 | 12 | 829 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | C2 | 83.8675 | 83.8675 | 313.9208 | 576.6828 | 793.8143 | C2 | 8219.0103 | 44701.352 | 32333.8387 | 6343.5109 | 793.8143 | 92391.5261 |  | 8302.8778 | 52584.8925 | 32333.8387 | 0 | 0 | 93221.6089 |  | 6206.1915 | 35811.402 | 69690.4095 | 61128.3779 | 0 | 172836.3809 |  | 6206.1915 | 36482.3417 | 69690.4095 | 56514.9154 | 0 | 168893.858 |  | 3354.6981 | 22644.2121 | 112383.6334 | 85925.7387 | 9525.7711 | 233834.0534 |  | 3354.6981 | 29185.8733 | 112383.6334 | 40944.4795 | 9525.7711 | 195394.4555
|  |  | 317 | 317 | C3 | 44 | 244 | 29 | 0 | 0 | 317 | 44 | 244 | 29 | 0 | 0 | 317 | 0 | 8 | 0 | -8 | 0 | 0 | 38 | 181 | 50 | 48 | 0 | 317 | 0 | 31 | 0 | -31 | 0 | 0 | 20 | 102 | 135 | 57 | 3 | 317 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | C3 | 125.8012 | 125.8012 | 470.8811 | 865.0242 | 1190.7214 | C3 | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 4780.4448 | 22770.0132 | 23544.0573 | 41521.1623 | 0 | 92615.6776 |  | 4780.4448 | 23776.4227 | 23544.0573 | 34600.9686 | 0 | 86701.8933 |  | 2516.0236 | 12831.7202 | 63568.9546 | 49306.3803 | 3572.1642 | 131795.2428 |  | 2516.0236 | 16731.5567 | 63568.9546 | 22490.6296 | 3572.1642 | 108879.3287
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | C4 | 209.6686 | 209.6686 | 784.8019 | 1441.707 | 1984.5357 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2989 | 2989 |  | 637 | 1818 | 530 | 4 | 0 |  | 619 | 1724 | 530 | 31 | 2 |  | 0 | 49 | 0 | -49 | 0 |  | 549 | 1286 | 810 | 337 | 7 |  | 0 | 289 | 0 | -289 | 0 |  | 271 | 1010 | 1113 | 542 | 53 | [22 empty] | 41757.6044 | 130992.5734 | 133447.7166 | 14417.0703 | 1349.4842 | 321964.449 |  | 42839.4945 | 138876.1139 | 133447.7166 | 1614.7119 | 0 | 316778.037 |  | 36641.6898 | 98384.9081 | 211457.0264 | 176522.6082 | 3889.6899 | 526895.9223 |  | 36641.6898 | 101999.5952 | 211457.0264 | 151667.5791 | 3889.6899 | 505655.5804 |  | 18257.9443 | 72931.1363 | 312194.1994 | 270867.9159 | 34213.3947 | 708464.5907 |  | 18257.9443 | 93939.9331 | 312194.1994 | 126408.872 | 34213.3947 | 585014.3435
| HV Switchgear (GM) - Distribution |  | 4606 | 4606 | C1 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 1477 | 2931 | 42 | 88 | 68 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 4101 | 52 | 28 | 157 | 4606 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | C1 | 13.6425 | 13.6425 | 51.2806 | 94.0237 | 160.8309 | C1 | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458
|  |  | 22477 | 22477 | C2 | 5578 | 7761 | 6551 | 2065 | 522 | 22477 | 4662 | 7508 | 6551 | 2291 | 2419 | 23431 | 0 | 0 | 0 | 0 | 0 | 0 | 4507 | 8127 | 1170 | 6052 | 2621 | 22477 | 0 | 0 | 0 | 0 | 0 | 0 | 2324 | 9700 | 1039 | 1616 | 7798 | 22477 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | C2 | 19.4893 | 19.4893 | 73.2581 | 134.3195 | 229.7585 | C2 | 90858.975 | 146325.4364 | 479913.5676 | 307726.0048 | 555785.7551 | 1580609.7388 |  | 108711.146 | 151256.2216 | 479913.5676 | 277369.7948 | 119933.9248 | 1137184.6548 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394
|  |  | 585 | 585 | C3 | 91 | 195 | 229 | 49 | 21 | 585 | 91 | 195 | 229 | 49 | 21 | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 137 | 98 | 175 | 173 | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 74 | 44 | 362 | 585 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | C3 | 29.2339 | 29.2339 | 109.8871 | 201.4793 | 344.6377 | C3 | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | C4 | 48.7232 | 48.7232 | 183.1452 | 335.7988 | 574.3962 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27668 | 27668 |  | 8838 | 9250 | 6897 | 2136 | 547 |  | 7922 | 8997 | 6897 | 2362 | 2444 |  | 0 | 0 | 0 | 0 | 0 |  | 5986 | 11195 | 1310 | 6315 | 2862 |  | 0 | 0 | 0 | 0 | 0 |  | 2592 | 13906 | 1165 | 1688 | 8317 | [22 empty] | 136752.3071 | 169679.4282 | 511077.5474 | 319667.0095 | 563666.4708 | 1700842.763 |  | 154604.4781 | 174610.2134 | 511077.5474 | 289310.7995 | 127814.6406 | 1257417.679 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309
| HV Transformer (GM) |  | 9731 | 9731 | C1 | 1332 | 2840 | 5559 | 0 | 0 | 9731 | 1259 | 2840 | 5559 | 62 | 11 | 9731 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 3228 | 5574 | 199 | 0 | 9731 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 3457 | 5717 | 418 | 0 | 9731 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | C1 | 45.0878 | 54.95 | 154.9879 | 295.6111 | 498.624 | C1 | 56765.5022 | 156058.1406 | 861577.5631 | 18327.889 | 5484.864 | 1098213.959 |  | 60056.9094 | 156058.1406 | 861577.5631 | 0 | 0 | 1077692.6132 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129
|  |  | 5287 | 5287 | C2 | 651 | 1916 | 2720 | 0 | 0 | 5287 | 595 | 1714 | 2720 | 50 | 6 | 5085 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 1888 | 2913 | 104 | 0 | 5287 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 2009 | 2988 | 218 | 0 | 5287 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | C2 | 64.4111 | 78.5001 | 221.4112 | 422.3016 | 712.32 | C2 | 38324.6044 | 134549.1212 | 602238.5762 | 21115.0795 | 4273.92 | 800501.3013 |  | 41931.626 | 150406.1355 | 602238.5762 | 0 | 0 | 794576.3377 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768
|  |  | 4141 | 4141 | C3 | 566 | 1209 | 2366 | 0 | 0 | 4141 | 518 | 1209 | 2366 | 43 | 5 | 4141 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 1374 | 2370 | 86 | 0 | 4141 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1471 | 2433 | 178 | 0 | 4141 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | C3 | 96.6166 | 117.7501 | 332.1169 | 633.4524 | 1068.48 | C3 | 50047.4245 | 142359.8783 | 785788.4953 | 27238.4526 | 5342.4 | 1010776.6506 |  | 54685.0237 | 142359.8783 | 785788.4953 | 0 | 0 | 982833.3973 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638
|  |  | 2071 | 2071 | C4 | 283 | 605 | 1183 | 0 | 0 | 2071 | 260 | 605 | 1183 | 21 | 2 | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 687 | 1186 | 43 | 0 | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 736 | 1216 | 89 | 0 | 2071 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | C4 | 161.0277 | 196.2502 | 553.5281 | 1055.754 | 1780.8 | C4 | 41867.2149 | 118731.357 | 654823.746 | 22170.8335 | 3561.6 | 841154.7514 |  | 45570.8531 | 118731.357 | 654823.746 | 0 | 0 | 819125.9561 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399
|  |  | 21230 | 21230 |  | 2832 | 6570 | 11828 | 0 | 0 |  | 2632 | 6368 | 11828 | 176 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 1578 | 7177 | 12043 | 432 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 300 | 7673 | 12354 | 903 | 0 | [22 empty] | 187004.746 | 551698.4971 | 2904428.3807 | 88852.2546 | 18662.7838 | 3750646.6623 |  | 202244.4122 | 567555.5114 | 2904428.3807 | 0 | 0 | 3674228.3044 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 9772 | 9772 | C1 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 5094 | 2706 | 1021 | 393 | 9772 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 4298 | 2825 | 1534 | 733 | 9772 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | C1 | 19.1659 | 19.1659 | 72.1182 | 151.5867 | 233.6923 | C1 | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464
|  |  | 39560 | 39560 | C2 | 4761 | 27072 | 6789 | 938 | 0 | 39560 | 3776 | 27093 | 6789 | 938 | 985 | 39581 | 0 | 0 | 0 | 0 | 0 | 0 | 3243 | 20614 | 10962 | 4136 | 605 | 39560 | 0 | 0 | 0 | 0 | 0 | 0 | 2533 | 17389 | 11440 | 6215 | 1983 | 39560 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | C2 | 27.3798 | 27.3798 | 103.026 | 216.5524 | 333.8462 | C2 | 103386.0983 | 741800.7314 | 699443.6721 | 203126.197 | 328838.4663 | 2076595.1651 |  | 130355.1944 | 741225.7558 | 699443.6721 | 203126.197 | 0 | 1774150.8193 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443
|  |  | 18629 | 18629 | C3 | 2618 | 12458 | 3162 | 391 | 0 | 18629 | 2100 | 12458 | 3162 | 391 | 518 | 18629 | 0 | 0 | 0 | 0 | 0 | 0 | 1581 | 9711 | 5159 | 1947 | 231 | 18629 | 0 | 0 | 0 | 0 | 0 | 0 | 1246 | 8194 | 5385 | 2925 | 879 | 18629 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | C3 | 41.0697 | 41.0697 | 154.539 | 324.8287 | 500.7692 | C3 | 86246.3479 | 511646.1916 | 488652.4285 | 127008.0112 | 259398.4653 | 1472951.4445 |  | 107520.4471 | 511646.1916 | 488652.4285 | 127008.0112 | 0 | 1234827.0783 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012
|  |  | 41 | 41 | C4 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 39 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 22 | 11 | 4 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18 | 12 | 6 | 3 | 41 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | C4 | 68.4495 | 68.4495 | 257.5651 | 541.3811 | 834.6154 | C4 | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033
|  |  | 68002 | 68002 |  | 8123 | 46800 | 11571 | 1508 | 0 |  | 6620 | 46821 | 11571 | 1508 | 1503 |  | 0 | 0 | 0 | 0 | 0 |  | 5384 | 35441 | 18838 | 7108 | 1231 |  | 0 | 0 | 0 | 0 | 0 |  | 4163 | 29899 | 19662 | 10680 | 3598 | [22 empty] | 203990.4097 | 1394704.751 | 1304927.611 | 357268.2301 | 588236.9315 | 3849127.9333 |  | 252233.6049 | 1394129.7753 | 1304927.611 | 357268.2301 | 0 | 3308559.2213 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 |  | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 |  | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 |  | 421769.7369 | 1988951.0413 | 5387189.5593 | 2895760.4449 | 1087810.4144 | 11781481.1968 |  | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 |  | 216627.3123 | 1903561.9461 | 5645515.65 | 3309090.4207 | 3251872.7081 | 14326668.0372
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 217 | 217 | C1 | 136 | 76 | 5 | 0 | 0 | 217 | 136 | 76 | 5 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 71 | 13 | 2 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 117 | 18 | 2 | 0 | 217 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | C1 | 165.6424 | 165.6424 | 625.0091 | 1143.9769 | 1952.7416 | C1 | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772
|  |  | 505 | 505 | C2 | 153 | 280 | 69 | 3 | 0 | 505 | 153 | 271 | 69 | 3 | 0 | 496 | 0 | 5 | 0 | -5 | 0 | 0 | 112 | 227 | 143 | 11 | 12 | 505 | 0 | 8 | 0 | -5 | -3 | 0 | 74 | 190 | 207 | 17 | 17 | 505 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | C2 | 236.6321 | 236.6321 | 892.8701 | 1634.2527 | 2789.6309 | C2 | 36204.7037 | 64127.2857 | 61608.0394 | 4902.758 | 0 | 166842.7867 |  | 36204.7037 | 66256.9741 | 61608.0394 | 4902.758 | 0 | 168972.4752 |  | 26502.7897 | 53715.4755 | 127680.4294 | 17976.7792 | 33475.5706 | 259351.0444 |  | 26502.7897 | 54898.6357 | 127680.4294 | 9805.516 | 33475.5706 | 252362.9413 |  | 17510.7717 | 44960.0896 | 184824.1181 | 27782.2952 | 47423.725 | 322500.9996 |  | 17510.7717 | 46853.146 | 184824.1181 | 19611.0319 | 39054.8323 | 307853.9001
|  |  | 70 | 70 | C3 | 8 | 54 | 8 | 0 | 0 | 70 | 8 | 54 | 8 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 41 | 16 | 0 | 5 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32 | 26 | 2 | 5 | 70 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | C3 | 354.9481 | 354.9481 | 1339.3052 | 2451.379 | 4184.4463 | C3 | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037
|  |  | 6 | 6 | C4 | 2 | 3 | 1 | 0 | 0 | 6 | 2 | 3 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 6 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | C4 | 591.5801 | 591.5801 | 2232.1753 | 4085.6316 | 6974.0772 | C4 | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616
|  |  | 798 | 798 |  | 299 | 413 | 83 | 3 | 0 |  | 299 | 404 | 83 | 3 | 0 |  | 0 | 5 | 0 | -5 | 0 |  | 253 | 341 | 174 | 13 | 17 |  | 0 | 8 | 0 | -5 | -3 |  | 159 | 341 | 255 | 21 | 22 | [22 empty] | 62754.8198 | 97658.0472 | 77679.7018 | 4902.758 | 0 | 242995.3268 |  | 62754.8198 | 99787.7357 | 77679.7018 | 4902.758 | 0 | 245125.0153 |  | 52224.6935 | 81212.1197 | 161698.7816 | 20264.733 | 54397.8022 | 369798.13 |  | 52224.6935 | 82395.28 | 161698.7816 | 12093.4697 | 54397.8022 | 362810.027 |  | 32536.9069 | 76881.7532 | 239824.9185 | 34973.0069 | 68345.9566 | 452562.5421 |  | 32536.9069 | 78774.8096 | 239824.9185 | 26801.7436 | 59977.064 | 437915.4426
| EHV Transformer |  | 194 | 194 | C1 | 21 | 140 | 22 | 8 | 3 | 194 | 21 | 140 | 22 | 8 | 3 | 194 | 0 | 2 | 0 | -2 | 0 | 0 | 11 | 109 | 52 | 14 | 8 | 194 | 0 | 6 | 0 | -6 | 0 | 0 | 5 | 86 | 78 | 16 | 9 | 194 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | C1 | 890.0227 | 890.0227 | 3333.6634 | 6914.518 | 14150.0662 | C1 | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 9790.2493 | 97012.4705 | 173350.4943 | 96803.2517 | 113200.5292 | 490156.995 |  | 9790.2493 | 98792.5158 | 173350.4943 | 82974.2157 | 113200.5292 | 478108.0044 |  | 4450.1133 | 76541.9492 | 260025.7415 | 110632.2876 | 127350.5954 | 579000.687 |  | 4450.1133 | 81882.0852 | 260025.7415 | 69145.1798 | 127350.5954 | 542853.7151
|  |  | 259 | 259 | C2 | 29 | 154 | 59 | 11 | 6 | 259 | 26 | 143 | 59 | 11 | 9 | 248 | 0 | 9 | 0 | -4 | -5 | 0 | 22 | 120 | 84 | 23 | 10 | 259 | 0 | 20 | 0 | -15 | -5 | 0 | 12 | 89 | 96 | 46 | 16 | 259 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | C2 | 1271.461 | 1271.461 | 4762.3762 | 9877.8828 | 20214.3802 | C2 | 33057.9847 | 181818.9159 | 280980.1968 | 108656.711 | 181929.422 | 786443.2304 |  | 36872.3676 | 195804.9863 | 280980.1968 | 108656.711 | 121286.2813 | 743600.5431 |  | 27972.1409 | 152575.314 | 400039.6022 | 227191.3049 | 202143.8022 | 1009922.1643 |  | 27972.1409 | 164018.4626 | 400039.6022 | 187679.7736 | 101071.9011 | 880781.8804 |  | 15257.5314 | 113160.0246 | 457188.1168 | 454382.6098 | 323430.0835 | 1363418.3661 |  | 15257.5314 | 138589.2436 | 457188.1168 | 306214.3675 | 222358.1824 | 1139607.4417
|  |  | 42 | 42 | C3 | 4 | 29 | 7 | 0 | 2 | 42 | 3 | 29 | 7 | 0 | 3 | 42 | 0 | 1 | 0 | 0 | -1 | 0 | 4 | 17 | 18 | 1 | 2 | 42 | 0 | 5 | 0 | -4 | -1 | 0 | 2 | 9 | 23 | 5 | 3 | 42 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | C3 | 1907.1914 | 1907.1914 | 7143.5643 | 14816.8242 | 30321.5703 | C3 | 5721.5743 | 55308.5513 | 50004.9503 | 0 | 90964.711 | 201999.7869 |  | 7628.7657 | 55308.5513 | 50004.9503 | 0 | 60643.1407 | 173585.408 |  | 7628.7657 | 32422.2542 | 128584.1579 | 14816.8242 | 60643.1407 | 244095.1427 |  | 7628.7657 | 34329.4457 | 128584.1579 | 14816.8242 | 30321.5703 | 215680.7638 |  | 3814.3829 | 17164.7228 | 164301.9795 | 74084.1212 | 90964.711 | 350329.9173 |  | 3814.3829 | 26700.68 | 164301.9795 | 14816.8242 | 60643.1407 | 270277.0072
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | C4 | 3178.6524 | 3178.6524 | 11905.9405 | 24694.7071 | 50535.9505 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 495 | 495 |  | 54 | 323 | 88 | 19 | 11 |  | 50 | 312 | 88 | 19 | 15 |  | 0 | 12 | 0 | -6 | -6 |  | 37 | 246 | 154 | 38 | 20 |  | 0 | 31 | 0 | -25 | -6 |  | 19 | 184 | 197 | 67 | 28 | [22 empty] | 57470.035 | 361730.6403 | 404325.7408 | 163972.8548 | 315344.3314 | 1302843.6024 |  | 63191.6092 | 375716.7108 | 404325.7408 | 163972.8548 | 224379.6204 | 1231586.5361 |  | 45391.1559 | 282010.0388 | 701974.2544 | 338811.3808 | 375987.4721 | 1744174.3019 |  | 45391.1559 | 297140.4241 | 701974.2544 | 285470.8135 | 244594.0006 | 1574570.6486 |  | 23522.0276 | 206866.6966 | 881515.8378 | 639099.0186 | 541745.3899 | 2292748.9704 |  | 23522.0276 | 247172.0087 | 881515.8378 | 390176.3715 | 410351.9184 | 1952738.164
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | C1 | 74.7619 | 74.7619 | 280.2348 | 577.8137 | 1188.9171 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 199818 | 199818 | 199818 | 199818 | 199818 | C2 | 106.8027 | 106.8027 | 400.3354 | 825.4482 | 1698.453 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 7 | C3 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 299727 | 299727 | 299727 | 299727 | 299727 | C3 | 160.2041 | 160.2041 | 600.503 | 1238.1722 | 2547.6795 | C3 | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 499545 | 499545 | 499545 | 499545 | 499545 | C4 | 267.0068 | 267.0068 | 1000.8384 | 2063.6204 | 4246.1325 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 7 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 7 | [22 empty] | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565
| EHV UG Cable (Oil) |  | 126 | 126 | C1 | 2 | 69 | 41 | 3 | 11 | 126 | 2 | 84 | 38 | 0 | 2 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 59 | 2 | 17 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 80 | 5 | 18 | 126 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | C1 | 116.2368 | 116.2368 | 435.6977 | 898.3615 | 1848.4805 | C1 | 232.4736 | 9763.8917 | 16556.5141 | 0 | 3696.9611 | 30249.8405 |  | 232.4736 | 8020.3396 | 17863.6073 | 2695.0846 | 20333.286 | 49144.7912 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233
|  |  | 175 | 175 | C2 | 3 | 96 | 56 | 5 | 15 | 175 | 3 | 117 | 51 | 5 | 5 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 82 | 3 | 23 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 111 | 6 | 24 | 175 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 310669 | 310669 | 310669 | 310669 | 310669 | C2 | 166.0526 | 166.0526 | 622.4253 | 1283.3736 | 2640.6865 | C2 | 498.1577 | 19428.1519 | 31743.6924 | 6416.8682 | 13203.4325 | 71290.3028 |  | 498.1577 | 15941.0477 | 34855.8191 | 6416.8682 | 39610.2975 | 97322.1903 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185
|  |  | 145 | 145 | C3 | 2 | 80 | 47 | 3 | 13 | 145 | 2 | 90 | 42 | 11 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 68 | 3 | 19 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 92 | 6 | 21 | 145 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | C3 | 249.0789 | 249.0789 | 933.638 | 1925.0605 | 3961.0298 | C3 | 498.1577 | 22417.0984 | 39212.7965 | 21175.665 | 0 | 83303.7177 |  | 498.1577 | 19926.3097 | 43880.9866 | 5775.1814 | 51493.3868 | 121574.0221 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353
|  |  | 13 | 13 | C4 | 0 | 8 | 4 | 0 | 1 | 13 | 0 | 9 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 1 | 2 | 13 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | C4 | 415.1315 | 415.1315 | 1556.0634 | 3208.4341 | 6601.7163 | C4 | 0 | 3736.1831 | 6224.2534 | 0 | 0 | 9960.4365 |  | 0 | 3321.0516 | 6224.2534 | 0 | 6601.7163 | 16147.0213 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363
|  |  | 459 | 459 |  | 7 | 253 | 148 | 11 | 40 |  | 7 | 300 | 135 | 16 | 7 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 175 | 215 | 8 | 61 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 85 | 291 | 18 | 65 | [22 empty] | 1228.7891 | 55345.3251 | 93737.2564 | 27592.5332 | 16900.3936 | 194804.2974 |  | 1228.7891 | 47208.7486 | 102824.6664 | 14887.1342 | 118038.6865 | 284188.0249 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 338 | 338 | C1 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 208 | 16 | 12 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 189 | 25 | 22 | 338 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | C1 | 0 | 0 | 12.1985 | 42.3409 | 98.717 | C1 | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812
|  |  | 166 | 166 | C2 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 103 | 7 | 5 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 94 | 11 | 10 | 166 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 215767 | 215767 | 215767 | 215767 | 215767 | C2 | 0 | 0 | 17.4264 | 60.487 | 141.0242 | C2 | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834
|  |  | 15 | 15 | C3 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | C3 | 0 | 0 | 26.1396 | 90.7306 | 211.5363 | C3 | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236
|  |  | 56 | 56 | C4 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 3 | 2 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 5 | 4 | 56 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | C4 | 0 | 0 | 43.5661 | 151.2176 | 352.5606 | C4 | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312
|  |  | 575 | 575 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 354 | 27 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 322 | 42 | 37 | [22 empty] | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331
| EHV OHL Support - Poles |  | 673 | 673 | C1 | 61 | 499 | 96 | 11 | 6 | 673 | 61 | 499 | 96 | 11 | 6 | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 355 | 210 | 61 | 20 | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 279 | 245 | 80 | 45 | 673 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | C1 | 15.4993 | 15.4993 | 58.3259 | 122.6046 | 189.0162 | C1 | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224
|  |  | 43 | 43 | C2 | 3 | 37 | 3 | 0 | 0 | 43 | 3 | 37 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 14 | 4 | 2 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 16 | 5 | 2 | 43 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 64595 | 64595 | 64595 | 64595 | 64595 | C2 | 22.1418 | 22.1418 | 83.3227 | 175.1494 | 270.0232 | C2 | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934
|  |  | 10397 | 10397 | C3 | 952 | 7695 | 1492 | 161 | 97 | 10397 | 847 | 7695 | 1492 | 161 | 202 | 10397 | 0 | 0 | 0 | 0 | 0 | 0 | 517 | 5488 | 3249 | 936 | 207 | 10397 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 4313 | 3785 | 1239 | 588 | 10397 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | C3 | 33.2127 | 33.2127 | 124.9841 | 262.7241 | 405.0348 | C3 | 28131.1917 | 255572.0426 | 186476.2173 | 42298.5864 | 81817.0254 | 594295.0634 |  | 31618.5295 | 255572.0426 | 186476.2173 | 42298.5864 | 39288.3736 | 555253.7494 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911
|  |  | 638 | 638 | C4 | 58 | 473 | 91 | 10 | 6 | 638 | 58 | 473 | 91 | 10 | 6 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 338 | 199 | 57 | 19 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 264 | 232 | 76 | 43 | 638 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | C4 | 55.3546 | 55.3546 | 208.3068 | 437.8736 | 675.058 | C4 | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144
|  |  | 11751 | 11751 |  | 1074 | 8704 | 1682 | 182 | 109 |  | 969 | 8704 | 1682 | 182 | 214 |  | 0 | 0 | 0 | 0 | 0 |  | 571 | 6202 | 3672 | 1058 | 248 |  | 0 | 0 | 0 | 0 | 0 |  | 520 | 4875 | 4278 | 1400 | 678 | [22 empty] | 32353.6382 | 290308.1414 | 211281.3871 | 48025.9726 | 87001.4705 | 668970.6099 |  | 35840.976 | 290308.1414 | 211281.3871 | 48025.9726 | 44472.8187 | 629929.2959 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229
| EHV OHL Fittings and Conductors (Tower Lines) |  | 64 | 64 | C1 | 1 | 0 | 8 | 42 | 13 | 64 | 0 | 0 | 8 | 42 | 14 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 33 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 12 | 49 | 64 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | C1 | 0 | 0 | 12.2256 | 39.8434 | 77.3125 | C1 | 0 | 0 | 97.8044 | 1673.4214 | 1082.3745 | 2853.6003 |  | 0 | 0 | 97.8044 | 1673.4214 | 1005.062 | 2776.2878 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822
|  |  | 18 | 18 | C2 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 14 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | C2 | 0 | 0 | 17.4651 | 56.9191 | 110.4464 | C2 | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | C3 | 0 | 0 | 26.1976 | 85.3786 | 165.6696 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | C4 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | C4 | 0 | 0 | 43.6627 | 142.2977 | 276.1159 | C4 | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159
|  |  | 83 | 83 |  | 1 | 0 | 11 | 54 | 17 |  | 0 | 0 | 11 | 54 | 18 |  | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 11 | 42 | 29 |  | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 2 | 16 | 64 | [22 empty] | 0 | 0 | 150.1997 | 2441.8291 | 1524.16 | 4116.1888 |  | 0 | 0 | 150.1997 | 2441.8291 | 1446.8475 | 4038.8763 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 |  | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 |  | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 |  | 116633.465 | 618964.1785 | 1480381.969 | 600259.309 | 585883.812 | 3402122.7335 |  | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 |  | 73402.6279 | 504177.5181 | 1866154.1248 | 816683.1718 | 968245.1114 | 4228662.5541
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 128 | 128 | C1 | 56 | 56 | 9 | 7 | 0 | 128 | 56 | 53 | 9 | 10 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 76 | 5 | 8 | 10 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 99 | 6 | 1 | 20 | 128 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | C1 | 566.8931 | 566.8931 | 2163.712 | 3830.461 | 5875.081 | C1 | 31746.0137 | 30045.3344 | 19473.4083 | 38304.6103 | 0 | 119569.3666 |  | 31746.0137 | 31746.0137 | 19473.4083 | 26813.2272 | 0 | 109778.6628 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572
|  |  | 91 | 91 | C2 | 14 | 52 | 9 | 15 | 1 | 91 | 7 | 29 | 9 | 23 | 4 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 55 | 5 | 2 | 20 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 51 | 1 | 0 | 30 | 91 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | C2 | 809.8473 | 809.8473 | 3091.0172 | 5472.0872 | 8392.9729 | C2 | 5668.931 | 23485.5714 | 27819.1546 | 125858.0053 | 33571.8916 | 216403.5539 |  | 11337.862 | 42112.059 | 27819.1546 | 82081.3078 | 8392.9729 | 171743.3563 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 7288.6256 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 303471.0417 |  | 7288.6256 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 303471.0417
|  |  | 13 | 13 | C3 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 4 | 13 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | C3 | 1214.7709 | 1214.7709 | 4636.5258 | 8208.1308 | 12589.4594 | C3 | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758
|  |  | 2 | 2 | C4 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | C4 | 2024.6182 | 2024.6182 | 7727.543 | 13680.218 | 20982.4323 | C4 | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362
|  |  | 234 | 234 |  | 71 | 117 | 20 | 25 | 1 |  | 64 | 91 | 20 | 36 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 39 | 140 | 11 | 11 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 11 | 160 | 7 | 2 | 54 | [22 empty] | 39439.5629 | 64463.8441 | 59656.6316 | 188787.0079 | 33571.8916 | 385918.9382 |  | 45108.4939 | 84791.011 | 59656.6316 | 133518.9273 | 8392.9729 | 331468.0368 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 8422.4118 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572037.2109 |  | 8422.4118 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572037.2109
| 132kV Transformer |  | 41 | 41 | C1 | 6 | 26 | 5 | 3 | 1 | 41 | 5 | 25 | 5 | 4 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 6 | 3 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18 | 15 | 3 | 3 | 41 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | C1 | 2793.658 | 2793.658 | 10463.908 | 21703.7153 | 44415.0999 | C1 | 13968.29 | 69841.4502 | 52319.5402 | 86814.8611 | 88830.1998 | 311774.3413 |  | 16761.948 | 72635.1082 | 52319.5402 | 65111.1458 | 44415.0999 | 251242.8421 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262
|  |  | 125 | 125 | C2 | 19 | 79 | 24 | 1 | 2 | 125 | 18 | 75 | 24 | 3 | 3 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 70 | 35 | 6 | 2 | 125 | 0 | 7 | 0 | -7 | 0 | 0 | 7 | 67 | 34 | 15 | 2 | 125 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469152 | 469152 | 469152 | 469152 | 469152 | C2 | 3990.94 | 3990.94 | 14948.44 | 31005.3075 | 63450.1427 | C2 | 71836.9202 | 299320.5007 | 358762.5611 | 93015.9226 | 190350.4282 | 1013286.3329 |  | 75827.8602 | 315284.2608 | 358762.5611 | 31005.3075 | 126900.2855 | 907780.2751 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 27936.5801 | 267392.9807 | 508246.9616 | 465079.6129 | 126900.2855 | 1395556.4207 |  | 27936.5801 | 295329.5607 | 508246.9616 | 248042.4602 | 126900.2855 | 1206455.8481
|  |  | 17 | 17 | C3 | 3 | 9 | 4 | 1 | 0 | 17 | 2 | 9 | 4 | 1 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 5 | 3 | 0 | 17 | 0 | 2 | 0 | -2 | 0 | 0 | 1 | 6 | 6 | 4 | 0 | 17 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 703728 | 703728 | 703728 | 703728 | 703728 | C3 | 5986.41 | 5986.41 | 22422.6601 | 46507.9613 | 95175.2141 | C3 | 11972.82 | 53877.6901 | 89690.6403 | 46507.9613 | 95175.2141 | 297224.3259 |  | 17959.23 | 53877.6901 | 89690.6403 | 46507.9613 | 0 | 208035.5217 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757 |  | 5986.41 | 47891.2801 | 134535.9604 | 93015.9226 | 0 | 281429.5731
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1172880 | 1172880 | 1172880 | 1172880 | 1172880 | C4 | 9977.35 | 9977.35 | 37371.1001 | 77513.2688 | 158625.3569 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 183 | 183 |  | 28 | 114 | 33 | 5 | 3 |  | 25 | 109 | 33 | 8 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 19 | 102 | 46 | 12 | 4 |  | 0 | 9 | 0 | -9 | 0 |  | 10 | 91 | 55 | 22 | 5 | [22 empty] | 97778.0302 | 423039.6411 | 500772.7416 | 226338.7449 | 374355.8422 | 1622285 |  | 110549.0383 | 441797.0591 | 500772.7416 | 142624.4146 | 171315.3854 | 1367058.639 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 39510.3061 | 353597.2849 | 799741.5425 | 716222.6038 | 260145.5853 | 2169217.3226 |  | 39510.3061 | 393506.685 | 799741.5425 | 406169.5286 | 260145.5853 | 1899073.6474
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | C1 | 262.0625 | 262.0625 | 982.3054 | 2025.4074 | 4167.5049 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 700421 | 700421 | 700421 | 700421 | 700421 | C2 | 374.375 | 374.375 | 1403.2935 | 2893.4392 | 5953.5785 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 25 | C3 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 16 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | C3 | 561.5625 | 561.5625 | 2104.9402 | 4340.1587 | 8930.3678 | C3 | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | C4 | 935.9376 | 935.9376 | 3508.2337 | 7233.5979 | 14883.9463 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 25 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 16 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | [22 empty] | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938
| 132kV UG Cable (Oil) |  | 34 | 34 | C1 | 11 | 11 | 9 | 1 | 2 | 34 | 10 | 16 | 7 | 1 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 8 | 3 | 3 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 11 | 3 | 3 | 34 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | C1 | 306.3424 | 306.3424 | 1148.2826 | 2367.6343 | 4871.6755 | C1 | 3063.4242 | 4901.4787 | 8037.9781 | 2367.6343 | 0 | 18370.5154 |  | 3369.7666 | 3369.7666 | 10334.5433 | 2367.6343 | 9743.3511 | 29185.0619 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592
|  |  | 30 | 30 | C2 | 9 | 11 | 8 | 0 | 2 | 30 | 9 | 15 | 7 | 1 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 8 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 10 | 3 | 3 | 30 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 818769 | 818769 | 818769 | 818769 | 818769 | C2 | 437.632 | 437.632 | 1640.4037 | 3382.3347 | 6959.5365 | C2 | 3938.6883 | 6564.4805 | 11482.8258 | 3382.3347 | 6959.5365 | 32327.8658 |  | 3938.6883 | 4813.9523 | 13123.2295 | 0 | 13919.073 | 35794.9431 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991
|  |  | 36 | 36 | C3 | 12 | 11 | 9 | 1 | 3 | 36 | 11 | 17 | 7 | 1 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 9 | 3 | 3 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 11 | 4 | 3 | 36 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | C3 | 656.448 | 656.448 | 2460.6055 | 5073.5021 | 10439.3048 | C3 | 7220.9285 | 11159.6168 | 17224.2388 | 5073.5021 | 0 | 40678.2862 |  | 7877.3765 | 7220.9285 | 22145.4498 | 5073.5021 | 31317.9143 | 73635.1712 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484
|  |  | 134 | 134 | C4 | 43 | 45 | 34 | 2 | 10 | 134 | 40 | 62 | 28 | 3 | 1 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 33 | 13 | 10 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 27 | 42 | 13 | 13 | 134 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | C4 | 1094.0801 | 1094.0801 | 4101.0092 | 8455.8368 | 17398.8413 | C4 | 43763.2031 | 67832.9647 | 114828.2584 | 25367.5105 | 17398.8413 | 269190.778 |  | 47045.4433 | 49233.6034 | 139434.3138 | 16911.6737 | 173988.4125 | 426613.4467 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879
|  |  | 234 | 234 |  | 75 | 78 | 60 | 4 | 17 |  | 70 | 110 | 49 | 6 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 68 | 58 | 22 | 18 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 47 | 74 | 23 | 22 | [22 empty] | 57986.244 | 90458.5407 | 151573.3011 | 36190.9817 | 24358.3777 | 360567.4453 |  | 62231.2747 | 64638.2509 | 185037.5364 | 24352.8101 | 228968.7509 | 565228.623 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 51.5767 | 120.25 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2258 | 2258 | C2 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 964 | 486 | 18 | 2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 789 | 962 | 465 | 42 | 2258 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 73.681 | 171.7857 | C2 | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20420.9767 | 34261.6691 | 7214.9986 | 61897.6443 |  | 0 | 0 | 20420.9767 | 34261.6691 | 7214.9986 | 61897.6443
|  |  | 312 | 312 | C3 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 67 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 64 | 6 | 312 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 110.5215 | 257.6785 | C3 | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594
|  |  | 5 | 5 | C4 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 184.2025 | 429.4642 | C4 | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407
|  |  | 2575 | 2575 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 901 | 1099 | 554 | 21 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 900 | 1097 | 530 | 48 | [22 empty] | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24762.0263 | 41519.2484 | 8761.0697 | 75042.3444 |  | 0 | 0 | 24762.0263 | 41519.2484 | 8761.0697 | 75042.3444
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 48.4269 | 93.9681 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1003 | 1003 | C2 | 215 | 464 | 324 | 0 | 0 | 1003 | 189 | 464 | 350 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 420 | 280 | 125 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 494 | 244 | 239 | 0 | 1003 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 69.1813 | 134.2401 | C2 | 0 | 0 | 7429.6693 | 0 | 0 | 7429.6693 |  | 0 | 0 | 6877.751 | 0 | 0 | 6877.751 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5179.5409 | 16534.3366 | 0 | 21713.8775 |  | 0 | 0 | 5179.5409 | 16534.3366 | 0 | 21713.8775
|  |  | 147 | 147 | C3 | 31 | 68 | 48 | 0 | 0 | 147 | 31 | 68 | 48 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 62 | 45 | 18 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 39 | 36 | 0 | 147 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 103.772 | 201.3602 | C3 | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077
|  |  | 1 | 1 | C4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 172.9533 | 335.6003 | C4 | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533
|  |  | 1151 | 1151 |  | 246 | 532 | 373 | 0 | 0 |  | 220 | 532 | 399 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 200 | 482 | 325 | 144 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26 | 566 | 283 | 276 | 0 | [22 empty] | 0 | 0 | 9011.1274 | 0 | 0 | 9011.1274 |  | 0 | 0 | 8459.2092 | 0 | 0 | 8459.2092 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 6421.357 | 20443.0815 | 0 | 26864.4385 |  | 0 | 0 | 6421.357 | 20443.0815 | 0 | 26864.4385
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 |  | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 |  | 104168.4338 | 543013.1739 | 1075342.409 | 633112.3321 | 1204810.9809 | 3560447.3297
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 313807 | 313807 |  | 50304 | 158234 | 82171 | 21650 | 1448 |  | 44998 | 157737 | 82173 | 22091 | 7478 |  | 0 | 66 | 0 | -60 | -6 |  | 34863 | 125195 | 95392 | 49327 | 9031 |  | 0 | 337 | 0 | -328 | -9 |  | 23791 | 112928 | 92300 | 61502 | 23287 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 |  | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 |  | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 |  | 1112634.7766 | 4521311.529 | 11286792.2183 | 9888697.1133 | 3673506.6963 | 30482942.3336 |  | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 |  | 723438.3877 | 4133302.2044 | 11632351.22 | 12334290.6255 | 8199990.8378 | 37023373.2754
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 | LV Network | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 | HV Network | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 | HV Network | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 | HV Network | 421769.7369 | 1988951.0413 | 5387189.5593 | 2895760.4449 | 1087810.4144 | 11781481.1968 | HV Network | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 | HV Network | 216627.3123 | 1903561.9461 | 5645515.65 | 3309090.4207 | 3251872.7081 | 14326668.0372
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 | EHV Network | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 | EHV Network | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 | EHV Network | 116633.465 | 618964.1785 | 1480381.969 | 600259.309 | 585883.812 | 3402122.7335 | EHV Network | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 | EHV Network | 73402.6279 | 504177.5181 | 1866154.1248 | 816683.1718 | 968245.1114 | 4228662.5541
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 | 132kV Network | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 | 132kV Network | 104168.4338 | 543013.1739 | 1075342.409 | 633112.3321 | 1204810.9809 | 3560447.3297
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 | Total | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 | Total | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 | Total | 1112634.7766 | 4521311.529 | 11286792.2183 | 9888697.1133 | 3673506.6963 | 30482942.3336 | Total | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 | Total | 723438.3877 | 4133302.2044 | 11632351.22 | 12334290.6255 | 8199990.8378 | 37023373.2754
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SPN - HVP
Secondary deliverables RIIO-ED1 - HVP - Asset Replacement and Refurbishment driven | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SPN | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 1 | 1 | C1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 1 | Yes |  | C1 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | 7688.1 | C1 | 8.3151 | 19.0395 | 58.9198 | 96.0302 | 154.2283 | C1 | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198 |  | 0 | 0 | 58.9198 | 0 | 0 | 58.9198
|  |  | 13779 | 13779 | C2 | 1531 | 1533 | 9111 | 1558 | 46 | 13779 | 1486 | 1347 | 9111 | 1558 | 91 | 13593 | 0 | 0 | 0 | 0 | 0 | 0 | 961 | 1371 | 9146 | 2111 | 190 | 13779 | 0 | 0 | 0 | 0 | 0 | 0 | 45 | 1480 | 8545 | 3378 | 331 | 13779 | No |  | C2 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C2 | 10983 | 10983 | 10983 | 10983 | 10983 | C2 | 11.8787 | 27.1994 | 84.1712 | 137.186 | 220.3262 | C2 | 17651.8005 | 36637.5281 | 766883.8029 | 213735.7565 | 20049.6801 | 1054958.5681 |  | 18186.3436 | 41696.6077 | 766883.8029 | 213735.7565 | 10135.0031 | 1050637.5138 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 11415.4645 | 37290.3125 | 769829.7949 | 289599.6034 | 41861.9693 | 1149997.1447 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857 |  | 534.5431 | 40255.042 | 719242.9037 | 463414.2398 | 72927.9571 | 1296374.6857
|  |  | 6600 | 6600 | C3 | 644 | 1451 | 3831 | 655 | 19 | 6600 | 590 | 1451 | 3831 | 655 | 73 | 6600 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 1445 | 3801 | 877 | 43 | 6600 | 0 | 0 | 0 | 0 | 0 | 0 | 54 | 1489 | 3551 | 1404 | 102 | 6600 |  |  | C3 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C3 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | 16474.5 | C3 | 17.8181 | 40.799 | 126.2568 | 205.779 | 330.4892 | C3 | 10512.6807 | 59199.3911 | 483689.8006 | 134785.2252 | 24125.7139 | 712312.8115 |  | 11474.8582 | 59199.3911 | 483689.8006 | 134785.2252 | 6279.2954 | 695428.5705 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 7733.0566 | 58954.597 | 479902.0966 | 180468.1564 | 14211.037 | 741268.9436 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035 |  | 962.1776 | 60749.7542 | 448337.8966 | 288913.6735 | 33709.9016 | 832673.4035
|  |  | 606 | 606 | C4 | 59 | 133 | 352 | 60 | 2 | 606 | 54 | 133 | 352 | 60 | 7 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 132 | 349 | 81 | 4 | 606 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 137 | 326 | 129 | 9 | 606 |  |  | C4 | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061 | C4 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | 27457.5 | C4 | 29.6968 | 67.9984 | 210.428 | 342.9649 | 550.8154 | C4 | 1603.6293 | 9043.7848 | 74070.656 | 20577.897 | 3855.7077 | 109151.6747 |  | 1752.1134 | 9043.7848 | 74070.656 | 20577.897 | 1101.6308 | 106546.0819 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 1187.8735 | 8975.7864 | 73439.372 | 27780.1609 | 2203.2615 | 113586.4543 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074 |  | 148.4842 | 9315.7783 | 68599.528 | 44242.4785 | 4957.3385 | 127263.6074
|  |  | 20986 | 20986 |  | 2234 | 3117 | 13295 | 2273 | 67 |  | 2130 | 2931 | 13295 | 2273 | 171 |  | 0 | 0 | 0 | 0 | 0 |  | 1435 | 2948 | 13297 | 3069 | 237 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 3106 | 12423 | 4911 | 442 | [22 empty] | 29768.1104 | 104880.704 | 1324703.1793 | 369098.8787 | 48031.1017 | 1876481.9741 |  | 31413.3153 | 109939.7836 | 1324703.1793 | 369098.8787 | 17515.9293 | 1852671.0861 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 20336.3947 | 105220.6959 | 1323230.1833 | 497847.9207 | 58276.2678 | 2004911.4625 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165 |  | 1645.2048 | 110320.5745 | 1236239.2482 | 796570.3917 | 111595.1972 | 2256370.6165
| LV UGB |  | 677 | 677 | C1 | 91 | 126 | 187 | 258 | 15 | 677 | 86 | 126 | 187 | 258 | 20 | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 73 | 135 | 384 | 30 | 677 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 66 | 485 | 46 | 676 |  |  | C1 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C1 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | 7739.9 | C1 | 11.0956 | 16.6433 | 55.4778 | 122.0512 | 238.5547 | C1 | 954.2186 | 2097.0618 | 10374.3535 | 31489.2142 | 4771.0931 | 49685.9412 |  | 1009.6964 | 2097.0618 | 10374.3535 | 31489.2142 | 3578.3198 | 48548.6457 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 610.2561 | 1214.9644 | 7489.5065 | 46867.6676 | 7156.6396 | 63339.0342 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176 |  | 510.396 | 549.2305 | 3661.5365 | 59194.8406 | 10973.514 | 74889.5176
|  |  | 19687 | 19687 | C2 | 2638 | 3677 | 5444 | 7503 | 425 | 19687 | 2493 | 3677 | 5444 | 7503 | 569 | 19686 | 0 | 0 | 0 | 0 | 0 | 0 | 1594 | 2136 | 3923 | 11170 | 863 | 19686 | 0 | 0 | 0 | 0 | 0 | 0 | 1334 | 963 | 1930 | 14111 | 1350 | 19688 |  |  | C2 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C2 | 11057 | 11057 | 11057 | 11057 | 11057 | C2 | 15.8508 | 23.7762 | 79.254 | 174.3589 | 340.7924 | C2 | 39516.0631 | 87425.1287 | 431458.9798 | 1308214.6945 | 193910.8534 | 2060525.7195 |  | 41814.4302 | 87425.1287 | 431458.9798 | 1308214.6945 | 144836.7534 | 2013749.9866 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 25266.1871 | 50785.9872 | 310913.5889 | 1947588.7161 | 294103.8076 | 2628658.2869 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375 |  | 21144.9772 | 22896.4914 | 152960.2923 | 2460378.1892 | 460069.6874 | 3117449.6375
|  |  | 4474 | 4474 | C3 | 599 | 836 | 1237 | 1705 | 97 | 4474 | 567 | 836 | 1237 | 1705 | 129 | 4474 | 0 | 0 | 0 | 0 | 0 | 0 | 362 | 486 | 892 | 2539 | 196 | 4475 | 0 | 0 | 0 | 0 | 0 | 0 | 303 | 219 | 439 | 3207 | 307 | 4475 |  |  | C3 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C3 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | 16585.5 | C3 | 23.7762 | 35.6643 | 118.8811 | 261.5383 | 511.1885 | C3 | 13481.1118 | 29815.3689 | 147055.8665 | 445922.8417 | 65943.3219 | 702218.5107 |  | 14241.9505 | 29815.3689 | 147055.8665 | 445922.8417 | 49585.2885 | 686621.3161 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 8606.9885 | 17332.858 | 106041.9021 | 664045.8035 | 100192.9541 | 896220.5062 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747 |  | 7204.192 | 7810.4854 | 52188.7837 | 838753.4037 | 156934.8822 | 1062891.747
|  |  | 3369 | 3369 | C4 | 451 | 629 | 932 | 1284 | 73 | 3369 | 427 | 629 | 932 | 1284 | 97 | 3369 | 0 | 0 | 0 | 0 | 0 | 0 | 273 | 366 | 671 | 1912 | 148 | 3370 | 0 | 0 | 0 | 0 | 0 | 0 | 228 | 165 | 330 | 2415 | 231 | 3369 |  |  | C4 | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821 | C4 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | 27642.5 | C4 | 39.627 | 59.4405 | 198.1351 | 435.8972 | 851.9809 | C4 | 16920.737 | 37388.0922 | 184661.9072 | 559692.0124 | 82642.1475 | 881304.8964 |  | 17871.7854 | 37388.0922 | 184661.9072 | 559692.0124 | 62194.6059 | 861808.4032 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 10818.1761 | 21755.2333 | 132948.6478 | 833435.4578 | 126093.1736 | 1125050.6885 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691 |  | 9034.9603 | 9807.6871 | 65384.5809 | 1052691.7523 | 196807.5885 | 1333726.5691
|  |  | 28207 | 28207 |  | 3779 | 5268 | 7800 | 10750 | 610 |  | 3573 | 5268 | 7800 | 10750 | 815 |  | 0 | 0 | 0 | 0 | 0 |  | 2284 | 3061 | 5621 | 16005 | 1237 |  | 0 | 0 | 0 | 0 | 0 |  | 1911 | 1380 | 2765 | 20218 | 1934 | [22 empty] | 70872.1304 | 156725.6516 | 773551.1071 | 2345318.7627 | 347267.4159 | 3693735.0677 |  | 74937.8626 | 156725.6516 | 773551.1071 | 2345318.7627 | 260194.9676 | 3610728.3516 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 45301.6078 | 91089.0429 | 557393.6453 | 3491937.645 | 527546.5748 | 4713268.5159 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711 |  | 37894.5255 | 41063.8944 | 274195.1933 | 4411018.1858 | 824785.6721 | 5588957.4711
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C1 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | 9737.7 | C1 | 14.8033 | 14.8033 | 29.7404 | 81.901 | 162.3867 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 124969 | 124969 | C2 | 21863 | 72930 | 26079 | 4097 | 0 | 124969 | 19674 | 73119 | 26079 | 4097 | 2189 | 125158 | 0 | 0 | 0 | 0 | 0 | 0 | 16316 | 54726 | 37003 | 13968 | 2956 | 124969 | 0 | 0 | 0 | 0 | 0 | 0 | 13510 | 48074 | 35619 | 19954 | 7812 | 124969 |  |  | C2 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C2 | 13911 | 13911 | 13911 | 13911 | 13911 | C2 | 21.1475 | 21.1475 | 42.4864 | 117.0014 | 231.981 | C2 | 416056.8929 | 1546287.6868 | 1108001.6864 | 479354.7947 | 507806.3433 | 4057507.4041 |  | 462348.8792 | 1542290.7999 | 1108001.6864 | 479354.7947 | 0 | 3591996.1602 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 345043.421 | 1157320.8051 | 1572122.6429 | 1634275.7559 | 685735.7473 | 5394498.3721 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865 |  | 285703.3965 | 1016647.3045 | 1513321.5257 | 2334646.2223 | 1812235.3375 | 6962553.7865
|  |  | 1184 | 1184 | C3 | 143 | 852 | 189 | 0 | 0 | 1184 | 124 | 852 | 189 | 0 | 19 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 143 | 529 | 350 | 132 | 30 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 126 | 456 | 337 | 189 | 76 | 1184 |  |  | C3 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C3 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | 20866.5 | C3 | 31.7213 | 31.7213 | 63.7295 | 175.5021 | 347.9715 | C3 | 3933.4442 | 27026.5685 | 12044.882 | 0 | 6611.4576 | 49616.3524 |  | 4536.1494 | 27026.5685 | 12044.882 | 0 | 0 | 43607.6 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 4536.1494 | 16780.5807 | 22305.3371 | 23166.28 | 10439.1436 | 77227.4909 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956 |  | 3996.8869 | 14464.924 | 21476.8531 | 33169.901 | 26445.8306 | 99554.3956
|  |  | 2 | 2 | C4 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 | 0 | 0 | 2 |  |  | C4 | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676 | C4 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | 34777.5 | C4 | 52.8689 | 52.8689 | 106.2159 | 292.5035 | 579.9524 | C4 | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848 |  | 0 | 52.8689 | 106.2159 | 0 | 0 | 159.0848
|  |  | 126155 | 126155 |  | 22006 | 73783 | 26269 | 4097 | 0 |  | 19798 | 73972 | 26269 | 4097 | 2208 |  | 0 | 0 | 0 | 0 | 0 |  | 16459 | 55256 | 37354 | 14100 | 2986 |  | 0 | 0 | 0 | 0 | 0 |  | 13636 | 48531 | 35957 | 20143 | 7888 | [22 empty] | 419990.3371 | 1573367.1242 | 1120152.7843 | 479354.7947 | 514417.8009 | 4107282.8413 |  | 466885.0286 | 1569370.2373 | 1120152.7843 | 479354.7947 | 0 | 3635762.845 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 349579.5704 | 1174154.2547 | 1594534.1958 | 1657442.036 | 696174.8909 | 5471884.9478 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669 |  | 289700.2834 | 1031165.0974 | 1534904.5947 | 2367816.1233 | 1838681.1681 | 7062267.2669
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 |  | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 |  | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 1843 | 1843 | C1 | 494 | 947 | 398 | 4 | 0 | 1843 | 477 | 947 | 398 | 20 | 1 | 1843 | 0 | 0 | 0 | 0 | 0 | 0 | 437 | 678 | 538 | 183 | 7 | 1843 | 0 | 0 | 0 | 0 | 0 | 0 | 211 | 638 | 620 | 336 | 38 | 1843 |  |  | C1 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C1 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | 33524.0887 | C1 | 58.7072 | 58.7072 | 219.7445 | 403.678 | 555.67 | C1 | 28003.3423 | 55595.734 | 87458.3248 | 8073.5593 | 555.67 | 179686.6303 |  | 29001.3649 | 55595.734 | 87458.3248 | 1614.7119 | 0 | 173670.1356 |  | 25655.0536 | 39803.4928 | 118222.5596 | 73873.068 | 3889.6899 | 261443.8638 |  | 25655.0536 | 39803.4928 | 118222.5596 | 73873.068 | 3889.6899 | 261443.8638 |  | 12387.2227 | 37455.2041 | 136241.6114 | 135635.7969 | 21115.4594 | 342835.2945 |  | 12387.2227 | 37455.2041 | 136241.6114 | 135635.7969 | 21115.4594 | 342835.2945
|  |  | 829 | 829 | C2 | 99 | 627 | 103 | 0 | 0 | 829 | 98 | 533 | 103 | 11 | 1 | 746 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 427 | 222 | 106 | 0 | 829 | 0 | 0 | 0 | 0 | 0 | 0 | 40 | 270 | 358 | 149 | 12 | 829 |  |  | C2 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C2 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | 47891.5553 | C2 | 83.8675 | 83.8675 | 313.9208 | 576.6828 | 793.8143 | C2 | 8219.0103 | 44701.352 | 32333.8387 | 6343.5109 | 793.8143 | 92391.5261 |  | 8302.8778 | 52584.8925 | 32333.8387 | 0 | 0 | 93221.6089 |  | 6206.1915 | 35811.402 | 69690.4095 | 61128.3779 | 0 | 172836.3809 |  | 6206.1915 | 35811.402 | 69690.4095 | 61128.3779 | 0 | 172836.3809 |  | 3354.6981 | 22644.2121 | 112383.6334 | 85925.7387 | 9525.7711 | 233834.0534 |  | 3354.6981 | 22644.2121 | 112383.6334 | 85925.7387 | 9525.7711 | 233834.0534
|  |  | 317 | 317 | C3 | 44 | 244 | 29 | 0 | 0 | 317 | 44 | 244 | 29 | 0 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 38 | 181 | 50 | 48 | 0 | 317 | 0 | 0 | 0 | 0 | 0 | 0 | 20 | 102 | 135 | 57 | 3 | 317 |  |  | C3 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C3 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | 71837.3329 | C3 | 125.8012 | 125.8012 | 470.8811 | 865.0242 | 1190.7214 | C3 | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 5535.2518 | 30695.4875 | 13655.5532 | 0 | 0 | 49886.2925 |  | 4780.4448 | 22770.0132 | 23544.0573 | 41521.1623 | 0 | 92615.6776 |  | 4780.4448 | 22770.0132 | 23544.0573 | 41521.1623 | 0 | 92615.6776 |  | 2516.0236 | 12831.7202 | 63568.9546 | 49306.3803 | 3572.1642 | 131795.2428 |  | 2516.0236 | 12831.7202 | 63568.9546 | 49306.3803 | 3572.1642 | 131795.2428
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575 | C4 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | 119728.8881 | C4 | 209.6686 | 209.6686 | 784.8019 | 1441.707 | 1984.5357 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2989 | 2989 |  | 637 | 1818 | 530 | 4 | 0 |  | 619 | 1724 | 530 | 31 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 549 | 1286 | 810 | 337 | 7 |  | 0 | 0 | 0 | 0 | 0 |  | 271 | 1010 | 1113 | 542 | 53 | [22 empty] | 41757.6044 | 130992.5734 | 133447.7166 | 14417.0703 | 1349.4842 | 321964.449 |  | 42839.4945 | 138876.1139 | 133447.7166 | 1614.7119 | 0 | 316778.037 |  | 36641.6898 | 98384.9081 | 211457.0264 | 176522.6082 | 3889.6899 | 526895.9223 |  | 36641.6898 | 98384.9081 | 211457.0264 | 176522.6082 | 3889.6899 | 526895.9223 |  | 18257.9443 | 72931.1363 | 312194.1994 | 270867.9159 | 34213.3947 | 708464.5907 |  | 18257.9443 | 72931.1363 | 312194.1994 | 270867.9159 | 34213.3947 | 708464.5907
| HV Switchgear (GM) - Distribution |  | 4606 | 4606 | C1 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 3169 | 1294 | 117 | 22 | 4 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 1477 | 2931 | 42 | 88 | 68 | 4606 | 0 | 0 | 0 | 0 | 0 | 0 | 268 | 4101 | 52 | 28 | 157 | 4606 |  |  | C1 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C1 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | 24423.1056 | C1 | 13.6425 | 13.6425 | 51.2806 | 94.0237 | 160.8309 | C1 | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 43233.0468 | 17653.3804 | 5999.8353 | 2068.5205 | 643.3237 | 69598.1068 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 20149.9559 | 39986.1345 | 2153.787 | 8274.082 | 10936.5035 | 81500.4629 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458 |  | 3656.187 | 55947.8463 | 2666.5935 | 2632.6625 | 25250.4566 | 90153.7458
|  |  | 22477 | 22477 | C2 | 5578 | 7761 | 6551 | 2065 | 522 | 22477 | 4662 | 7508 | 6551 | 2291 | 2419 | 23431 | 0 | 0 | 0 | 0 | 0 | 0 | 4507 | 8127 | 1170 | 6052 | 2621 | 22477 | 0 | 0 | 0 | 0 | 0 | 0 | 2324 | 9700 | 1039 | 1616 | 7798 | 22477 |  |  | C2 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C2 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | 34890.1509 | C2 | 19.4893 | 19.4893 | 73.2581 | 134.3195 | 229.7585 | C2 | 90858.975 | 146325.4364 | 479913.5676 | 307726.0048 | 555785.7551 | 1580609.7388 |  | 108711.146 | 151256.2216 | 479913.5676 | 277369.7948 | 119933.9248 | 1137184.6548 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 87838.1382 | 158389.2943 | 85711.9331 | 812901.694 | 602196.9674 | 1747038.027 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394 |  | 45293.0626 | 189045.9154 | 76115.127 | 217060.3334 | 1791656.6011 | 2319171.0394
|  |  | 585 | 585 | C3 | 91 | 195 | 229 | 49 | 21 | 585 | 91 | 195 | 229 | 49 | 21 | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 137 | 98 | 175 | 173 | 585 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 74 | 44 | 362 | 585 |  |  | C3 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C3 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | 52335.2263 | C3 | 29.2339 | 29.2339 | 109.8871 | 201.4793 | 344.6377 | C3 | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 2660.2853 | 5700.6114 | 25164.1445 | 9872.4842 | 7237.392 | 50634.9174 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 58.4678 | 4005.0449 | 10768.9352 | 35258.8722 | 59622.3247 | 109713.6448 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456 |  | 0 | 3069.56 | 8131.6449 | 8865.0879 | 124758.8528 | 144825.1456
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852 | C4 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | 87225.3772 | C4 | 48.7232 | 48.7232 | 183.1452 | 335.7988 | 574.3962 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27668 | 27668 |  | 8838 | 9250 | 6897 | 2136 | 547 |  | 7922 | 8997 | 6897 | 2362 | 2444 |  | 0 | 0 | 0 | 0 | 0 |  | 5986 | 11195 | 1310 | 6315 | 2862 |  | 0 | 0 | 0 | 0 | 0 |  | 2592 | 13906 | 1165 | 1688 | 8317 | [22 empty] | 136752.3071 | 169679.4282 | 511077.5474 | 319667.0095 | 563666.4708 | 1700842.763 |  | 154604.4781 | 174610.2134 | 511077.5474 | 289310.7995 | 127814.6406 | 1257417.679 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 108046.5619 | 202380.4737 | 98634.6554 | 856434.6482 | 672755.7955 | 1938252.1347 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309 |  | 48949.2496 | 248063.3217 | 86913.3654 | 228558.0837 | 1941665.9105 | 2554149.9309
| HV Transformer (GM) |  | 9731 | 9731 | C1 | 1332 | 2840 | 5559 | 0 | 0 | 9731 | 1259 | 2840 | 5559 | 62 | 11 | 9731 | 0 | 0 | 0 | 0 | 0 | 0 | 730 | 3228 | 5574 | 199 | 0 | 9731 | 0 | 0 | 0 | 0 | 0 | 0 | 139 | 3457 | 5717 | 418 | 0 | 9731 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | 51116.562 | C1 | 45.0878 | 54.95 | 154.9879 | 295.6111 | 498.624 | C1 | 56765.5022 | 156058.1406 | 861577.5631 | 18327.889 | 5484.864 | 1098213.959 |  | 60056.9094 | 156058.1406 | 861577.5631 | 0 | 0 | 1077692.6132 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 32914.072 | 177378.7598 | 863902.3812 | 58826.6115 | 0 | 1133021.8245 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129 |  | 6267.2 | 189962.3212 | 886065.6464 | 123565.4453 | 0 | 1205860.6129
|  |  | 5287 | 5287 | C2 | 651 | 1916 | 2720 | 0 | 0 | 5287 | 595 | 1714 | 2720 | 50 | 6 | 5085 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 1888 | 2913 | 104 | 0 | 5287 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 2009 | 2988 | 218 | 0 | 5287 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | 73023.66 | C2 | 64.4111 | 78.5001 | 221.4112 | 422.3016 | 712.32 | C2 | 38324.6044 | 134549.1212 | 602238.5762 | 21115.0795 | 4273.92 | 800501.3013 |  | 41931.626 | 150406.1355 | 602238.5762 | 0 | 0 | 794576.3377 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 24605.0401 | 148208.1336 | 644970.9458 | 43919.3654 | 0 | 861703.4849 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768 |  | 4637.5992 | 157706.6421 | 661576.7889 | 92061.7466 | 0 | 915982.7768
|  |  | 4141 | 4141 | C3 | 566 | 1209 | 2366 | 0 | 0 | 4141 | 518 | 1209 | 2366 | 43 | 5 | 4141 | 0 | 0 | 0 | 0 | 0 | 0 | 311 | 1374 | 2370 | 86 | 0 | 4141 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 1471 | 2433 | 178 | 0 | 4141 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | 109535.49 | C3 | 96.6166 | 117.7501 | 332.1169 | 633.4524 | 1068.48 | C3 | 50047.4245 | 142359.8783 | 785788.4953 | 27238.4526 | 5342.4 | 1010776.6506 |  | 54685.0237 | 142359.8783 | 785788.4953 | 0 | 0 | 982833.3973 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 30047.7781 | 161788.6458 | 787116.9627 | 54476.9051 | 0 | 1033430.2917 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638 |  | 5700.3823 | 173210.4061 | 808040.325 | 112754.5245 | 0 | 1099705.638
|  |  | 2071 | 2071 | C4 | 283 | 605 | 1183 | 0 | 0 | 2071 | 260 | 605 | 1183 | 21 | 2 | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 155 | 687 | 1186 | 43 | 0 | 2071 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 736 | 1216 | 89 | 0 | 2071 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | 182559.15 | C4 | 161.0277 | 196.2502 | 553.5281 | 1055.754 | 1780.8 | C4 | 41867.2149 | 118731.357 | 654823.746 | 22170.8335 | 3561.6 | 841154.7514 |  | 45570.8531 | 118731.357 | 654823.746 | 0 | 0 | 819125.9561 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 24959.3012 | 134823.8715 | 656484.3304 | 45397.4209 | 0 | 861664.924 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399 |  | 4830.8325 | 144440.1302 | 673090.1735 | 93962.1038 | 0 | 916323.2399
|  |  | 21230 | 21230 |  | 2832 | 6570 | 11828 | 0 | 0 |  | 2632 | 6368 | 11828 | 176 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 1578 | 7177 | 12043 | 432 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 300 | 7673 | 12354 | 903 | 0 | [22 empty] | 187004.746 | 551698.4971 | 2904428.3807 | 88852.2546 | 18662.7838 | 3750646.6623 |  | 202244.4122 | 567555.5114 | 2904428.3807 | 0 | 0 | 3674228.3044 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 112526.1913 | 622199.4107 | 2952474.6201 | 202620.3029 | 0 | 3889820.525 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676 |  | 21436.014 | 665319.4995 | 3028772.9338 | 422343.8202 | 0 | 4137872.2676
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 9772 | 9772 | C1 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 742 | 7231 | 1620 | 179 | 0 | 9772 | 0 | 0 | 0 | 0 | 0 | 0 | 558 | 5094 | 2706 | 1021 | 393 | 9772 | 0 | 0 | 0 | 0 | 0 | 0 | 382 | 4298 | 2825 | 1534 | 733 | 9772 |  |  | C1 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C1 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | 18601.2171 | C1 | 19.1659 | 19.1659 | 72.1182 | 151.5867 | 233.6923 | C1 | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 14221.0645 | 138588.2982 | 116831.5104 | 27134.0218 | 0 | 296774.8949 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 10694.5471 | 97630.8658 | 195151.8933 | 154770.0352 | 91841.0782 | 550088.4197 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464 |  | 7321.3566 | 82374.8452 | 203733.9611 | 232534.0195 | 171296.464 | 697260.6464
|  |  | 39560 | 39560 | C2 | 4761 | 27072 | 6789 | 938 | 0 | 39560 | 3776 | 27093 | 6789 | 938 | 985 | 39581 | 0 | 0 | 0 | 0 | 0 | 0 | 3243 | 20614 | 10962 | 4136 | 605 | 39560 | 0 | 0 | 0 | 0 | 0 | 0 | 2533 | 17389 | 11440 | 6215 | 1983 | 39560 |  |  | C2 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C2 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | 26573.1672 | C2 | 27.3798 | 27.3798 | 103.026 | 216.5524 | 333.8462 | C2 | 103386.0983 | 741800.7314 | 699443.6721 | 203126.197 | 328838.4663 | 2076595.1651 |  | 130355.1944 | 741225.7558 | 699443.6721 | 203126.197 | 0 | 1774150.8193 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 88792.6687 | 564407.0527 | 1129371.2673 | 895660.9283 | 201976.926 | 2880208.8429 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443 |  | 69353.0156 | 476107.2203 | 1178617.7065 | 1345873.4694 | 662016.9326 | 3731968.3443
|  |  | 18629 | 18629 | C3 | 2618 | 12458 | 3162 | 391 | 0 | 18629 | 2100 | 12458 | 3162 | 391 | 518 | 18629 | 0 | 0 | 0 | 0 | 0 | 0 | 1581 | 9711 | 5159 | 1947 | 231 | 18629 | 0 | 0 | 0 | 0 | 0 | 0 | 1246 | 8194 | 5385 | 2925 | 879 | 18629 |  |  | C3 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C3 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | 39859.7509 | C3 | 41.0697 | 41.0697 | 154.539 | 324.8287 | 500.7692 | C3 | 86246.3479 | 511646.1916 | 488652.4285 | 127008.0112 | 259398.4653 | 1472951.4445 |  | 107520.4471 | 511646.1916 | 488652.4285 | 127008.0112 | 0 | 1234827.0783 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 64931.1791 | 398827.7546 | 797266.8812 | 632441.4268 | 115677.694 | 2009144.9356 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012 |  | 51172.8331 | 336525.0356 | 832192.7031 | 950123.8692 | 440176.1602 | 2610190.6012
|  |  | 41 | 41 | C4 | 2 | 39 | 0 | 0 | 0 | 41 | 2 | 39 | 0 | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 22 | 11 | 4 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18 | 12 | 6 | 3 | 41 |  |  | C4 | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563 | C4 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | 66432.9181 | C4 | 68.4495 | 68.4495 | 257.5651 | 541.3811 | 834.6154 | C4 | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 2669.5298 | 0 | 0 | 0 | 2806.4288 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 136.899 | 1505.8886 | 2833.2156 | 2165.5245 | 1669.2308 | 8310.7585 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033 |  | 136.899 | 1232.0907 | 3090.7807 | 3248.2867 | 2503.8462 | 10211.9033
|  |  | 68002 | 68002 |  | 8123 | 46800 | 11571 | 1508 | 0 |  | 6620 | 46821 | 11571 | 1508 | 1503 |  | 0 | 0 | 0 | 0 | 0 |  | 5384 | 35441 | 18838 | 7108 | 1231 |  | 0 | 0 | 0 | 0 | 0 |  | 4163 | 29899 | 19662 | 10680 | 3598 | [22 empty] | 203990.4097 | 1394704.751 | 1304927.611 | 357268.2301 | 588236.9315 | 3849127.9333 |  | 252233.6049 | 1394129.7753 | 1304927.611 | 357268.2301 | 0 | 3308559.2213 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 164555.2938 | 1062371.5617 | 2124623.2575 | 1685037.9147 | 411164.929 | 5447752.9567 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952 |  | 127984.1043 | 896239.1918 | 2217635.1514 | 2531779.6448 | 1275993.403 | 7049631.4952
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 |  | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 |  | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 |  | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 |  | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 |  | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 217 | 217 | C1 | 136 | 76 | 5 | 0 | 0 | 217 | 136 | 76 | 5 | 0 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 131 | 71 | 13 | 2 | 0 | 217 | 0 | 0 | 0 | 0 | 0 | 0 | 80 | 117 | 18 | 2 | 0 | 217 |  |  | C1 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C1 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | 37487.9198 | C1 | 165.6424 | 165.6424 | 625.0091 | 1143.9769 | 1952.7416 | C1 | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 22527.3712 | 12588.8251 | 3125.0455 | 0 | 0 | 38241.2418 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 21699.159 | 11760.6129 | 8125.1182 | 2287.9537 | 0 | 43872.8439 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772 |  | 13251.3948 | 19380.1649 | 11250.1637 | 2287.9537 | 0 | 46169.6772
|  |  | 505 | 505 | C2 | 153 | 280 | 69 | 3 | 0 | 505 | 153 | 271 | 69 | 3 | 0 | 496 | 0 | 0 | 0 | 0 | 0 | 0 | 112 | 227 | 143 | 11 | 12 | 505 | 0 | 0 | 0 | 0 | 0 | 0 | 74 | 190 | 207 | 17 | 17 | 505 |  |  | C2 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C2 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | 53554.1711 | C2 | 236.6321 | 236.6321 | 892.8701 | 1634.2527 | 2789.6309 | C2 | 36204.7037 | 64127.2857 | 61608.0394 | 4902.758 | 0 | 166842.7867 |  | 36204.7037 | 66256.9741 | 61608.0394 | 4902.758 | 0 | 168972.4752 |  | 26502.7897 | 53715.4755 | 127680.4294 | 17976.7792 | 33475.5706 | 259351.0444 |  | 26502.7897 | 53715.4755 | 127680.4294 | 17976.7792 | 33475.5706 | 259351.0444 |  | 17510.7717 | 44960.0896 | 184824.1181 | 27782.2952 | 47423.725 | 322500.9996 |  | 17510.7717 | 44960.0896 | 184824.1181 | 27782.2952 | 47423.725 | 322500.9996
|  |  | 70 | 70 | C3 | 8 | 54 | 8 | 0 | 0 | 70 | 8 | 54 | 8 | 0 | 0 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 41 | 16 | 0 | 5 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 32 | 26 | 2 | 5 | 70 |  |  | C3 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C3 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | 80331.2566 | C3 | 354.9481 | 354.9481 | 1339.3052 | 2451.379 | 4184.4463 | C3 | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 19167.1961 | 10714.4416 | 0 | 0 | 32721.2223 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 2839.5846 | 14552.8711 | 21428.8833 | 0 | 20922.2316 | 59743.5706 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037 |  | 1774.7404 | 11358.3384 | 34821.9353 | 4902.758 | 20922.2316 | 73780.0037
|  |  | 6 | 6 | C4 | 2 | 3 | 1 | 0 | 0 | 6 | 2 | 3 | 1 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 2 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 4 | 0 | 0 | 6 |  |  | C4 | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209 | C4 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | 133885.4278 | C4 | 591.5801 | 591.5801 | 2232.1753 | 4085.6316 | 6974.0772 | C4 | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1774.7404 | 2232.1753 | 0 | 0 | 5190.076 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 1183.1603 | 1183.1603 | 4464.3507 | 0 | 0 | 6830.6712 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616 |  | 0 | 1183.1603 | 8928.7014 | 0 | 0 | 10111.8616
|  |  | 798 | 798 |  | 299 | 413 | 83 | 3 | 0 |  | 299 | 404 | 83 | 3 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 253 | 341 | 174 | 13 | 17 |  | 0 | 0 | 0 | 0 | 0 |  | 159 | 341 | 255 | 21 | 22 | [22 empty] | 62754.8198 | 97658.0472 | 77679.7018 | 4902.758 | 0 | 242995.3268 |  | 62754.8198 | 99787.7357 | 77679.7018 | 4902.758 | 0 | 245125.0153 |  | 52224.6935 | 81212.1197 | 161698.7816 | 20264.733 | 54397.8022 | 369798.13 |  | 52224.6935 | 81212.1197 | 161698.7816 | 20264.733 | 54397.8022 | 369798.13 |  | 32536.9069 | 76881.7532 | 239824.9185 | 34973.0069 | 68345.9566 | 452562.5421 |  | 32536.9069 | 76881.7532 | 239824.9185 | 34973.0069 | 68345.9566 | 452562.5421
| EHV Transformer |  | 194 | 194 | C1 | 21 | 140 | 22 | 8 | 3 | 194 | 21 | 140 | 22 | 8 | 3 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 109 | 52 | 14 | 8 | 194 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 86 | 78 | 16 | 9 | 194 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | 104625.9559 | C1 | 890.0227 | 890.0227 | 3333.6634 | 6914.518 | 14150.0662 | C1 | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 18690.476 | 124603.1731 | 73340.5937 | 55316.1438 | 42450.1985 | 314400.5851 |  | 9790.2493 | 97012.4705 | 173350.4943 | 96803.2517 | 113200.5292 | 490156.995 |  | 9790.2493 | 97012.4705 | 173350.4943 | 96803.2517 | 113200.5292 | 490156.995 |  | 4450.1133 | 76541.9492 | 260025.7415 | 110632.2876 | 127350.5954 | 579000.687 |  | 4450.1133 | 76541.9492 | 260025.7415 | 110632.2876 | 127350.5954 | 579000.687
|  |  | 259 | 259 | C2 | 29 | 154 | 59 | 11 | 6 | 259 | 26 | 143 | 59 | 11 | 9 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 120 | 84 | 23 | 10 | 259 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 89 | 96 | 46 | 16 | 259 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | 149465.6513 | C2 | 1271.461 | 1271.461 | 4762.3762 | 9877.8828 | 20214.3802 | C2 | 33057.9847 | 181818.9159 | 280980.1968 | 108656.711 | 181929.422 | 786443.2304 |  | 36872.3676 | 195804.9863 | 280980.1968 | 108656.711 | 121286.2813 | 743600.5431 |  | 27972.1409 | 152575.314 | 400039.6022 | 227191.3049 | 202143.8022 | 1009922.1643 |  | 27972.1409 | 152575.314 | 400039.6022 | 227191.3049 | 202143.8022 | 1009922.1643 |  | 15257.5314 | 113160.0246 | 457188.1168 | 454382.6098 | 323430.0835 | 1363418.3661 |  | 15257.5314 | 113160.0246 | 457188.1168 | 454382.6098 | 323430.0835 | 1363418.3661
|  |  | 42 | 42 | C3 | 4 | 29 | 7 | 0 | 2 | 42 | 3 | 29 | 7 | 0 | 3 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 17 | 18 | 1 | 2 | 42 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 9 | 23 | 5 | 3 | 42 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | 224198.4769 | C3 | 1907.1914 | 1907.1914 | 7143.5643 | 14816.8242 | 30321.5703 | C3 | 5721.5743 | 55308.5513 | 50004.9503 | 0 | 90964.711 | 201999.7869 |  | 7628.7657 | 55308.5513 | 50004.9503 | 0 | 60643.1407 | 173585.408 |  | 7628.7657 | 32422.2542 | 128584.1579 | 14816.8242 | 60643.1407 | 244095.1427 |  | 7628.7657 | 32422.2542 | 128584.1579 | 14816.8242 | 60643.1407 | 244095.1427 |  | 3814.3829 | 17164.7228 | 164301.9795 | 74084.1212 | 90964.711 | 350329.9173 |  | 3814.3829 | 17164.7228 | 164301.9795 | 74084.1212 | 90964.711 | 350329.9173
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | 373664.1282 | C4 | 3178.6524 | 3178.6524 | 11905.9405 | 24694.7071 | 50535.9505 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 495 | 495 |  | 54 | 323 | 88 | 19 | 11 |  | 50 | 312 | 88 | 19 | 15 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 246 | 154 | 38 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 19 | 184 | 197 | 67 | 28 | [22 empty] | 57470.035 | 361730.6403 | 404325.7408 | 163972.8548 | 315344.3314 | 1302843.6024 |  | 63191.6092 | 375716.7108 | 404325.7408 | 163972.8548 | 224379.6204 | 1231586.5361 |  | 45391.1559 | 282010.0388 | 701974.2544 | 338811.3808 | 375987.4721 | 1744174.3019 |  | 45391.1559 | 282010.0388 | 701974.2544 | 338811.3808 | 375987.4721 | 1744174.3019 |  | 23522.0276 | 206866.6966 | 881515.8378 | 639099.0186 | 541745.3899 | 2292748.9704 |  | 23522.0276 | 206866.6966 | 881515.8378 | 639099.0186 | 541745.3899 | 2292748.9704
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | 139872.6 | C1 | 74.7619 | 74.7619 | 280.2348 | 577.8137 | 1188.9171 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 199818 | 199818 | 199818 | 199818 | 199818 | C2 | 106.8027 | 106.8027 | 400.3354 | 825.4482 | 1698.453 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 7 | C3 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 7 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 299727 | 299727 | 299727 | 299727 | 299727 | C3 | 160.2041 | 160.2041 | 600.503 | 1238.1722 | 2547.6795 | C3 | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 499545 | 499545 | 499545 | 499545 | 499545 | C4 | 267.0068 | 267.0068 | 1000.8384 | 2063.6204 | 4246.1325 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7 | 7 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 7 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 7 | [22 empty] | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 8667.2057 | 0 | 8667.2057 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565 |  | 0 | 0 | 0 | 0 | 17833.7565 | 17833.7565
| EHV UG Cable (Oil) |  | 126 | 126 | C1 | 2 | 69 | 41 | 3 | 11 | 126 | 2 | 84 | 38 | 0 | 2 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 59 | 2 | 17 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 80 | 5 | 18 | 126 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | 217468.3 | C1 | 116.2368 | 116.2368 | 435.6977 | 898.3615 | 1848.4805 | C1 | 232.4736 | 9763.8917 | 16556.5141 | 0 | 3696.9611 | 30249.8405 |  | 232.4736 | 8020.3396 | 17863.6073 | 2695.0846 | 20333.286 | 49144.7912 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 5579.3667 | 25706.1666 | 1796.7231 | 31424.1694 | 64506.4258 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233 |  | 0 | 2673.4465 | 34855.8191 | 4491.8077 | 33272.6499 | 75293.7233
|  |  | 175 | 175 | C2 | 3 | 96 | 56 | 5 | 15 | 175 | 3 | 117 | 51 | 5 | 5 | 181 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 67 | 82 | 3 | 23 | 175 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 111 | 6 | 24 | 175 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 310669 | 310669 | 310669 | 310669 | 310669 | C2 | 166.0526 | 166.0526 | 622.4253 | 1283.3736 | 2640.6865 | C2 | 498.1577 | 19428.1519 | 31743.6924 | 6416.8682 | 13203.4325 | 71290.3028 |  | 498.1577 | 15941.0477 | 34855.8191 | 6416.8682 | 39610.2975 | 97322.1903 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 11125.5229 | 51038.878 | 3850.1209 | 60735.7895 | 126750.3113 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185 |  | 0 | 5645.7877 | 69089.2129 | 7700.2418 | 63376.476 | 145811.7185
|  |  | 145 | 145 | C3 | 2 | 80 | 47 | 3 | 13 | 145 | 2 | 90 | 42 | 11 | 0 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 55 | 68 | 3 | 19 | 145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 26 | 92 | 6 | 21 | 145 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | 466003.5 | C3 | 249.0789 | 249.0789 | 933.638 | 1925.0605 | 3961.0298 | C3 | 498.1577 | 22417.0984 | 39212.7965 | 21175.665 | 0 | 83303.7177 |  | 498.1577 | 19926.3097 | 43880.9866 | 5775.1814 | 51493.3868 | 121574.0221 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 13699.3379 | 63487.3848 | 5775.1814 | 75259.5652 | 158221.4693 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353 |  | 0 | 6476.0506 | 85894.6971 | 11550.3628 | 83181.6248 | 187102.7353
|  |  | 13 | 13 | C4 | 0 | 8 | 4 | 0 | 1 | 13 | 0 | 9 | 4 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 6 | 0 | 2 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 8 | 1 | 2 | 13 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | 776672.5 | C4 | 415.1315 | 415.1315 | 1556.0634 | 3208.4341 | 6601.7163 | C4 | 0 | 3736.1831 | 6224.2534 | 0 | 0 | 9960.4365 |  | 0 | 3321.0516 | 6224.2534 | 0 | 6601.7163 | 16147.0213 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 2075.6573 | 9336.3801 | 0 | 13203.4325 | 24615.4699 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363 |  | 0 | 830.2629 | 12448.5068 | 3208.4341 | 13203.4325 | 29690.6363
|  |  | 459 | 459 |  | 7 | 253 | 148 | 11 | 40 |  | 7 | 300 | 135 | 16 | 7 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 175 | 215 | 8 | 61 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 85 | 291 | 18 | 65 | [22 empty] | 1228.7891 | 55345.3251 | 93737.2564 | 27592.5332 | 16900.3936 | 194804.2974 |  | 1228.7891 | 47208.7486 | 102824.6664 | 14887.1342 | 118038.6865 | 284188.0249 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 32479.8847 | 149568.8096 | 11422.0254 | 180622.9566 | 374093.6763 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134 |  | 0 | 15625.5478 | 202288.236 | 26950.8464 | 193034.1831 | 437898.8134
| EHV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 338 | 338 | C1 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 113 | 206 | 16 | 3 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 208 | 16 | 12 | 338 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102 | 189 | 25 | 22 | 338 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | 151036.9 | C1 | 0 | 0 | 12.1985 | 42.3409 | 98.717 | C1 | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2512.89 | 677.4549 | 296.1509 | 3486.4958 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2537.287 | 677.4549 | 1184.6036 | 4399.3454 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812 |  | 0 | 0 | 2305.5156 | 1058.5232 | 2171.7732 | 5535.812
|  |  | 166 | 166 | C2 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 56 | 101 | 7 | 2 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 103 | 7 | 5 | 166 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 94 | 11 | 10 | 166 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 215767 | 215767 | 215767 | 215767 | 215767 | C2 | 0 | 0 | 17.4264 | 60.487 | 141.0242 | C2 | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1760.0686 | 423.4093 | 282.0485 | 2465.5264 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1794.9214 | 423.4093 | 705.1212 | 2923.4519 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834 |  | 0 | 0 | 1638.0836 | 665.3575 | 1410.2423 | 3713.6834
|  |  | 15 | 15 | C3 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 5 | 9 | 1 | 0 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 1 | 1 | 15 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | 323650.5 | C3 | 0 | 0 | 26.1396 | 90.7306 | 211.5363 | C3 | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 0 | 325.9873 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236 |  | 0 | 0 | 235.2567 | 90.7306 | 211.5363 | 537.5236
|  |  | 56 | 56 | C4 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 19 | 34 | 3 | 0 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 34 | 3 | 2 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 30 | 5 | 4 | 56 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | 539417.5 | C4 | 0 | 0 | 43.5661 | 151.2176 | 352.5606 | C4 | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 0 | 1934.8987 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1481.2458 | 453.6528 | 705.1212 | 2640.0198 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312 |  | 0 | 0 | 1306.9816 | 756.088 | 1410.2423 | 3473.312
|  |  | 575 | 575 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 193 | 350 | 27 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 354 | 27 | 20 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 174 | 322 | 42 | 37 | [22 empty] | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 5989.4612 | 1645.2475 | 578.1994 | 8212.9081 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 6048.711 | 1645.2475 | 2806.3822 | 10500.3408 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331 |  | 0 | 0 | 5485.8376 | 2570.6993 | 5203.7942 | 13260.331
| EHV OHL Support - Poles |  | 673 | 673 | C1 | 61 | 499 | 96 | 11 | 6 | 673 | 61 | 499 | 96 | 11 | 6 | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 355 | 210 | 61 | 20 | 673 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 279 | 245 | 80 | 45 | 673 |  |  | C1 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C1 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | 45216.5 | C1 | 15.4993 | 15.4993 | 58.3259 | 122.6046 | 189.0162 | C1 | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 945.456 | 7734.1403 | 5599.2859 | 1348.6506 | 1134.0974 | 16761.6302 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 418.4805 | 5502.2441 | 12248.4379 | 7478.8805 | 3780.3246 | 29428.3676 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224 |  | 371.9827 | 4324.2989 | 14289.8442 | 9808.3679 | 8505.7304 | 37300.224
|  |  | 43 | 43 | C2 | 3 | 37 | 3 | 0 | 0 | 43 | 3 | 37 | 3 | 0 | 0 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 21 | 14 | 4 | 2 | 43 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 19 | 16 | 5 | 2 | 43 |  |  | C2 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C2 | 64595 | 64595 | 64595 | 64595 | 64595 | C2 | 22.1418 | 22.1418 | 83.3227 | 175.1494 | 270.0232 | C2 | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 66.4255 | 819.2476 | 249.9681 | 0 | 0 | 1135.6412 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 44.2837 | 464.9784 | 1166.5179 | 700.5977 | 540.0464 | 2916.424 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934 |  | 22.1418 | 420.6947 | 1333.1633 | 875.7471 | 540.0464 | 3191.7934
|  |  | 10397 | 10397 | C3 | 952 | 7695 | 1492 | 161 | 97 | 10397 | 847 | 7695 | 1492 | 161 | 202 | 10397 | 0 | 0 | 0 | 0 | 0 | 0 | 517 | 5488 | 3249 | 936 | 207 | 10397 | 0 | 0 | 0 | 0 | 0 | 0 | 472 | 4313 | 3785 | 1239 | 588 | 10397 |  |  | C3 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C3 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | 96892.5 | C3 | 33.2127 | 33.2127 | 124.9841 | 262.7241 | 405.0348 | C3 | 28131.1917 | 255572.0426 | 186476.2173 | 42298.5864 | 81817.0254 | 594295.0634 |  | 31618.5295 | 255572.0426 | 186476.2173 | 42298.5864 | 39288.3736 | 555253.7494 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 17170.9871 | 182271.5231 | 406073.2105 | 245909.7942 | 83842.1993 | 935267.7142 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911 |  | 15676.4138 | 143246.5523 | 473064.6666 | 325515.2084 | 238160.4501 | 1195663.2911
|  |  | 638 | 638 | C4 | 58 | 473 | 91 | 10 | 6 | 638 | 58 | 473 | 91 | 10 | 6 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 338 | 199 | 57 | 19 | 638 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 264 | 232 | 76 | 43 | 638 |  |  | C4 | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802 | C4 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | 161487.5 | C4 | 55.3546 | 55.3546 | 208.3068 | 437.8736 | 675.058 | C4 | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 3210.565 | 26182.7109 | 18955.9157 | 4378.7357 | 4050.3478 | 56778.275 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 1383.8642 | 18709.8441 | 41453.0465 | 24958.7932 | 12826.1013 | 99331.6494 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144 |  | 1273.1551 | 14613.6061 | 48327.1698 | 33278.391 | 29027.4925 | 126519.8144
|  |  | 11751 | 11751 |  | 1074 | 8704 | 1682 | 182 | 109 |  | 969 | 8704 | 1682 | 182 | 214 |  | 0 | 0 | 0 | 0 | 0 |  | 571 | 6202 | 3672 | 1058 | 248 |  | 0 | 0 | 0 | 0 | 0 |  | 520 | 4875 | 4278 | 1400 | 678 | [22 empty] | 32353.6382 | 290308.1414 | 211281.3871 | 48025.9726 | 87001.4705 | 668970.6099 |  | 35840.976 | 290308.1414 | 211281.3871 | 48025.9726 | 44472.8187 | 629929.2959 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 19017.6155 | 206948.5897 | 460941.2128 | 279048.0656 | 100988.6716 | 1066944.1552 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229 |  | 17343.6934 | 162605.152 | 537014.8439 | 369477.7143 | 276233.7193 | 1362675.1229
| EHV OHL Fittings and Conductors (Tower Lines) |  | 64 | 64 | C1 | 1 | 0 | 8 | 42 | 13 | 64 | 0 | 0 | 8 | 42 | 14 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 8 | 33 | 22 | 64 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 2 | 12 | 49 | 64 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | 151371.9421 | C1 | 0 | 0 | 12.2256 | 39.8434 | 77.3125 | C1 | 0 | 0 | 97.8044 | 1673.4214 | 1082.3745 | 2853.6003 |  | 0 | 0 | 97.8044 | 1673.4214 | 1005.062 | 2776.2878 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 97.8044 | 1314.8311 | 1700.8742 | 3113.5097 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822 |  | 0 | 0 | 24.4511 | 478.1204 | 3788.3107 | 4290.8822
|  |  | 18 | 18 | C2 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 3 | 11 | 4 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 8 | 7 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 14 | 18 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | 216245.6316 | C2 | 0 | 0 | 17.4651 | 56.9191 | 110.4464 | C2 | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 626.11 | 441.7855 | 1120.2908 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 52.3952 | 455.3528 | 773.1246 | 1280.8726 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256 |  | 0 | 0 | 0 | 227.6764 | 1546.2493 | 1773.9256
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | 324368.4474 | C3 | 0 | 0 | 26.1976 | 85.3786 | 165.6696 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1 | 1 | C4 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | 540614.0789 | C4 | 0 | 0 | 43.6627 | 142.2977 | 276.1159 | C4 | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 142.2977 | 0 | 142.2977 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159 |  | 0 | 0 | 0 | 0 | 276.1159 | 276.1159
|  |  | 83 | 83 |  | 1 | 0 | 11 | 54 | 17 |  | 0 | 0 | 11 | 54 | 18 |  | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 11 | 42 | 29 |  | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 2 | 16 | 64 | [22 empty] | 0 | 0 | 150.1997 | 2441.8291 | 1524.16 | 4116.1888 |  | 0 | 0 | 150.1997 | 2441.8291 | 1446.8475 | 4038.8763 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 150.1997 | 1912.4816 | 2473.9988 | 4536.68 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237 |  | 0 | 0 | 24.4511 | 705.7968 | 5610.6759 | 6340.9237
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 |  | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 |  | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 |  | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 |  | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 |  | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 128 | 128 | C1 | 56 | 56 | 9 | 7 | 0 | 128 | 56 | 53 | 9 | 10 | 0 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 76 | 5 | 8 | 10 | 128 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 99 | 6 | 1 | 20 | 128 |  |  | C1 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C1 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | 109611.7045 | C1 | 566.8931 | 566.8931 | 2163.712 | 3830.461 | 5875.081 | C1 | 31746.0137 | 30045.3344 | 19473.4083 | 38304.6103 | 0 | 119569.3666 |  | 31746.0137 | 31746.0137 | 19473.4083 | 26813.2272 | 0 | 109778.6628 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 16439.8999 | 43083.8757 | 10818.5601 | 30643.6882 | 58750.8104 | 159736.8344 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572 |  | 1133.7862 | 56122.4171 | 12982.2722 | 3830.461 | 117501.6207 | 191570.5572
|  |  | 91 | 92 | C2 | 14 | 52 | 9 | 15 | 1 | 91 | 7 | 29 | 9 | 23 | 4 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 55 | 5 | 2 | 20 | 91 | 1 | 0 | 0 | 0 | 0 | 1 | 9 | 51 | 1 | 0 | 30 | 91 |  |  | C2 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C2 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | 156588.1492 | C2 | 809.8473 | 809.8473 | 3091.0172 | 5472.0872 | 8392.9729 | C2 | 5668.931 | 23485.5714 | 27819.1546 | 125858.0053 | 33571.8916 | 216403.5539 |  | 11337.862 | 42112.059 | 27819.1546 | 82081.3078 | 8392.9729 | 171743.3563 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 7288.6256 | 44541.6008 | 15455.0859 | 10944.1744 | 167859.4582 | 246088.9449 |  | 7288.6256 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 303471.0417 |  | 8098.4729 | 41302.2117 | 3091.0172 | 0 | 251789.1873 | 304280.889
|  |  | 13 | 13 | C3 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 9 | 1 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 1 | 3 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 0 | 0 | 4 | 13 |  |  | C3 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C3 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | 234882.2239 | C3 | 1214.7709 | 1214.7709 | 4636.5258 | 8208.1308 | 12589.4594 | C3 | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 4636.5258 | 24624.3923 | 0 | 40193.8565 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 0 | 10932.9384 | 0 | 8208.1308 | 37768.3781 | 56909.4473 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758 |  | 0 | 10932.9384 | 0 | 0 | 50357.8375 | 61290.7758
|  |  | 2 | 2 | C4 | 1 | 0 | 1 | 0 | 0 | 2 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 2 |  |  | C4 | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599 | C4 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | 391470.3731 | C4 | 2024.6182 | 2024.6182 | 7727.543 | 13680.218 | 20982.4323 | C4 | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 2024.6182 | 0 | 7727.543 | 0 | 0 | 9752.1612 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362 |  | 0 | 2024.6182 | 0 | 13680.218 | 0 | 15704.8362
|  |  | 234 | 235 |  | 71 | 117 | 20 | 25 | 1 |  | 64 | 91 | 20 | 36 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 39 | 140 | 11 | 11 | 33 |  | 1 | 0 | 0 | 0 | 0 |  | 11 | 160 | 7 | 2 | 54 | [22 empty] | 39439.5629 | 64463.8441 | 59656.6316 | 188787.0079 | 33571.8916 | 385918.9382 |  | 45108.4939 | 84791.011 | 59656.6316 | 133518.9273 | 8392.9729 | 331468.0368 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 25753.1438 | 98558.4149 | 34001.189 | 49795.9934 | 264378.6466 | 472487.3877 |  | 8422.4118 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572037.2109 |  | 9232.2591 | 110382.1853 | 16073.2893 | 17510.679 | 419648.6455 | 572847.0582
| 132kV Transformer |  | 41 | 41 | C1 | 6 | 26 | 5 | 3 | 1 | 41 | 5 | 25 | 5 | 4 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 26 | 6 | 3 | 2 | 41 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 18 | 15 | 3 | 3 | 41 |  |  | C1 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C1 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | 328406.4 | C1 | 2793.658 | 2793.658 | 10463.908 | 21703.7153 | 44415.0999 | C1 | 13968.29 | 69841.4502 | 52319.5402 | 86814.8611 | 88830.1998 | 311774.3413 |  | 16761.948 | 72635.1082 | 52319.5402 | 65111.1458 | 44415.0999 | 251242.8421 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 11174.632 | 72635.1082 | 62783.4482 | 65111.1458 | 88830.1998 | 300534.5341 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262 |  | 5587.316 | 50285.8441 | 156958.6205 | 65111.1458 | 133245.2998 | 411188.2262
|  |  | 125 | 125 | C2 | 19 | 79 | 24 | 1 | 2 | 125 | 18 | 75 | 24 | 3 | 3 | 123 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 70 | 35 | 6 | 2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 67 | 34 | 15 | 2 | 125 |  |  | C2 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C2 | 469152 | 469152 | 469152 | 469152 | 469152 | C2 | 3990.94 | 3990.94 | 14948.44 | 31005.3075 | 63450.1427 | C2 | 71836.9202 | 299320.5007 | 358762.5611 | 93015.9226 | 190350.4282 | 1013286.3329 |  | 75827.8602 | 315284.2608 | 358762.5611 | 31005.3075 | 126900.2855 | 907780.2751 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 47891.2801 | 279365.8007 | 523195.4017 | 186031.8451 | 126900.2855 | 1163384.6131 |  | 27936.5801 | 267392.9807 | 508246.9616 | 465079.6129 | 126900.2855 | 1395556.4207 |  | 27936.5801 | 267392.9807 | 508246.9616 | 465079.6129 | 126900.2855 | 1395556.4207
|  |  | 17 | 17 | C3 | 3 | 9 | 4 | 1 | 0 | 17 | 2 | 9 | 4 | 1 | 1 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 5 | 3 | 0 | 17 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 6 | 4 | 0 | 17 |  |  | C3 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C3 | 703728 | 703728 | 703728 | 703728 | 703728 | C3 | 5986.41 | 5986.41 | 22422.6601 | 46507.9613 | 95175.2141 | C3 | 11972.82 | 53877.6901 | 89690.6403 | 46507.9613 | 95175.2141 | 297224.3259 |  | 17959.23 | 53877.6901 | 89690.6403 | 46507.9613 | 0 | 208035.5217 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 17959.23 | 35918.4601 | 112113.3004 | 139523.8839 | 0 | 305514.8743 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757 |  | 5986.41 | 35918.4601 | 134535.9604 | 186031.8451 | 0 | 362472.6757
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524 | C4 | 1172880 | 1172880 | 1172880 | 1172880 | 1172880 | C4 | 9977.35 | 9977.35 | 37371.1001 | 77513.2688 | 158625.3569 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 183 | 183 |  | 28 | 114 | 33 | 5 | 3 |  | 25 | 109 | 33 | 8 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 19 | 102 | 46 | 12 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 10 | 91 | 55 | 22 | 5 | [22 empty] | 97778.0302 | 423039.6411 | 500772.7416 | 226338.7449 | 374355.8422 | 1622285 |  | 110549.0383 | 441797.0591 | 500772.7416 | 142624.4146 | 171315.3854 | 1367058.639 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 77025.1422 | 387919.369 | 698092.1502 | 390666.8748 | 215730.4853 | 1769434.0215 |  | 39510.3061 | 353597.2849 | 799741.5425 | 716222.6038 | 260145.5853 | 2169217.3226 |  | 39510.3061 | 353597.2849 | 799741.5425 | 716222.6038 | 260145.5853 | 2169217.3226
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | 490294.7 | C1 | 262.0625 | 262.0625 | 982.3054 | 2025.4074 | 4167.5049 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 700421 | 700421 | 700421 | 700421 | 700421 | C2 | 374.375 | 374.375 | 1403.2935 | 2893.4392 | 5953.5785 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 25 | C3 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 16 | 19 | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 25 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 25 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | 1050631.5 | C3 | 561.5625 | 561.5625 | 2104.9402 | 4340.1587 | 8930.3678 | C3 | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | 1751052.5 | C4 | 935.9376 | 935.9376 | 3508.2337 | 7233.5979 | 14883.9463 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25 | 25 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 16 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 25 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 25 | [22 empty] | 0 | 0 | 0 | 69442.5396 | 169676.9873 | 239119.5269 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 108503.9682 | 0 | 108503.9682 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938 |  | 0 | 0 | 0 | 0 | 223259.1938 | 223259.1938
| 132kV UG Cable (Oil) |  | 34 | 34 | C1 | 11 | 11 | 9 | 1 | 2 | 34 | 10 | 16 | 7 | 1 | 0 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 10 | 8 | 3 | 3 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 7 | 11 | 3 | 3 | 34 |  |  | C1 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C1 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | 573138.3 | C1 | 306.3424 | 306.3424 | 1148.2826 | 2367.6343 | 4871.6755 | C1 | 3063.4242 | 4901.4787 | 8037.9781 | 2367.6343 | 0 | 18370.5154 |  | 3369.7666 | 3369.7666 | 10334.5433 | 2367.6343 | 9743.3511 | 29185.0619 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 3063.4242 | 9186.2607 | 7102.903 | 14615.0266 | 37031.0387 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592 |  | 3063.4242 | 2144.3969 | 12631.1084 | 7102.903 | 14615.0266 | 39556.8592
|  |  | 30 | 30 | C2 | 9 | 11 | 8 | 0 | 2 | 30 | 9 | 15 | 7 | 1 | 1 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 8 | 8 | 3 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 5 | 10 | 3 | 3 | 30 |  |  | C2 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C2 | 818769 | 818769 | 818769 | 818769 | 818769 | C2 | 437.632 | 437.632 | 1640.4037 | 3382.3347 | 6959.5365 | C2 | 3938.6883 | 6564.4805 | 11482.8258 | 3382.3347 | 6959.5365 | 32327.8658 |  | 3938.6883 | 4813.9523 | 13123.2295 | 0 | 13919.073 | 35794.9431 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 3501.0562 | 13123.2295 | 10147.0042 | 13919.073 | 44629.0513 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991 |  | 3938.6883 | 2188.1602 | 16404.0369 | 10147.0042 | 20878.6095 | 53556.4991
|  |  | 36 | 36 | C3 | 12 | 11 | 9 | 1 | 3 | 36 | 11 | 17 | 7 | 1 | 0 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 11 | 9 | 3 | 3 | 36 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 8 | 11 | 4 | 3 | 36 |  |  | C3 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C3 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | 1228153.5 | C3 | 656.448 | 656.448 | 2460.6055 | 5073.5021 | 10439.3048 | C3 | 7220.9285 | 11159.6168 | 17224.2388 | 5073.5021 | 0 | 40678.2862 |  | 7877.3765 | 7220.9285 | 22145.4498 | 5073.5021 | 31317.9143 | 73635.1712 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 7220.9285 | 22145.4498 | 15220.5063 | 31317.9143 | 82469.2794 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484 |  | 6564.4805 | 5251.5844 | 27066.6609 | 20294.0084 | 31317.9143 | 90494.6484
|  |  | 134 | 134 | C4 | 43 | 45 | 34 | 2 | 10 | 134 | 40 | 62 | 28 | 3 | 1 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 39 | 33 | 13 | 10 | 134 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 27 | 42 | 13 | 13 | 134 |  |  | C4 | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085 | C4 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | 2046922.5 | C4 | 1094.0801 | 1094.0801 | 4101.0092 | 8455.8368 | 17398.8413 | C4 | 43763.2031 | 67832.9647 | 114828.2584 | 25367.5105 | 17398.8413 | 269190.778 |  | 47045.4433 | 49233.6034 | 139434.3138 | 16911.6737 | 173988.4125 | 426613.4467 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 42669.123 | 135333.3045 | 109925.879 | 173988.4125 | 504585.842 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879 |  | 42669.123 | 29540.1621 | 172242.3876 | 109925.879 | 226184.9363 | 580562.4879
|  |  | 234 | 234 |  | 75 | 78 | 60 | 4 | 17 |  | 70 | 110 | 49 | 6 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 68 | 58 | 22 | 18 |  | 0 | 0 | 0 | 0 | 0 |  | 68 | 47 | 74 | 23 | 22 | [22 empty] | 57986.244 | 90458.5407 | 151573.3011 | 36190.9817 | 24358.3777 | 360567.4453 |  | 62231.2747 | 64638.2509 | 185037.5364 | 24352.8101 | 228968.7509 | 565228.623 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 56454.5319 | 179788.2446 | 142396.2925 | 233840.4264 | 668715.2114 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946 |  | 56235.7159 | 39124.3035 | 228344.1939 | 147469.7946 | 292996.4867 | 764170.4946
| 132kV UG Cable (Non Pressurised) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 51.5767 | 120.25 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2258 | 2188 | C2 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 790 | 994 | 456 | 18 | 2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 790 | 964 | 486 | 18 | 2258 | 0 | 0 | 0 | -70 | 0 | -70 | 0 | 789 | 962 | 465 | 42 | 2258 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 73.681 | 171.7857 | C2 | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 21100.2607 | 33598.54 | 3092.1423 | 57790.943 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20463.4319 | 35808.9702 | 3092.1423 | 59364.5444 |  | 0 | 0 | 20420.9767 | 34261.6691 | 7214.9986 | 61897.6443 |  | 0 | 0 | 20420.9767 | 29103.9984 | 7214.9986 | 56739.9737
|  |  | 312 | 312 | C3 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 109 | 137 | 63 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 67 | 3 | 312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 133 | 64 | 6 | 312 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 110.5215 | 257.6785 | C3 | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4362.2772 | 6962.8553 | 773.0356 | 12098.1681 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7404.9414 | 773.0356 | 12412.8884 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594 |  | 0 | 0 | 4234.9115 | 7073.3768 | 1546.0711 | 12854.3594
|  |  | 5 | 5 | C4 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 2 | 1 | 0 | 5 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 184.2025 | 429.4642 | C4 | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407 |  | 0 | 0 | 106.1381 | 184.2025 | 0 | 290.3407
|  |  | 2575 | 2505 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 901 | 1133 | 520 | 21 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 901 | 1099 | 554 | 21 |  | 0 | 0 | 0 | -70 | 0 |  | 0 | 900 | 1097 | 530 | 48 | [22 empty] | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 25568.6761 | 40745.5978 | 3865.1778 | 70179.4517 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24804.4815 | 43398.1141 | 3865.1778 | 72067.7735 |  | 0 | 0 | 24762.0263 | 41519.2484 | 8761.0697 | 75042.3444 |  | 0 | 0 | 24762.0263 | 36361.5778 | 8761.0697 | 69884.6738
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C1 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | 183982.4 | C1 | 0 | 0 | 14.8593 | 48.4269 | 93.9681 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1003 | 981 | C2 | 215 | 464 | 324 | 0 | 0 | 1003 | 189 | 464 | 350 | 0 | 0 | 1003 | 0 | 0 | 0 | 0 | 0 | 0 | 178 | 420 | 280 | 125 | 0 | 1003 | 0 | 0 | -22 | 0 | 0 | -22 | 26 | 494 | 244 | 239 | 0 | 1003 |  |  | C2 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C2 | 262832 | 262832 | 262832 | 262832 | 262832 | C2 | 0 | 0 | 21.2276 | 69.1813 | 134.2401 | C2 | 0 | 0 | 7429.6693 | 0 | 0 | 7429.6693 |  | 0 | 0 | 6877.751 | 0 | 0 | 6877.751 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5943.7354 | 8647.6656 | 0 | 14591.401 |  | 0 | 0 | 5179.5409 | 16534.3366 | 0 | 21713.8775 |  | 0 | 0 | 4712.5331 | 16534.3366 | 0 | 21246.8697
|  |  | 147 | 147 | C3 | 31 | 68 | 48 | 0 | 0 | 147 | 31 | 68 | 48 | 0 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 62 | 45 | 18 | 0 | 147 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 39 | 36 | 0 | 147 |  |  | C3 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C3 | 394248 | 394248 | 394248 | 394248 | 394248 | C3 | 0 | 0 | 31.8414 | 103.772 | 201.3602 | C3 | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1528.3891 | 0 | 0 | 1528.3891 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1432.8648 | 1867.8958 | 0 | 3300.7606 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077 |  | 0 | 0 | 1241.8161 | 3735.7915 | 0 | 4977.6077
|  |  | 1 | 1 | C4 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 1 |  |  | C4 | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074 | C4 | 657080 | 657080 | 657080 | 657080 | 657080 | C4 | 0 | 0 | 53.0691 | 172.9533 | 335.6003 | C4 | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 53.0691 | 0 | 0 | 53.0691 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533 |  | 0 | 0 | 0 | 172.9533 | 0 | 172.9533
|  |  | 1151 | 1129 |  | 246 | 532 | 373 | 0 | 0 |  | 220 | 532 | 399 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 200 | 482 | 325 | 144 | 0 |  | 0 | 0 | -22 | 0 | 0 |  | 26 | 566 | 283 | 276 | 0 | [22 empty] | 0 | 0 | 9011.1274 | 0 | 0 | 9011.1274 |  | 0 | 0 | 8459.2092 | 0 | 0 | 8459.2092 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 7376.6002 | 10688.5147 | 0 | 18065.1149 |  | 0 | 0 | 6421.357 | 20443.0815 | 0 | 26864.4385 |  | 0 | 0 | 5954.3492 | 20443.0815 | 0 | 26397.4307
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 |  | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 |  | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 |  | 104978.2811 | 503103.7738 | 1074875.4013 | 938007.7367 | 1204810.9809 | 3825776.1737
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 313807 | 313716 |  | 50304 | 158234 | 82171 | 21650 | 1448 |  | 44998 | 157737 | 82173 | 22091 | 7478 |  | 0 | 0 | 0 | 0 | 0 |  | 34863 | 125195 | 95392 | 49327 | 9031 |  | 1 | 0 | -22 | -70 | 0 |  | 23791 | 112928 | 92300 | 61502 | 23287 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 |  | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 |  | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 |  | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 |  | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 |  | 724248.235 | 4030185.639 | 11631884.2122 | 13040738.9845 | 8339753.2019 | 37766810.2725
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 520630.578 | 1834973.4798 | 3218407.0707 | 3193772.4361 | 909716.3185 | 9677499.8831 | LV Network | 573236.2064 | 1836035.6725 | 3218407.0707 | 3193772.4361 | 277710.8969 | 9099162.2826 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 415217.5729 | 1370463.9934 | 3475158.0245 | 5647227.6017 | 1281997.7336 | 12190064.9261 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545 | LV Network | 329240.0137 | 1182549.5663 | 3045339.0362 | 7575404.7009 | 2775062.0374 | 14907595.3545
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 569505.0672 | 2247075.2497 | 4853881.2557 | 780204.5644 | 1171915.6704 | 9622581.8075 | HV Network | 651921.9898 | 2275171.6141 | 4853881.2557 | 648193.7414 | 127814.6406 | 8556983.2416 | HV Network | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 | HV Network | 421769.7369 | 1985336.3541 | 5387189.5593 | 2920615.474 | 1087810.4144 | 11802721.5388 | HV Network | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844 | HV Network | 216627.3123 | 1882553.1493 | 5645515.65 | 3453549.4646 | 3251872.7081 | 14450118.2844
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 153807.282 | 805042.1541 | 793163.747 | 257248.401 | 421348.5549 | 2430610.139 | EHV Network | 163016.1941 | 813021.3366 | 802251.1569 | 244543.002 | 388916.1726 | 2411747.8622 | EHV Network | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 | EHV Network | 116633.465 | 602650.6329 | 1480381.969 | 661771.1395 | 717277.2835 | 3578714.4899 | EHV Network | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46 | EHV Network | 73402.6279 | 461979.1496 | 1866154.1248 | 1073777.0822 | 1108007.4755 | 4583320.46
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 195203.8372 | 577962.0259 | 746582.4778 | 561504.872 | 605828.2767 | 2687081.4896 | 132kV Network | 217888.8069 | 591226.321 | 779494.7949 | 449745.718 | 412542.287 | 2450897.9279 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 159014.0019 | 542932.3158 | 944062.6656 | 745449.7577 | 717814.7362 | 3109273.4772 | 132kV Network | 104168.4338 | 503103.7738 | 1075342.409 | 943165.4073 | 1204810.9809 | 3830591.0048 | 132kV Network | 104978.2811 | 503103.7738 | 1074875.4013 | 938007.7367 | 1204810.9809 | 3825776.1737
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 1439146.7645 | 5465052.9095 | 9612034.5512 | 4792730.2734 | 3108808.8205 | 24417773.3191 | Total | 1606063.1973 | 5515454.9442 | 9654034.2782 | 4536254.8975 | 1206983.9971 | 22518791.3143 | Total | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 | Total | 1112634.7766 | 4501383.2963 | 11286792.2183 | 9975063.973 | 3804900.1677 | 30680774.4319 | Total | 723438.3877 | 4030185.639 | 11632351.22 | 13045896.6551 | 8339753.2019 | 37771625.1037 | Total | 724248.235 | 4030185.639 | 11631884.2122 | 13040738.9845 | 8339753.2019 | 37766810.2725
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SPN - Average Cons. of Failure
Secondary deliverables RIIO-ED1 - Average Consequence of Asset Failure
SPN
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period |  |  |  |  | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure
| LV Network | [5 empty] | LV Network
| LV Switchgear and Other | 771 | 8778 | 1000 | 434 | 10983 | LV Switchgear and Other | 771 | 8778 | 1000 | 434 | 10983
| LV UGB | 621 | 8504 | 1500 | 432 | 11057 | LV UGB | 621 | 8504 | 1500 | 432 | 11057
| LV OHL Support | 1080 | 7589 | 4620 | 622 | 13911 | LV OHL Support | 1080 | 7589 | 4620 | 622 | 13911
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| HV Network | [5 empty] | HV Network
| HV Switchgear (GM) - Primary | 29898 | 6624 | 4548 | 6821.5553 | 47891.5553 | HV Switchgear (GM) - Primary | 29898 | 6624 | 4548 | 6821.5553 | 47891.5553
| HV Switchgear (GM) - Distribution | 18453 | 8993 | 4795 | 2649.1509 | 34890.1509 | HV Switchgear (GM) - Distribution | 18453 | 8993 | 4795 | 2649.1509 | 34890.1509
| HV Transformer (GM) | 33088 | 6465 | 2557 | 30913.66 | 73023.66 | HV Transformer (GM) | 33088 | 6465 | 2557 | 30913.66 | 73023.66
| HV UG Cable | N/A | N/A | N/A | N/A | N/A | HV UG Cable | N/A | N/A | N/A | N/A | 0
| HV OHL Support - Poles | 13405 | 7196 | 4672 | 1300.1672 | 26573.1672 | HV OHL Support - Poles | 13405 | 7196 | 4672 | 1300.1672 | 26573.1672
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| EHV Network | [5 empty] | EHV Network
| EHV Switchgear (GM) | 31240 | 3448 | 5996 | 12870.1711 | 53554.1711 | EHV Switchgear (GM) | 31240 | 3448 | 5996 | 12870.1711 | 53554.1711
| EHV Transformer | 91438 | 794 | 23658 | 33575.6513 | 149465.6513 | EHV Transformer | 91438 | 794 | 23658 | 33575.6513 | 149465.6513
| EHV UG Cable (Gas) | 108834 | 301 | 1500 | 89183 | 199818 | EHV UG Cable (Gas) | 108834 | 301 | 1500 | 89183 | 199818
| EHV UG Cable (Oil) | 108834 | 301 | 112351 | 89183 | 310669 | EHV UG Cable (Oil) | 108834 | 301 | 112351 | 89183 | 310669
| EHV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | N/A | EHV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | 0
| EHV OHL Support - Towers | 150009 | 19324 | 14770 | 31664 | 215767 | EHV OHL Support - Towers | 150009 | 19324 | 14770 | 31664 | 215767
| EHV OHL Support - Poles | 39067 | 19324 | 4620 | 1584 | 64595 | EHV OHL Support - Poles | 39067 | 19324 | 4620 | 1584 | 64595
| EHV OHL Fittings and Conductors (Tower Lines) | 150009 | 19802.6316 | 14770 | 31664 | 216245.6316 | EHV OHL Fittings and Conductors (Tower Lines) | 150009 | 19802.6316 | 14770 | 31664 | 216245.6316
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| 132kV Network | [5 empty] | 132kV Network
| 132kV CBs | 99671 | 3874 | 22653 | 30390.1492 | 156588.1492 | 132kV CBs | 99671 | 3874 | 22653 | 30390.1492 | 156588.1492
| 132kV Transformer | 260799 | 691 | 65370 | 142292 | 469152 | 132kV Transformer | 260799 | 691 | 65370 | 142292 | 469152
| 132kV UG Cable (Gas) | 609924 | 301 | 1500 | 88696 | 700421 | 132kV UG Cable (Gas) | 609924 | 301 | 1500 | 88696 | 700421
| 132kV UG Cable (Oil) | 609924 | 301 | 119848 | 88696 | 818769 | 132kV UG Cable (Oil) | 609924 | 301 | 119848 | 88696 | 818769
| 132kV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | N/A | 132kV UG Cable (Non Pressurised) | N/A | N/A | N/A | N/A | 0
| 132kV OHL Support - Tower | 188744 | 17099 | 14770 | 42219 | 262832 | 132kV OHL Support - Tower | 188744 | 17099 | 14770 | 42219 | 262832
| 132kV OHL Fittings and Conductors (Tower Lines) | 188744 | 17099 | 14770 | 42219 | 262832 | 132kV OHL Fittings and Conductors (Tower Lines) | 188744 | 17099 | 14770 | 42219 | 262832
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| Other | [5 empty] | Other
| Submarine Cables | N/A | N/A | N/A | N/A | N/A | Submarine Cables | N/A | N/A | N/A | N/A | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]

## SPN - Probs. of Failure
Probabilities of Asset Failure
SPN
Price base (2012/13)
Average Probabilities of Asset Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0.0021631 | 0 | 0.004953 | 0.004953 | 0.010375 | 0.010375 | 0.014607 | 0.014607 | 0.025514 | LV Switchgear and Other | 0.0010816 | 0.0024765 | 0.0076638 | 0.012491 | 0.020061
| LV UGB | 0 | 0.0028671 | 0 | 0.0043007 | 0.0043007 | 0.010035 | 0.010035 | 0.021503 | 0.021503 | 0.04014 | LV UGB | 0.0014336 | 0.0021503 | 0.0071678 | 0.015769 | 0.030821
| LV OHL Support | 0 | 0.0030404 | 0 | 0.0030404 | 0.0030404 | 0.0030679 | 0.0030679 | 0.013754 | 0.013754 | 0.019599 | LV OHL Support | 0.0015202 | 0.0015202 | 0.0030542 | 0.0084107 | 0.016676
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear (at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB and LV Pillar OD (not at s/s) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| HV Network | [10 empty] | HV Network
| HV Switchgear (GM) - Primary | 0 | 0.0035024 | 0 | 0.0035024 | 0.0035024 | 0.0096073 | 0.0096073 | 0.014476 | 0.014476 | 0.018675 | HV Switchgear (GM) - Primary | 0.0017512 | 0.0017512 | 0.0065548 | 0.012041 | 0.016575
| HV Switchgear (GM) - Distribution | 0 | 0.0011172 | 0 | 0.0011172 | 0.0011172 | 0.0030822 | 0.0030822 | 0.0046174 | 0.0046174 | 0.008553 | HV Switchgear (GM) - Distribution | 0.00055859 | 0.00055859 | 0.0020997 | 0.0038498 | 0.0065852
| HV Transformer (GM) | 0 | 0.0017641 | 0 | 0.00215 | 0.00215 | 0.0039141 | 0.0039141 | 0.0076521 | 0.0076521 | 0.011857 | HV Transformer (GM) | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546
| HV UG Cable | 0 | 0.0017641 | 0 | 0.00215 | 0.00215 | 0.0039141 | 0.0039141 | 0.0076521 | 0.0076521 | 0.011857 | HV UG Cable | 0.00088206 | 0.001075 | 0.003032 | 0.0057831 | 0.0097546
| HV OHL Support - Poles | 0 | 0.0020607 | 0 | 0.0020607 | 0.0020607 | 0.0056934 | 0.0056934 | 0.010605 | 0.010605 | 0.014521 | HV OHL Support - Poles | 0.0010304 | 0.0010304 | 0.0038771 | 0.0081493 | 0.012563
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| EHV Network | [10 empty] | EHV Network
| EHV Switchgear (GM) | 0 | 0.0088371 | 0 | 0.0088371 | 0.0088371 | 0.024507 | 0.024507 | 0.036524 | 0.036524 | 0.067655 | EHV Switchgear (GM) | 0.0044186 | 0.0044186 | 0.016672 | 0.030516 | 0.05209
| EHV Transformer | 0 | 0.017013 | 0 | 0.017013 | 0.017013 | 0.046712 | 0.046712 | 0.085464 | 0.085464 | 0.18502 | EHV Transformer | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524
| EHV UG Cable (Gas) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | EHV UG Cable (Gas) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| EHV UG Cable (Oil) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | EHV UG Cable (Oil) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.00039914 | 0.00039914 | 0.00090805 | EHV OHL Support - Towers | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359
| EHV OHL Support - Poles | 0 | 0.00068556 | 0 | 0.00068556 | 0.00068556 | 0.0018943 | 0.0018943 | 0.0035287 | 0.0035287 | 0.0048318 | EHV OHL Support - Poles | 0.00034278 | 0.00034278 | 0.0012899 | 0.0027115 | 0.0041802
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.0003649 | 0.0003649 | 0.00065659 | EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| 132kV Network | [10 empty] | 132kV Network
| 132kV CBs | 0 | 0.010344 | 0 | 0.010344 | 0.010344 | 0.029136 | 0.029136 | 0.040756 | 0.040756 | 0.066443 | 132kV CBs | 0.0051718 | 0.0051718 | 0.01974 | 0.034946 | 0.053599
| 132kV Transformer | 0 | 0.017013 | 0 | 0.017013 | 0.017013 | 0.046712 | 0.046712 | 0.085464 | 0.085464 | 0.18502 | 132kV Transformer | 0.0085067 | 0.0085067 | 0.031863 | 0.066088 | 0.13524
| 132kV UG Cable (Gas) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | 132kV UG Cable (Gas) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| 132kV UG Cable (Oil) | 0 | 0.001069 | 0 | 0.001069 | 0.001069 | 0.002938 | 0.002938 | 0.005324 | 0.005324 | 0.011676 | 132kV UG Cable (Oil) | 0.0005345 | 0.0005345 | 0.0020035 | 0.004131 | 0.0085
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.00039914 | 0.00039914 | 0.00090805 | 132kV OHL Support - Tower | 0 | 0 | 8.0765e-05 | 0.00028033 | 0.00065359
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0.00016153 | 0.00016153 | 0.0003649 | 0.0003649 | 0.00065659 | 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 8.0765e-05 | 0.00026322 | 0.00051074
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Conductor (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Other | [10 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 9099162.2826 | 12190064.9261 | 10396305.9572 | 14907595.3545 | 11612576.808
HV Network | 8556983.2416 | 11802721.5388 | 10301465.643 | 14450118.2844 | 11182569.2947
EHV Network | 2411747.8622 | 3578714.4899 | 2975621.3215 | 4583320.46 | 3384517.3715
132kV Network | 2450897.9279 | 3109273.4772 | 2685164.5968 | 3830591.0048 | 2815560.6524
Other | 0 | 0 | 0 | 0 | 0
Total | 22518791.3143 | 30680774.4319 | 26358557.5185 | 37771625.1037 | 28995224.1266
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary Deliverables Target)
LV Network |  | 3090902.6434 | -1793758.9689 | 5808433.0718 | -3295018.5465
HV Network |  | 3245738.2972 | -1501255.8957 | 5893135.0428 | -3267548.9897
EHV Network |  | 1166966.6277 | -603093.1684 | 2171572.5978 | -1198803.0885
132kV Network |  | 658375.5493 | -424108.8804 | 1379693.0769 | -1015030.3524
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 8161983.1176 | -4322216.9134 | 15252833.7893 | -8776400.9771