## SWALES - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWALES | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | C1 | 42.3124 | 42.3124 | 58.8809 | 144.8589 | 303.514 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 8621 | 0 | 0 | -4035 | -4586 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 17457 | 0 | 0 | -8170 | -9287 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4715 | 4715 | 4715 | 4715 | 4715 | C2 | 60.4463 | 60.4463 | 84.1156 | 206.9413 | 433.5914 | C2 | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 829565.0212 | 4625048.6445 | 301890.8884 | 1042363.58 | 1268688.4364 | 8067556.5705 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 1139352.3087 | 4625048.6445 | 301890.8884 | 406018.9287 | 379826.0664 | 6852136.8367
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | C3 | 90.6694 | 90.6694 | 126.1734 | 310.412 | 650.3871 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | C4 | 151.1157 | 151.1157 | 210.289 | 517.3534 | 1083.9785 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 8621 | 0 | 0 | -4035 | -4586 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 17457 | 0 | 0 | -8170 | -9287 |  | 1392 | 76515 | 3589 | 10132 | 10163 | [22 empty] | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 829565.0212 | 4625048.6445 | 301890.8884 | 1042363.58 | 1268688.4364 | 8067556.5705 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 1139352.3087 | 4625048.6445 | 301890.8884 | 406018.9287 | 379826.0664 | 6852136.8367
| LV Switchgear (at s/s) |  | 278 | 278 | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | C1 | 82.0156 | 82.0156 | 114.0623 | 280.6537 | 588.0628 | C1 | 22308.2388 | 0 | 0 | 0 | 0 | 22308.2388 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324
|  |  | 7511 | 7511 | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 368 | -24 | -62 | -11 | -271 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 736 | -52 | -94 | -47 | -543 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 6096 | 6096 | 6096 | 6096 | 6096 | C2 | 117.1651 | 117.1651 | 162.9461 | 400.9339 | 840.0898 | C2 | 411483.9014 | 131107.7693 | 359459.0525 | 119478.3082 | 224303.9659 | 1245832.9973 |  | 445930.4467 | 130404.7786 | 356200.1309 | 111860.5637 | 106691.3995 | 1151087.3194 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 414647.3597 | 160281.8842 | 343490.3366 | 176410.9248 | 47045.0266 | 1141875.5318 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677 |  | 366609.6605 | 216755.472 | 303079.7088 | 241362.2198 | 58806.2832 | 1186613.3443
|  |  | 76 | 76 | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 6 | -2 | -1 | 0 | -3 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 12 | -2 | -3 | -1 | -6 | 0 | 23 | 16 | 22 | 9 | 6 | 76 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 9144 | 9144 | 9144 | 9144 | 9144 | C3 | 175.7477 | 175.7477 | 244.4191 | 601.4009 | 1260.1346 | C3 | 4569.4397 | 2284.7198 | 6599.3162 | 3007.0044 | 6300.6732 | 22761.1534 |  | 5975.4211 | 2284.7198 | 5866.0589 | 3007.0044 | 0 | 17133.2042 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 6326.9165 | 1933.2245 | 6110.478 | 1202.8018 | 2520.2693 | 18093.69 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959 |  | 6151.1688 | 2460.4675 | 4643.9633 | 4811.207 | 0 | 18066.8066
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 15240 | 15240 | 15240 | 15240 | 15240 | C4 | 292.9128 | 292.9128 | 407.3652 | 1002.3348 | 2100.2244 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7865 | 7865 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 374 | -26 | -63 | -11 | -274 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 748 | -54 | -97 | -48 | -549 |  | 2694 | 1918 | 1976 | 658 | 619 | [22 empty] | 438361.58 | 133392.4891 | 366058.3687 | 122485.3126 | 230604.6391 | 1290902.3895 |  | 474706.2002 | 132689.4984 | 362066.1898 | 114867.5681 | 106691.3995 | 1191020.856 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 443774.6085 | 162215.1086 | 349600.8146 | 177613.7266 | 49565.2958 | 1182769.5542 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096 |  | 395561.1616 | 219215.9395 | 307723.6721 | 246173.4269 | 58806.2832 | 1227480.4833
| LV UGB and LV Pillar OD (not at s/s) |  | 103 | 103 | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | C1 | 70.2164 | 70.2164 | 97.6527 | 240.2775 | 503.4613 | C1 | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919
|  |  | 3635 | 3635 | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 123 | 0 | 0 | 0 | -123 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 250 | 0 | 0 | 0 | -250 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5219 | 5219 | 5219 | 5219 | 5219 | C2 | 100.3092 | 100.3092 | 139.5039 | 343.2536 | 719.2304 | C2 | 45339.7494 | 52060.4644 | 303560.4211 | 95767.7628 | 146003.7692 | 642732.1668 |  | 51157.6818 | 52060.4644 | 303281.4134 | 95767.7628 | 110042.2497 | 612309.572 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 56674.6867 | 30694.6091 | 300909.8476 | 116706.2342 | 192034.5141 | 697019.8917 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192 |  | 68611.4791 | 7824.116 | 287656.9799 | 152061.3581 | 264676.7835 | 780830.7167
|  |  | 581 | 581 | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 5 | 0 | 0 | 0 | -5 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 6 | 0 | 0 | 0 | -6 | 0 | 25 | 0 | 544 | 6 | 6 | 581 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | C3 | 150.4638 | 150.4638 | 209.2558 | 514.8804 | 1078.8456 | C3 | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 4513.9131 | 150.4638 | 114672.1811 | 514.8804 | 1078.8456 | 120930.284 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083 |  | 4664.3769 | 0 | 113835.1579 | 3089.2827 | 0 | 121588.8175
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | C4 | 250.773 | 250.773 | 348.7597 | 858.1341 | 1798.076 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4319 | 4319 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 128 | 0 | 0 | 0 | -128 |  | 570 | 307 | 2705 | 341 | 396 |  | 256 | 0 | 0 | 0 | -256 |  | 562 | 78 | 2606 | 449 | 624 | [22 empty] | 56333.6355 | 52511.8557 | 418023.3465 | 96282.6432 | 151397.9971 | 774549.478 |  | 62151.5679 | 52511.8557 | 417744.3387 | 96282.6432 | 115436.4776 | 744126.8832 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 68420.8917 | 30845.0729 | 415582.0287 | 117221.1146 | 193113.3597 | 825182.4676 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194 |  | 80508.1479 | 7824.116 | 401492.1379 | 155150.6408 | 264676.7835 | 909651.826
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 |  | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 1341760.5214 | 4818108.826 | 1067073.7318 | 1337198.4212 | 1511367.092 | 10075508.5923 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 |  | 1615421.6182 | 4852088.7001 | 1011106.6983 | 807342.9963 | 703309.1331 | 8989269.1461
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 631 | 631 | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 21 | 0 | 0 | -8 | -13 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 31 | 0 | 0 | -1 | -30 | 0 | 217 | 260 | 61 | 45 | 48 | 631 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 36715 | 36715 | 36715 | 36715 | 36715 | C1 | 470.6863 | 470.6863 | 654.9956 | 1611.4213 | 3376.3114 | C1 | 184979.7159 | 55540.9834 | 56329.6216 | 35451.2697 | 47268.3596 | 379569.9502 |  | 185921.0885 | 55540.9834 | 56329.6216 | 32228.427 | 40515.7368 | 370535.8573 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 146383.4393 | 98844.123 | 45194.6964 | 46731.2191 | 40515.7368 | 377669.2147 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046 |  | 116730.2024 | 122378.438 | 39954.7316 | 70902.5394 | 60773.6052 | 410739.5166
|  |  | 1416 | 1416 | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 60 | 0 | -6 | -22 | -32 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 117 | 0 | -2 | -14 | -101 | 0 | 550 | 467 | 143 | 119 | 137 | 1416 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 52450 | 52450 | 52450 | 52450 | 52450 | C2 | 672.409 | 672.409 | 935.708 | 2302.0305 | 4823.302 | C2 | 532547.928 | 199705.473 | 212405.716 | 195672.5925 | 159168.966 | 1299500.6755 |  | 537927.2 | 198360.655 | 209598.592 | 165746.196 | 120582.55 | 1232215.193 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 487496.525 | 268963.6 | 179655.936 | 147329.952 | 168815.57 | 1252261.583 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005 |  | 448496.803 | 314015.003 | 131934.828 | 241713.2025 | 173638.872 | 1309798.7085
|  |  | 31 | 31 | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 5 | 0 | 0 | -1 | -4 | 0 | 7 | 4 | 8 | 8 | 4 | 31 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 78675 | 78675 | 78675 | 78675 | 78675 | C3 | 1008.6135 | 1008.6135 | 1403.562 | 3453.0457 | 7234.953 | C3 | 5043.0675 | 9077.5215 | 19649.868 | 13812.183 | 14469.906 | 62052.546 |  | 7060.2945 | 9077.5215 | 19649.868 | 3453.0457 | 0 | 39240.7297 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225 |  | 12103.362 | 4034.454 | 11228.496 | 24171.3202 | 0 | 51537.6322
|  |  | 185 | 185 | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 7 | 0 | 0 | -2 | -5 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 24 | 0 | 0 | -1 | -23 | 0 | 59 | 67 | 20 | 16 | 23 | 185 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 131125 | 131125 | 131125 | 131125 | 131125 | C4 | 1681.0225 | 1681.0225 | 2339.27 | 5755.0763 | 12058.255 | C4 | 154654.07 | 73964.99 | 79535.18 | 80571.0675 | 48233.02 | 436958.3275 |  | 154654.07 | 73964.99 | 79535.18 | 69060.915 | 36174.765 | 413389.92 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 137843.845 | 95818.2825 | 63160.29 | 86326.1438 | 48233.02 | 431381.5812 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32 |  | 139524.8675 | 112628.5075 | 46785.4 | 86326.1438 | 0 | 385264.9188
|  |  | 2263 | 2263 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 88 | 0 | -6 | -32 | -50 |  | 1037 | 672 | 308 | 144 | 102 |  | 177 | 0 | -2 | -17 | -158 |  | 833 | 798 | 232 | 188 | 212 | [22 empty] | 877224.7814 | 338288.9679 | 367920.3856 | 325507.1127 | 269140.2516 | 2178081.4992 |  | 885562.653 | 336944.1499 | 365113.2616 | 270488.5837 | 197273.0518 | 2055381.7001 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 778784.1038 | 468669.073 | 307660.7904 | 294199.4979 | 264799.2798 | 2114112.7449 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476 |  | 716855.2349 | 553056.4025 | 229903.4556 | 423113.2059 | 234412.4772 | 2157340.7761
| HV Switchgear (GM) - Distribution |  | 254 | 254 | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | C1 | 131.855 | 131.855 | 183.4862 | 451.413 | 945.8178 | C1 | 31645.1957 | 1582.2598 | 0 | 0 | 0 | 33227.4555 |  | 31908.9056 | 1582.2598 | 0 | 0 | 0 | 33491.1654 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526
|  |  | 9267 | 9203 | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 373 | -60 | -3 | 0 | -340 | -30 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 788 | -112 | -25 | -47 | -668 | -64 | 3289 | 3436 | 1342 | 281 | 919 | 9267 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 14693 | 14693 | 14693 | 14693 | 14693 | C2 | 188.3643 | 188.3643 | 262.1231 | 644.8758 | 1351.1683 | C2 | 1026961.9455 | 378988.8911 | 267365.5824 | 108339.1294 | 708012.1787 | 2489667.7271 |  | 1060114.0553 | 373903.0561 | 264220.105 | 107694.2536 | 647209.6061 | 2453141.076 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 881921.4653 | 547386.5396 | 298296.1106 | 105114.7505 | 470206.5614 | 2302925.4274 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162 |  | 767961.088 | 626122.8002 | 345216.149 | 150900.9302 | 339143.2383 | 2229344.2058
|  |  | 1084 | 1068 | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 114 | -1 | 0 | -4 | -119 | -10 | 367 | 298 | 224 | 22 | 173 | 1084 | 190 | -11 | -1 | -2 | -192 | -16 | 279 | 326 | 216 | 50 | 213 | 1084 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | C3 | 282.5464 | 282.5464 | 393.1847 | 967.3137 | 2026.7524 | C3 | 128276.0611 | 68658.7728 | 78636.936 | 33855.9779 | 291852.3485 | 601280.0962 |  | 137600.0919 | 67811.1336 | 77850.5666 | 25150.155 | 269558.0719 | 577970.0191 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 135904.8136 | 83916.2778 | 88073.3683 | 17411.6458 | 109444.6307 | 434750.7362 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405 |  | 132514.2569 | 89002.1128 | 84534.7062 | 46431.0554 | 42561.8008 | 395043.9322
|  |  | 4 | 4 | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | C4 | 470.9106 | 470.9106 | 655.3078 | 1612.1894 | 3377.9207 | C4 | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128
|  |  | 10609 | 10529 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 487 | -61 | -3 | -4 | -459 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 978 | -123 | -26 | -49 | -860 |  | 3735 | 3843 | 1567 | 332 | 1132 | [22 empty] | 1186883.2023 | 449700.8343 | 347968.4418 | 142195.1073 | 999864.5272 | 3126612.1129 |  | 1229623.0529 | 443767.3601 | 344036.595 | 132844.4086 | 916767.678 | 3067039.0946 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 1047493.6499 | 634731.0469 | 389541.1686 | 122526.3963 | 579651.1921 | 2773943.4538 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867 |  | 922495.1269 | 725805.1666 | 432817.6957 | 198944.175 | 381705.0391 | 2661767.2034
| HV Transformer (GM) |  | 1331 | 1331 | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 118 | 0 | 0 | 0 | -118 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 207 | 0 | 0 | -15 | -192 | 0 | 276 | 144 | 535 | 156 | 220 | 1331 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | C1 | 205.6982 | 205.6982 | 286.0725 | 703.8903 | 1474.884 | C1 | 66646.2187 | 32706.0148 | 177078.8645 | 57719.0022 | 197634.451 | 531784.5513 |  | 77753.9219 | 32294.6183 | 175076.3571 | 57719.0022 | 150438.1642 | 493282.0638 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 92564.1927 | 27563.5596 | 168496.6901 | 87282.3936 | 50146.0547 | 426052.8908 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769 |  | 99352.2335 | 29620.5417 | 153048.7763 | 99248.5282 | 41296.751 | 422566.8306
|  |  | 5824 | 5824 | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 281 | 0 | 0 | -15 | -266 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 594 | 0 | 0 | -224 | -370 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 15289 | 15289 | 15289 | 15289 | 15289 | C2 | 293.8546 | 293.8546 | 408.675 | 1005.5575 | 2106.9771 | C2 | 877155.9213 | 272697.0502 | 556206.6342 | 192061.4882 | 632093.127 | 2530214.2209 |  | 945624.0384 | 269464.6499 | 550893.8596 | 191055.9307 | 318153.5406 | 2275192.0192 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 910361.4888 | 297086.9804 | 605656.3055 | 234294.9045 | 0 | 2047399.6793 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914 |  | 848064.3179 | 377603.1353 | 617507.8797 | 96533.5229 | 96920.9461 | 2036629.8019
|  |  | 1184 | 1184 | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 35 | 0 | 0 | -4 | -31 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 69 | 0 | 0 | -31 | -38 | 0 | 607 | 291 | 204 | 35 | 47 | 1184 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | C3 | 440.7819 | 440.7819 | 613.0125 | 1508.3363 | 3160.4656 | C3 | 339842.8218 | 82426.2097 | 91951.8682 | 22625.0444 | 158023.2817 | 694869.2259 |  | 359678.0059 | 81544.646 | 91338.8558 | 22625.0444 | 60048.8471 | 615235.3992 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 330586.4025 | 101820.612 | 110955.2544 | 33183.3985 | 0 | 576545.6673 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152 |  | 297968.5441 | 128267.5242 | 125054.5408 | 6033.3452 | 28444.1907 | 585768.145
|  |  | 2 | 2 | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | C4 | 734.6365 | 734.6365 | 1021.6874 | 2513.8938 | 5267.4427 | C4 | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729
|  |  | 8341 | 8341 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 434 | 0 | 0 | -19 | -415 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 870 | 0 | 0 | -270 | -600 |  | 3175 | 1722 | 2250 | 511 | 683 | [22 empty] | 1284379.5983 | 388563.9111 | 825237.3669 | 272405.5349 | 987750.8598 | 3758337.271 |  | 1383790.6027 | 384038.5506 | 817309.0725 | 271399.9773 | 528640.5519 | 3385178.755 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 1333512.084 | 427940.4249 | 885108.25 | 354760.6966 | 50146.0547 | 3051467.5102 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564 |  | 1245385.0955 | 536960.474 | 895611.1968 | 201815.3963 | 166661.8878 | 3046434.0504
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4766.226 | 4766.226 | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 30792 | 30792 | 30792 | 30792 | 30792 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 892.414 | 892.414 | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 46188 | 46188 | 46188 | 46188 | 46188 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 76980 | 76980 | 76980 | 76980 | 76980 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5658.64 | 5658.64 |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | C1 | 61.3552 | 61.3552 | 85.3805 | 210.0532 | 440.1114 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 149285 | 149285 | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 12699 | 0 | 0 | -4978 | -7721 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 25798 | 0 | 0 | -9850 | -15948 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6837 | 6837 | 6837 | 6837 | 6837 | C2 | 87.6503 | 87.6503 | 121.9721 | 300.0759 | 628.7305 | C2 | 371812.7423 | 10036577.4824 | 324201.7886 | 3475479.4213 | 10084837.5408 | 24292908.9754 |  | 867738.366 | 10036577.4824 | 291269.327 | 3232117.842 | 7368092.9639 | 21795795.9813 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 1624599.0519 | 10036577.4824 | 291269.327 | 2195655.5798 | 4110640.1398 | 18258741.5809 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093 |  | 2347889.6576 | 10036577.4824 | 291269.327 | 1205104.9349 | 997795.3352 | 14878636.7371
|  |  | 10797 | 10797 | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 918 | 0 | 0 | -361 | -557 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 1866 | 0 | 0 | -712 | -1154 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | C3 | 131.4755 | 131.4755 | 182.9581 | 450.1139 | 943.0958 | C3 | 40231.5061 | 1089011.6493 | 35127.959 | 377195.444 | 1093991.1048 | 2635557.6632 |  | 94004.9896 | 1089011.6493 | 31651.7548 | 350638.7242 | 798802.1257 | 2364109.2436 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 176177.1834 | 1089011.6493 | 31468.7966 | 237660.1366 | 447027.3997 | 1981345.1656 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929 |  | 254668.0629 | 1089011.6493 | 31468.7966 | 130983.1434 | 107512.9189 | 1613644.5712
|  |  | 149 | 149 | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 12 | 0 | 0 | -3 | -9 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 26 | 0 | 0 | -10 | -16 | 0 | 1 | 114 | 3 | 14 | 17 | 149 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | C4 | 219.1258 | 219.1258 | 304.9302 | 750.1898 | 1571.8263 | C4 | 876.5034 | 24980.3469 | 914.7906 | 8252.0881 | 26721.0471 | 61744.7761 |  | 2191.2585 | 24980.3469 | 609.8604 | 8252.0881 | 18861.9156 | 54895.4695 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 3944.2653 | 24980.3469 | 914.7906 | 6751.7084 | 7859.1315 | 44450.2427 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968 |  | 5916.3979 | 24980.3469 | 914.7906 | 3000.7593 | 1571.8263 | 36384.121
|  |  | 160231 | 160231 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 13629 | 0 | 0 | -5342 | -8287 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 27690 | 0 | 0 | -10572 | -17118 |  | 1061 | 122904 | 2563 | 14883 | 18820 | [22 empty] | 412920.7517 | 11150569.4786 | 360244.5383 | 3860926.9533 | 11205549.6927 | 26990211.4147 |  | 963934.6142 | 11150569.4786 | 323530.9422 | 3591008.6543 | 8185757.0051 | 24214800.6944 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 1804720.5006 | 11150569.4786 | 323652.9143 | 2440067.4248 | 4565526.671 | 20284536.9893 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702 |  | 2608474.1184 | 11150569.4786 | 323652.9143 | 1339088.8376 | 1106880.0805 | 16528665.4294
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 |  | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 4964510.3383 | 12681910.0234 | 1905963.1233 | 3211554.0156 | 5460123.1976 | 28224060.6982 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 |  | 5493209.5757 | 12966391.5218 | 1881985.2624 | 2162961.6148 | 1889659.4846 | 24394207.4593
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 285 | 285 | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 9 | 0 | 0 | 0 | -9 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 22 | 0 | 0 | 0 | -22 | 0 | 127 | 117 | 7 | 0 | 34 | 285 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 87556 | 87556 | 87556 | 87556 | 87556 | C1 | 1122.4679 | 1122.4679 | 1561.999 | 3842.8328 | 8051.6498 | C1 | 234595.7953 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 350532.1971 |  | 239085.667 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 355022.0688 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 202044.2256 | 89797.4336 | 0 | 96070.821 | 0 | 387912.4802 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576 |  | 167247.7201 | 131328.7466 | 10933.9933 | 0 | 96619.7971 | 406130.2571
|  |  | 314 | 314 | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 38 | 0 | 0 | -37 | -1 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 77 | 0 | 0 | -8 | -69 | 0 | 150 | 57 | 20 | 17 | 70 | 314 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 125080 | 125080 | 125080 | 125080 | 125080 | C2 | 1603.5256 | 1603.5256 | 2231.4272 | 5489.7612 | 11502.3568 | C2 | 288634.608 | 22449.3584 | 247688.4192 | 10979.5224 | 23004.7136 | 592756.6216 |  | 322308.6456 | 22449.3584 | 218679.8656 | 0 | 11502.3568 | 574940.2264 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 365603.8368 | 35277.5632 | 80331.3792 | 153713.3136 | 0 | 634926.0928 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596 |  | 364000.3112 | 91400.9592 | 44628.544 | 49407.8508 | 11502.3568 | 560940.022
|  |  | 63 | 63 | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 10 | 0 | 0 | -9 | -1 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 23 | 0 | 0 | -2 | -21 | 0 | 28 | 8 | 2 | 4 | 21 | 63 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 187620 | 187620 | 187620 | 187620 | 187620 | C3 | 2405.2884 | 2405.2884 | 3347.1408 | 8234.6418 | 17253.5352 | C3 | 69753.3636 | 2405.2884 | 90372.8016 | 8234.6418 | 0 | 170766.0954 |  | 84185.094 | 2405.2884 | 87025.6608 | 8234.6418 | 0 | 181850.685 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 101022.1128 | 9621.1536 | 23429.9856 | 82346.418 | 0 | 216419.67 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704 |  | 122669.7084 | 19242.3072 | 6694.2816 | 16469.2836 | 0 | 165075.5808
|  |  | 45 | 45 | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 8 | 0 | -1 | -7 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 10 | 0 | 0 | -3 | -7 | 0 | 18 | 4 | 13 | 3 | 7 | 45 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 312700 | 312700 | 312700 | 312700 | 312700 | C4 | 4008.814 | 4008.814 | 5578.568 | 13724.403 | 28755.892 | C4 | 36079.326 | 12026.442 | 184092.744 | 0 | 0 | 232198.512 |  | 88193.908 | 12026.442 | 111571.36 | 0 | 0 | 211791.71 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 120264.42 | 0 | 83678.52 | 0 | 0 | 203942.94 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745 |  | 112246.792 | 16035.256 | 72521.384 | 0 | 0 | 200803.432
|  |  | 707 | 707 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 65 | 0 | -1 | -53 | -11 |  | 415 | 106 | 59 | 116 | 11 |  | 132 | 0 | 0 | -13 | -119 |  | 323 | 186 | 42 | 24 | 132 | [22 empty] | 629063.0929 | 79534.8698 | 564327.9389 | 42271.1612 | 31056.3634 | 1346253.4261 |  | 733773.3146 | 79534.8698 | 459450.8605 | 31291.6388 | 19554.0066 | 1323604.6902 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 788934.5952 | 134696.1504 | 187439.8848 | 332130.5526 | 0 | 1443201.183 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326 |  | 766164.5317 | 258007.269 | 134778.2029 | 65877.1344 | 108122.1539 | 1332949.2919
| EHV Transformer |  | 103 | 103 | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 9 | 0 | 0 | 0 | -9 | 0 | 44 | 6 | 13 | 10 | 30 | 103 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | C1 | 2639.1188 | 2639.1188 | 3672.5335 | 9035.1735 | 18930.8396 | C1 | 89730.0389 | 18473.8315 | 143228.8057 | 135527.6018 | 151446.717 | 538406.9949 |  | 121399.4643 | 13195.594 | 117521.0714 | 108422.0815 | 151446.717 | 511984.9281 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979 |  | 139873.2959 | 15834.7127 | 47742.9352 | 90351.7345 | 397547.632 | 691350.3104
|  |  | 113 | 113 | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 18 | 0 | 0 | 0 | -18 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 28 | 0 | 0 | 0 | -28 | 0 | 32 | 12 | 11 | 18 | 40 | 113 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 294085 | 294085 | 294085 | 294085 | 294085 | C2 | 3770.1697 | 3770.1697 | 5246.4764 | 12907.3906 | 27044.0566 | C2 | 143266.4486 | 18850.8485 | 152147.8156 | 361406.9382 | 324528.6792 | 1000200.7301 |  | 158347.1274 | 18850.8485 | 152147.8156 | 361406.9382 | 243396.5094 | 934149.2391 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 196048.8244 | 49012.2061 | 110176.0044 | 141981.2971 | 432704.9056 | 929923.2377 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029 |  | 226210.182 | 45242.0364 | 57711.2404 | 232333.0317 | 324528.6792 | 886025.1697
|  |  | 62 | 62 | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 7 | 0 | 0 | -1 | -6 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 13 | 0 | 0 | 0 | -13 | 0 | 17 | 6 | 15 | 8 | 16 | 62 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | C3 | 5655.2545 | 5655.2545 | 7869.7146 | 19361.086 | 40566.0849 | C3 | 96139.3273 | 5655.2545 | 220352.0088 | 232333.0317 | 121698.2547 | 676177.8771 |  | 124415.6001 | 5655.2545 | 220352.0088 | 212971.9457 | 0 | 563394.8092 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 141381.3637 | 28276.2727 | 157394.292 | 154888.6878 | 162264.3396 | 644204.9559 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198 |  | 169657.6365 | 33931.5273 | 118045.719 | 154888.6878 | 121698.2547 | 598221.8253
|  |  | 8 | 8 | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | C4 | 9425.4243 | 9425.4243 | 13116.191 | 32268.4766 | 67610.1415 | C4 | 56552.5455 | 0 | 0 | 64536.9532 | 135220.283 | 256309.7817 |  | 75403.394 | 0 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394
|  |  | 286 | 286 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 25 | 0 | 0 | -1 | -24 |  | 104 | 25 | 60 | 39 | 58 |  | 50 | 0 | 0 | 0 | -50 |  | 97 | 28 | 39 | 36 | 86 | [22 empty] | 385688.3603 | 42979.9346 | 515728.6301 | 793804.525 | 732893.9339 | 2471095.3838 |  | 479565.5858 | 37701.697 | 490020.8958 | 682800.9654 | 394843.2264 | 2084932.3703 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 515382.198 | 109334.9213 | 337348.4325 | 468538.2806 | 860000.9999 | 2290604.8323 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146 |  | 573442.8114 | 132709.9734 | 223499.8946 | 477573.454 | 843774.5659 | 2251000.6994
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C1 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | C1 | 757.237 | 757.237 | 25660.7739 | 62636.827 | 131244.019 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 4.244 | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | -2.16 | -2.16 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | -4.32 | -4.32 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564 |  |  | C2 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C2 | 8232 | 8232 | 8232 | 8232 | 8232 | C2 | 1081.7671 | 1081.7671 | 36658.2485 | 89481.1814 | 187491.4558 | C2 | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 672906.8347 | 776099.8042 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 267925.2903 | 481623.8355
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C3 | 12348 | 12348 | 12348 | 12348 | 12348 | C3 | 1622.6507 | 1622.6507 | 54987.3727 | 134221.7722 | 281237.1836 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C4 | 20580 | 20580 | 20580 | 20580 | 20580 | C4 | 2704.4178 | 2704.4178 | 91645.6212 | 223702.9536 | 468728.6394 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | -2.16 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | -4.32 |  | 0 | 0 | 0.723 | 2.092 | 5.749 | [22 empty] | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 672906.8347 | 776099.8042 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 267925.2903 | 481623.8355
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | C1 | 190.2375 | 190.2375 | 6447.0548 | 15737.162 | 32974.1524 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 75074 | 75074 | 75074 | 75074 | 75074 | C2 | 271.7679 | 271.7679 | 9210.0783 | 22481.66 | 47105.932 | C2 | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 112611 | 112611 | 112611 | 112611 | 112611 | C3 | 407.6518 | 407.6518 | 13815.1175 | 33722.4901 | 70658.8981 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 187685 | 187685 | 187685 | 187685 | 187685 | C4 | 679.4197 | 679.4197 | 23025.1958 | 56204.1501 | 117764.8301 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0 | [22 empty] | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
| EHV UG Cable (Non Pressurised) |  | 123.955 | 123.955 | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 208.376 | 208.376 | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 53241 | 53241 | 53241 | 53241 | 53241 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 71.937 | 71.937 | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.622 | 3.622 | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 407.89 | 407.89 |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 188 | 188 | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 8 | 0 | -8 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 14 | 0 | -14 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | C1 | 106.093 | 106.093 | 106.093 | 5372.7104 | 18408.139 | C1 | 2652.3254 | 9336.1853 | 5941.2088 | 69845.2355 | 110448.8339 | 198223.7889 |  | 3288.8835 | 9336.1853 | 5941.2088 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 8063.0691 | 8063.0691 | 26863.5521 | 0 | 46278.5738 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349 |  | 3182.7904 | 8593.5342 | 7532.6041 | 32236.2625 | 0 | 51545.1912
|  |  | 66 | 66 | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 2 | 0 | -2 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 285965 | 285965 | 285965 | 285965 | 285965 | C2 | 151.5615 | 151.5615 | 151.5615 | 7675.3006 | 26297.3414 | C2 | 1212.4916 | 4546.8435 | 3182.7904 | 38376.503 | 52594.6828 | 99913.3114 |  | 1515.6145 | 5153.0893 | 3182.7904 | 7675.3006 | 0 | 17526.7949 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534 |  | 1515.6145 | 3940.5977 | 4546.8435 | 0 | 0 | 10003.0557
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | C3 | 227.3422 | 227.3422 | 227.3422 | 11512.9509 | 39446.0121 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | C4 | 378.9036 | 378.9036 | 378.9036 | 19188.2515 | 65743.3535 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 8 | 0 | -8 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 16 | 0 | -16 | 0 |  | 40 | 91 | 101 | 22 | 0 | [22 empty] | 3864.817 | 13883.0288 | 9123.9993 | 108221.7385 | 163043.5167 | 298137.1002 |  | 4804.498 | 14489.2746 | 9123.9993 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 12609.9126 | 11852.1054 | 34538.8527 | 0 | 63805.3687 |  | 4698.405 | 10745.7068 | 12079.4476 | 122804.8096 | 0 | 150328.3689 |  | 4698.405 | 12534.1319 | 12079.4476 | 32236.2625 | 0 | 61548.247
| EHV OHL Support - Poles |  | 2475 | 2475 | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 223 | 0 | 0 | -79 | -144 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 451 | 0 | 0 | -159 | -292 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | C1 | 114.0865 | 114.0865 | 158.7599 | 390.5815 | 818.3612 | C1 | 13690.3754 | 134964.2845 | 31116.949 | 176542.8375 | 428821.2877 | 785135.7342 |  | 25897.6269 | 134964.2845 | 30323.1493 | 170684.1151 | 357623.8601 | 719493.0359 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 40614.7805 | 134964.2845 | 30323.1493 | 150373.8771 | 294610.045 | 650886.1364 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372 |  | 55674.1935 | 134964.2845 | 30323.1493 | 129673.0577 | 229959.5073 | 580594.1923
|  |  | 17510 | 17510 | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 1577 | 0 | 0 | -555 | -1022 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 3191 | 0 | 0 | -1123 | -2068 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12713 | 12713 | 12713 | 12713 | 12713 | C2 | 162.9807 | 162.9807 | 226.7999 | 557.9736 | 1169.0875 | C2 | 138859.5223 | 1364474.0855 | 315025.0889 | 1787189.3447 | 4325623.676 | 7931171.7174 |  | 261257.998 | 1364474.0855 | 306406.6919 | 1723580.3577 | 3618325.7506 | 7274044.8838 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 410385.3019 | 1364474.0855 | 306406.6919 | 1519920.0047 | 2976496.7241 | 6577682.8081 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879 |  | 562935.1996 | 1364311.1049 | 306406.6919 | 1311237.8895 | 2319469.5603 | 5864360.4462
|  |  | 264 | 264 | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 24 | 0 | 0 | -8 | -16 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 48 | 0 | 0 | -17 | -31 | 0 | 4 | 127 | 20 | 52 | 61 | 264 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | C3 | 244.471 | 244.471 | 340.1999 | 836.9604 | 1753.6312 | C3 | 2933.6519 | 30803.3447 | 7144.1975 | 40174.097 | 98203.3483 | 179258.6395 |  | 5867.3038 | 30803.3447 | 6803.9976 | 39337.1367 | 82420.6673 | 165232.4501 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 9289.8976 | 31047.8157 | 6803.9976 | 34315.3746 | 66637.9864 | 148095.0719 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402 |  | 12712.4915 | 31047.8157 | 6803.9976 | 29293.6124 | 52608.9366 | 132466.8538
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | C4 | 407.4516 | 407.4516 | 566.9998 | 1394.9339 | 2922.7187 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20249 | 20249 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 1824 | 0 | 0 | -642 | -1182 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 3690 | 0 | 0 | -1299 | -2391 |  | 304 | 9681 | 1562 | 4016 | 4686 | [22 empty] | 155483.5496 | 1530241.7148 | 353286.2354 | 2003906.2793 | 4852648.312 | 8895566.0911 |  | 293022.9286 | 1530241.7148 | 343533.8388 | 1933601.6095 | 4058370.2781 | 8158770.3698 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 460289.98 | 1530486.1858 | 343533.8388 | 1704609.2564 | 3337744.7554 | 7376664.0163 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653 |  | 631321.8846 | 1530323.2051 | 343533.8388 | 1470204.5596 | 2602038.0042 | 6577421.4924
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 164 | 164 | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 41 | 0 | 0 | 0 | -41 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 55 | 0 | 0 | 0 | -55 | 0 | 0 | 29 | 0 | 73 | 62 | 164 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | C1 | 273.0697 | 273.0697 | 380.4935 | 935.6531 | 1960.6893 | C1 | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 11195.8559 | 7919.0201 | 15219.7382 | 39297.4297 | 23528.2721 | 97160.316 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346 |  | 15018.8311 | 7919.0201 | 0 | 68302.6755 | 13724.8254 | 104965.3521
|  |  | 280 | 280 | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 59 | 0 | 0 | -51 | -8 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 117 | 0 | 0 | -97 | -20 | 0 | 0 | 0 | 6 | 254 | 20 | 280 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117147 | 117147 | 117147 | 117147 | 117147 | C2 | 390.0995 | 390.0995 | 543.5621 | 1336.6473 | 2800.9848 | C2 | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 23015.8711 | 0 | 101646.109 | 45446.0072 | 0 | 170107.9872 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745 |  | 45641.6427 | 0 | 3261.3725 | 209853.6214 | 0 | 258756.6365
|  |  | 153 | 153 | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 35 | 0 | 0 | 0 | -35 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 57 | 0 | 0 | -22 | -35 | 0 | 0 | 0 | 15 | 103 | 35 | 153 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | C3 | 585.1493 | 585.1493 | 815.3431 | 2004.9709 | 4201.4772 | C3 | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 20480.2243 | 0 | 96210.4882 | 0 | 0 | 116690.7124 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504 |  | 33353.5081 | 0 | 12230.1468 | 162402.6433 | 0 | 207986.2982
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | C4 | 975.2488 | 975.2488 | 1358.9052 | 3341.6182 | 7002.4619 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 135 | 0 | 0 | -51 | -84 |  | 0 | 29 | 345 | 127 | 96 |  | 229 | 0 | 0 | -119 | -110 |  | 0 | 29 | 21 | 430 | 117 | [22 empty] | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 54691.9513 | 7919.0201 | 213076.3354 | 84743.4369 | 23528.2721 | 383959.0157 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595 |  | 94013.9819 | 7919.0201 | 15491.5193 | 440558.9402 | 13724.8254 | 571708.2868
| EHV OHL Conductor (Tower Lines) |  | 23.103 | 23.103 | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | C1 | 6.1139 | 6.1139 | 8.4066 | 21.3987 | 44.3259 | C1 | 44.3992 | 0 | 42.2433 | 0 | 479.4285 | 566.0711 |  | 110.5273 | 0 | 42.2433 | 0 | 0 | 152.7706 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585
|  |  | 31.689 | 31.689 | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 109177 | 109177 | 109177 | 109177 | 109177 | C2 | 8.7342 | 8.7342 | 12.0095 | 30.5696 | 63.3227 | C2 | 0 | 0 | 366.3489 | 0 | 74.974 | 441.3229 |  | 10.3412 | 0 | 366.3489 | 0 | 0 | 376.6901 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558
|  |  | 8.297 | 8.297 | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | C3 | 13.1012 | 13.1012 | 18.0142 | 45.8543 | 94.984 | C3 | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346
|  |  | 5.911 | 5.911 | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | C4 | 21.8354 | 21.8354 | 30.0237 | 76.4239 | 158.3067 | C4 | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417
|  |  | 69 | 69 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0 | [22 empty] | 44.3992 | 0 | 735.526 | 0 | 554.4026 | 1334.3278 |  | 120.8685 | 0 | 735.526 | 0 | 0 | 856.3945 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 |  | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 |  | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 |  | 1824522.1193 | 1795187.6106 | 1200173.0425 | 2625918.4044 | 4894180.8621 | 12339982.0387 |  | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 |  | 2070060.2396 | 1941635.0199 | 759598.3376 | 2675072.1559 | 3835584.8397 | 11281950.5927
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 93 | 93 | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 1 | 0 | 0 | -1 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 60 | 16 | 2 | 3 | 93 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | C1 | 2362.7016 | 2362.7016 | 3287.8781 | 8088.8436 | 16948.0533 | C1 | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 80331.8558 | 103958.8722 | 42742.4154 | 16177.6872 | 0 | 243210.8306 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149 |  | 30715.1213 | 141762.0985 | 52606.0497 | 16177.6872 | 33896.1066 | 275157.0633
|  |  | 75 | 75 | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 2 | 0 | 0 | -2 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 3 | 0 | 0 | 0 | -3 | 0 | 23 | 37 | 12 | 0 | 3 | 75 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 263283 | 263283 | 263283 | 263283 | 263283 | C2 | 3375.2881 | 3375.2881 | 4696.9687 | 11555.4909 | 24211.5047 | C2 | 148512.6746 | 81006.9134 | 37575.7498 | 11555.4909 | 0 | 278650.8287 |  | 148512.6746 | 81006.9134 | 32878.781 | 0 | 0 | 262398.3691 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 111384.506 | 118135.0821 | 28181.8123 | 11555.4909 | 0 | 269256.8913 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223 |  | 87757.4896 | 124885.6582 | 56363.6246 | 0 | 0 | 269006.7724
|  |  | 52 | 52 | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 2 | 0 | 0 | 0 | -2 | 0 | 11 | 31 | 6 | 0 | 4 | 52 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | C3 | 5062.9321 | 5062.9321 | 7045.4531 | 17333.2363 | 36317.257 | C3 | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943 |  | 65818.1172 | 156950.8948 | 42272.7185 | 0 | 72634.514 | 337676.2445
|  |  | 9 | 9 | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | C4 | 8438.2201 | 8438.2201 | 11742.4218 | 28888.7272 | 60528.7617 | C4 | 25314.6604 | 42191.1007 | 11742.4218 | 0 | 0 | 79248.183 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813
|  |  | 229 | 229 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 3 | 0 | 0 | -3 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 6 | 0 | 0 | 0 | -6 |  | 50 | 133 | 34 | 2 | 10 | [22 empty] | 365881.2257 | 379719.9067 | 90181.7994 | 28888.7272 | 0 | 864671.6591 |  | 374319.4459 | 379719.9067 | 73742.4089 | 17333.2363 | 0 | 845114.9978 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 301413.2238 | 426298.882 | 99106.04 | 27733.1781 | 36317.257 | 890868.5808 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129 |  | 218043.6087 | 465789.7523 | 151242.3928 | 16177.6872 | 106530.6206 | 957784.0615
| 132kV Transformer |  | 54 | 54 | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 4 | 0 | 0 | 0 | -4 | 0 | 15 | 27 | 5 | 0 | 7 | 54 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | C1 | 11467.5067 | 11467.5067 | 15957.9032 | 39259.6621 | 82258.3395 | C1 | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728 |  | 217882.6267 | 309622.68 | 79789.516 | 0 | 246775.0186 | 854069.8412
|  |  | 56 | 56 | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 4 | 0 | 0 | 0 | -4 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 8 | 0 | 0 | 0 | -8 | 0 | 21 | 12 | 15 | 0 | 8 | 56 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 1277859 | 1277859 | 1277859 | 1277859 | 1277859 | C2 | 16382.1524 | 16382.1524 | 22797.0046 | 56085.2315 | 117511.9136 | C2 | 393171.6571 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1564265.5377 |  | 409553.8095 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1580647.69 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 425935.9619 | 294878.7428 | 182376.0365 | 0 | 470047.6546 | 1373238.3958 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061 |  | 475082.419 | 196585.8286 | 341955.0684 | 0 | 0 | 1013623.316
|  |  | 11 | 11 | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 2 | 3 | 2 | 1 | 3 | 11 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | C3 | 24573.2286 | 24573.2286 | 34195.5068 | 84127.8473 | 176267.8705 | C3 | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 172012.6 | 24573.2286 | 102586.5205 | 0 | 0 | 299172.3491 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152 |  | 122866.1429 | 73719.6857 | 68391.0137 | 84127.8473 | 0 | 349104.6895
|  |  | 10 | 10 | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 2 | 0 | 0 | 0 | -2 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 2 | 0 | 3 | 10 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | C4 | 40955.3809 | 40955.3809 | 56992.5114 | 140213.0788 | 293779.7841 | C4 | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 245732.2857 | 81910.7619 | 56992.5114 | 140213.0788 | 0 | 524848.6378 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799 |  | 286687.6666 | 40955.3809 | 113985.0228 | 0 | 0 | 441628.0704
|  |  | 131 | 131 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 9 | 0 | 0 | 0 | -9 |  | 52 | 41 | 17 | 2 | 19 |  | 18 | 0 | 0 | 0 | -18 |  | 42 | 43 | 24 | 1 | 21 | [22 empty] | 1012417.0171 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3955144.8381 |  | 1028799.1695 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3971526.9905 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 1095965.9942 | 630712.8666 | 421744.5844 | 179472.7408 | 963597.6918 | 3291493.8779 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739 |  | 1102518.8552 | 620883.5752 | 604120.6208 | 84127.8473 | 246775.0186 | 2658425.9171
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 15.74 | 15.74 | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | C1 | 216.5404 | 216.5404 | 7338.4477 | 17913.0384 | 37533.2768 | C1 | 2083.9852 | 1278.8878 | 1541.074 | 6663.6503 | 0 | 11567.5973 |  | 2083.9852 | 1278.8878 | 1541.074 | 0 | 0 | 4903.947 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901
|  |  | 24.539 | 24.539 | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 85454 | 85454 | 85454 | 85454 | 85454 | C2 | 309.3435 | 309.3435 | 10483.4967 | 25590.0548 | 53618.9668 | C2 | 2161.6922 | 4234.2936 | 40508.2313 | 24566.4526 | 0 | 71470.6698 |  | 2161.3829 | 4234.2936 | 40508.2313 | 0 | 0 | 46903.9078 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219
|  |  | 14.188 | 14.188 | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 128181 | 128181 | 128181 | 128181 | 128181 | C3 | 464.0152 | 464.0152 | 15725.2451 | 38385.0823 | 80428.4503 | C3 | 4729.7071 | 1834.7162 | 644.735 | 37502.2254 | 0 | 44711.3837 |  | 4729.7071 | 1834.7162 | 644.735 | 0 | 0 | 7209.1584 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074
|  |  | 0.708 | 0.708 | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 213635 | 213635 | 213635 | 213635 | 213635 | C4 | 773.3587 | 773.3587 | 26208.7418 | 63975.1371 | 134047.4171 | C4 | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538
|  |  | 55.175 | 55.175 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0 | [22 empty] | 8975.3845 | 7895.4355 | 42694.0404 | 68732.3283 | 0 | 128297.1887 |  | 8975.0752 | 7895.4355 | 42694.0404 | 0 | 0 | 59564.5511 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573
| 132kV UG Cable (Non Pressurised) |  | 8.145 | 8.145 | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25.492 | 25.492 | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 452934 | 452934 | 452934 | 452934 | 452934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5.672 | 5.672 | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 679401 | 679401 | 679401 | 679401 | 679401 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1132335 | 1132335 | 1132335 | 1132335 | 1132335 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 39.309 | 39.309 |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 704 | 704 | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 5 | 10 | 0 | -10 | -5 | 0 | 66 | 368 | 233 | 32 | 5 | 704 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | C1 | 342.7699 | 342.7699 | 342.7699 | 17358.3835 | 59473.8058 | C1 | 23993.8908 | 137107.9472 | 66154.5845 | 711693.7237 | 0 | 938950.1461 |  | 25364.9702 | 137107.9472 | 66154.5845 | 642260.1896 | 0 | 870887.6916 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 22622.8113 | 126139.3114 | 79865.3792 | 555468.2721 | 297369.0289 | 1081464.803 |  | 24336.6606 | 129567.0101 | 79865.3792 | 381884.4371 | 0 | 615653.4871
|  |  | 1006 | 1006 | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 10 | 28 | 0 | -28 | -10 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 23 | 55 | 0 | -55 | -23 | 0 | 164 | 470 | 247 | 102 | 23 | 1006 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 923908 | 923908 | 923908 | 923908 | 923908 | C2 | 489.6712 | 489.6712 | 489.6712 | 24797.6907 | 84962.5797 | C2 | 75899.0422 | 239449.2364 | 112624.3852 | 3273295.175 | 0 | 3701267.8388 |  | 80795.7546 | 239449.2364 | 112624.3852 | 3025318.2678 | 0 | 3458187.644 |  | 80795.7546 | 235042.1952 | 115562.4126 | 2777341.3606 | 1104513.5358 | 4313255.2589 |  | 85692.467 | 248752.9899 | 115562.4126 | 2083006.0205 | 254887.739 | 2787901.6291 |  | 80306.0834 | 230145.4828 | 120948.7963 | 2529364.4534 | 1954139.3326 | 4914904.1485 |  | 91568.5219 | 257077.401 | 120948.7963 | 1165491.4638 | 0 | 1635086.183
|  |  | 668 | 668 | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 20 | 0 | -20 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 5 | 31 | 0 | -31 | -5 | 0 | 57 | 350 | 168 | 88 | 5 | 668 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1385862 | 1385862 | 1385862 | 1385862 | 1385862 | C3 | 734.5069 | 734.5069 | 734.5069 | 37196.5361 | 127443.8695 | C3 | 35990.8361 | 260015.4284 | 123397.1525 | 3608063.9998 | 0 | 4027467.4168 |  | 43335.9047 | 260015.4284 | 123397.1525 | 3236098.639 | 0 | 3662847.1246 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 274705.5656 | 124131.6593 | 2492167.9174 | 127443.8695 | 3060315.9029 |  | 41866.891 | 257077.401 | 123397.1525 | 3273295.175 | 637219.3476 | 4332855.9671 |  | 45539.4253 | 279847.1137 | 123397.1525 | 2120202.5566 | 0 | 2568986.248
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 2309770 | 2309770 | 2309770 | 2309770 | 2309770 | C4 | 1224.1781 | 1224.1781 | 1224.1781 | 61994.2268 | 212406.4492 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2378 | 2378 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 10 | 48 | 0 | -48 | -10 |  | 294 | 1198 | 636 | 235 | 15 |  | 33 | 96 | 0 | -96 | -33 |  | 287 | 1188 | 648 | 222 | 33 | [22 empty] | 135883.7691 | 636572.612 | 302176.1222 | 7593052.8985 | 0 | 8667685.4018 |  | 149496.6296 | 636572.612 | 302176.1222 | 6903677.0964 | 0 | 7991922.4602 |  | 147342.0761 | 619825.8556 | 318873.9115 | 6638341.8057 | 1291431.2111 | 9015814.8601 |  | 152238.7885 | 648226.7875 | 318873.9115 | 5200075.744 | 441805.4143 | 6761220.6458 |  | 144795.7857 | 613362.1952 | 324211.328 | 6358127.9006 | 2888727.7091 | 10329224.9186 |  | 161444.6078 | 666491.5248 | 324211.328 | 3667578.4575 | 0 | 4819725.9181
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1291 | 1291 | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 75 | 0 | 0 | -72 | -3 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 135 | 0 | 0 | 0 | -135 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | C1 | 25.0391 | 25.0391 | 34.4288 | 81.3771 | 172.1439 | C1 | 0 | 450.704 | 43276.9752 | 162.7542 | 2410.0145 | 46300.448 |  | 300.4693 | 450.704 | 43276.9752 | 162.7542 | 344.2878 | 44535.1906 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 2178.4027 | 350.5476 | 38904.5203 | 4801.2497 | 172.1439 | 46406.8642 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985 |  | 3680.7495 | 0 | 723.0044 | 91386.499 | 0 | 95790.2528
|  |  | 2037 | 2037 | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 150 | 0 | 0 | -150 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 333 | 0 | 0 | 0 | -333 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 447127 | 447127 | 447127 | 447127 | 447127 | C2 | 35.7702 | 35.7702 | 49.184 | 116.253 | 245.9199 | C2 | 214.621 | 321.9314 | 95859.5575 | 0 | 17214.3895 | 113610.4994 |  | 2825.8426 | 321.9314 | 95859.5575 | 0 | 0 | 99007.3316 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 8191.3666 | 143.0806 | 79727.2154 | 21274.3027 | 0 | 109335.9653 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197 |  | 14737.3059 | 0 | 491.8397 | 187748.6273 | 0 | 202977.7729
|  |  | 1379 | 1379 | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 99 | 0 | 0 | -84 | -15 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 223 | 0 | 0 | 0 | -223 | 0 | 201 | 20 | 60 | 875 | 223 | 1379 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | C3 | 53.6552 | 53.6552 | 73.776 | 174.3795 | 368.8798 | C3 | 6867.8707 | 3809.522 | 78202.5123 | 8195.8379 | 25821.5842 | 122897.3272 |  | 10784.7032 | 3809.522 | 78202.5123 | 8195.8379 | 0 | 100992.5755 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 16096.572 | 1502.3467 | 68390.3103 | 15694.1577 | 12541.9124 | 114225.2991 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439 |  | 22749.8218 | 1073.1048 | 4426.5573 | 152582.0887 | 0 | 180831.5726
|  |  | 13 | 13 | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | C4 | 89.4254 | 89.4254 | 122.9599 | 290.6325 | 614.7996 | C4 | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231
|  |  | 4720 | 4720 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 324 | 0 | 0 | -306 | -18 |  | 292 | 46 | 3691 | 638 | 53 |  | 691 | 0 | 0 | 0 | -691 |  | 292 | 20 | 91 | 3626 | 691 | [22 empty] | 7082.4917 | 4582.1575 | 218937.5241 | 8358.5921 | 45445.9883 | 284406.7537 |  | 13911.0152 | 4582.1575 | 218937.5241 | 8358.5921 | 344.2878 | 246133.5767 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 26466.3414 | 1995.9749 | 188620.5249 | 41769.7101 | 12714.0562 | 271566.6076 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853 |  | 41167.8771 | 1073.1048 | 5641.4014 | 435495.4382 | 0 | 483377.8215
| 132kV OHL Conductor (Tower Lines) |  | 293.476 | 293.476 | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 13.845 | 0 | 0 | -13.845 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 22.579 | 0 | 0 | -8.707 | -13.872 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | C1 | 25.4967 | 25.4967 | 35.058 | 89.2386 | 184.8514 | C1 | 1678.2977 | 2783.8875 | 4083.0677 | 0 | 369.5179 | 8914.7708 |  | 1741.7336 | 2783.8875 | 4065.9594 | 0 | 0 | 8591.5805 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 1454.5637 | 3418.0425 | 3587.9082 | 2.4094 | 0 | 8462.9239 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739 |  | 1303.3681 | 3641.3685 | 2340.4386 | 2925.3307 | 0 | 10210.5058
|  |  | 461.16 | 461.159 | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 7.916 | 0 | 0 | -7.916 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 35.264 | 0 | 0 | -8.813 | -26.452 | -0.001 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 455299 | 455299 | 455299 | 455299 | 455299 | C2 | 36.4239 | 36.4239 | 50.0829 | 127.4837 | 264.0734 | C2 | 1764.1926 | 5199.3689 | 13484.3674 | 94.083 | 0 | 20542.0118 |  | 1979.7493 | 5199.3689 | 13224.938 | 0 | 0 | 20404.0562 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1798.686 | 5120.6204 | 13581.3779 | 2.0397 | 0 | 20502.7241 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628 |  | 2325.3759 | 4885.2854 | 10975.6153 | 5615.0204 | 0 | 23801.297
|  |  | 331.02 | 331.02 | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 24.14 | 0 | 0 | -24.14 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 42.756 | 0 | 0 | -1.652 | -41.104 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | C3 | 54.6359 | 54.6359 | 75.1243 | 191.2256 | 396.1101 | C3 | 3961.9208 | 7489.7596 | 7995.7083 | 2489.1834 | 780.7331 | 22717.3052 |  | 5578.8151 | 7489.7596 | 6898.3672 | 0 | 0 | 19966.9419 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 5392.2882 | 7624.9834 | 6197.9079 | 1962.5481 | 0 | 21177.7276 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424 |  | 5093.6485 | 5352.7318 | 8828.5367 | 4264.5217 | 0 | 23539.4386
|  |  | 3.344 | 3.344 | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | C4 | 91.0598 | 91.0598 | 125.2072 | 318.7093 | 660.1836 | C4 | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693
|  |  | 1089 | 1088.999 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 45.901 | 0 | 0 | -45.901 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 100.599 | 0 | 0 | -19.172 | -81.428 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428 | [22 empty] | 7404.4111 | 15473.016 | 25981.8364 | 2583.2664 | 1150.251 | 52592.7808 |  | 9300.298 | 15473.016 | 24607.9576 | 0 | 0 | 49381.2715 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 8645.5379 | 16163.6463 | 23785.887 | 1966.9973 | 0 | 50562.0685 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373 |  | 8722.3924 | 13879.3857 | 22563.2835 | 12804.8728 | 0 | 57969.9344
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 |  | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 |  | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 |  | 1593580.6049 | 1731156.5846 | 1103682.4945 | 5451018.3703 | 1454434.4194 | 11333872.4738 |  | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 |  | 1539947.0154 | 1774975.9208 | 1216973.0316 | 4216184.303 | 353305.6392 | 9101385.91
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 332299.578 | 332215.257 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 26201.901 | -31 | -73 | -10600.901 | -15539.16 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 53125.599 | -65 | -125 | -20688.172 | -32331.748 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 |  | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 |  | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 |  | 9724373.5839 | 21026363.0445 | 5276892.3921 | 12625689.2114 | 13320105.5711 | 61973423.8031 |  | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 |  | 10718638.4489 | 21535091.1626 | 4869663.3299 | 9861561.07 | 6781859.0967 | 53766813.1081
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 | LV Network | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 1341760.5214 | 4818108.826 | 1067073.7318 | 1337198.4212 | 1511367.092 | 10075508.5923 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 | LV Network | 1615421.6182 | 4852088.7001 | 1011106.6983 | 807342.9963 | 703309.1331 | 8989269.1461
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 | HV Network | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 4964510.3383 | 12681910.0234 | 1905963.1233 | 3211554.0156 | 5460123.1976 | 28224060.6982 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 | HV Network | 5493209.5757 | 12966391.5218 | 1881985.2624 | 2162961.6148 | 1889659.4846 | 24394207.4593
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 | EHV Network | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 | EHV Network | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 | EHV Network | 1824522.1193 | 1795187.6106 | 1200173.0425 | 2625918.4044 | 4894180.8621 | 12339982.0387 | EHV Network | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 | EHV Network | 2070060.2396 | 1941635.0199 | 759598.3376 | 2675072.1559 | 3835584.8397 | 11281950.5927
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 | 132kV Network | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 | 132kV Network | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 | 132kV Network | 1593580.6049 | 1731156.5846 | 1103682.4945 | 5451018.3703 | 1454434.4194 | 11333872.4738 | 132kV Network | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 | 132kV Network | 1539947.0154 | 1774975.9208 | 1216973.0316 | 4216184.303 | 353305.6392 | 9101385.91
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 | Total | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 | Total | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 | Total | 9724373.5839 | 21026363.0445 | 5276892.3921 | 12625689.2114 | 13320105.5711 | 61973423.8031 | Total | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 | Total | 10718638.4489 | 21535091.1626 | 4869663.3299 | 9861561.07 | 6781859.0967 | 53766813.1081
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWALES - Asset Rep
Secondary deliverables RIIO-ED1 - Asset replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWALES | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | C1 | 42.3124 | 42.3124 | 58.8809 | 144.8589 | 303.514 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 8621 | 0 | 0 | -4035 | -4586 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 17457 | 0 | 0 | -8170 | -9287 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4715 | 4715 | 4715 | 4715 | 4715 | C2 | 60.4463 | 60.4463 | 84.1156 | 206.9413 | 433.5914 | C2 | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 829565.0212 | 4625048.6445 | 301890.8884 | 1042363.58 | 1268688.4364 | 8067556.5705 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 1139352.3087 | 4625048.6445 | 301890.8884 | 406018.9287 | 379826.0664 | 6852136.8367
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | C3 | 90.6694 | 90.6694 | 126.1734 | 310.412 | 650.3871 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | C4 | 151.1157 | 151.1157 | 210.289 | 517.3534 | 1083.9785 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 8621 | 0 | 0 | -4035 | -4586 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 17457 | 0 | 0 | -8170 | -9287 |  | 1392 | 76515 | 3589 | 10132 | 10163 | [22 empty] | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 829565.0212 | 4625048.6445 | 301890.8884 | 1042363.58 | 1268688.4364 | 8067556.5705 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 1139352.3087 | 4625048.6445 | 301890.8884 | 406018.9287 | 379826.0664 | 6852136.8367
| LV Switchgear (at s/s) |  | 278 | 278 | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | C1 | 82.0156 | 82.0156 | 114.0623 | 280.6537 | 588.0628 | C1 | 22308.2388 | 0 | 0 | 0 | 0 | 22308.2388 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324
|  |  | 7511 | 7511 | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 368 | -24 | -62 | -11 | -271 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 736 | -52 | -94 | -47 | -543 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 6096 | 6096 | 6096 | 6096 | 6096 | C2 | 117.1651 | 117.1651 | 162.9461 | 400.9339 | 840.0898 | C2 | 411483.9014 | 131107.7693 | 359459.0525 | 119478.3082 | 224303.9659 | 1245832.9973 |  | 445930.4467 | 130404.7786 | 356200.1309 | 111860.5637 | 106691.3995 | 1151087.3194 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 414647.3597 | 160281.8842 | 343490.3366 | 176410.9248 | 47045.0266 | 1141875.5318 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677 |  | 366609.6605 | 216755.472 | 303079.7088 | 241362.2198 | 58806.2832 | 1186613.3443
|  |  | 76 | 76 | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 6 | -2 | -1 | 0 | -3 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 12 | -2 | -3 | -1 | -6 | 0 | 23 | 16 | 22 | 9 | 6 | 76 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 9144 | 9144 | 9144 | 9144 | 9144 | C3 | 175.7477 | 175.7477 | 244.4191 | 601.4009 | 1260.1346 | C3 | 4569.4397 | 2284.7198 | 6599.3162 | 3007.0044 | 6300.6732 | 22761.1534 |  | 5975.4211 | 2284.7198 | 5866.0589 | 3007.0044 | 0 | 17133.2042 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 6326.9165 | 1933.2245 | 6110.478 | 1202.8018 | 2520.2693 | 18093.69 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959 |  | 6151.1688 | 2460.4675 | 4643.9633 | 4811.207 | 0 | 18066.8066
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 15240 | 15240 | 15240 | 15240 | 15240 | C4 | 292.9128 | 292.9128 | 407.3652 | 1002.3348 | 2100.2244 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7865 | 7865 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 374 | -26 | -63 | -11 | -274 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 748 | -54 | -97 | -48 | -549 |  | 2694 | 1918 | 1976 | 658 | 619 | [22 empty] | 438361.58 | 133392.4891 | 366058.3687 | 122485.3126 | 230604.6391 | 1290902.3895 |  | 474706.2002 | 132689.4984 | 362066.1898 | 114867.5681 | 106691.3995 | 1191020.856 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 443774.6085 | 162215.1086 | 349600.8146 | 177613.7266 | 49565.2958 | 1182769.5542 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096 |  | 395561.1616 | 219215.9395 | 307723.6721 | 246173.4269 | 58806.2832 | 1227480.4833
| LV UGB and LV Pillar OD (not at s/s) |  | 103 | 103 | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | C1 | 70.2164 | 70.2164 | 97.6527 | 240.2775 | 503.4613 | C1 | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919
|  |  | 3635 | 3635 | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 123 | 0 | 0 | 0 | -123 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 250 | 0 | 0 | 0 | -250 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5219 | 5219 | 5219 | 5219 | 5219 | C2 | 100.3092 | 100.3092 | 139.5039 | 343.2536 | 719.2304 | C2 | 45339.7494 | 52060.4644 | 303560.4211 | 95767.7628 | 146003.7692 | 642732.1668 |  | 51157.6818 | 52060.4644 | 303281.4134 | 95767.7628 | 110042.2497 | 612309.572 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 56674.6867 | 30694.6091 | 300909.8476 | 116706.2342 | 192034.5141 | 697019.8917 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192 |  | 68611.4791 | 7824.116 | 287656.9799 | 152061.3581 | 264676.7835 | 780830.7167
|  |  | 581 | 581 | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 5 | 0 | 0 | 0 | -5 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 6 | 0 | 0 | 0 | -6 | 0 | 25 | 0 | 544 | 6 | 6 | 581 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | C3 | 150.4638 | 150.4638 | 209.2558 | 514.8804 | 1078.8456 | C3 | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 4513.9131 | 150.4638 | 114672.1811 | 514.8804 | 1078.8456 | 120930.284 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083 |  | 4664.3769 | 0 | 113835.1579 | 3089.2827 | 0 | 121588.8175
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | C4 | 250.773 | 250.773 | 348.7597 | 858.1341 | 1798.076 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4319 | 4319 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 128 | 0 | 0 | 0 | -128 |  | 570 | 307 | 2705 | 341 | 396 |  | 256 | 0 | 0 | 0 | -256 |  | 562 | 78 | 2606 | 449 | 624 | [22 empty] | 56333.6355 | 52511.8557 | 418023.3465 | 96282.6432 | 151397.9971 | 774549.478 |  | 62151.5679 | 52511.8557 | 417744.3387 | 96282.6432 | 115436.4776 | 744126.8832 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 68420.8917 | 30845.0729 | 415582.0287 | 117221.1146 | 193113.3597 | 825182.4676 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194 |  | 80508.1479 | 7824.116 | 401492.1379 | 155150.6408 | 264676.7835 | 909651.826
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 |  | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 1341760.5214 | 4818108.826 | 1067073.7318 | 1337198.4212 | 1511367.092 | 10075508.5923 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 |  | 1615421.6182 | 4852088.7001 | 1011106.6983 | 807342.9963 | 703309.1331 | 8989269.1461
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 631 | 631 | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 21 | 0 | 0 | -8 | -13 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 31 | 0 | 0 | -1 | -30 | 0 | 217 | 260 | 61 | 45 | 48 | 631 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 36715 | 36715 | 36715 | 36715 | 36715 | C1 | 470.6863 | 470.6863 | 654.9956 | 1611.4213 | 3376.3114 | C1 | 184979.7159 | 55540.9834 | 56329.6216 | 35451.2697 | 47268.3596 | 379569.9502 |  | 185921.0885 | 55540.9834 | 56329.6216 | 32228.427 | 40515.7368 | 370535.8573 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 146383.4393 | 98844.123 | 45194.6964 | 46731.2191 | 40515.7368 | 377669.2147 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046 |  | 116730.2024 | 122378.438 | 39954.7316 | 70902.5394 | 60773.6052 | 410739.5166
|  |  | 1416 | 1416 | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 60 | 0 | -6 | -22 | -32 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 117 | 0 | -2 | -14 | -101 | 0 | 550 | 467 | 143 | 119 | 137 | 1416 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 52450 | 52450 | 52450 | 52450 | 52450 | C2 | 672.409 | 672.409 | 935.708 | 2302.0305 | 4823.302 | C2 | 532547.928 | 199705.473 | 212405.716 | 195672.5925 | 159168.966 | 1299500.6755 |  | 537927.2 | 198360.655 | 209598.592 | 165746.196 | 120582.55 | 1232215.193 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 487496.525 | 268963.6 | 179655.936 | 147329.952 | 168815.57 | 1252261.583 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005 |  | 448496.803 | 314015.003 | 131934.828 | 241713.2025 | 173638.872 | 1309798.7085
|  |  | 31 | 31 | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 5 | 0 | 0 | -1 | -4 | 0 | 7 | 4 | 8 | 8 | 4 | 31 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 78675 | 78675 | 78675 | 78675 | 78675 | C3 | 1008.6135 | 1008.6135 | 1403.562 | 3453.0457 | 7234.953 | C3 | 5043.0675 | 9077.5215 | 19649.868 | 13812.183 | 14469.906 | 62052.546 |  | 7060.2945 | 9077.5215 | 19649.868 | 3453.0457 | 0 | 39240.7297 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225 |  | 12103.362 | 4034.454 | 11228.496 | 24171.3202 | 0 | 51537.6322
|  |  | 185 | 185 | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 7 | 0 | 0 | -2 | -5 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 24 | 0 | 0 | -1 | -23 | 0 | 59 | 67 | 20 | 16 | 23 | 185 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 131125 | 131125 | 131125 | 131125 | 131125 | C4 | 1681.0225 | 1681.0225 | 2339.27 | 5755.0763 | 12058.255 | C4 | 154654.07 | 73964.99 | 79535.18 | 80571.0675 | 48233.02 | 436958.3275 |  | 154654.07 | 73964.99 | 79535.18 | 69060.915 | 36174.765 | 413389.92 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 137843.845 | 95818.2825 | 63160.29 | 86326.1438 | 48233.02 | 431381.5812 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32 |  | 139524.8675 | 112628.5075 | 46785.4 | 86326.1438 | 0 | 385264.9188
|  |  | 2263 | 2263 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 88 | 0 | -6 | -32 | -50 |  | 1037 | 672 | 308 | 144 | 102 |  | 177 | 0 | -2 | -17 | -158 |  | 833 | 798 | 232 | 188 | 212 | [22 empty] | 877224.7814 | 338288.9679 | 367920.3856 | 325507.1127 | 269140.2516 | 2178081.4992 |  | 885562.653 | 336944.1499 | 365113.2616 | 270488.5837 | 197273.0518 | 2055381.7001 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 778784.1038 | 468669.073 | 307660.7904 | 294199.4979 | 264799.2798 | 2114112.7449 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476 |  | 716855.2349 | 553056.4025 | 229903.4556 | 423113.2059 | 234412.4772 | 2157340.7761
| HV Switchgear (GM) - Distribution |  | 254 | 254 | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | C1 | 131.855 | 131.855 | 183.4862 | 451.413 | 945.8178 | C1 | 31645.1957 | 1582.2598 | 0 | 0 | 0 | 33227.4555 |  | 31908.9056 | 1582.2598 | 0 | 0 | 0 | 33491.1654 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526
|  |  | 9267 | 9203 | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 373 | -60 | -3 | 0 | -340 | -30 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 788 | -112 | -25 | -47 | -668 | -64 | 3289 | 3436 | 1342 | 281 | 919 | 9267 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 14693 | 14693 | 14693 | 14693 | 14693 | C2 | 188.3643 | 188.3643 | 262.1231 | 644.8758 | 1351.1683 | C2 | 1026961.9455 | 378988.8911 | 267365.5824 | 108339.1294 | 708012.1787 | 2489667.7271 |  | 1060114.0553 | 373903.0561 | 264220.105 | 107694.2536 | 647209.6061 | 2453141.076 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 881921.4653 | 547386.5396 | 298296.1106 | 105114.7505 | 470206.5614 | 2302925.4274 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162 |  | 767961.088 | 626122.8002 | 345216.149 | 150900.9302 | 339143.2383 | 2229344.2058
|  |  | 1084 | 1068 | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 114 | -1 | 0 | -4 | -119 | -10 | 367 | 298 | 224 | 22 | 173 | 1084 | 190 | -11 | -1 | -2 | -192 | -16 | 279 | 326 | 216 | 50 | 213 | 1084 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | C3 | 282.5464 | 282.5464 | 393.1847 | 967.3137 | 2026.7524 | C3 | 128276.0611 | 68658.7728 | 78636.936 | 33855.9779 | 291852.3485 | 601280.0962 |  | 137600.0919 | 67811.1336 | 77850.5666 | 25150.155 | 269558.0719 | 577970.0191 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 135904.8136 | 83916.2778 | 88073.3683 | 17411.6458 | 109444.6307 | 434750.7362 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405 |  | 132514.2569 | 89002.1128 | 84534.7062 | 46431.0554 | 42561.8008 | 395043.9322
|  |  | 4 | 4 | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | C4 | 470.9106 | 470.9106 | 655.3078 | 1612.1894 | 3377.9207 | C4 | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128
|  |  | 10609 | 10529 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 487 | -61 | -3 | -4 | -459 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 978 | -123 | -26 | -49 | -860 |  | 3735 | 3843 | 1567 | 332 | 1132 | [22 empty] | 1186883.2023 | 449700.8343 | 347968.4418 | 142195.1073 | 999864.5272 | 3126612.1129 |  | 1229623.0529 | 443767.3601 | 344036.595 | 132844.4086 | 916767.678 | 3067039.0946 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 1047493.6499 | 634731.0469 | 389541.1686 | 122526.3963 | 579651.1921 | 2773943.4538 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867 |  | 922495.1269 | 725805.1666 | 432817.6957 | 198944.175 | 381705.0391 | 2661767.2034
| HV Transformer (GM) |  | 1331 | 1331 | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 118 | 0 | 0 | 0 | -118 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 207 | 0 | 0 | -15 | -192 | 0 | 276 | 144 | 535 | 156 | 220 | 1331 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | C1 | 205.6982 | 205.6982 | 286.0725 | 703.8903 | 1474.884 | C1 | 66646.2187 | 32706.0148 | 177078.8645 | 57719.0022 | 197634.451 | 531784.5513 |  | 77753.9219 | 32294.6183 | 175076.3571 | 57719.0022 | 150438.1642 | 493282.0638 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 92564.1927 | 27563.5596 | 168496.6901 | 87282.3936 | 50146.0547 | 426052.8908 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769 |  | 99352.2335 | 29620.5417 | 153048.7763 | 99248.5282 | 41296.751 | 422566.8306
|  |  | 5824 | 5824 | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 281 | 0 | 0 | -15 | -266 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 594 | 0 | 0 | -224 | -370 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 15289 | 15289 | 15289 | 15289 | 15289 | C2 | 293.8546 | 293.8546 | 408.675 | 1005.5575 | 2106.9771 | C2 | 877155.9213 | 272697.0502 | 556206.6342 | 192061.4882 | 632093.127 | 2530214.2209 |  | 945624.0384 | 269464.6499 | 550893.8596 | 191055.9307 | 318153.5406 | 2275192.0192 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 910361.4888 | 297086.9804 | 605656.3055 | 234294.9045 | 0 | 2047399.6793 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914 |  | 848064.3179 | 377603.1353 | 617507.8797 | 96533.5229 | 96920.9461 | 2036629.8019
|  |  | 1184 | 1184 | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 35 | 0 | 0 | -4 | -31 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 69 | 0 | 0 | -31 | -38 | 0 | 607 | 291 | 204 | 35 | 47 | 1184 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | C3 | 440.7819 | 440.7819 | 613.0125 | 1508.3363 | 3160.4656 | C3 | 339842.8218 | 82426.2097 | 91951.8682 | 22625.0444 | 158023.2817 | 694869.2259 |  | 359678.0059 | 81544.646 | 91338.8558 | 22625.0444 | 60048.8471 | 615235.3992 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 330586.4025 | 101820.612 | 110955.2544 | 33183.3985 | 0 | 576545.6673 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152 |  | 297968.5441 | 128267.5242 | 125054.5408 | 6033.3452 | 28444.1907 | 585768.145
|  |  | 2 | 2 | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | C4 | 734.6365 | 734.6365 | 1021.6874 | 2513.8938 | 5267.4427 | C4 | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729
|  |  | 8341 | 8341 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 434 | 0 | 0 | -19 | -415 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 870 | 0 | 0 | -270 | -600 |  | 3175 | 1722 | 2250 | 511 | 683 | [22 empty] | 1284379.5983 | 388563.9111 | 825237.3669 | 272405.5349 | 987750.8598 | 3758337.271 |  | 1383790.6027 | 384038.5506 | 817309.0725 | 271399.9773 | 528640.5519 | 3385178.755 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 1333512.084 | 427940.4249 | 885108.25 | 354760.6966 | 50146.0547 | 3051467.5102 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564 |  | 1245385.0955 | 536960.474 | 895611.1968 | 201815.3963 | 166661.8878 | 3046434.0504
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4766.226 | 4766.226 | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 30792 | 30792 | 30792 | 30792 | 30792 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 892.414 | 892.414 | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 46188 | 46188 | 46188 | 46188 | 46188 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 76980 | 76980 | 76980 | 76980 | 76980 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5658.64 | 5658.64 |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | C1 | 61.3552 | 61.3552 | 85.3805 | 210.0532 | 440.1114 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 149285 | 149285 | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 12699 | 0 | 0 | -4978 | -7721 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 25798 | 0 | 0 | -9850 | -15948 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6837 | 6837 | 6837 | 6837 | 6837 | C2 | 87.6503 | 87.6503 | 121.9721 | 300.0759 | 628.7305 | C2 | 371812.7423 | 10036577.4824 | 324201.7886 | 3475479.4213 | 10084837.5408 | 24292908.9754 |  | 867738.366 | 10036577.4824 | 291269.327 | 3232117.842 | 7368092.9639 | 21795795.9813 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 1624599.0519 | 10036577.4824 | 291269.327 | 2195655.5798 | 4110640.1398 | 18258741.5809 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093 |  | 2347889.6576 | 10036577.4824 | 291269.327 | 1205104.9349 | 997795.3352 | 14878636.7371
|  |  | 10797 | 10797 | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 918 | 0 | 0 | -361 | -557 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 1866 | 0 | 0 | -712 | -1154 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | C3 | 131.4755 | 131.4755 | 182.9581 | 450.1139 | 943.0958 | C3 | 40231.5061 | 1089011.6493 | 35127.959 | 377195.444 | 1093991.1048 | 2635557.6632 |  | 94004.9896 | 1089011.6493 | 31651.7548 | 350638.7242 | 798802.1257 | 2364109.2436 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 176177.1834 | 1089011.6493 | 31468.7966 | 237660.1366 | 447027.3997 | 1981345.1656 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929 |  | 254668.0629 | 1089011.6493 | 31468.7966 | 130983.1434 | 107512.9189 | 1613644.5712
|  |  | 149 | 149 | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 12 | 0 | 0 | -3 | -9 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 26 | 0 | 0 | -10 | -16 | 0 | 1 | 114 | 3 | 14 | 17 | 149 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | C4 | 219.1258 | 219.1258 | 304.9302 | 750.1898 | 1571.8263 | C4 | 876.5034 | 24980.3469 | 914.7906 | 8252.0881 | 26721.0471 | 61744.7761 |  | 2191.2585 | 24980.3469 | 609.8604 | 8252.0881 | 18861.9156 | 54895.4695 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 3944.2653 | 24980.3469 | 914.7906 | 6751.7084 | 7859.1315 | 44450.2427 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968 |  | 5916.3979 | 24980.3469 | 914.7906 | 3000.7593 | 1571.8263 | 36384.121
|  |  | 160231 | 160231 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 13629 | 0 | 0 | -5342 | -8287 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 27690 | 0 | 0 | -10572 | -17118 |  | 1061 | 122904 | 2563 | 14883 | 18820 | [22 empty] | 412920.7517 | 11150569.4786 | 360244.5383 | 3860926.9533 | 11205549.6927 | 26990211.4147 |  | 963934.6142 | 11150569.4786 | 323530.9422 | 3591008.6543 | 8185757.0051 | 24214800.6944 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 1804720.5006 | 11150569.4786 | 323652.9143 | 2440067.4248 | 4565526.671 | 20284536.9893 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702 |  | 2608474.1184 | 11150569.4786 | 323652.9143 | 1339088.8376 | 1106880.0805 | 16528665.4294
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 |  | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 4964510.3383 | 12681910.0234 | 1905963.1233 | 3211554.0156 | 5460123.1976 | 28224060.6982 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 |  | 5493209.5757 | 12966391.5218 | 1881985.2624 | 2162961.6148 | 1889659.4846 | 24394207.4593
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 285 | 285 | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 9 | 0 | 0 | 0 | -9 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 22 | 0 | 0 | 0 | -22 | 0 | 127 | 117 | 7 | 0 | 34 | 285 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 87556 | 87556 | 87556 | 87556 | 87556 | C1 | 1122.4679 | 1122.4679 | 1561.999 | 3842.8328 | 8051.6498 | C1 | 234595.7953 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 350532.1971 |  | 239085.667 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 355022.0688 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 202044.2256 | 89797.4336 | 0 | 96070.821 | 0 | 387912.4802 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576 |  | 167247.7201 | 131328.7466 | 10933.9933 | 0 | 96619.7971 | 406130.2571
|  |  | 314 | 314 | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 38 | 0 | 0 | -37 | -1 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 77 | 0 | 0 | -8 | -69 | 0 | 150 | 57 | 20 | 17 | 70 | 314 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 125080 | 125080 | 125080 | 125080 | 125080 | C2 | 1603.5256 | 1603.5256 | 2231.4272 | 5489.7612 | 11502.3568 | C2 | 288634.608 | 22449.3584 | 247688.4192 | 10979.5224 | 23004.7136 | 592756.6216 |  | 322308.6456 | 22449.3584 | 218679.8656 | 0 | 11502.3568 | 574940.2264 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 365603.8368 | 35277.5632 | 80331.3792 | 153713.3136 | 0 | 634926.0928 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596 |  | 364000.3112 | 91400.9592 | 44628.544 | 49407.8508 | 11502.3568 | 560940.022
|  |  | 63 | 63 | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 10 | 0 | 0 | -9 | -1 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 23 | 0 | 0 | -2 | -21 | 0 | 28 | 8 | 2 | 4 | 21 | 63 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 187620 | 187620 | 187620 | 187620 | 187620 | C3 | 2405.2884 | 2405.2884 | 3347.1408 | 8234.6418 | 17253.5352 | C3 | 69753.3636 | 2405.2884 | 90372.8016 | 8234.6418 | 0 | 170766.0954 |  | 84185.094 | 2405.2884 | 87025.6608 | 8234.6418 | 0 | 181850.685 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 101022.1128 | 9621.1536 | 23429.9856 | 82346.418 | 0 | 216419.67 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704 |  | 122669.7084 | 19242.3072 | 6694.2816 | 16469.2836 | 0 | 165075.5808
|  |  | 45 | 45 | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 8 | 0 | -1 | -7 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 10 | 0 | 0 | -3 | -7 | 0 | 18 | 4 | 13 | 3 | 7 | 45 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 312700 | 312700 | 312700 | 312700 | 312700 | C4 | 4008.814 | 4008.814 | 5578.568 | 13724.403 | 28755.892 | C4 | 36079.326 | 12026.442 | 184092.744 | 0 | 0 | 232198.512 |  | 88193.908 | 12026.442 | 111571.36 | 0 | 0 | 211791.71 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 120264.42 | 0 | 83678.52 | 0 | 0 | 203942.94 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745 |  | 112246.792 | 16035.256 | 72521.384 | 0 | 0 | 200803.432
|  |  | 707 | 707 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 65 | 0 | -1 | -53 | -11 |  | 415 | 106 | 59 | 116 | 11 |  | 132 | 0 | 0 | -13 | -119 |  | 323 | 186 | 42 | 24 | 132 | [22 empty] | 629063.0929 | 79534.8698 | 564327.9389 | 42271.1612 | 31056.3634 | 1346253.4261 |  | 733773.3146 | 79534.8698 | 459450.8605 | 31291.6388 | 19554.0066 | 1323604.6902 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 788934.5952 | 134696.1504 | 187439.8848 | 332130.5526 | 0 | 1443201.183 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326 |  | 766164.5317 | 258007.269 | 134778.2029 | 65877.1344 | 108122.1539 | 1332949.2919
| EHV Transformer |  | 103 | 103 | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 9 | 0 | 0 | 0 | -9 | 0 | 44 | 6 | 13 | 10 | 30 | 103 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | C1 | 2639.1188 | 2639.1188 | 3672.5335 | 9035.1735 | 18930.8396 | C1 | 89730.0389 | 18473.8315 | 143228.8057 | 135527.6018 | 151446.717 | 538406.9949 |  | 121399.4643 | 13195.594 | 117521.0714 | 108422.0815 | 151446.717 | 511984.9281 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979 |  | 139873.2959 | 15834.7127 | 47742.9352 | 90351.7345 | 397547.632 | 691350.3104
|  |  | 113 | 113 | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 18 | 0 | 0 | 0 | -18 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 28 | 0 | 0 | 0 | -28 | 0 | 32 | 12 | 11 | 18 | 40 | 113 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 294085 | 294085 | 294085 | 294085 | 294085 | C2 | 3770.1697 | 3770.1697 | 5246.4764 | 12907.3906 | 27044.0566 | C2 | 143266.4486 | 18850.8485 | 152147.8156 | 361406.9382 | 324528.6792 | 1000200.7301 |  | 158347.1274 | 18850.8485 | 152147.8156 | 361406.9382 | 243396.5094 | 934149.2391 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 196048.8244 | 49012.2061 | 110176.0044 | 141981.2971 | 432704.9056 | 929923.2377 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029 |  | 226210.182 | 45242.0364 | 57711.2404 | 232333.0317 | 324528.6792 | 886025.1697
|  |  | 62 | 62 | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 7 | 0 | 0 | -1 | -6 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 13 | 0 | 0 | 0 | -13 | 0 | 17 | 6 | 15 | 8 | 16 | 62 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | C3 | 5655.2545 | 5655.2545 | 7869.7146 | 19361.086 | 40566.0849 | C3 | 96139.3273 | 5655.2545 | 220352.0088 | 232333.0317 | 121698.2547 | 676177.8771 |  | 124415.6001 | 5655.2545 | 220352.0088 | 212971.9457 | 0 | 563394.8092 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 141381.3637 | 28276.2727 | 157394.292 | 154888.6878 | 162264.3396 | 644204.9559 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198 |  | 169657.6365 | 33931.5273 | 118045.719 | 154888.6878 | 121698.2547 | 598221.8253
|  |  | 8 | 8 | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | C4 | 9425.4243 | 9425.4243 | 13116.191 | 32268.4766 | 67610.1415 | C4 | 56552.5455 | 0 | 0 | 64536.9532 | 135220.283 | 256309.7817 |  | 75403.394 | 0 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394
|  |  | 286 | 286 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 25 | 0 | 0 | -1 | -24 |  | 104 | 25 | 60 | 39 | 58 |  | 50 | 0 | 0 | 0 | -50 |  | 97 | 28 | 39 | 36 | 86 | [22 empty] | 385688.3603 | 42979.9346 | 515728.6301 | 793804.525 | 732893.9339 | 2471095.3838 |  | 479565.5858 | 37701.697 | 490020.8958 | 682800.9654 | 394843.2264 | 2084932.3703 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 515382.198 | 109334.9213 | 337348.4325 | 468538.2806 | 860000.9999 | 2290604.8323 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146 |  | 573442.8114 | 132709.9734 | 223499.8946 | 477573.454 | 843774.5659 | 2251000.6994
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C1 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | C1 | 757.237 | 757.237 | 25660.7739 | 62636.827 | 131244.019 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 4.244 | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | -2.16 | -2.16 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | -4.32 | -4.32 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564 |  |  | C2 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C2 | 8232 | 8232 | 8232 | 8232 | 8232 | C2 | 1081.7671 | 1081.7671 | 36658.2485 | 89481.1814 | 187491.4558 | C2 | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 672906.8347 | 776099.8042 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 267925.2903 | 481623.8355
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C3 | 12348 | 12348 | 12348 | 12348 | 12348 | C3 | 1622.6507 | 1622.6507 | 54987.3727 | 134221.7722 | 281237.1836 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C4 | 20580 | 20580 | 20580 | 20580 | 20580 | C4 | 2704.4178 | 2704.4178 | 91645.6212 | 223702.9536 | 468728.6394 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 4.244 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | -2.16 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | -4.32 |  | 0 | 0 | 0.723 | 2.092 | 5.749 | [22 empty] | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 672906.8347 | 776099.8042 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 267925.2903 | 481623.8355
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | C1 | 190.2375 | 190.2375 | 6447.0548 | 15737.162 | 32974.1524 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 75074 | 75074 | 75074 | 75074 | 75074 | C2 | 271.7679 | 271.7679 | 9210.0783 | 22481.66 | 47105.932 | C2 | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 112611 | 112611 | 112611 | 112611 | 112611 | C3 | 407.6518 | 407.6518 | 13815.1175 | 33722.4901 | 70658.8981 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 187685 | 187685 | 187685 | 187685 | 187685 | C4 | 679.4197 | 679.4197 | 23025.1958 | 56204.1501 | 117764.8301 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0 | [22 empty] | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
| EHV UG Cable (Non Pressurised) |  | 123.955 | 123.955 | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 208.376 | 208.376 | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 53241 | 53241 | 53241 | 53241 | 53241 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 71.937 | 71.937 | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.622 | 3.622 | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 407.89 | 407.89 |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 188 | 188 | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | C1 | 106.093 | 106.093 | 106.093 | 5372.7104 | 18408.139 | C1 | 2652.3254 | 9336.1853 | 5941.2088 | 69845.2355 | 110448.8339 | 198223.7889 |  | 3288.8835 | 9336.1853 | 5941.2088 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349
|  |  | 66 | 66 | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 285965 | 285965 | 285965 | 285965 | 285965 | C2 | 151.5615 | 151.5615 | 151.5615 | 7675.3006 | 26297.3414 | C2 | 1212.4916 | 4546.8435 | 3182.7904 | 38376.503 | 52594.6828 | 99913.3114 |  | 1515.6145 | 5153.0893 | 3182.7904 | 7675.3006 | 0 | 17526.7949 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | C3 | 227.3422 | 227.3422 | 227.3422 | 11512.9509 | 39446.0121 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | C4 | 378.9036 | 378.9036 | 378.9036 | 19188.2515 | 65743.3535 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0 | [22 empty] | 3864.817 | 13883.0288 | 9123.9993 | 108221.7385 | 163043.5167 | 298137.1002 |  | 4804.498 | 14489.2746 | 9123.9993 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4698.405 | 10745.7068 | 12079.4476 | 122804.8096 | 0 | 150328.3689 |  | 4698.405 |  | 12079.4476 |  | 0 | 16777.8525
| EHV OHL Support - Poles |  | 2475 | 2475 | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 223 | 0 | 0 | -79 | -144 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 451 | 0 | 0 | -159 | -292 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | C1 | 114.0865 | 114.0865 | 158.7599 | 390.5815 | 818.3612 | C1 | 13690.3754 | 134964.2845 | 31116.949 | 176542.8375 | 428821.2877 | 785135.7342 |  | 25897.6269 | 134964.2845 | 30323.1493 | 170684.1151 | 357623.8601 | 719493.0359 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 40614.7805 | 134964.2845 | 30323.1493 | 150373.8771 | 294610.045 | 650886.1364 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372 |  | 55674.1935 | 134964.2845 | 30323.1493 | 129673.0577 | 229959.5073 | 580594.1923
|  |  | 17510 | 17510 | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 1577 | 0 | 0 | -555 | -1022 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 3191 | 0 | 0 | -1123 | -2068 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12713 | 12713 | 12713 | 12713 | 12713 | C2 | 162.9807 | 162.9807 | 226.7999 | 557.9736 | 1169.0875 | C2 | 138859.5223 | 1364474.0855 | 315025.0889 | 1787189.3447 | 4325623.676 | 7931171.7174 |  | 261257.998 | 1364474.0855 | 306406.6919 | 1723580.3577 | 3618325.7506 | 7274044.8838 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 410385.3019 | 1364474.0855 | 306406.6919 | 1519920.0047 | 2976496.7241 | 6577682.8081 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879 |  | 562935.1996 | 1364311.1049 | 306406.6919 | 1311237.8895 | 2319469.5603 | 5864360.4462
|  |  | 264 | 264 | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 24 | 0 | 0 | -8 | -16 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 48 | 0 | 0 | -17 | -31 | 0 | 4 | 127 | 20 | 52 | 61 | 264 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | C3 | 244.471 | 244.471 | 340.1999 | 836.9604 | 1753.6312 | C3 | 2933.6519 | 30803.3447 | 7144.1975 | 40174.097 | 98203.3483 | 179258.6395 |  | 5867.3038 | 30803.3447 | 6803.9976 | 39337.1367 | 82420.6673 | 165232.4501 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 9289.8976 | 31047.8157 | 6803.9976 | 34315.3746 | 66637.9864 | 148095.0719 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402 |  | 12712.4915 | 31047.8157 | 6803.9976 | 29293.6124 | 52608.9366 | 132466.8538
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | C4 | 407.4516 | 407.4516 | 566.9998 | 1394.9339 | 2922.7187 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20249 | 20249 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 1824 | 0 | 0 | -642 | -1182 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 3690 | 0 | 0 | -1299 | -2391 |  | 304 | 9681 | 1562 | 4016 | 4686 | [22 empty] | 155483.5496 | 1530241.7148 | 353286.2354 | 2003906.2793 | 4852648.312 | 8895566.0911 |  | 293022.9286 | 1530241.7148 | 343533.8388 | 1933601.6095 | 4058370.2781 | 8158770.3698 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 460289.98 | 1530486.1858 | 343533.8388 | 1704609.2564 | 3337744.7554 | 7376664.0163 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653 |  | 631321.8846 | 1530323.2051 | 343533.8388 | 1470204.5596 | 2602038.0042 | 6577421.4924
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 164 | 164 | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 41 | 0 | 0 | 0 | -41 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 55 | 0 | 0 | 0 | -55 | 0 | 0 | 29 | 0 | 73 | 62 | 164 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | C1 | 273.0697 | 273.0697 | 380.4935 | 935.6531 | 1960.6893 | C1 | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 11195.8559 | 7919.0201 | 15219.7382 | 39297.4297 | 23528.2721 | 97160.316 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346 |  | 15018.8311 | 7919.0201 | 0 | 68302.6755 | 13724.8254 | 104965.3521
|  |  | 280 | 280 | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 59 | 0 | 0 | -51 | -8 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 117 | 0 | 0 | -97 | -20 | 0 | 0 | 0 | 6 | 254 | 20 | 280 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117147 | 117147 | 117147 | 117147 | 117147 | C2 | 390.0995 | 390.0995 | 543.5621 | 1336.6473 | 2800.9848 | C2 | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 23015.8711 | 0 | 101646.109 | 45446.0072 | 0 | 170107.9872 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745 |  | 45641.6427 | 0 | 3261.3725 | 209853.6214 | 0 | 258756.6365
|  |  | 153 | 153 | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 35 | 0 | 0 | 0 | -35 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 57 | 0 | 0 | -22 | -35 | 0 | 0 | 0 | 15 | 103 | 35 | 153 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | C3 | 585.1493 | 585.1493 | 815.3431 | 2004.9709 | 4201.4772 | C3 | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 20480.2243 | 0 | 96210.4882 | 0 | 0 | 116690.7124 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504 |  | 33353.5081 | 0 | 12230.1468 | 162402.6433 | 0 | 207986.2982
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | C4 | 975.2488 | 975.2488 | 1358.9052 | 3341.6182 | 7002.4619 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 135 | 0 | 0 | -51 | -84 |  | 0 | 29 | 345 | 127 | 96 |  | 229 | 0 | 0 | -119 | -110 |  | 0 | 29 | 21 | 430 | 117 | [22 empty] | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 54691.9513 | 7919.0201 | 213076.3354 | 84743.4369 | 23528.2721 | 383959.0157 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595 |  | 94013.9819 | 7919.0201 | 15491.5193 | 440558.9402 | 13724.8254 | 571708.2868
| EHV OHL Conductor (Tower Lines) |  | 23.103 | 23.103 | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | C1 | 6.1139 | 6.1139 | 8.4066 | 21.3987 | 44.3259 | C1 | 44.3992 | 0 | 42.2433 | 0 | 479.4285 | 566.0711 |  | 110.5273 | 0 | 42.2433 | 0 | 0 | 152.7706 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585
|  |  | 31.689 | 31.689 | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 109177 | 109177 | 109177 | 109177 | 109177 | C2 | 8.7342 | 8.7342 | 12.0095 | 30.5696 | 63.3227 | C2 | 0 | 0 | 366.3489 | 0 | 74.974 | 441.3229 |  | 10.3412 | 0 | 366.3489 | 0 | 0 | 376.6901 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558
|  |  | 8.297 | 8.297 | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | C3 | 13.1012 | 13.1012 | 18.0142 | 45.8543 | 94.984 | C3 | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346
|  |  | 5.911 | 5.911 | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | C4 | 21.8354 | 21.8354 | 30.0237 | 76.4239 | 158.3067 | C4 | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417
|  |  | 69 | 69 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0 | [22 empty] | 44.3992 | 0 | 735.526 | 0 | 554.4026 | 1334.3278 |  | 120.8685 | 0 | 735.526 | 0 | 0 | 856.3945 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 |  | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 |  | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 |  | 1824522.1193 | 1794338.8664 | 1200173.0425 | 2668900.0877 | 4894180.8621 | 12382114.978 |  | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 |  | 2070060.2396 | 1929100.888 | 759598.3376 | 2642835.8933 | 3835584.8397 | 11237180.1983
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 93 | 93 | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 1 | 0 | 0 | -1 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 60 | 16 | 2 | 3 | 93 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | C1 | 2362.7016 | 2362.7016 | 3287.8781 | 8088.8436 | 16948.0533 | C1 | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 80331.8558 | 103958.8722 | 42742.4154 | 16177.6872 | 0 | 243210.8306 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149 |  | 30715.1213 | 141762.0985 | 52606.0497 | 16177.6872 | 33896.1066 | 275157.0633
|  |  | 75 | 75 | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 2 | 0 | 0 | -2 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 3 | 0 | 0 | 0 | -3 | 0 | 23 | 37 | 12 | 0 | 3 | 75 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 263283 | 263283 | 263283 | 263283 | 263283 | C2 | 3375.2881 | 3375.2881 | 4696.9687 | 11555.4909 | 24211.5047 | C2 | 148512.6746 | 81006.9134 | 37575.7498 | 11555.4909 | 0 | 278650.8287 |  | 148512.6746 | 81006.9134 | 32878.781 | 0 | 0 | 262398.3691 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 111384.506 | 118135.0821 | 28181.8123 | 11555.4909 | 0 | 269256.8913 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223 |  | 87757.4896 | 124885.6582 | 56363.6246 | 0 | 0 | 269006.7724
|  |  | 52 | 52 | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 2 | 0 | 0 | 0 | -2 | 0 | 11 | 31 | 6 | 0 | 4 | 52 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | C3 | 5062.9321 | 5062.9321 | 7045.4531 | 17333.2363 | 36317.257 | C3 | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943 |  | 65818.1172 | 156950.8948 | 42272.7185 | 0 | 72634.514 | 337676.2445
|  |  | 9 | 9 | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | C4 | 8438.2201 | 8438.2201 | 11742.4218 | 28888.7272 | 60528.7617 | C4 | 25314.6604 | 42191.1007 | 11742.4218 | 0 | 0 | 79248.183 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813
|  |  | 229 | 229 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 3 | 0 | 0 | -3 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 6 | 0 | 0 | 0 | -6 |  | 50 | 133 | 34 | 2 | 10 | [22 empty] | 365881.2257 | 379719.9067 | 90181.7994 | 28888.7272 | 0 | 864671.6591 |  | 374319.4459 | 379719.9067 | 73742.4089 | 17333.2363 | 0 | 845114.9978 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 301413.2238 | 426298.882 | 99106.04 | 27733.1781 | 36317.257 | 890868.5808 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129 |  | 218043.6087 | 465789.7523 | 151242.3928 | 16177.6872 | 106530.6206 | 957784.0615
| 132kV Transformer |  | 54 | 54 | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 4 | 0 | 0 | 0 | -4 | 0 | 15 | 27 | 5 | 0 | 7 | 54 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | C1 | 11467.5067 | 11467.5067 | 15957.9032 | 39259.6621 | 82258.3395 | C1 | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728 |  | 217882.6267 | 309622.68 | 79789.516 | 0 | 246775.0186 | 854069.8412
|  |  | 56 | 56 | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 4 | 0 | 0 | 0 | -4 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 8 | 0 | 0 | 0 | -8 | 0 | 21 | 12 | 15 | 0 | 8 | 56 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 1277859 | 1277859 | 1277859 | 1277859 | 1277859 | C2 | 16382.1524 | 16382.1524 | 22797.0046 | 56085.2315 | 117511.9136 | C2 | 393171.6571 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1564265.5377 |  | 409553.8095 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1580647.69 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 425935.9619 | 294878.7428 | 182376.0365 | 0 | 470047.6546 | 1373238.3958 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061 |  | 475082.419 | 196585.8286 | 341955.0684 | 0 | 0 | 1013623.316
|  |  | 11 | 11 | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 3 | 0 | 0 | 0 | -3 | 0 | 2 | 3 | 2 | 1 | 3 | 11 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | C3 | 24573.2286 | 24573.2286 | 34195.5068 | 84127.8473 | 176267.8705 | C3 | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 172012.6 | 24573.2286 | 102586.5205 | 0 | 0 | 299172.3491 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152 |  | 122866.1429 | 73719.6857 | 68391.0137 | 84127.8473 | 0 | 349104.6895
|  |  | 10 | 10 | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 2 | 0 | 0 | 0 | -2 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 3 | 0 | 0 | 0 | -3 | 0 | 4 | 1 | 2 | 0 | 3 | 10 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | C4 | 40955.3809 | 40955.3809 | 56992.5114 | 140213.0788 | 293779.7841 | C4 | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 245732.2857 | 81910.7619 | 56992.5114 | 140213.0788 | 0 | 524848.6378 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799 |  | 286687.6666 | 40955.3809 | 113985.0228 | 0 | 0 | 441628.0704
|  |  | 131 | 131 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 9 | 0 | 0 | 0 | -9 |  | 52 | 41 | 17 | 2 | 19 |  | 18 | 0 | 0 | 0 | -18 |  | 42 | 43 | 24 | 1 | 21 | [22 empty] | 1012417.0171 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3955144.8381 |  | 1028799.1695 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3971526.9905 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 1095965.9942 | 630712.8666 | 421744.5844 | 179472.7408 | 963597.6918 | 3291493.8779 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739 |  | 1102518.8552 | 620883.5752 | 604120.6208 | 84127.8473 | 246775.0186 | 2658425.9171
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 15.74 | 15.74 | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | C1 | 216.5404 | 216.5404 | 7338.4477 | 17913.0384 | 37533.2768 | C1 | 2083.9852 | 1278.8878 | 1541.074 | 6663.6503 | 0 | 11567.5973 |  | 2083.9852 | 1278.8878 | 1541.074 | 0 | 0 | 4903.947 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901
|  |  | 24.539 | 24.539 | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 85454 | 85454 | 85454 | 85454 | 85454 | C2 | 309.3435 | 309.3435 | 10483.4967 | 25590.0548 | 53618.9668 | C2 | 2161.6922 | 4234.2936 | 40508.2313 | 24566.4526 | 0 | 71470.6698 |  | 2161.3829 | 4234.2936 | 40508.2313 | 0 | 0 | 46903.9078 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219
|  |  | 14.188 | 14.188 | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 128181 | 128181 | 128181 | 128181 | 128181 | C3 | 464.0152 | 464.0152 | 15725.2451 | 38385.0823 | 80428.4503 | C3 | 4729.7071 | 1834.7162 | 644.735 | 37502.2254 | 0 | 44711.3837 |  | 4729.7071 | 1834.7162 | 644.735 | 0 | 0 | 7209.1584 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074
|  |  | 0.708 | 0.708 | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 213635 | 213635 | 213635 | 213635 | 213635 | C4 | 773.3587 | 773.3587 | 26208.7418 | 63975.1371 | 134047.4171 | C4 | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538
|  |  | 55.175 | 55.175 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0 | [22 empty] | 8975.3845 | 7895.4355 | 42694.0404 | 68732.3283 | 0 | 128297.1887 |  | 8975.0752 | 7895.4355 | 42694.0404 | 0 | 0 | 59564.5511 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573
| 132kV UG Cable (Non Pressurised) |  | 8.145 | 8.145 | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25.492 | 25.492 | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 452934 | 452934 | 452934 | 452934 | 452934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5.672 | 5.672 | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 679401 | 679401 | 679401 | 679401 | 679401 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1132335 | 1132335 | 1132335 | 1132335 | 1132335 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 39.309 | 39.309 |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 704 | 704 | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 5 | 0 | 0 | 0 | -5 | 0 | 66 | 368 | 233 | 32 | 5 | 704 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | C1 | 342.7699 | 342.7699 | 342.7699 | 17358.3835 | 59473.8058 | C1 | 23993.8908 | 137107.9472 | 66154.5845 | 711693.7237 | 0 | 938950.1461 |  | 25364.9702 | 137107.9472 | 66154.5845 | 642260.1896 | 0 | 870887.6916 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 22622.8113 | 126139.3114 | 79865.3792 | 555468.2721 | 297369.0289 | 1081464.803 |  | 24336.6606 | 126139.3114 | 79865.3792 | 555468.2721 | 0 | 785809.6234
|  |  | 1006 | 1006 | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 10 | 0 | 0 | 0 | -10 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 23 | 0 | 0 | 0 | -23 | 0 | 164 | 470 | 247 | 102 | 23 | 1006 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 923908 | 923908 | 923908 | 923908 | 923908 | C2 | 489.6712 | 489.6712 | 489.6712 | 24797.6907 | 84962.5797 | C2 | 75899.0422 | 239449.2364 | 112624.3852 | 3273295.175 | 0 | 3701267.8388 |  | 80795.7546 | 239449.2364 | 112624.3852 | 3025318.2678 | 0 | 3458187.644 |  | 80795.7546 | 235042.1952 | 115562.4126 | 2777341.3606 | 1104513.5358 | 4313255.2589 |  | 85692.467 | 235042.1952 | 115562.4126 | 2777341.3606 | 254887.739 | 3468526.1745 |  | 80306.0834 | 230145.4828 | 120948.7963 | 2529364.4534 | 1954139.3326 | 4914904.1485 |  | 91568.5219 | 230145.4828 | 120948.7963 | 2529364.4534 | 0 | 2972027.2544
|  |  | 668 | 668 | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 5 | 0 | 0 | 0 | -5 | 0 | 57 | 350 | 168 | 88 | 5 | 668 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1385862 | 1385862 | 1385862 | 1385862 | 1385862 | C3 | 734.5069 | 734.5069 | 734.5069 | 37196.5361 | 127443.8695 | C3 | 35990.8361 | 260015.4284 | 123397.1525 | 3608063.9998 | 0 | 4027467.4168 |  | 43335.9047 | 260015.4284 | 123397.1525 | 3236098.639 | 0 | 3662847.1246 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 257077.401 | 123397.1525 | 3273295.175 | 637219.3476 | 4332855.9671 |  | 45539.4253 | 257077.401 | 123397.1525 | 3273295.175 | 0 | 3699309.1538
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 2309770 | 2309770 | 2309770 | 2309770 | 2309770 | C4 | 1224.1781 | 1224.1781 | 1224.1781 | 61994.2268 | 212406.4492 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2378 | 2378 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 10 | 0 | 0 | 0 | -10 |  | 294 | 1198 | 636 | 235 | 15 |  | 33 | 0 | 0 | 0 | -33 |  | 287 | 1188 | 648 | 222 | 33 | [22 empty] | 135883.7691 | 636572.612 | 302176.1222 | 7593052.8985 | 0 | 8667685.4018 |  | 149496.6296 | 636572.612 | 302176.1222 | 6903677.0964 | 0 | 7991922.4602 |  | 147342.0761 | 619825.8556 | 318873.9115 | 6638341.8057 | 1291431.2111 | 9015814.8601 |  | 152238.7885 | 619825.8556 | 318873.9115 | 6638341.8057 | 441805.4143 | 8171085.7757 |  | 144795.7857 | 613362.1952 | 324211.328 | 6358127.9006 | 2888727.7091 | 10329224.9186 |  | 161444.6078 | 613362.1952 | 324211.328 | 6358127.9006 | 0 | 7457146.0317
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1291 | 1291 | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 75 | 0 | 0 | -72 | -3 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 135 | 0 | 0 | 0 | -135 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | C1 | 25.0391 | 25.0391 | 34.4288 | 81.3771 | 172.1439 | C1 | 0 | 450.704 | 43276.9752 | 162.7542 | 2410.0145 | 46300.448 |  | 300.4693 | 450.704 | 43276.9752 | 162.7542 | 344.2878 | 44535.1906 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 2178.4027 | 350.5476 | 38904.5203 | 4801.2497 | 172.1439 | 46406.8642 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985 |  | 3680.7495 | 0 | 723.0044 | 91386.499 | 0 | 95790.2528
|  |  | 2037 | 2037 | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 150 | 0 | 0 | -150 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 333 | 0 | 0 | 0 | -333 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 447127 | 447127 | 447127 | 447127 | 447127 | C2 | 35.7702 | 35.7702 | 49.184 | 116.253 | 245.9199 | C2 | 214.621 | 321.9314 | 95859.5575 | 0 | 17214.3895 | 113610.4994 |  | 2825.8426 | 321.9314 | 95859.5575 | 0 | 0 | 99007.3316 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 8191.3666 | 143.0806 | 79727.2154 | 21274.3027 | 0 | 109335.9653 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197 |  | 14737.3059 | 0 | 491.8397 | 187748.6273 | 0 | 202977.7729
|  |  | 1379 | 1379 | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 99 | 0 | 0 | -84 | -15 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 223 | 0 | 0 | 0 | -223 | 0 | 201 | 20 | 60 | 875 | 223 | 1379 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | C3 | 53.6552 | 53.6552 | 73.776 | 174.3795 | 368.8798 | C3 | 6867.8707 | 3809.522 | 78202.5123 | 8195.8379 | 25821.5842 | 122897.3272 |  | 10784.7032 | 3809.522 | 78202.5123 | 8195.8379 | 0 | 100992.5755 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 16096.572 | 1502.3467 | 68390.3103 | 15694.1577 | 12541.9124 | 114225.2991 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439 |  | 22749.8218 | 1073.1048 | 4426.5573 | 152582.0887 | 0 | 180831.5726
|  |  | 13 | 13 | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | C4 | 89.4254 | 89.4254 | 122.9599 | 290.6325 | 614.7996 | C4 | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231
|  |  | 4720 | 4720 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 324 | 0 | 0 | -306 | -18 |  | 292 | 46 | 3691 | 638 | 53 |  | 691 | 0 | 0 | 0 | -691 |  | 292 | 20 | 91 | 3626 | 691 | [22 empty] | 7082.4917 | 4582.1575 | 218937.5241 | 8358.5921 | 45445.9883 | 284406.7537 |  | 13911.0152 | 4582.1575 | 218937.5241 | 8358.5921 | 344.2878 | 246133.5767 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 26466.3414 | 1995.9749 | 188620.5249 | 41769.7101 | 12714.0562 | 271566.6076 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853 |  | 41167.8771 | 1073.1048 | 5641.4014 | 435495.4382 | 0 | 483377.8215
| 132kV OHL Conductor (Tower Lines) |  | 293.476 | 293.476 | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 13.845 | 0 | 0 | -13.845 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 22.579 | 0 | 0 | -8.707 | -13.872 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | C1 | 25.4967 | 25.4967 | 35.058 | 89.2386 | 184.8514 | C1 | 1678.2977 | 2783.8875 | 4083.0677 | 0 | 369.5179 | 8914.7708 |  | 1741.7336 | 2783.8875 | 4065.9594 | 0 | 0 | 8591.5805 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 1454.5637 | 3418.0425 | 3587.9082 | 2.4094 | 0 | 8462.9239 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739 |  | 1303.3681 | 3641.3685 | 2340.4386 | 2925.3307 | 0 | 10210.5058
|  |  | 461.16 | 461.159 | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 7.916 | 0 | 0 | -7.916 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 35.264 | 0 | 0 | -8.813 | -26.452 | -0.001 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 455299 | 455299 | 455299 | 455299 | 455299 | C2 | 36.4239 | 36.4239 | 50.0829 | 127.4837 | 264.0734 | C2 | 1764.1926 | 5199.3689 | 13484.3674 | 94.083 | 0 | 20542.0118 |  | 1979.7493 | 5199.3689 | 13224.938 | 0 | 0 | 20404.0562 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1798.686 | 5120.6204 | 13581.3779 | 2.0397 | 0 | 20502.7241 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628 |  | 2325.3759 | 4885.2854 | 10975.6153 | 5615.0204 | 0 | 23801.297
|  |  | 331.02 | 331.02 | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 24.14 | 0 | 0 | -24.14 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 42.756 | 0 | 0 | -1.652 | -41.104 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | C3 | 54.6359 | 54.6359 | 75.1243 | 191.2256 | 396.1101 | C3 | 3961.9208 | 7489.7596 | 7995.7083 | 2489.1834 | 780.7331 | 22717.3052 |  | 5578.8151 | 7489.7596 | 6898.3672 | 0 | 0 | 19966.9419 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 5392.2882 | 7624.9834 | 6197.9079 | 1962.5481 | 0 | 21177.7276 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424 |  | 5093.6485 | 5352.7318 | 8828.5367 | 4264.5217 | 0 | 23539.4386
|  |  | 3.344 | 3.344 | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | C4 | 91.0598 | 91.0598 | 125.2072 | 318.7093 | 660.1836 | C4 | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693
|  |  | 1089 | 1088.999 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 45.901 | 0 | 0 | -45.901 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 100.599 | 0 | 0 | -19.172 | -81.428 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428 | [22 empty] | 7404.4111 | 15473.016 | 25981.8364 | 2583.2664 | 1150.251 | 52592.7808 |  | 9300.298 | 15473.016 | 24607.9576 | 0 | 0 | 49381.2715 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 8645.5379 | 16163.6463 | 23785.887 | 1966.9973 | 0 | 50562.0685 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373 |  | 8722.3924 | 13879.3857 | 22563.2835 | 12804.8728 | 0 | 57969.9344
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 |  | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 |  | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 |  | 1593580.6049 | 1702755.6527 | 1103682.4945 | 6889284.4321 | 1454434.4194 | 12743737.6037 |  | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 |  | 1539947.0154 | 1721846.5912 | 1216973.0316 | 6906733.7461 | 353305.6392 | 11738806.0236
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 332299.578 | 332215.257 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 26201.901 | -87 | -73 | -10544.901 | -15539.16 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 53125.599 | -177 | -125 | -20576.172 | -32331.748 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 |  | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 |  | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 |  | 9724373.5839 | 20997113.3685 | 5276892.3921 | 14106936.9565 | 13320105.5711 | 63425421.8721 |  | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 |  | 10718638.4489 | 21469427.7011 | 4869663.3299 | 12519874.2506 | 6781859.0967 | 56359462.8272
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 | LV Network | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 1341760.5214 | 4818108.826 | 1067073.7318 | 1337198.4212 | 1511367.092 | 10075508.5923 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 | LV Network | 1615421.6182 | 4852088.7001 | 1011106.6983 | 807342.9963 | 703309.1331 | 8989269.1461
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 | HV Network | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 4964510.3383 | 12681910.0234 | 1905963.1233 | 3211554.0156 | 5460123.1976 | 28224060.6982 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 | HV Network | 5493209.5757 | 12966391.5218 | 1881985.2624 | 2162961.6148 | 1889659.4846 | 24394207.4593
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 | EHV Network | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 | EHV Network | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 | EHV Network | 1824522.1193 | 1794338.8664 | 1200173.0425 | 2668900.0877 | 4894180.8621 | 12382114.978 | EHV Network | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 | EHV Network | 2070060.2396 | 1929100.888 | 759598.3376 | 2642835.8933 | 3835584.8397 | 11237180.1983
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 | 132kV Network | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 | 132kV Network | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 | 132kV Network | 1593580.6049 | 1702755.6527 | 1103682.4945 | 6889284.4321 | 1454434.4194 | 12743737.6037 | 132kV Network | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 | 132kV Network | 1539947.0154 | 1721846.5912 | 1216973.0316 | 6906733.7461 | 353305.6392 | 11738806.0236
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 | Total | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 | Total | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 | Total | 9724373.5839 | 20997113.3685 | 5276892.3921 | 14106936.9565 | 13320105.5711 | 63425421.8721 | Total | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 | Total | 10718638.4489 | 21469427.7011 | 4869663.3299 | 12519874.2506 | 6781859.0967 | 56359462.8272
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWALES - Refurb
Secondary deliverables RIIO-ED1 - Refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWALES | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | C1 | 42.3124 | 42.3124 | 58.8809 | 144.8589 | 303.514 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 0 | 0 | 0 | 0 | 0 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4715 | 4715 | 4715 | 4715 | 4715 | C2 | 60.4463 | 60.4463 | 84.1156 | 206.9413 | 433.5914 | C2 | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | C3 | 90.6694 | 90.6694 | 126.1734 | 310.412 | 650.3871 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | C4 | 151.1157 | 151.1157 | 210.289 | 517.3534 | 1083.9785 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163 | [22 empty] | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389
| LV Switchgear (at s/s) |  | 278 | 278 | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | C1 | 82.0156 | 82.0156 | 114.0623 | 280.6537 | 588.0628 | C1 | 22308.2388 | 0 | 0 | 0 | 0 | 22308.2388 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324
|  |  | 7511 | 7511 | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 0 | 0 | 0 | 0 | 0 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 0 | 0 | 0 | 0 | 0 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 6096 | 6096 | 6096 | 6096 | 6096 | C2 | 117.1651 | 117.1651 | 162.9461 | 400.9339 | 840.0898 | C2 | 411483.9014 | 131107.7693 | 359459.0525 | 119478.3082 | 224303.9659 | 1245832.9973 |  | 445930.4467 | 130404.7786 | 356200.1309 | 111860.5637 | 106691.3995 | 1151087.3194 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677
|  |  | 76 | 76 | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 22 | 9 | 6 | 76 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 9144 | 9144 | 9144 | 9144 | 9144 | C3 | 175.7477 | 175.7477 | 244.4191 | 601.4009 | 1260.1346 | C3 | 4569.4397 | 2284.7198 | 6599.3162 | 3007.0044 | 6300.6732 | 22761.1534 |  | 5975.4211 | 2284.7198 | 5866.0589 | 3007.0044 | 0 | 17133.2042 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 15240 | 15240 | 15240 | 15240 | 15240 | C4 | 292.9128 | 292.9128 | 407.3652 | 1002.3348 | 2100.2244 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7865 | 7865 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619 | [22 empty] | 438361.58 | 133392.4891 | 366058.3687 | 122485.3126 | 230604.6391 | 1290902.3895 |  | 474706.2002 | 132689.4984 | 362066.1898 | 114867.5681 | 106691.3995 | 1191020.856 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096
| LV UGB and LV Pillar OD (not at s/s) |  | 103 | 103 | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | C1 | 70.2164 | 70.2164 | 97.6527 | 240.2775 | 503.4613 | C1 | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919
|  |  | 3635 | 3635 | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5219 | 5219 | 5219 | 5219 | 5219 | C2 | 100.3092 | 100.3092 | 139.5039 | 343.2536 | 719.2304 | C2 | 45339.7494 | 52060.4644 | 303560.4211 | 95767.7628 | 146003.7692 | 642732.1668 |  | 51157.6818 | 52060.4644 | 303281.4134 | 95767.7628 | 110042.2497 | 612309.572 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192
|  |  | 581 | 581 | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 544 | 6 | 6 | 581 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | C3 | 150.4638 | 150.4638 | 209.2558 | 514.8804 | 1078.8456 | C3 | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | C4 | 250.773 | 250.773 | 348.7597 | 858.1341 | 1798.076 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4319 | 4319 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624 | [22 empty] | 56333.6355 | 52511.8557 | 418023.3465 | 96282.6432 | 151397.9971 | 774549.478 |  | 62151.5679 | 52511.8557 | 417744.3387 | 96282.6432 | 115436.4776 | 744126.8832 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 |  | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 631 | 631 | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 260 | 61 | 45 | 48 | 631 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 36715 | 36715 | 36715 | 36715 | 36715 | C1 | 470.6863 | 470.6863 | 654.9956 | 1611.4213 | 3376.3114 | C1 | 184979.7159 | 55540.9834 | 56329.6216 | 35451.2697 | 47268.3596 | 379569.9502 |  | 185921.0885 | 55540.9834 | 56329.6216 | 32228.427 | 40515.7368 | 370535.8573 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046
|  |  | 1416 | 1416 | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 467 | 143 | 119 | 137 | 1416 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 52450 | 52450 | 52450 | 52450 | 52450 | C2 | 672.409 | 672.409 | 935.708 | 2302.0305 | 4823.302 | C2 | 532547.928 | 199705.473 | 212405.716 | 195672.5925 | 159168.966 | 1299500.6755 |  | 537927.2 | 198360.655 | 209598.592 | 165746.196 | 120582.55 | 1232215.193 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005
|  |  | 31 | 31 | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 8 | 8 | 4 | 31 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 78675 | 78675 | 78675 | 78675 | 78675 | C3 | 1008.6135 | 1008.6135 | 1403.562 | 3453.0457 | 7234.953 | C3 | 5043.0675 | 9077.5215 | 19649.868 | 13812.183 | 14469.906 | 62052.546 |  | 7060.2945 | 9077.5215 | 19649.868 | 3453.0457 | 0 | 39240.7297 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225
|  |  | 185 | 185 | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 67 | 20 | 16 | 23 | 185 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 131125 | 131125 | 131125 | 131125 | 131125 | C4 | 1681.0225 | 1681.0225 | 2339.27 | 5755.0763 | 12058.255 | C4 | 154654.07 | 73964.99 | 79535.18 | 80571.0675 | 48233.02 | 436958.3275 |  | 154654.07 | 73964.99 | 79535.18 | 69060.915 | 36174.765 | 413389.92 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32
|  |  | 2263 | 2263 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212 | [22 empty] | 877224.7814 | 338288.9679 | 367920.3856 | 325507.1127 | 269140.2516 | 2178081.4992 |  | 885562.653 | 336944.1499 | 365113.2616 | 270488.5837 | 197273.0518 | 2055381.7001 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476
| HV Switchgear (GM) - Distribution |  | 254 | 254 | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | C1 | 131.855 | 131.855 | 183.4862 | 451.413 | 945.8178 | C1 | 31645.1957 | 1582.2598 | 0 | 0 | 0 | 33227.4555 |  | 31908.9056 | 1582.2598 | 0 | 0 | 0 | 33491.1654 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526
|  |  | 9267 | 9267 | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 0 | 0 | 0 | 0 | 0 | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 0 | 0 | 0 | 0 | 0 | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 14693 | 14693 | 14693 | 14693 | 14693 | C2 | 188.3643 | 188.3643 | 262.1231 | 644.8758 | 1351.1683 | C2 | 1026961.9455 | 378988.8911 | 267365.5824 | 108339.1294 | 708012.1787 | 2489667.7271 |  | 1060114.0553 | 373903.0561 | 264220.105 | 107694.2536 | 647209.6061 | 2453141.076 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162
|  |  | 1084 | 1084 | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 326 | 216 | 50 | 213 | 1084 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | C3 | 282.5464 | 282.5464 | 393.1847 | 967.3137 | 2026.7524 | C3 | 128276.0611 | 68658.7728 | 78636.936 | 33855.9779 | 291852.3485 | 601280.0962 |  | 137600.0919 | 67811.1336 | 77850.5666 | 25150.155 | 269558.0719 | 577970.0191 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405
|  |  | 4 | 4 | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | C4 | 470.9106 | 470.9106 | 655.3078 | 1612.1894 | 3377.9207 | C4 | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128
|  |  | 10609 | 10609 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 0 | 0 | 0 | 0 | 0 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 0 | 0 | 0 | 0 | 0 |  | 3735 | 3843 | 1567 | 332 | 1132 | [22 empty] | 1186883.2023 | 449700.8343 | 347968.4418 | 142195.1073 | 999864.5272 | 3126612.1129 |  | 1229623.0529 | 443767.3601 | 344036.595 | 132844.4086 | 916767.678 | 3067039.0946 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867
| HV Transformer (GM) |  | 1331 | 1331 | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 144 | 535 | 156 | 220 | 1331 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | C1 | 205.6982 | 205.6982 | 286.0725 | 703.8903 | 1474.884 | C1 | 66646.2187 | 32706.0148 | 177078.8645 | 57719.0022 | 197634.451 | 531784.5513 |  | 77753.9219 | 32294.6183 | 175076.3571 | 57719.0022 | 150438.1642 | 493282.0638 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769
|  |  | 5824 | 5824 | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 0 | 0 | 0 | 0 | 0 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 0 | 0 | 0 | 0 | 0 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 15289 | 15289 | 15289 | 15289 | 15289 | C2 | 293.8546 | 293.8546 | 408.675 | 1005.5575 | 2106.9771 | C2 | 877155.9213 | 272697.0502 | 556206.6342 | 192061.4882 | 632093.127 | 2530214.2209 |  | 945624.0384 | 269464.6499 | 550893.8596 | 191055.9307 | 318153.5406 | 2275192.0192 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914
|  |  | 1184 | 1184 | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 291 | 204 | 35 | 47 | 1184 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | C3 | 440.7819 | 440.7819 | 613.0125 | 1508.3363 | 3160.4656 | C3 | 339842.8218 | 82426.2097 | 91951.8682 | 22625.0444 | 158023.2817 | 694869.2259 |  | 359678.0059 | 81544.646 | 91338.8558 | 22625.0444 | 60048.8471 | 615235.3992 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152
|  |  | 2 | 2 | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | C4 | 734.6365 | 734.6365 | 1021.6874 | 2513.8938 | 5267.4427 | C4 | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729
|  |  | 8341 | 8341 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 0 | 0 | 0 | 0 | 0 |  | 3175 | 1722 | 2250 | 511 | 683 | [22 empty] | 1284379.5983 | 388563.9111 | 825237.3669 | 272405.5349 | 987750.8598 | 3758337.271 |  | 1383790.6027 | 384038.5506 | 817309.0725 | 271399.9773 | 528640.5519 | 3385178.755 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4766.226 | 4766.226 | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 30792 | 30792 | 30792 | 30792 | 30792 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 892.414 | 892.414 | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 46188 | 46188 | 46188 | 46188 | 46188 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 76980 | 76980 | 76980 | 76980 | 76980 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5658.64 | 5658.64 |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | C1 | 61.3552 | 61.3552 | 85.3805 | 210.0532 | 440.1114 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 149285 | 149285 | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 0 | 0 | 0 | 0 | 0 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 0 | 0 | 0 | 0 | 0 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6837 | 6837 | 6837 | 6837 | 6837 | C2 | 87.6503 | 87.6503 | 121.9721 | 300.0759 | 628.7305 | C2 | 371812.7423 | 10036577.4824 | 324201.7886 | 3475479.4213 | 10084837.5408 | 24292908.9754 |  | 867738.366 | 10036577.4824 | 291269.327 | 3232117.842 | 7368092.9639 | 21795795.9813 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093
|  |  | 10797 | 10797 | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | C3 | 131.4755 | 131.4755 | 182.9581 | 450.1139 | 943.0958 | C3 | 40231.5061 | 1089011.6493 | 35127.959 | 377195.444 | 1093991.1048 | 2635557.6632 |  | 94004.9896 | 1089011.6493 | 31651.7548 | 350638.7242 | 798802.1257 | 2364109.2436 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929
|  |  | 149 | 149 | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 3 | 14 | 17 | 149 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | C4 | 219.1258 | 219.1258 | 304.9302 | 750.1898 | 1571.8263 | C4 | 876.5034 | 24980.3469 | 914.7906 | 8252.0881 | 26721.0471 | 61744.7761 |  | 2191.2585 | 24980.3469 | 609.8604 | 8252.0881 | 18861.9156 | 54895.4695 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968
|  |  | 160231 | 160231 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820 | [22 empty] | 412920.7517 | 11150569.4786 | 360244.5383 | 3860926.9533 | 11205549.6927 | 26990211.4147 |  | 963934.6142 | 11150569.4786 | 323530.9422 | 3591008.6543 | 8185757.0051 | 24214800.6944 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 |  | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 285 | 285 | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 117 | 7 | 0 | 34 | 285 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 87556 | 87556 | 87556 | 87556 | 87556 | C1 | 1122.4679 | 1122.4679 | 1561.999 | 3842.8328 | 8051.6498 | C1 | 234595.7953 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 350532.1971 |  | 239085.667 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 355022.0688 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576
|  |  | 314 | 314 | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 57 | 20 | 17 | 70 | 314 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 125080 | 125080 | 125080 | 125080 | 125080 | C2 | 1603.5256 | 1603.5256 | 2231.4272 | 5489.7612 | 11502.3568 | C2 | 288634.608 | 22449.3584 | 247688.4192 | 10979.5224 | 23004.7136 | 592756.6216 |  | 322308.6456 | 22449.3584 | 218679.8656 | 0 | 11502.3568 | 574940.2264 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596
|  |  | 63 | 63 | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 187620 | 187620 | 187620 | 187620 | 187620 | C3 | 2405.2884 | 2405.2884 | 3347.1408 | 8234.6418 | 17253.5352 | C3 | 69753.3636 | 2405.2884 | 90372.8016 | 8234.6418 | 0 | 170766.0954 |  | 84185.094 | 2405.2884 | 87025.6608 | 8234.6418 | 0 | 181850.685 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704
|  |  | 45 | 45 | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 312700 | 312700 | 312700 | 312700 | 312700 | C4 | 4008.814 | 4008.814 | 5578.568 | 13724.403 | 28755.892 | C4 | 36079.326 | 12026.442 | 184092.744 | 0 | 0 | 232198.512 |  | 88193.908 | 12026.442 | 111571.36 | 0 | 0 | 211791.71 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745
|  |  | 707 | 707 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 323 | 186 | 42 | 24 | 132 | [22 empty] | 629063.0929 | 79534.8698 | 564327.9389 | 42271.1612 | 31056.3634 | 1346253.4261 |  | 733773.3146 | 79534.8698 | 459450.8605 | 31291.6388 | 19554.0066 | 1323604.6902 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326
| EHV Transformer |  | 103 | 103 | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 6 | 13 | 10 | 30 | 103 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | C1 | 2639.1188 | 2639.1188 | 3672.5335 | 9035.1735 | 18930.8396 | C1 | 89730.0389 | 18473.8315 | 143228.8057 | 135527.6018 | 151446.717 | 538406.9949 |  | 121399.4643 | 13195.594 | 117521.0714 | 108422.0815 | 151446.717 | 511984.9281 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979
|  |  | 113 | 113 | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 294085 | 294085 | 294085 | 294085 | 294085 | C2 | 3770.1697 | 3770.1697 | 5246.4764 | 12907.3906 | 27044.0566 | C2 | 143266.4486 | 18850.8485 | 152147.8156 | 361406.9382 | 324528.6792 | 1000200.7301 |  | 158347.1274 | 18850.8485 | 152147.8156 | 361406.9382 | 243396.5094 | 934149.2391 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029
|  |  | 62 | 62 | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | C3 | 5655.2545 | 5655.2545 | 7869.7146 | 19361.086 | 40566.0849 | C3 | 96139.3273 | 5655.2545 | 220352.0088 | 232333.0317 | 121698.2547 | 676177.8771 |  | 124415.6001 | 5655.2545 | 220352.0088 | 212971.9457 | 0 | 563394.8092 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198
|  |  | 8 | 8 | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | C4 | 9425.4243 | 9425.4243 | 13116.191 | 32268.4766 | 67610.1415 | C4 | 56552.5455 | 0 | 0 | 64536.9532 | 135220.283 | 256309.7817 |  | 75403.394 | 0 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394
|  |  | 286 | 286 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 0 | 0 | 0 | 0 | 0 |  | 97 | 28 | 39 | 36 | 86 | [22 empty] | 385688.3603 | 42979.9346 | 515728.6301 | 793804.525 | 732893.9339 | 2471095.3838 |  | 479565.5858 | 37701.697 | 490020.8958 | 682800.9654 | 394843.2264 | 2084932.3703 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C1 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | C1 | 757.237 | 757.237 | 25660.7739 | 62636.827 | 131244.019 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 8.564 | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564 |  |  | C2 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C2 | 8232 | 8232 | 8232 | 8232 | 8232 | C2 | 1081.7671 | 1081.7671 | 36658.2485 | 89481.1814 | 187491.4558 | C2 | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C3 | 12348 | 12348 | 12348 | 12348 | 12348 | C3 | 1622.6507 | 1622.6507 | 54987.3727 | 134221.7722 | 281237.1836 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C4 | 20580 | 20580 | 20580 | 20580 | 20580 | C4 | 2704.4178 | 2704.4178 | 91645.6212 | 223702.9536 | 468728.6394 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 8.564 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749 | [22 empty] | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | C1 | 190.2375 | 190.2375 | 6447.0548 | 15737.162 | 32974.1524 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 75074 | 75074 | 75074 | 75074 | 75074 | C2 | 271.7679 | 271.7679 | 9210.0783 | 22481.66 | 47105.932 | C2 | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 112611 | 112611 | 112611 | 112611 | 112611 | C3 | 407.6518 | 407.6518 | 13815.1175 | 33722.4901 | 70658.8981 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 187685 | 187685 | 187685 | 187685 | 187685 | C4 | 679.4197 | 679.4197 | 23025.1958 | 56204.1501 | 117764.8301 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0 | [22 empty] | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
| EHV UG Cable (Non Pressurised) |  | 123.955 | 123.955 | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 208.376 | 208.376 | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 53241 | 53241 | 53241 | 53241 | 53241 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 71.937 | 71.937 | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.622 | 3.622 | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 407.89 | 407.89 |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 188 | 188 | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 8 | 0 | -8 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 14 | 0 | -14 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | C1 | 106.093 | 106.093 | 106.093 | 5372.7104 | 18408.139 | C1 | 2652.3254 | 9336.1853 | 5941.2088 | 69845.2355 | 110448.8339 | 198223.7889 |  | 3288.8835 | 9336.1853 | 5941.2088 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 8063.0691 | 8063.0691 | 26863.5521 | 0 | 46278.5738 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349 |  | 3182.7904 | 8593.5342 | 7532.6041 | 32236.2625 | 0 | 51545.1912
|  |  | 66 | 66 | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 2 | 0 | -2 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 285965 | 285965 | 285965 | 285965 | 285965 | C2 | 151.5615 | 151.5615 | 151.5615 | 7675.3006 | 26297.3414 | C2 | 1212.4916 | 4546.8435 | 3182.7904 | 38376.503 | 52594.6828 | 99913.3114 |  | 1515.6145 | 5153.0893 | 3182.7904 | 7675.3006 | 0 | 17526.7949 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534 |  | 1515.6145 | 3940.5977 | 4546.8435 | 0 | 0 | 10003.0557
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | C3 | 227.3422 | 227.3422 | 227.3422 | 11512.9509 | 39446.0121 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | C4 | 378.9036 | 378.9036 | 378.9036 | 19188.2515 | 65743.3535 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 8 | 0 | -8 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 16 | 0 | -16 | 0 |  | 40 | 91 | 101 | 22 | 0 | [22 empty] | 3864.817 | 13883.0288 | 9123.9993 | 108221.7385 | 163043.5167 | 298137.1002 |  | 4804.498 | 14489.2746 | 9123.9993 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 12609.9126 | 11852.1054 | 34538.8527 | 0 | 63805.3687 |  | 4698.405 | 10745.7068 | 12079.4476 | 122804.8096 | 0 | 150328.3689 |  | 4698.405 |  | 12079.4476 |  | 0 | 16777.8525
| EHV OHL Support - Poles |  | 2475 | 2475 | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | C1 | 114.0865 | 114.0865 | 158.7599 | 390.5815 | 818.3612 | C1 | 13690.3754 | 134964.2845 | 31116.949 | 176542.8375 | 428821.2877 | 785135.7342 |  | 25897.6269 | 134964.2845 | 30323.1493 | 170684.1151 | 357623.8601 | 719493.0359 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372
|  |  | 17510 | 17510 | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12713 | 12713 | 12713 | 12713 | 12713 | C2 | 162.9807 | 162.9807 | 226.7999 | 557.9736 | 1169.0875 | C2 | 138859.5223 | 1364474.0855 | 315025.0889 | 1787189.3447 | 4325623.676 | 7931171.7174 |  | 261257.998 | 1364474.0855 | 306406.6919 | 1723580.3577 | 3618325.7506 | 7274044.8838 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879
|  |  | 264 | 264 | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | C3 | 244.471 | 244.471 | 340.1999 | 836.9604 | 1753.6312 | C3 | 2933.6519 | 30803.3447 | 7144.1975 | 40174.097 | 98203.3483 | 179258.6395 |  | 5867.3038 | 30803.3447 | 6803.9976 | 39337.1367 | 82420.6673 | 165232.4501 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | C4 | 407.4516 | 407.4516 | 566.9998 | 1394.9339 | 2922.7187 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20249 | 20249 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 0 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 0 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686 | [22 empty] | 155483.5496 | 1530241.7148 | 353286.2354 | 2003906.2793 | 4852648.312 | 8895566.0911 |  | 293022.9286 | 1530241.7148 | 343533.8388 | 1933601.6095 | 4058370.2781 | 8158770.3698 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 164 | 164 | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | C1 | 273.0697 | 273.0697 | 380.4935 | 935.6531 | 1960.6893 | C1 | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346
|  |  | 280 | 280 | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117147 | 117147 | 117147 | 117147 | 117147 | C2 | 390.0995 | 390.0995 | 543.5621 | 1336.6473 | 2800.9848 | C2 | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745
|  |  | 153 | 153 | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | C3 | 585.1493 | 585.1493 | 815.3431 | 2004.9709 | 4201.4772 | C3 | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | C4 | 975.2488 | 975.2488 | 1358.9052 | 3341.6182 | 7002.4619 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117 | [22 empty] | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595
| EHV OHL Conductor (Tower Lines) |  | 23.103 | 23.103 | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | C1 | 6.1139 | 6.1139 | 8.4066 | 21.3987 | 44.3259 | C1 | 44.3992 | 0 | 42.2433 | 0 | 479.4285 | 566.0711 |  | 110.5273 | 0 | 42.2433 | 0 | 0 | 152.7706 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585
|  |  | 31.689 | 31.689 | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 109177 | 109177 | 109177 | 109177 | 109177 | C2 | 8.7342 | 8.7342 | 12.0095 | 30.5696 | 63.3227 | C2 | 0 | 0 | 366.3489 | 0 | 74.974 | 441.3229 |  | 10.3412 | 0 | 366.3489 | 0 | 0 | 376.6901 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558
|  |  | 8.297 | 8.297 | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | C3 | 13.1012 | 13.1012 | 18.0142 | 45.8543 | 94.984 | C3 | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346
|  |  | 5.911 | 5.911 | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | C4 | 21.8354 | 21.8354 | 30.0237 | 76.4239 | 158.3067 | C4 | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417
|  |  | 69 | 69 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0 | [22 empty] | 44.3992 | 0 | 735.526 | 0 | 554.4026 | 1334.3278 |  | 120.8685 | 0 | 735.526 | 0 | 0 | 856.3945 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 |  | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 |  | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 |  | 1246891.6658 | 1795187.6106 | 1205751.6105 | 3433979.2153 | 7721130.0381 | 15402940.1403 |  | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 |  | 946376.7012 | 1929100.888 | 759598.3376 | 3621095.7241 | 10656838.8377 | 17913010.4886
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 93 | 93 | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | C1 | 2362.7016 | 2362.7016 | 3287.8781 | 8088.8436 | 16948.0533 | C1 | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149
|  |  | 75 | 75 | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 37 | 12 | 0 | 3 | 75 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 263283 | 263283 | 263283 | 263283 | 263283 | C2 | 3375.2881 | 3375.2881 | 4696.9687 | 11555.4909 | 24211.5047 | C2 | 148512.6746 | 81006.9134 | 37575.7498 | 11555.4909 | 0 | 278650.8287 |  | 148512.6746 | 81006.9134 | 32878.781 | 0 | 0 | 262398.3691 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223
|  |  | 52 | 52 | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | C3 | 5062.9321 | 5062.9321 | 7045.4531 | 17333.2363 | 36317.257 | C3 | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943
|  |  | 9 | 9 | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | C4 | 8438.2201 | 8438.2201 | 11742.4218 | 28888.7272 | 60528.7617 | C4 | 25314.6604 | 42191.1007 | 11742.4218 | 0 | 0 | 79248.183 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813
|  |  | 229 | 229 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10 | [22 empty] | 365881.2257 | 379719.9067 | 90181.7994 | 28888.7272 | 0 | 864671.6591 |  | 374319.4459 | 379719.9067 | 73742.4089 | 17333.2363 | 0 | 845114.9978 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129
| 132kV Transformer |  | 54 | 54 | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | C1 | 11467.5067 | 11467.5067 | 15957.9032 | 39259.6621 | 82258.3395 | C1 | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728
|  |  | 56 | 56 | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 15 | 0 | 8 | 56 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 1277859 | 1277859 | 1277859 | 1277859 | 1277859 | C2 | 16382.1524 | 16382.1524 | 22797.0046 | 56085.2315 | 117511.9136 | C2 | 393171.6571 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1564265.5377 |  | 409553.8095 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1580647.69 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061
|  |  | 11 | 11 | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | C3 | 24573.2286 | 24573.2286 | 34195.5068 | 84127.8473 | 176267.8705 | C3 | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152
|  |  | 10 | 10 | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | C4 | 40955.3809 | 40955.3809 | 56992.5114 | 140213.0788 | 293779.7841 | C4 | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799
|  |  | 131 | 131 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21 | [22 empty] | 1012417.0171 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3955144.8381 |  | 1028799.1695 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3971526.9905 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 15.74 | 15.74 | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | C1 | 216.5404 | 216.5404 | 7338.4477 | 17913.0384 | 37533.2768 | C1 | 2083.9852 | 1278.8878 | 1541.074 | 6663.6503 | 0 | 11567.5973 |  | 2083.9852 | 1278.8878 | 1541.074 | 0 | 0 | 4903.947 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901
|  |  | 24.539 | 24.539 | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 85454 | 85454 | 85454 | 85454 | 85454 | C2 | 309.3435 | 309.3435 | 10483.4967 | 25590.0548 | 53618.9668 | C2 | 2161.6922 | 4234.2936 | 40508.2313 | 24566.4526 | 0 | 71470.6698 |  | 2161.3829 | 4234.2936 | 40508.2313 | 0 | 0 | 46903.9078 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219
|  |  | 14.188 | 14.188 | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 128181 | 128181 | 128181 | 128181 | 128181 | C3 | 464.0152 | 464.0152 | 15725.2451 | 38385.0823 | 80428.4503 | C3 | 4729.7071 | 1834.7162 | 644.735 | 37502.2254 | 0 | 44711.3837 |  | 4729.7071 | 1834.7162 | 644.735 | 0 | 0 | 7209.1584 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074
|  |  | 0.708 | 0.708 | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 213635 | 213635 | 213635 | 213635 | 213635 | C4 | 773.3587 | 773.3587 | 26208.7418 | 63975.1371 | 134047.4171 | C4 | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538
|  |  | 55.175 | 55.175 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0 | [22 empty] | 8975.3845 | 7895.4355 | 42694.0404 | 68732.3283 | 0 | 128297.1887 |  | 8975.0752 | 7895.4355 | 42694.0404 | 0 | 0 | 59564.5511 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573
| 132kV UG Cable (Non Pressurised) |  | 8.145 | 8.145 | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25.492 | 25.492 | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 452934 | 452934 | 452934 | 452934 | 452934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5.672 | 5.672 | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 679401 | 679401 | 679401 | 679401 | 679401 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1132335 | 1132335 | 1132335 | 1132335 | 1132335 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 39.309 | 39.309 |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 704 | 704 | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 10 | 0 | -10 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | C1 | 342.7699 | 342.7699 | 342.7699 | 17358.3835 | 59473.8058 | C1 | 23993.8908 | 137107.9472 | 66154.5845 | 711693.7237 | 0 | 938950.1461 |  | 25364.9702 | 137107.9472 | 66154.5845 | 642260.1896 | 0 | 870887.6916 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 22622.8113 | 126139.3114 | 79865.3792 | 555468.2721 | 297369.0289 | 1081464.803 |  | 22622.8113 | 129567.0101 | 79865.3792 | 381884.4371 | 297369.0289 | 911308.6666
|  |  | 1006 | 1006 | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 28 | 0 | -28 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 55 | 0 | -55 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 923908 | 923908 | 923908 | 923908 | 923908 | C2 | 489.6712 | 489.6712 | 489.6712 | 24797.6907 | 84962.5797 | C2 | 75899.0422 | 239449.2364 | 112624.3852 | 3273295.175 | 0 | 3701267.8388 |  | 80795.7546 | 239449.2364 | 112624.3852 | 3025318.2678 | 0 | 3458187.644 |  | 80795.7546 | 235042.1952 | 115562.4126 | 2777341.3606 | 1104513.5358 | 4313255.2589 |  | 80795.7546 | 248752.9899 | 115562.4126 | 2083006.0205 | 1104513.5358 | 3632630.7135 |  | 80306.0834 | 230145.4828 | 120948.7963 | 2529364.4534 | 1954139.3326 | 4914904.1485 |  | 80306.0834 | 257077.401 | 120948.7963 | 1165491.4638 | 1954139.3326 | 3577963.0771
|  |  | 668 | 668 | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 20 | 0 | -20 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 31 | 0 | -31 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1385862 | 1385862 | 1385862 | 1385862 | 1385862 | C3 | 734.5069 | 734.5069 | 734.5069 | 37196.5361 | 127443.8695 | C3 | 35990.8361 | 260015.4284 | 123397.1525 | 3608063.9998 | 0 | 4027467.4168 |  | 43335.9047 | 260015.4284 | 123397.1525 | 3236098.639 | 0 | 3662847.1246 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 274705.5656 | 124131.6593 | 2492167.9174 | 127443.8695 | 3060315.9029 |  | 41866.891 | 257077.401 | 123397.1525 | 3273295.175 | 637219.3476 | 4332855.9671 |  | 41866.891 | 279847.1137 | 123397.1525 | 2120202.5566 | 637219.3476 | 3202533.0613
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 2309770 | 2309770 | 2309770 | 2309770 | 2309770 | C4 | 1224.1781 | 1224.1781 | 1224.1781 | 61994.2268 | 212406.4492 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2378 | 2378 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 48 | 0 | -48 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 96 | 0 | -96 | 0 |  | 287 | 1188 | 648 | 222 | 33 | [22 empty] | 135883.7691 | 636572.612 | 302176.1222 | 7593052.8985 | 0 | 8667685.4018 |  | 149496.6296 | 636572.612 | 302176.1222 | 6903677.0964 | 0 | 7991922.4602 |  | 147342.0761 | 619825.8556 | 318873.9115 | 6638341.8057 | 1291431.2111 | 9015814.8601 |  | 147342.0761 | 648226.7875 | 318873.9115 | 5200075.744 | 1291431.2111 | 7605949.7302 |  | 144795.7857 | 613362.1952 | 324211.328 | 6358127.9006 | 2888727.7091 | 10329224.9186 |  | 144795.7857 | 666491.5248 | 324211.328 | 3667578.4575 | 2888727.7091 | 7691804.805
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1291 | 1291 | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | C1 | 25.0391 | 25.0391 | 34.4288 | 81.3771 | 172.1439 | C1 | 0 | 450.704 | 43276.9752 | 162.7542 | 2410.0145 | 46300.448 |  | 300.4693 | 450.704 | 43276.9752 | 162.7542 | 344.2878 | 44535.1906 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985
|  |  | 2037 | 2037 | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 447127 | 447127 | 447127 | 447127 | 447127 | C2 | 35.7702 | 35.7702 | 49.184 | 116.253 | 245.9199 | C2 | 214.621 | 321.9314 | 95859.5575 | 0 | 17214.3895 | 113610.4994 |  | 2825.8426 | 321.9314 | 95859.5575 | 0 | 0 | 99007.3316 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197
|  |  | 1379 | 1379 | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | C3 | 53.6552 | 53.6552 | 73.776 | 174.3795 | 368.8798 | C3 | 6867.8707 | 3809.522 | 78202.5123 | 8195.8379 | 25821.5842 | 122897.3272 |  | 10784.7032 | 3809.522 | 78202.5123 | 8195.8379 | 0 | 100992.5755 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439
|  |  | 13 | 13 | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | C4 | 89.4254 | 89.4254 | 122.9599 | 290.6325 | 614.7996 | C4 | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231
|  |  | 4720 | 4720 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691 | [22 empty] | 7082.4917 | 4582.1575 | 218937.5241 | 8358.5921 | 45445.9883 | 284406.7537 |  | 13911.0152 | 4582.1575 | 218937.5241 | 8358.5921 | 344.2878 | 246133.5767 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853
| 132kV OHL Conductor (Tower Lines) |  | 293.476 | 293.476 | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | C1 | 25.4967 | 25.4967 | 35.058 | 89.2386 | 184.8514 | C1 | 1678.2977 | 2783.8875 | 4083.0677 | 0 | 369.5179 | 8914.7708 |  | 1741.7336 | 2783.8875 | 4065.9594 | 0 | 0 | 8591.5805 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739
|  |  | 461.16 | 461.16 | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 455299 | 455299 | 455299 | 455299 | 455299 | C2 | 36.4239 | 36.4239 | 50.0829 | 127.4837 | 264.0734 | C2 | 1764.1926 | 5199.3689 | 13484.3674 | 94.083 | 0 | 20542.0118 |  | 1979.7493 | 5199.3689 | 13224.938 | 0 | 0 | 20404.0562 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628
|  |  | 331.02 | 331.02 | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | C3 | 54.6359 | 54.6359 | 75.1243 | 191.2256 | 396.1101 | C3 | 3961.9208 | 7489.7596 | 7995.7083 | 2489.1834 | 780.7331 | 22717.3052 |  | 5578.8151 | 7489.7596 | 6898.3672 | 0 | 0 | 19966.9419 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424
|  |  | 3.344 | 3.344 | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | C4 | 91.0598 | 91.0598 | 125.2072 | 318.7093 | 660.1836 | C4 | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693
|  |  | 1089 | 1089 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428 | [22 empty] | 7404.4111 | 15473.016 | 25981.8364 | 2583.2664 | 1150.251 | 52592.7808 |  | 9300.298 | 15473.016 | 24607.9576 | 0 | 0 | 49381.2715 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 |  | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 |  | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 |  | 1343895.9872 | 1731156.5846 | 1103682.4945 | 5527024.0365 | 3896520.6787 | 13602279.7815 |  | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 |  | 1095717.6713 | 1774975.9208 | 1216973.0316 | 4218400.7222 | 6296744.2258 | 14602811.5717
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 332299.578 | 332299.578 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 0 | 56 | 0 | -56 | 0 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 0 | 112 | 0 | -112 | 0 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 |  | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 |  | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 |  | 6795554.5081 | 21041110.9048 | 5299218.6536 | 16107726.1311 | 28088350.9813 | 77331961.1788 |  | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 |  | 4880649.1992 | 21553205.9197 | 4894531.1975 | 16161541.5089 | 38733097.6504 | 86223025.4756
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 | LV Network | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 | HV Network | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 | EHV Network | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 | EHV Network | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 | EHV Network | 1246891.6658 | 1795187.6106 | 1205751.6105 | 3433979.2153 | 7721130.0381 | 15402940.1403 | EHV Network | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 | EHV Network | 946376.7012 | 1929100.888 | 759598.3376 | 3621095.7241 | 10656838.8377 | 17913010.4886
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 | 132kV Network | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 | 132kV Network | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 | 132kV Network | 1343895.9872 | 1731156.5846 | 1103682.4945 | 5527024.0365 | 3896520.6787 | 13602279.7815 | 132kV Network | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 | 132kV Network | 1095717.6713 | 1774975.9208 | 1216973.0316 | 4218400.7222 | 6296744.2258 | 14602811.5717
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 | Total | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 | Total | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 | Total | 6795554.5081 | 21041110.9048 | 5299218.6536 | 16107726.1311 | 28088350.9813 | 77331961.1788 | Total | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 | Total | 4880649.1992 | 21553205.9197 | 4894531.1975 | 16161541.5089 | 38733097.6504 | 86223025.4756
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWALES - HVP
Secondary deliverables RIIO-ED1 - HVP - Asset Replacement and Refurbishment driven | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWALES | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of failure | [5 empty] | Criticality/consequence of failure | [5 empty] | Probability of failure x Consequence of failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | 3300.5 | C1 | 42.3124 | 42.3124 | 58.8809 | 144.8589 | 303.514 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 | C2 | 8724 | 76515 | 3589 | 8037 | 4926 | 101791 | 4524 | 76515 | 3799 | 8807 | 8286 | 101931 | 0 | 0 | 0 | 0 | 0 | 0 | 5103 | 76515 | 3589 | 9072 | 7512 | 101791 | 0 | 0 | 0 | 0 | 0 | 0 | 1392 | 76515 | 3589 | 10132 | 10163 | 101791 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4715 | 4715 | 4715 | 4715 | 4715 | C2 | 60.4463 | 60.4463 | 84.1156 | 206.9413 | 433.5914 | C2 | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | 7072.5 | C3 | 90.6694 | 90.6694 | 126.1734 | 310.412 | 650.3871 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | 11787.5 | C4 | 151.1157 | 151.1157 | 210.289 | 517.3534 | 1083.9785 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 101791 | 101791 |  | 8724 | 76515 | 3589 | 8037 | 4926 |  | 4524 | 76515 | 3799 | 8807 | 8286 |  | 0 | 0 | 0 | 0 | 0 |  | 5103 | 76515 | 3589 | 9072 | 7512 |  | 0 | 0 | 0 | 0 | 0 |  | 1392 | 76515 | 3589 | 10132 | 10163 | [22 empty] | 273459.0612 | 4625048.6445 | 319555.1644 | 1822532.4694 | 3592738.3404 | 10633333.68 |  | 527333.5212 | 4625048.6445 | 301890.8884 | 1663187.6299 | 2135871.2364 | 9253331.9205 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 308457.4689 | 4625048.6445 | 301890.8884 | 1877371.9272 | 3257138.5968 | 10369907.5258 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389 |  | 84141.2496 | 4625048.6445 | 301890.8884 | 2096729.7582 | 4406589.3982 | 11514399.9389
| LV Switchgear (at s/s) |  | 278 | 278 | C1 | 278 | 0 | 0 | 0 | 0 | 278 | 272 | 0 | 0 | 0 | 0 | 272 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 0 | 0 | 278 | 0 | 0 | 0 | 0 | 278 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | 4267.2 | C1 | 82.0156 | 82.0156 | 114.0623 | 280.6537 | 588.0628 | C1 | 22308.2388 | 0 | 0 | 0 | 0 | 22308.2388 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324 |  | 22800.3324 | 0 | 0 | 0 | 0 | 22800.3324
|  |  | 7511 | 7511 | C2 | 3806 | 1113 | 2186 | 279 | 127 | 7511 | 3512 | 1119 | 2206 | 298 | 267 | 7402 | 0 | 0 | 0 | 0 | 0 | 0 | 3171 | 1392 | 2170 | 451 | 327 | 7511 | 0 | 0 | 0 | 0 | 0 | 0 | 2393 | 1902 | 1954 | 649 | 613 | 7511 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 6096 | 6096 | 6096 | 6096 | 6096 | C2 | 117.1651 | 117.1651 | 162.9461 | 400.9339 | 840.0898 | C2 | 411483.9014 | 131107.7693 | 359459.0525 | 119478.3082 | 224303.9659 | 1245832.9973 |  | 445930.4467 | 130404.7786 | 356200.1309 | 111860.5637 | 106691.3995 | 1151087.3194 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 371530.5955 | 163093.847 | 353592.9936 | 180821.1979 | 274709.3515 | 1343747.9856 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677 |  | 280376.1322 | 222848.0582 | 318396.6403 | 260206.1141 | 514975.0229 | 1596801.9677
|  |  | 76 | 76 | C3 | 34 | 13 | 24 | 5 | 0 | 76 | 26 | 13 | 27 | 5 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 13 | 26 | 2 | 5 | 76 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 16 | 22 | 9 | 6 | 76 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 9144 | 9144 | 9144 | 9144 | 9144 | C3 | 175.7477 | 175.7477 | 244.4191 | 601.4009 | 1260.1346 | C3 | 4569.4397 | 2284.7198 | 6599.3162 | 3007.0044 | 6300.6732 | 22761.1534 |  | 5975.4211 | 2284.7198 | 5866.0589 | 3007.0044 | 0 | 17133.2042 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 5272.4304 | 2284.7198 | 6354.8971 | 1202.8018 | 6300.6732 | 21415.5223 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959 |  | 4042.1966 | 2811.9629 | 5377.2206 | 5412.6079 | 7560.8078 | 25204.7959
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 15240 | 15240 | 15240 | 15240 | 15240 | C4 | 292.9128 | 292.9128 | 407.3652 | 1002.3348 | 2100.2244 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7865 | 7865 |  | 4118 | 1126 | 2210 | 284 | 127 |  | 3810 | 1132 | 2233 | 303 | 272 |  | 0 | 0 | 0 | 0 | 0 |  | 3479 | 1405 | 2196 | 453 | 332 |  | 0 | 0 | 0 | 0 | 0 |  | 2694 | 1918 | 1976 | 658 | 619 | [22 empty] | 438361.58 | 133392.4891 | 366058.3687 | 122485.3126 | 230604.6391 | 1290902.3895 |  | 474706.2002 | 132689.4984 | 362066.1898 | 114867.5681 | 106691.3995 | 1191020.856 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 399603.3583 | 165378.5669 | 359947.8907 | 182023.9997 | 281010.0247 | 1387963.8403 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096 |  | 307218.6612 | 225660.0211 | 323773.861 | 265618.722 | 522535.8307 | 1644807.096
| LV UGB and LV Pillar OD (not at s/s) |  | 103 | 103 | C1 | 103 | 0 | 0 | 0 | 0 | 103 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 103 | 0 | 0 | 0 | 0 | 103 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | 3653.3 | C1 | 70.2164 | 70.2164 | 97.6527 | 240.2775 | 503.4613 | C1 | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919 |  | 7232.2919 | 0 | 0 | 0 | 0 | 7232.2919
|  |  | 3635 | 3635 | C2 | 510 | 519 | 2174 | 279 | 153 | 3635 | 452 | 519 | 2176 | 279 | 203 | 3629 | 0 | 0 | 0 | 0 | 0 | 0 | 442 | 306 | 2157 | 340 | 390 | 3635 | 0 | 0 | 0 | 0 | 0 | 0 | 434 | 78 | 2062 | 443 | 618 | 3635 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5219 | 5219 | 5219 | 5219 | 5219 | C2 | 100.3092 | 100.3092 | 139.5039 | 343.2536 | 719.2304 | C2 | 45339.7494 | 52060.4644 | 303560.4211 | 95767.7628 | 146003.7692 | 642732.1668 |  | 51157.6818 | 52060.4644 | 303281.4134 | 95767.7628 | 110042.2497 | 612309.572 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 44336.6576 | 30694.6091 | 300909.8476 | 116706.2342 | 280499.8521 | 773147.2005 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192 |  | 43534.1841 | 7824.116 | 287656.9799 | 152061.3581 | 444484.381 | 935561.0192
|  |  | 581 | 581 | C3 | 25 | 3 | 547 | 1 | 5 | 581 | 25 | 3 | 547 | 1 | 5 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 1 | 548 | 1 | 6 | 581 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 0 | 544 | 6 | 6 | 581 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | 7828.5 | C3 | 150.4638 | 150.4638 | 209.2558 | 514.8804 | 1078.8456 | C3 | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 451.3913 | 114462.9253 | 514.8804 | 5394.2279 | 124585.0193 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 3761.5943 | 150.4638 | 114672.1811 | 514.8804 | 6473.0735 | 125572.1931 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083 |  | 3761.5943 | 0 | 113835.1579 | 3089.2827 | 6473.0735 | 127159.1083
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | 13047.5 | C4 | 250.773 | 250.773 | 348.7597 | 858.1341 | 1798.076 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4319 | 4319 |  | 638 | 522 | 2721 | 280 | 158 |  | 580 | 522 | 2723 | 280 | 208 |  | 0 | 0 | 0 | 0 | 0 |  | 570 | 307 | 2705 | 341 | 396 |  | 0 | 0 | 0 | 0 | 0 |  | 562 | 78 | 2606 | 449 | 624 | [22 empty] | 56333.6355 | 52511.8557 | 418023.3465 | 96282.6432 | 151397.9971 | 774549.478 |  | 62151.5679 | 52511.8557 | 417744.3387 | 96282.6432 | 115436.4776 | 744126.8832 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 55330.5437 | 30845.0729 | 415582.0287 | 117221.1146 | 286972.9256 | 905951.6855 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194 |  | 54528.0702 | 7824.116 | 401492.1379 | 155150.6408 | 450957.4545 | 1069952.4194
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 |  | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 |  | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 631 | 631 | C1 | 395 | 118 | 86 | 20 | 12 | 631 | 393 | 118 | 86 | 22 | 14 | 633 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 210 | 69 | 37 | 25 | 631 | 0 | 0 | 0 | 0 | 0 | 0 | 217 | 260 | 61 | 45 | 48 | 631 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 36715 | 36715 | 36715 | 36715 | 36715 | C1 | 470.6863 | 470.6863 | 654.9956 | 1611.4213 | 3376.3114 | C1 | 184979.7159 | 55540.9834 | 56329.6216 | 35451.2697 | 47268.3596 | 379569.9502 |  | 185921.0885 | 55540.9834 | 56329.6216 | 32228.427 | 40515.7368 | 370535.8573 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 136499.027 | 98844.123 | 45194.6964 | 59622.5899 | 84407.785 | 424568.2214 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046 |  | 102138.9271 | 122378.438 | 39954.7316 | 72513.9607 | 162062.9472 | 499049.0046
|  |  | 1416 | 1416 | C2 | 800 | 295 | 224 | 72 | 25 | 1416 | 792 | 297 | 227 | 85 | 33 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 665 | 400 | 198 | 86 | 67 | 1416 | 0 | 0 | 0 | 0 | 0 | 0 | 550 | 467 | 143 | 119 | 137 | 1416 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 52450 | 52450 | 52450 | 52450 | 52450 | C2 | 672.409 | 672.409 | 935.708 | 2302.0305 | 4823.302 | C2 | 532547.928 | 199705.473 | 212405.716 | 195672.5925 | 159168.966 | 1299500.6755 |  | 537927.2 | 198360.655 | 209598.592 | 165746.196 | 120582.55 | 1232215.193 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 447151.985 | 268963.6 | 185270.184 | 197974.623 | 323161.234 | 1422521.626 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005 |  | 369824.95 | 314015.003 | 133806.244 | 273941.6295 | 660792.374 | 1752380.2005
|  |  | 31 | 31 | C3 | 7 | 9 | 14 | 1 | 0 | 31 | 5 | 9 | 14 | 4 | 2 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 5 | 14 | 4 | 1 | 31 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 4 | 8 | 8 | 4 | 31 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 78675 | 78675 | 78675 | 78675 | 78675 | C3 | 1008.6135 | 1008.6135 | 1403.562 | 3453.0457 | 7234.953 | C3 | 5043.0675 | 9077.5215 | 19649.868 | 13812.183 | 14469.906 | 62052.546 |  | 7060.2945 | 9077.5215 | 19649.868 | 3453.0457 | 0 | 39240.7297 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 5043.0675 | 19649.868 | 13812.183 | 7234.953 | 52800.366 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225 |  | 7060.2945 | 4034.454 | 11228.496 | 27624.366 | 28939.812 | 78887.4225
|  |  | 185 | 185 | C4 | 92 | 44 | 34 | 12 | 3 | 185 | 92 | 44 | 34 | 14 | 4 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 57 | 27 | 17 | 9 | 185 | 0 | 0 | 0 | 0 | 0 | 0 | 59 | 67 | 20 | 16 | 23 | 185 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 131125 | 131125 | 131125 | 131125 | 131125 | C4 | 1681.0225 | 1681.0225 | 2339.27 | 5755.0763 | 12058.255 | C4 | 154654.07 | 73964.99 | 79535.18 | 80571.0675 | 48233.02 | 436958.3275 |  | 154654.07 | 73964.99 | 79535.18 | 69060.915 | 36174.765 | 413389.92 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 126076.6875 | 95818.2825 | 63160.29 | 97836.2962 | 108524.295 | 491415.8513 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32 |  | 99180.3275 | 112628.5075 | 46785.4 | 92081.22 | 277339.865 | 628015.32
|  |  | 2263 | 2263 |  | 1294 | 466 | 358 | 105 | 40 |  | 1282 | 468 | 361 | 125 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 1037 | 672 | 308 | 144 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 833 | 798 | 232 | 188 | 212 | [22 empty] | 877224.7814 | 338288.9679 | 367920.3856 | 325507.1127 | 269140.2516 | 2178081.4992 |  | 885562.653 | 336944.1499 | 365113.2616 | 270488.5837 | 197273.0518 | 2055381.7001 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 716787.994 | 468669.073 | 313275.0384 | 369245.6922 | 523328.267 | 2391306.0646 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476 |  | 578204.4991 | 553056.4025 | 231774.8716 | 466161.1763 | 1129134.9982 | 2958331.9476
| HV Switchgear (GM) - Distribution |  | 254 | 254 | C1 | 242 | 12 | 0 | 0 | 0 | 254 | 240 | 12 | 0 | 0 | 0 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 225 | 26 | 3 | 0 | 0 | 254 | 0 | 0 | 0 | 0 | 0 | 0 | 167 | 81 | 6 | 0 | 0 | 254 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | 10285.1 | C1 | 131.855 | 131.855 | 183.4862 | 451.413 | 945.8178 | C1 | 31645.1957 | 1582.2598 | 0 | 0 | 0 | 33227.4555 |  | 31908.9056 | 1582.2598 | 0 | 0 | 0 | 33491.1654 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 29667.3709 | 3428.2295 | 550.4586 | 0 | 0 | 33646.059 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526 |  | 22019.782 | 10680.2535 | 1100.9171 | 0 | 0 | 33800.9526
|  |  | 9267 | 9267 | C2 | 5628 | 1985 | 1008 | 167 | 479 | 9267 | 5452 | 2012 | 1020 | 168 | 524 | 9176 | 0 | 0 | 0 | 0 | 0 | 0 | 4309 | 2966 | 1141 | 163 | 688 | 9267 | 0 | 0 | 0 | 0 | 0 | 0 | 3289 | 3436 | 1342 | 281 | 919 | 9267 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 14693 | 14693 | 14693 | 14693 | 14693 | C2 | 188.3643 | 188.3643 | 262.1231 | 644.8758 | 1351.1683 | C2 | 1026961.9455 | 378988.8911 | 267365.5824 | 108339.1294 | 708012.1787 | 2489667.7271 |  | 1060114.0553 | 373903.0561 | 264220.105 | 107694.2536 | 647209.6061 | 2453141.076 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 811661.5963 | 558688.3952 | 299082.4799 | 105114.7505 | 929603.7766 | 2704150.9986 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162 |  | 619530.0511 | 647219.5974 | 351769.227 | 181210.0914 | 1241723.6493 | 3041452.6162
|  |  | 1084 | 1084 | C3 | 487 | 240 | 198 | 26 | 133 | 1084 | 454 | 243 | 200 | 35 | 144 | 1076 | 0 | 0 | 0 | 0 | 0 | 0 | 367 | 298 | 224 | 22 | 173 | 1084 | 0 | 0 | 0 | 0 | 0 | 0 | 279 | 326 | 216 | 50 | 213 | 1084 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | 22039.5 | C3 | 282.5464 | 282.5464 | 393.1847 | 967.3137 | 2026.7524 | C3 | 128276.0611 | 68658.7728 | 78636.936 | 33855.9779 | 291852.3485 | 601280.0962 |  | 137600.0919 | 67811.1336 | 77850.5666 | 25150.155 | 269558.0719 | 577970.0191 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 103694.5251 | 84198.8242 | 88073.3683 | 21280.9004 | 350628.1687 | 647875.7867 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405 |  | 78830.4428 | 92110.1231 | 84927.8909 | 48365.6827 | 431698.2655 | 735932.405
|  |  | 4 | 4 | C4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 1 | 3 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 1 | 0 | 4 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | 36732.5 | C4 | 470.9106 | 470.9106 | 655.3078 | 1612.1894 | 3377.9207 | C4 | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 470.9106 | 1965.9234 | 0 | 0 | 2436.834 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 2621.2312 | 0 | 0 | 2621.2312 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128 |  | 0 | 0 | 1965.9234 | 1612.1894 | 0 | 3578.1128
|  |  | 10609 | 10609 |  | 6357 | 2238 | 1209 | 193 | 612 |  | 6146 | 2268 | 1223 | 203 | 668 |  | 0 | 0 | 0 | 0 | 0 |  | 4901 | 3290 | 1372 | 185 | 861 |  | 0 | 0 | 0 | 0 | 0 |  | 3735 | 3843 | 1567 | 332 | 1132 | [22 empty] | 1186883.2023 | 449700.8343 | 347968.4418 | 142195.1073 | 999864.5272 | 3126612.1129 |  | 1229623.0529 | 443767.3601 | 344036.595 | 132844.4086 | 916767.678 | 3067039.0946 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 945023.4924 | 646315.4489 | 390327.538 | 126395.6509 | 1280231.9453 | 3388294.0755 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867 |  | 720380.2759 | 750009.974 | 439763.9584 | 231187.9635 | 1673421.9148 | 3814764.0867
| HV Transformer (GM) |  | 1331 | 1331 | C1 | 378 | 157 | 612 | 82 | 102 | 1331 | 324 | 159 | 619 | 82 | 134 | 1318 | 0 | 0 | 0 | 0 | 0 | 0 | 332 | 134 | 589 | 124 | 152 | 1331 | 0 | 0 | 0 | 0 | 0 | 0 | 276 | 144 | 535 | 156 | 220 | 1331 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | 10702.3 | C1 | 205.6982 | 205.6982 | 286.0725 | 703.8903 | 1474.884 | C1 | 66646.2187 | 32706.0148 | 177078.8645 | 57719.0022 | 197634.451 | 531784.5513 |  | 77753.9219 | 32294.6183 | 175076.3571 | 57719.0022 | 150438.1642 | 493282.0638 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 68291.8044 | 27563.5596 | 168496.6901 | 87282.3936 | 224182.3624 | 575816.8101 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769 |  | 56772.7049 | 29620.5417 | 153048.7763 | 109806.8823 | 324474.4719 | 673723.3769
|  |  | 5824 | 5824 | C2 | 3218 | 917 | 1348 | 190 | 151 | 5824 | 2985 | 928 | 1361 | 191 | 300 | 5765 | 0 | 0 | 0 | 0 | 0 | 0 | 2817 | 1011 | 1482 | 248 | 266 | 5824 | 0 | 0 | 0 | 0 | 0 | 0 | 2292 | 1285 | 1511 | 320 | 416 | 5824 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 15289 | 15289 | 15289 | 15289 | 15289 | C2 | 293.8546 | 293.8546 | 408.675 | 1005.5575 | 2106.9771 | C2 | 877155.9213 | 272697.0502 | 556206.6342 | 192061.4882 | 632093.127 | 2530214.2209 |  | 945624.0384 | 269464.6499 | 550893.8596 | 191055.9307 | 318153.5406 | 2275192.0192 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 827788.3519 | 297086.9804 | 605656.3055 | 249378.2674 | 560455.9059 | 2540365.8112 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914 |  | 673514.6974 | 377603.1353 | 617507.8797 | 321778.4096 | 876502.4694 | 2866906.5914
|  |  | 1184 | 1184 | C3 | 816 | 185 | 149 | 15 | 19 | 1184 | 771 | 187 | 150 | 15 | 50 | 1173 | 0 | 0 | 0 | 0 | 0 | 0 | 715 | 231 | 181 | 26 | 31 | 1184 | 0 | 0 | 0 | 0 | 0 | 0 | 607 | 291 | 204 | 35 | 47 | 1184 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | 22933.5 | C3 | 440.7819 | 440.7819 | 613.0125 | 1508.3363 | 3160.4656 | C3 | 339842.8218 | 82426.2097 | 91951.8682 | 22625.0444 | 158023.2817 | 694869.2259 |  | 359678.0059 | 81544.646 | 91338.8558 | 22625.0444 | 60048.8471 | 615235.3992 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 315159.0371 | 101820.612 | 110955.2544 | 39216.7437 | 97974.4347 | 665126.0817 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152 |  | 267554.5951 | 128267.5242 | 125054.5408 | 52791.7703 | 148541.8848 | 722210.3152
|  |  | 2 | 2 | C4 | 1 | 1 | 0 | 0 | 0 | 2 | 1 | 1 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | 2 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | 38222.5 | C4 | 734.6365 | 734.6365 | 1021.6874 | 2513.8938 | 5267.4427 | C4 | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 734.6365 | 734.6365 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729 |  | 0 | 1469.2729 | 0 | 0 | 0 | 1469.2729
|  |  | 8341 | 8341 |  | 4413 | 1260 | 2109 | 287 | 272 |  | 4081 | 1275 | 2130 | 288 | 484 |  | 0 | 0 | 0 | 0 | 0 |  | 3864 | 1378 | 2252 | 398 | 449 |  | 0 | 0 | 0 | 0 | 0 |  | 3175 | 1722 | 2250 | 511 | 683 | [22 empty] | 1284379.5983 | 388563.9111 | 825237.3669 | 272405.5349 | 987750.8598 | 3758337.271 |  | 1383790.6027 | 384038.5506 | 817309.0725 | 271399.9773 | 528640.5519 | 3385178.755 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 1211239.1933 | 427940.4249 | 885108.25 | 375877.4047 | 882612.703 | 3782777.9759 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564 |  | 997841.9973 | 536960.474 | 895611.1968 | 484377.0622 | 1349518.8261 | 4264309.5564
| HV UG Cable |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | 21554.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4766.226 | 4766.226 | C2 | 2634.097 | 1606.444 | 467.18 | 44.658 | 13.847 | 4766.226 | 2533.515 | 1616.109 | 469.983 | 44.706 | 26.902 | 4691.215 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 30792 | 30792 | 30792 | 30792 | 30792 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 892.414 | 892.414 | C3 | 341.524 | 370.744 | 160.001 | 10.621 | 9.524 | 892.414 | 318.176 | 372.974 | 160.854 | 10.63 | 15.496 | 878.13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 46188 | 46188 | 46188 | 46188 | 46188 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 76980 | 76980 | 76980 | 76980 | 76980 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5658.64 | 5658.64 |  | 2975.621 | 1977.188 | 627.181 | 55.279 | 23.371 |  | 2851.691 | 1989.083 | 630.837 | 55.336 | 42.398 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | 4785.9 | C1 | 61.3552 | 61.3552 | 85.3805 | 210.0532 | 440.1114 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 149285 | 149285 | C2 | 9900 | 114507 | 2388 | 10771 | 11719 | 149285 | 4242 | 114507 | 2658 | 11582 | 16040 | 149029 | 0 | 0 | 0 | 0 | 0 | 0 | 5836 | 114507 | 2388 | 12295 | 14259 | 149285 | 0 | 0 | 0 | 0 | 0 | 0 | 989 | 114507 | 2388 | 13866 | 17535 | 149285 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6837 | 6837 | 6837 | 6837 | 6837 | C2 | 87.6503 | 87.6503 | 121.9721 | 300.0759 | 628.7305 | C2 | 371812.7423 | 10036577.4824 | 324201.7886 | 3475479.4213 | 10084837.5408 | 24292908.9754 |  | 867738.366 | 10036577.4824 | 291269.327 | 3232117.842 | 7368092.9639 | 21795795.9813 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 511527.3842 | 10036577.4824 | 291269.327 | 3689433.5593 | 8965068.4847 | 23493876.2377 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093 |  | 86686.1863 | 10036577.4824 | 291269.327 | 4160852.8454 | 11024789.6682 | 25600175.5093
|  |  | 10797 | 10797 | C3 | 715 | 8283 | 173 | 779 | 847 | 10797 | 306 | 8283 | 192 | 838 | 1160 | 10779 | 0 | 0 | 0 | 0 | 0 | 0 | 422 | 8283 | 172 | 889 | 1031 | 10797 | 0 | 0 | 0 | 0 | 0 | 0 | 71 | 8283 | 172 | 1003 | 1268 | 10797 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | 10255.5 | C3 | 131.4755 | 131.4755 | 182.9581 | 450.1139 | 943.0958 | C3 | 40231.5061 | 1089011.6493 | 35127.959 | 377195.444 | 1093991.1048 | 2635557.6632 |  | 94004.9896 | 1089011.6493 | 31651.7548 | 350638.7242 | 798802.1257 | 2364109.2436 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 55482.6652 | 1089011.6493 | 31468.7966 | 400151.2527 | 972331.7492 | 2548446.113 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929 |  | 9334.7612 | 1089011.6493 | 31468.7966 | 451464.2367 | 1195845.449 | 2777124.8929
|  |  | 149 | 149 | C4 | 10 | 114 | 2 | 11 | 12 | 149 | 4 | 114 | 3 | 11 | 17 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 114 | 3 | 12 | 14 | 149 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 114 | 3 | 14 | 17 | 149 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | 17092.5 | C4 | 219.1258 | 219.1258 | 304.9302 | 750.1898 | 1571.8263 | C4 | 876.5034 | 24980.3469 | 914.7906 | 8252.0881 | 26721.0471 | 61744.7761 |  | 2191.2585 | 24980.3469 | 609.8604 | 8252.0881 | 18861.9156 | 54895.4695 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 1314.7551 | 24980.3469 | 914.7906 | 9002.2779 | 22005.5682 | 58217.7387 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968 |  | 219.1258 | 24980.3469 | 914.7906 | 10502.6575 | 26721.0471 | 63337.968
|  |  | 160231 | 160231 |  | 10625 | 122904 | 2563 | 11561 | 12578 |  | 4552 | 122904 | 2853 | 12431 | 17217 |  | 0 | 0 | 0 | 0 | 0 |  | 6264 | 122904 | 2563 | 13196 | 15304 |  | 0 | 0 | 0 | 0 | 0 |  | 1061 | 122904 | 2563 | 14883 | 18820 | [22 empty] | 412920.7517 | 11150569.4786 | 360244.5383 | 3860926.9533 | 11205549.6927 | 26990211.4147 |  | 963934.6142 | 11150569.4786 | 323530.9422 | 3591008.6543 | 8185757.0051 | 24214800.6944 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 568324.8046 | 11150569.4786 | 323652.9143 | 4098587.0899 | 9959405.8021 | 26100540.0894 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702 |  | 96240.0733 | 11150569.4786 | 323652.9143 | 4622819.7396 | 12247356.1643 | 28440638.3702
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 |  | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 |  | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 285 | 285 | C1 | 213 | 38 | 27 | 6 | 1 | 285 | 209 | 38 | 27 | 6 | 1 | 281 | 0 | 0 | 0 | 0 | 0 | 0 | 171 | 80 | 0 | 25 | 9 | 285 | 0 | 0 | 0 | 0 | 0 | 0 | 127 | 117 | 7 | 0 | 34 | 285 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 87556 | 87556 | 87556 | 87556 | 87556 | C1 | 1122.4679 | 1122.4679 | 1561.999 | 3842.8328 | 8051.6498 | C1 | 234595.7953 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 350532.1971 |  | 239085.667 | 42653.781 | 42173.9741 | 23056.997 | 8051.6498 | 355022.0688 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 191942.0143 | 89797.4336 | 0 | 96070.821 | 72464.8478 | 450275.1168 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576 |  | 142553.4258 | 131328.7466 | 10933.9933 | 0 | 273756.0918 | 558572.2576
|  |  | 314 | 314 | C2 | 201 | 14 | 98 | 0 | 1 | 314 | 180 | 14 | 111 | 2 | 2 | 309 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 22 | 36 | 65 | 1 | 314 | 0 | 0 | 0 | 0 | 0 | 0 | 150 | 57 | 20 | 17 | 70 | 314 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 125080 | 125080 | 125080 | 125080 | 125080 | C2 | 1603.5256 | 1603.5256 | 2231.4272 | 5489.7612 | 11502.3568 | C2 | 288634.608 | 22449.3584 | 247688.4192 | 10979.5224 | 23004.7136 | 592756.6216 |  | 322308.6456 | 22449.3584 | 218679.8656 | 0 | 11502.3568 | 574940.2264 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 304669.864 | 35277.5632 | 80331.3792 | 356834.478 | 11502.3568 | 788615.6412 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596 |  | 240528.84 | 91400.9592 | 44628.544 | 93325.9404 | 805164.976 | 1275049.2596
|  |  | 63 | 63 | C3 | 35 | 1 | 26 | 1 | 0 | 63 | 29 | 1 | 27 | 1 | 0 | 58 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 4 | 7 | 19 | 1 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 28 | 8 | 2 | 4 | 21 | 63 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 187620 | 187620 | 187620 | 187620 | 187620 | C3 | 2405.2884 | 2405.2884 | 3347.1408 | 8234.6418 | 17253.5352 | C3 | 69753.3636 | 2405.2884 | 90372.8016 | 8234.6418 | 0 | 170766.0954 |  | 84185.094 | 2405.2884 | 87025.6608 | 8234.6418 | 0 | 181850.685 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 76969.2288 | 9621.1536 | 23429.9856 | 156458.1942 | 17253.5352 | 283732.0974 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704 |  | 67348.0752 | 19242.3072 | 6694.2816 | 32938.5672 | 362324.2392 | 488547.4704
|  |  | 45 | 45 | C4 | 22 | 3 | 20 | 0 | 0 | 45 | 9 | 3 | 33 | 0 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 16 | 7 | 0 | 45 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 13 | 3 | 7 | 45 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 312700 | 312700 | 312700 | 312700 | 312700 | C4 | 4008.814 | 4008.814 | 5578.568 | 13724.403 | 28755.892 | C4 | 36079.326 | 12026.442 | 184092.744 | 0 | 0 | 232198.512 |  | 88193.908 | 12026.442 | 111571.36 | 0 | 0 | 211791.71 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 88193.908 | 0 | 89257.088 | 96070.821 | 0 | 273521.817 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745 |  | 72158.652 | 16035.256 | 72521.384 | 41173.209 | 201291.244 | 403179.745
|  |  | 707 | 707 |  | 471 | 56 | 171 | 7 | 2 |  | 427 | 56 | 198 | 9 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 415 | 106 | 59 | 116 | 11 |  | 0 | 0 | 0 | 0 | 0 |  | 323 | 186 | 42 | 24 | 132 | [22 empty] | 629063.0929 | 79534.8698 | 564327.9389 | 42271.1612 | 31056.3634 | 1346253.4261 |  | 733773.3146 | 79534.8698 | 459450.8605 | 31291.6388 | 19554.0066 | 1323604.6902 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 661775.0151 | 134696.1504 | 193018.4528 | 705434.3142 | 101220.7398 | 1796144.6724 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326 |  | 522588.993 | 258007.269 | 134778.2029 | 167437.7166 | 1642536.551 | 2725348.7326
| EHV Transformer |  | 103 | 103 | C1 | 46 | 5 | 32 | 12 | 8 | 103 | 34 | 7 | 39 | 15 | 8 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 5 | 19 | 19 | 14 | 103 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 6 | 13 | 10 | 30 | 103 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | 205859.5 | C1 | 2639.1188 | 2639.1188 | 3672.5335 | 9035.1735 | 18930.8396 | C1 | 89730.0389 | 18473.8315 | 143228.8057 | 135527.6018 | 151446.717 | 538406.9949 |  | 121399.4643 | 13195.594 | 117521.0714 | 108422.0815 | 151446.717 | 511984.9281 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 121399.4643 | 13195.594 | 69778.1361 | 171668.2956 | 265031.7547 | 641073.2447 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979 |  | 116121.2268 | 15834.7127 | 47742.9352 | 90351.7345 | 567925.1886 | 837975.7979
|  |  | 113 | 113 | C2 | 42 | 5 | 29 | 28 | 9 | 113 | 38 | 5 | 29 | 28 | 12 | 112 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 13 | 21 | 11 | 34 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 12 | 11 | 18 | 40 | 113 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 294085 | 294085 | 294085 | 294085 | 294085 | C2 | 3770.1697 | 3770.1697 | 5246.4764 | 12907.3906 | 27044.0566 | C2 | 143266.4486 | 18850.8485 | 152147.8156 | 361406.9382 | 324528.6792 | 1000200.7301 |  | 158347.1274 | 18850.8485 | 152147.8156 | 361406.9382 | 243396.5094 | 934149.2391 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 128185.7698 | 49012.2061 | 110176.0044 | 141981.2971 | 919497.9244 | 1348853.2019 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029 |  | 120645.4304 | 45242.0364 | 57711.2404 | 232333.0317 | 1081762.264 | 1537694.0029
|  |  | 62 | 62 | C3 | 22 | 1 | 28 | 11 | 0 | 62 | 17 | 1 | 28 | 12 | 3 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 5 | 20 | 9 | 10 | 62 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 6 | 15 | 8 | 16 | 62 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | 441127.5 | C3 | 5655.2545 | 5655.2545 | 7869.7146 | 19361.086 | 40566.0849 | C3 | 96139.3273 | 5655.2545 | 220352.0088 | 232333.0317 | 121698.2547 | 676177.8771 |  | 124415.6001 | 5655.2545 | 220352.0088 | 212971.9457 | 0 | 563394.8092 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 101794.5819 | 28276.2727 | 157394.292 | 174249.7738 | 405660.849 | 867375.7694 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198 |  | 96139.3273 | 33931.5273 | 118045.719 | 154888.6878 | 649057.3584 | 1052062.6198
|  |  | 8 | 8 | C4 | 8 | 0 | 0 | 0 | 0 | 8 | 6 | 0 | 0 | 2 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 2 | 0 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 4 | 0 | 0 | 0 | 8 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | 735212.5 | C4 | 9425.4243 | 9425.4243 | 13116.191 | 32268.4766 | 67610.1415 | C4 | 56552.5455 | 0 | 0 | 64536.9532 | 135220.283 | 256309.7817 |  | 75403.394 | 0 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 56552.5455 | 18850.8485 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394 |  | 37701.697 | 37701.697 | 0 | 0 | 0 | 75403.394
|  |  | 286 | 286 |  | 118 | 11 | 89 | 51 | 17 |  | 95 | 13 | 96 | 57 | 25 |  | 0 | 0 | 0 | 0 | 0 |  | 104 | 25 | 60 | 39 | 58 |  | 0 | 0 | 0 | 0 | 0 |  | 97 | 28 | 39 | 36 | 86 | [22 empty] | 385688.3603 | 42979.9346 | 515728.6301 | 793804.525 | 732893.9339 | 2471095.3838 |  | 479565.5858 | 37701.697 | 490020.8958 | 682800.9654 | 394843.2264 | 2084932.3703 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 407932.3615 | 109334.9213 | 337348.4325 | 487899.3666 | 1590190.5281 | 2932705.61 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146 |  | 370607.6815 | 132709.9734 | 223499.8946 | 477573.454 | 2298744.811 | 3503135.8146
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C1 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | 5762.4 | C1 | 757.237 | 757.237 | 25660.7739 | 62636.827 | 131244.019 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 8.564 | C2 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0.682 | 2.133 | 5.749 | 0 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.815 | 0 | 5.749 | 8.564 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.723 | 2.092 | 5.749 | 8.564 |  |  | C2 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C2 | 8232 | 8232 | 8232 | 8232 | 8232 | C2 | 1081.7671 | 1081.7671 | 36658.2485 | 89481.1814 | 187491.4558 | C2 | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C3 | 12348 | 12348 | 12348 | 12348 | 12348 | C3 | 1622.6507 | 1622.6507 | 54987.3727 | 134221.7722 | 281237.1836 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759 | C4 | 20580 | 20580 | 20580 | 20580 | 20580 | C4 | 2704.4178 | 2704.4178 | 91645.6212 | 223702.9536 | 468728.6394 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 8.564 | 8.564 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0.682 | 2.133 | 5.749 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 2.815 | 0 | 5.749 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0.723 | 2.092 | 5.749 | [22 empty] | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 737.7652 | 78192.044 | 514427.3121 | 0 | 593357.1213 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 103192.9695 | 0 | 1077888.3792 | 1181081.3486 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244 |  | 0 | 0 | 26503.9137 | 187194.6316 | 1077888.3792 | 1291586.9244
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | 52551.8 | C1 | 190.2375 | 190.2375 | 6447.0548 | 15737.162 | 32974.1524 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 | C2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.26 | 0.357 | 0.383 | 0 | 0 | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 1.259 | 0.357 | 0.384 | 0 | 0 | 2 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 75074 | 75074 | 75074 | 75074 | 75074 | C2 | 271.7679 | 271.7679 | 9210.0783 | 22481.66 | 47105.932 | C2 | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 112611 | 112611 | 112611 | 112611 | 112611 | C3 | 407.6518 | 407.6518 | 13815.1175 | 33722.4901 | 70658.8981 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 187685 | 187685 | 187685 | 187685 | 187685 | C4 | 679.4197 | 679.4197 | 23025.1958 | 56204.1501 | 117764.8301 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2 | 2 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.26 | 0.357 | 0.383 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 1.259 | 0.357 | 0.384 | 0 | 0 | [22 empty] | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.4275 | 97.0211 | 3527.46 | 0 | 0 | 3966.9087 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847 |  | 342.1558 | 97.0211 | 3536.6701 | 0 | 0 | 3975.847
| EHV UG Cable (Non Pressurised) |  | 123.955 | 123.955 | C1 | 69.864 | 29.469 | 16.889 | 1.766 | 5.967 | 123.955 | 65.598 | 29.469 | 16.889 | 1.766 | 5.967 | 119.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | 37268.7 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 208.376 | 208.376 | C2 | 87.316 | 53.912 | 37.706 | 6.509 | 22.933 | 208.376 | 80.613 | 53.912 | 37.706 | 6.509 | 22.933 | 201.673 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 53241 | 53241 | 53241 | 53241 | 53241 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 71.937 | 71.937 | C3 | 53 | 15.003 | 3.934 | 0 | 0 | 71.937 | 51.781 | 15.003 | 3.934 | 0 | 0 | 70.718 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | 79861.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.622 | 3.622 | C4 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 1.3 | 2.32 | 0.002 | 0 | 0 | 3.622 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | 133102.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 407.89 | 407.89 |  | 211.48 | 100.704 | 58.531 | 8.275 | 28.9 |  | 199.292 | 100.704 | 58.531 | 8.275 | 28.9 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 188 | 188 | C1 | 31 | 88 | 56 | 13 | 0 | 188 | 25 | 88 | 56 | 13 | 6 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 68 | 76 | 13 | 0 | 188 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 67 | 71 | 20 | 0 | 188 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | 200175.5 | C1 | 106.093 | 106.093 | 106.093 | 5372.7104 | 18408.139 | C1 | 2652.3254 | 9336.1853 | 5941.2088 | 69845.2355 | 110448.8339 | 198223.7889 |  | 3288.8835 | 9336.1853 | 5941.2088 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3288.8835 | 7214.325 | 8063.0691 | 69845.2355 | 0 | 88411.5131 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349 |  | 3182.7904 | 7108.232 | 7532.6041 | 107454.2084 | 0 | 125277.8349
|  |  | 66 | 66 | C2 | 10 | 34 | 21 | 1 | 0 | 66 | 8 | 30 | 21 | 5 | 2 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 30 | 25 | 1 | 0 | 66 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 24 | 30 | 2 | 0 | 66 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 285965 | 285965 | 285965 | 285965 | 285965 | C2 | 151.5615 | 151.5615 | 151.5615 | 7675.3006 | 26297.3414 | C2 | 1212.4916 | 4546.8435 | 3182.7904 | 38376.503 | 52594.6828 | 99913.3114 |  | 1515.6145 | 5153.0893 | 3182.7904 | 7675.3006 | 0 | 17526.7949 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 4546.8435 | 3789.0363 | 7675.3006 | 0 | 17526.7948 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534 |  | 1515.6145 | 3637.4748 | 4546.8435 | 15350.6012 | 0 | 25050.534
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | 428947.5 | C3 | 227.3422 | 227.3422 | 227.3422 | 11512.9509 | 39446.0121 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | 714912.5 | C4 | 378.9036 | 378.9036 | 378.9036 | 19188.2515 | 65743.3535 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 254 | 254 |  | 41 | 122 | 77 | 14 | 0 |  | 33 | 118 | 77 | 18 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 41 | 98 | 101 | 14 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 40 | 91 | 101 | 22 | 0 | [22 empty] | 3864.817 | 13883.0288 | 9123.9993 | 108221.7385 | 163043.5167 | 298137.1002 |  | 4804.498 | 14489.2746 | 9123.9993 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4804.498 | 11761.1685 | 11852.1054 | 77520.5361 | 0 | 105938.3079 |  | 4698.405 | 10745.7068 | 12079.4476 | 122804.8096 | 0 | 150328.3689 |  | 4698.405 |  | 12079.4476 |  | 0 | 16777.8525
| EHV OHL Support - Poles |  | 2475 | 2475 | C1 | 227 | 1183 | 191 | 437 | 437 | 2475 | 120 | 1183 | 196 | 452 | 524 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 133 | 1183 | 191 | 464 | 504 | 2475 | 0 | 0 | 0 | 0 | 0 | 0 | 37 | 1183 | 191 | 491 | 573 | 2475 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | 8899.1 | C1 | 114.0865 | 114.0865 | 158.7599 | 390.5815 | 818.3612 | C1 | 13690.3754 | 134964.2845 | 31116.949 | 176542.8375 | 428821.2877 | 785135.7342 |  | 25897.6269 | 134964.2845 | 30323.1493 | 170684.1151 | 357623.8601 | 719493.0359 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 15173.4994 | 134964.2845 | 30323.1493 | 181229.8155 | 412454.0629 | 774144.8118 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372 |  | 4221.1991 | 134964.2845 | 30323.1493 | 191775.516 | 468920.9882 | 830205.1372
|  |  | 17510 | 17510 | C2 | 1603 | 8372 | 1351 | 3089 | 3095 | 17510 | 852 | 8372 | 1389 | 3203 | 3700 | 17516 | 0 | 0 | 0 | 0 | 0 | 0 | 941 | 8372 | 1351 | 3279 | 3568 | 17511 | 0 | 0 | 0 | 0 | 0 | 0 | 263 | 8371 | 1351 | 3473 | 4052 | 17510 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12713 | 12713 | 12713 | 12713 | 12713 | C2 | 162.9807 | 162.9807 | 226.7999 | 557.9736 | 1169.0875 | C2 | 138859.5223 | 1364474.0855 | 315025.0889 | 1787189.3447 | 4325623.676 | 7931171.7174 |  | 261257.998 | 1364474.0855 | 306406.6919 | 1723580.3577 | 3618325.7506 | 7274044.8838 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 153364.8011 | 1364474.0855 | 306406.6919 | 1829595.336 | 4171304.1286 | 7825145.0432 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879 |  | 42863.9136 | 1364311.1049 | 306406.6919 | 1937842.2086 | 4737142.469 | 8388566.3879
|  |  | 264 | 264 | C3 | 24 | 126 | 20 | 47 | 47 | 264 | 12 | 126 | 21 | 48 | 56 | 263 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 127 | 20 | 49 | 54 | 264 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 127 | 20 | 52 | 61 | 264 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | 19069.5 | C3 | 244.471 | 244.471 | 340.1999 | 836.9604 | 1753.6312 | C3 | 2933.6519 | 30803.3447 | 7144.1975 | 40174.097 | 98203.3483 | 179258.6395 |  | 5867.3038 | 30803.3447 | 6803.9976 | 39337.1367 | 82420.6673 | 165232.4501 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 3422.5939 | 31047.8157 | 6803.9976 | 41011.0574 | 94696.0859 | 176981.5505 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402 |  | 977.884 | 31047.8157 | 6803.9976 | 43521.9385 | 106971.5044 | 189323.1402
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | 31782.5 | C4 | 407.4516 | 407.4516 | 566.9998 | 1394.9339 | 2922.7187 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20249 | 20249 |  | 1854 | 9681 | 1562 | 3573 | 3579 |  | 984 | 9681 | 1606 | 3703 | 4280 |  | 0 | 0 | 0 | 0 | 0 |  | 1088 | 9682 | 1562 | 3792 | 4126 |  | 0 | 0 | 0 | 0 | 0 |  | 304 | 9681 | 1562 | 4016 | 4686 | [22 empty] | 155483.5496 | 1530241.7148 | 353286.2354 | 2003906.2793 | 4852648.312 | 8895566.0911 |  | 293022.9286 | 1530241.7148 | 343533.8388 | 1933601.6095 | 4058370.2781 | 8158770.3698 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 171960.8944 | 1530486.1858 | 343533.8388 | 2051836.209 | 4678454.2775 | 8776271.4054 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653 |  | 48062.9966 | 1530323.2051 | 343533.8388 | 2173139.6631 | 5313034.9616 | 9408094.6653
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 164 | 164 | C1 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 29 | 98 | 37 | 0 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 40 | 42 | 53 | 164 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 29 | 0 | 73 | 62 | 164 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | 82002.9 | C1 | 273.0697 | 273.0697 | 380.4935 | 935.6531 | 1960.6893 | C1 | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 37288.3587 | 34619.1643 | 0 | 79826.543 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 0 | 7919.0201 | 15219.7382 | 39297.4297 | 103916.535 | 166352.723 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346 |  | 0 | 7919.0201 | 0 | 68302.6755 | 121562.739 | 197784.4346
|  |  | 280 | 280 | C2 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 187 | 85 | 8 | 280 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 254 | 20 | 280 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117147 | 117147 | 117147 | 117147 | 117147 | C2 | 390.0995 | 390.0995 | 543.5621 | 1336.6473 | 2800.9848 | C2 | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 152197.3824 | 0 | 0 | 152197.3824 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 0 | 0 | 101646.109 | 113615.0179 | 22407.8782 | 237669.0051 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745 |  | 0 | 0 | 3261.3725 | 339508.4066 | 56019.6954 | 398789.4745
|  |  | 153 | 153 | C3 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 118 | 35 | 0 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118 | 0 | 35 | 153 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 103 | 35 | 153 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | 175720.5 | C3 | 585.1493 | 585.1493 | 815.3431 | 2004.9709 | 4201.4772 | C3 | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 70173.9817 | 0 | 166384.4698 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 0 | 0 | 96210.4882 | 0 | 147051.7004 | 243262.1886 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504 |  | 0 | 0 | 12230.1468 | 206512.0032 | 147051.7004 | 365793.8504
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | 292867.5 | C4 | 975.2488 | 975.2488 | 1358.9052 | 3341.6182 | 7002.4619 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 597 | 597 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 29 | 496 | 72 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 345 | 127 | 96 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 29 | 21 | 430 | 117 | [22 empty] | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 285696.2292 | 104793.146 | 0 | 398408.3953 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 0 | 7919.0201 | 213076.3354 | 152912.4477 | 273376.1136 | 647283.9167 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595 |  | 0 | 7919.0201 | 15491.5193 | 614323.0853 | 324634.1348 | 962367.7595
| EHV OHL Conductor (Tower Lines) |  | 23.103 | 23.103 | C1 | 18.078 | 0 | 5.025 | 0 | 0 | 23.103 | 7.262 | 0 | 5.025 | 0 | 10.816 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.957 | 4.068 | 0 | 23.103 | 0 | 0 | 0 | 0 | 0 | 0 | 10.816 | 7.262 | 0.477 | 4.548 | 0 | 23.103 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | 76423.9 | C1 | 6.1139 | 6.1139 | 8.4066 | 21.3987 | 44.3259 | C1 | 44.3992 | 0 | 42.2433 | 0 | 479.4285 | 566.0711 |  | 110.5273 | 0 | 42.2433 | 0 | 0 | 152.7706 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 8.0451 | 87.0499 | 0 | 205.6223 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585 |  | 66.1281 | 44.3992 | 4.01 | 97.3213 | 0 | 211.8585
|  |  | 31.689 | 31.689 | C2 | 1.184 | 0 | 30.505 | 0 | 0 | 31.689 | 0 | 0 | 30.505 | 0 | 1.184 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 | 0 | 0 | 0 | 0 | 0 | 0 | 1.184 | 0 | 12.301 | 18.204 | 0 | 31.689 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 109177 | 109177 | 109177 | 109177 | 109177 | C2 | 8.7342 | 8.7342 | 12.0095 | 30.5696 | 63.3227 | C2 | 0 | 0 | 366.3489 | 0 | 74.974 | 441.3229 |  | 10.3412 | 0 | 366.3489 | 0 | 0 | 376.6901 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558 |  | 10.3412 | 0 | 147.7285 | 556.4883 | 0 | 714.558
|  |  | 8.297 | 8.297 | C3 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.567 | 5.73 | 0 | 8.297 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.283 | 7.014 | 0 | 8.297 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | 163765.5 | C3 | 13.1012 | 13.1012 | 18.0142 | 45.8543 | 94.984 | C3 | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 149.4639 | 0 | 0 | 149.4639 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 46.2425 | 262.7454 | 0 | 308.9878 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346 |  | 0 | 0 | 23.1122 | 321.6223 | 0 | 344.7346
|  |  | 5.911 | 5.911 | C4 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.911 | 0 | 5.911 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | 272942.5 | C4 | 21.8354 | 21.8354 | 30.0237 | 76.4239 | 158.3067 | C4 | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 177.4699 | 0 | 0 | 177.4699 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417 |  | 0 | 0 | 0 | 451.7417 | 0 | 451.7417
|  |  | 69 | 69 |  | 19.262 | 0 | 49.738 | 0 | 0 |  | 7.262 | 0 | 49.738 | 0 | 12 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 15.825 | 33.913 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 12 | 7.262 | 14.061 | 35.677 | 0 | [22 empty] | 44.3992 | 0 | 735.526 | 0 | 554.4026 | 1334.3278 |  | 120.8685 | 0 | 735.526 | 0 | 0 | 856.3945 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 202.0161 | 1358.0252 | 0 | 1680.9098 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928 |  | 76.4693 | 44.3992 | 174.8507 | 1427.1735 | 0 | 1722.8928
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 |  | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 |  | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 |  | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 |  | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 |  | 946376.7012 | 1929100.888 | 759598.3376 | 3621095.7241 | 10656838.8377 | 17913010.4886
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 93 | 93 | C1 | 47 | 40 | 6 | 0 | 0 | 93 | 47 | 40 | 6 | 0 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 44 | 13 | 3 | 0 | 93 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 60 | 16 | 2 | 3 | 93 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | 184298.1 | C1 | 2362.7016 | 2362.7016 | 3287.8781 | 8088.8436 | 16948.0533 | C1 | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 111046.9772 | 94508.0657 | 19727.2686 | 0 | 0 | 225282.3115 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 77969.1542 | 103958.8722 | 42742.4154 | 24266.5308 | 0 | 248936.9726 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149 |  | 28352.4197 | 141762.0985 | 52606.0497 | 16177.6872 | 50844.1598 | 289742.4149
|  |  | 75 | 75 | C2 | 44 | 24 | 7 | 0 | 0 | 75 | 44 | 24 | 8 | 1 | 0 | 77 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 35 | 6 | 3 | 0 | 75 | 0 | 0 | 0 | 0 | 0 | 0 | 23 | 37 | 12 | 0 | 3 | 75 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 263283 | 263283 | 263283 | 263283 | 263283 | C2 | 3375.2881 | 3375.2881 | 4696.9687 | 11555.4909 | 24211.5047 | C2 | 148512.6746 | 81006.9134 | 37575.7498 | 11555.4909 | 0 | 278650.8287 |  | 148512.6746 | 81006.9134 | 32878.781 | 0 | 0 | 262398.3691 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 104633.9299 | 118135.0821 | 28181.8123 | 34666.4726 | 0 | 285617.2969 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223 |  | 77631.6254 | 124885.6582 | 56363.6246 | 0 | 72634.514 | 331515.4223
|  |  | 52 | 52 | C3 | 16 | 32 | 3 | 1 | 0 | 52 | 16 | 32 | 3 | 1 | 0 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 32 | 4 | 0 | 1 | 52 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 31 | 6 | 0 | 4 | 52 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | 394924.5 | C3 | 5062.9321 | 5062.9321 | 7045.4531 | 17333.2363 | 36317.257 | C3 | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 81006.9134 | 162013.8269 | 21136.3592 | 17333.2363 | 0 | 281490.3359 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 75943.9814 | 162013.8269 | 28181.8123 | 0 | 36317.257 | 302456.8776 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943 |  | 55692.253 | 156950.8948 | 42272.7185 | 0 | 145269.0281 | 400184.8943
|  |  | 9 | 9 | C4 | 4 | 5 | 0 | 0 | 0 | 9 | 3 | 5 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 5 | 0 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | 658207.5 | C4 | 8438.2201 | 8438.2201 | 11742.4218 | 28888.7272 | 60528.7617 | C4 | 25314.6604 | 42191.1007 | 11742.4218 | 0 | 0 | 79248.183 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813 |  | 33752.8806 | 42191.1007 | 0 | 0 | 0 | 75943.9813
|  |  | 229 | 229 |  | 111 | 101 | 16 | 1 | 0 |  | 110 | 101 | 18 | 2 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 83 | 116 | 23 | 6 | 1 |  | 0 | 0 | 0 | 0 | 0 |  | 50 | 133 | 34 | 2 | 10 | [22 empty] | 365881.2257 | 379719.9067 | 90181.7994 | 28888.7272 | 0 | 864671.6591 |  | 374319.4459 | 379719.9067 | 73742.4089 | 17333.2363 | 0 | 845114.9978 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 292299.946 | 426298.882 | 99106.04 | 58933.0034 | 36317.257 | 912955.1284 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129 |  | 195429.1787 | 465789.7523 | 151242.3928 | 16177.6872 | 268747.7019 | 1097386.7129
| 132kV Transformer |  | 54 | 54 | C1 | 29 | 15 | 3 | 5 | 2 | 54 | 29 | 15 | 3 | 5 | 2 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 20 | 5 | 1 | 6 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 27 | 5 | 0 | 7 | 54 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | 894501.3 | C1 | 11467.5067 | 11467.5067 | 15957.9032 | 39259.6621 | 82258.3395 | C1 | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 332557.6933 | 172012.6 | 47873.7096 | 196298.3103 | 164516.6791 | 913258.9923 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 252285.1467 | 229350.1333 | 79789.516 | 39259.6621 | 493550.0373 | 1094234.4953 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728 |  | 172012.6 | 309622.68 | 79789.516 | 0 | 575808.3768 | 1137233.1728
|  |  | 56 | 56 | C2 | 25 | 17 | 6 | 3 | 5 | 56 | 24 | 17 | 6 | 3 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 18 | 8 | 0 | 8 | 56 | 0 | 0 | 0 | 0 | 0 | 0 | 21 | 12 | 15 | 0 | 8 | 56 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 1277859 | 1277859 | 1277859 | 1277859 | 1277859 | C2 | 16382.1524 | 16382.1524 | 22797.0046 | 56085.2315 | 117511.9136 | C2 | 393171.6571 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1564265.5377 |  | 409553.8095 | 278496.5905 | 136782.0274 | 168255.6945 | 587559.5682 | 1580647.69 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 360407.3524 | 294878.7428 | 182376.0365 | 0 | 940095.3091 | 1777757.4408 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061 |  | 344025.2 | 196585.8286 | 341955.0684 | 0 | 940095.3091 | 1822661.4061
|  |  | 11 | 11 | C3 | 5 | 0 | 3 | 0 | 3 | 11 | 5 | 0 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 3 | 0 | 3 | 11 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 3 | 2 | 1 | 3 | 11 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | 1916788.5 | C3 | 24573.2286 | 24573.2286 | 34195.5068 | 84127.8473 | 176267.8705 | C3 | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 122866.1429 | 0 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 98292.9143 | 24573.2286 | 102586.5205 | 0 | 528803.6114 | 754256.2748 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152 |  | 49146.4571 | 73719.6857 | 68391.0137 | 84127.8473 | 528803.6114 | 804188.6152
|  |  | 10 | 10 | C4 | 4 | 2 | 1 | 3 | 0 | 10 | 4 | 2 | 1 | 3 | 0 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 2 | 1 | 1 | 2 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 1 | 2 | 0 | 3 | 10 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | 3194647.5 | C4 | 40955.3809 | 40955.3809 | 56992.5114 | 140213.0788 | 293779.7841 | C4 | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 420639.2363 | 0 | 723364.0334 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 163821.5238 | 81910.7619 | 56992.5114 | 140213.0788 | 587559.5682 | 1030497.4441 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799 |  | 163821.5238 | 40955.3809 | 113985.0228 | 0 | 881339.3523 | 1200101.2799
|  |  | 131 | 131 |  | 63 | 34 | 13 | 11 | 10 |  | 62 | 34 | 13 | 11 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 52 | 41 | 17 | 2 | 19 |  | 0 | 0 | 0 | 0 | 0 |  | 42 | 43 | 24 | 1 | 21 | [22 empty] | 1012417.0171 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3955144.8381 |  | 1028799.1695 | 532419.9524 | 344234.7689 | 785193.2411 | 1280879.8587 | 3971526.9905 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 874806.9371 | 630712.8666 | 421744.5844 | 179472.7408 | 2550008.526 | 4656745.6549 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739 |  | 729005.7809 | 620883.5752 | 604120.6208 | 84127.8473 | 2926046.6496 | 4964184.4739
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 15.74 | 15.74 | C1 | 9.624 | 5.906 | 0.21 | 0 | 0 | 15.74 | 9.624 | 5.906 | 0.21 | 0.372 | 0 | 16.112 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 5.389 | 0.727 | 0 | 0 | 15.74 | 0 | 0 | 0 | 0 | 0 | 0 | 9.624 | 4.667 | 1.449 | 0 | 0 | 15.74 |  |  | C1 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C1 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | 59817.8 | C1 | 216.5404 | 216.5404 | 7338.4477 | 17913.0384 | 37533.2768 | C1 | 2083.9852 | 1278.8878 | 1541.074 | 6663.6503 | 0 | 11567.5973 |  | 2083.9852 | 1278.8878 | 1541.074 | 0 | 0 | 4903.947 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1166.9364 | 5335.0515 | 0 | 0 | 8585.973 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901 |  | 2083.9852 | 1010.5942 | 10633.4107 | 0 | 0 | 13727.9901
|  |  | 24.539 | 24.539 | C2 | 6.987 | 13.688 | 3.864 | 0 | 0 | 24.539 | 6.988 | 13.688 | 3.864 | 0.96 | 0 | 25.5 | 0 | 0 | 0 | 0 | 0 | 0 | 6.84 | 13.367 | 4.332 | 0 | 0 | 24.539 | 0 | 0 | 0 | 0 | 0 | 0 | 4.69 | 13.935 | 5.914 | 0 | 0 | 24.539 |  |  | C2 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C2 | 85454 | 85454 | 85454 | 85454 | 85454 | C2 | 309.3435 | 309.3435 | 10483.4967 | 25590.0548 | 53618.9668 | C2 | 2161.6922 | 4234.2936 | 40508.2313 | 24566.4526 | 0 | 71470.6698 |  | 2161.3829 | 4234.2936 | 40508.2313 | 0 | 0 | 46903.9078 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 2115.9094 | 4134.9943 | 45414.5078 | 0 | 0 | 51665.4115 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219 |  | 1450.8209 | 4310.7014 | 61999.3996 | 0 | 0 | 67760.9219
|  |  | 14.188 | 14.188 | C3 | 10.193 | 3.954 | 0.041 | 0 | 0 | 14.188 | 10.193 | 3.954 | 0.041 | 0.977 | 0 | 15.165 | 0 | 0 | 0 | 0 | 0 | 0 | 10.023 | 4.114 | 0.051 | 0 | 0 | 14.188 | 0 | 0 | 0 | 0 | 0 | 0 | 9.73 | 2.133 | 2.325 | 0 | 0 | 14.188 |  |  | C3 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C3 | 128181 | 128181 | 128181 | 128181 | 128181 | C3 | 464.0152 | 464.0152 | 15725.2451 | 38385.0823 | 80428.4503 | C3 | 4729.7071 | 1834.7162 | 644.735 | 37502.2254 | 0 | 44711.3837 |  | 4729.7071 | 1834.7162 | 644.735 | 0 | 0 | 7209.1584 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4650.8246 | 1908.9586 | 801.9875 | 0 | 0 | 7361.7707 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074 |  | 4514.8681 | 989.7445 | 36561.1948 | 0 | 0 | 42065.8074
|  |  | 0.708 | 0.708 | C4 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.708 | 0 | 0 | 0 | 0.708 |  |  | C4 | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746 | C4 | 213635 | 213635 | 213635 | 213635 | 213635 | C4 | 773.3587 | 773.3587 | 26208.7418 | 63975.1371 | 134047.4171 | C4 | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538 |  | 0 | 547.538 | 0 | 0 | 0 | 547.538
|  |  | 55.175 | 55.175 |  | 26.804 | 24.256 | 4.115 | 0 | 0 |  | 26.805 | 24.256 | 4.115 | 2.309 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 26.487 | 23.578 | 5.11 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 24.044 | 21.443 | 9.688 | 0 | 0 | [22 empty] | 8975.3845 | 7895.4355 | 42694.0404 | 68732.3283 | 0 | 128297.1887 |  | 8975.0752 | 7895.4355 | 42694.0404 | 0 | 0 | 59564.5511 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8850.7191 | 7758.4273 | 51551.5468 | 0 | 0 | 68160.6932 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573 |  | 8049.6742 | 6858.578 | 109194.0051 | 0 | 0 | 124102.2573
| 132kV UG Cable (Non Pressurised) |  | 8.145 | 8.145 | C1 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 8.145 | 0 | 0 | 0 | 0 | 8.145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | 317053.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 25.492 | 25.492 | C2 | 25.492 | 0 | 0 | 0 | 0 | 25.492 | 23.182 | 0 | 0 | 0 | 0 | 23.182 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 452934 | 452934 | 452934 | 452934 | 452934 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 5.672 | 5.672 | C3 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 5.672 | 0 | 0 | 0 | 0 | 5.672 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 679401 | 679401 | 679401 | 679401 | 679401 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1132335 | 1132335 | 1132335 | 1132335 | 1132335 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 39.309 | 39.309 |  | 39.309 | 0 | 0 | 0 | 0 |  | 36.999 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 704 | 704 | C1 | 74 | 400 | 193 | 37 | 0 | 704 | 70 | 400 | 193 | 41 | 0 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 72 | 364 | 231 | 36 | 1 | 704 | 0 | 0 | 0 | 0 | 0 | 0 | 66 | 368 | 233 | 32 | 5 | 704 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | 646735.6 | C1 | 342.7699 | 342.7699 | 342.7699 | 17358.3835 | 59473.8058 | C1 | 23993.8908 | 137107.9472 | 66154.5845 | 711693.7237 | 0 | 938950.1461 |  | 25364.9702 | 137107.9472 | 66154.5845 | 642260.1896 | 0 | 870887.6916 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 24679.4305 | 124768.232 | 79179.8395 | 624901.8061 | 59473.8058 | 913003.1139 |  | 22622.8113 | 126139.3114 | 79865.3792 | 555468.2721 | 297369.0289 | 1081464.803 |  | 22622.8113 | 126139.3114 | 79865.3792 | 555468.2721 | 297369.0289 | 1081464.803
|  |  | 1006 | 1006 | C2 | 165 | 489 | 230 | 122 | 0 | 1006 | 155 | 489 | 230 | 132 | 0 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 480 | 236 | 112 | 13 | 1006 | 0 | 0 | 0 | 0 | 0 | 0 | 164 | 470 | 247 | 102 | 23 | 1006 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 923908 | 923908 | 923908 | 923908 | 923908 | C2 | 489.6712 | 489.6712 | 489.6712 | 24797.6907 | 84962.5797 | C2 | 75899.0422 | 239449.2364 | 112624.3852 | 3273295.175 | 0 | 3701267.8388 |  | 80795.7546 | 239449.2364 | 112624.3852 | 3025318.2678 | 0 | 3458187.644 |  | 80795.7546 | 235042.1952 | 115562.4126 | 2777341.3606 | 1104513.5358 | 4313255.2589 |  | 80795.7546 | 235042.1952 | 115562.4126 | 2777341.3606 | 1104513.5358 | 4313255.2589 |  | 80306.0834 | 230145.4828 | 120948.7963 | 2529364.4534 | 1954139.3326 | 4914904.1485 |  | 80306.0834 | 230145.4828 | 120948.7963 | 2529364.4534 | 1954139.3326 | 4914904.1485
|  |  | 668 | 668 | C3 | 59 | 354 | 168 | 87 | 0 | 668 | 49 | 354 | 168 | 97 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 354 | 169 | 87 | 1 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 57 | 350 | 168 | 88 | 5 | 668 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1385862 | 1385862 | 1385862 | 1385862 | 1385862 | C3 | 734.5069 | 734.5069 | 734.5069 | 37196.5361 | 127443.8695 | C3 | 35990.8361 | 260015.4284 | 123397.1525 | 3608063.9998 | 0 | 4027467.4168 |  | 43335.9047 | 260015.4284 | 123397.1525 | 3236098.639 | 0 | 3662847.1246 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 260015.4284 | 124131.6593 | 3236098.639 | 127443.8695 | 3789556.4873 |  | 41866.891 | 257077.401 | 123397.1525 | 3273295.175 | 637219.3476 | 4332855.9671 |  | 41866.891 | 257077.401 | 123397.1525 | 3273295.175 | 637219.3476 | 4332855.9671
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 2309770 | 2309770 | 2309770 | 2309770 | 2309770 | C4 | 1224.1781 | 1224.1781 | 1224.1781 | 61994.2268 | 212406.4492 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2378 | 2378 |  | 298 | 1243 | 591 | 246 | 0 |  | 274 | 1243 | 591 | 270 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 294 | 1198 | 636 | 235 | 15 |  | 0 | 0 | 0 | 0 | 0 |  | 287 | 1188 | 648 | 222 | 33 | [22 empty] | 135883.7691 | 636572.612 | 302176.1222 | 7593052.8985 | 0 | 8667685.4018 |  | 149496.6296 | 636572.612 | 302176.1222 | 6903677.0964 | 0 | 7991922.4602 |  | 147342.0761 | 619825.8556 | 318873.9115 | 6638341.8057 | 1291431.2111 | 9015814.8601 |  | 147342.0761 | 619825.8556 | 318873.9115 | 6638341.8057 | 1291431.2111 | 9015814.8601 |  | 144795.7857 | 613362.1952 | 324211.328 | 6358127.9006 | 2888727.7091 | 10329224.9186 |  | 144795.7857 | 613362.1952 | 324211.328 | 6358127.9006 | 2888727.7091 | 10329224.9186
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1291 | 1291 | C1 | 12 | 18 | 1257 | 2 | 2 | 1291 | 0 | 18 | 1257 | 2 | 14 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 14 | 1130 | 131 | 4 | 1291 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 0 | 21 | 1123 | 135 | 1291 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | 312988.9 | C1 | 25.0391 | 25.0391 | 34.4288 | 81.3771 | 172.1439 | C1 | 0 | 450.704 | 43276.9752 | 162.7542 | 2410.0145 | 46300.448 |  | 300.4693 | 450.704 | 43276.9752 | 162.7542 | 344.2878 | 44535.1906 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 300.4693 | 350.5476 | 38904.5203 | 10660.4019 | 688.5756 | 50904.5147 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985 |  | 300.4693 | 0 | 723.0044 | 91386.499 | 23239.4258 | 115649.3985
|  |  | 2037 | 2037 | C2 | 79 | 9 | 1949 | 0 | 0 | 2037 | 6 | 9 | 1949 | 0 | 70 | 2034 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 4 | 1621 | 333 | 0 | 2037 | 0 | 0 | 0 | 0 | 0 | 0 | 79 | 0 | 10 | 1615 | 333 | 2037 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 447127 | 447127 | 447127 | 447127 | 447127 | C2 | 35.7702 | 35.7702 | 49.184 | 116.253 | 245.9199 | C2 | 214.621 | 321.9314 | 95859.5575 | 0 | 17214.3895 | 113610.4994 |  | 2825.8426 | 321.9314 | 95859.5575 | 0 | 0 | 99007.3316 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 2825.8426 | 143.0806 | 79727.2154 | 38712.2557 | 0 | 121408.3943 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197 |  | 2825.8426 | 0 | 491.8397 | 187748.6273 | 81891.3101 | 272957.6197
|  |  | 1379 | 1379 | C3 | 201 | 71 | 1060 | 47 | 0 | 1379 | 128 | 71 | 1060 | 47 | 70 | 1376 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 28 | 927 | 174 | 49 | 1379 | 0 | 0 | 0 | 0 | 0 | 0 | 201 | 20 | 60 | 875 | 223 | 1379 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | 670690.5 | C3 | 53.6552 | 53.6552 | 73.776 | 174.3795 | 368.8798 | C3 | 6867.8707 | 3809.522 | 78202.5123 | 8195.8379 | 25821.5842 | 122897.3272 |  | 10784.7032 | 3809.522 | 78202.5123 | 8195.8379 | 0 | 100992.5755 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 10784.7032 | 1502.3467 | 68390.3103 | 30342.0382 | 18075.109 | 129094.5074 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439 |  | 10784.7032 | 1073.1048 | 4426.5573 | 152582.0887 | 82260.1898 | 251126.6439
|  |  | 13 | 13 | C4 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 13 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | 1117817.5 | C4 | 89.4254 | 89.4254 | 122.9599 | 290.6325 | 614.7996 | C4 | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 1598.479 | 0 | 0 | 1598.479 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231 |  | 0 | 0 | 0 | 3778.2231 | 0 | 3778.2231
|  |  | 4720 | 4720 |  | 292 | 98 | 4279 | 49 | 2 |  | 134 | 98 | 4279 | 49 | 154 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 46 | 3691 | 638 | 53 |  | 0 | 0 | 0 | 0 | 0 |  | 292 | 20 | 91 | 3626 | 691 | [22 empty] | 7082.4917 | 4582.1575 | 218937.5241 | 8358.5921 | 45445.9883 | 284406.7537 |  | 13911.0152 | 4582.1575 | 218937.5241 | 8358.5921 | 344.2878 | 246133.5767 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 13911.0152 | 1995.9749 | 188620.5249 | 79714.6958 | 18763.6846 | 303005.8955 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853 |  | 13911.0152 | 1073.1048 | 5641.4014 | 435495.4382 | 187390.9257 | 643511.8853
| 132kV OHL Conductor (Tower Lines) |  | 293.476 | 293.476 | C1 | 68.312 | 109.186 | 115.978 | 0 | 0 | 293.476 | 65.824 | 109.186 | 116.466 | 0 | 1.999 | 293.475 | 0 | 0 | 0 | 0 | 0 | 0 | 43.204 | 134.058 | 102.342 | 13.872 | 0 | 293.476 | 0 | 0 | 0 | 0 | 0 | 0 | 28.54 | 142.817 | 66.759 | 41.488 | 13.872 | 293.476 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C1 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | 318709.3 | C1 | 25.4967 | 25.4967 | 35.058 | 89.2386 | 184.8514 | C1 | 1678.2977 | 2783.8875 | 4083.0677 | 0 | 369.5179 | 8914.7708 |  | 1741.7336 | 2783.8875 | 4065.9594 | 0 | 0 | 8591.5805 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 1101.5613 | 3418.0425 | 3587.9082 | 1237.9179 | 0 | 9345.4299 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739 |  | 727.6771 | 3641.3685 | 2340.4386 | 3702.3312 | 2564.2585 | 12976.0739
|  |  | 461.16 | 461.16 | C2 | 54.353 | 142.746 | 264.061 | 0 | 0 | 461.16 | 48.435 | 142.746 | 269.241 | 0.738 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 41.466 | 140.584 | 271.178 | 7.932 | 0 | 461.16 | 0 | 0 | 0 | 0 | 0 | 0 | 28.578 | 134.123 | 219.149 | 52.858 | 26.452 | 461.16 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C2 | 455299 | 455299 | 455299 | 455299 | 455299 | C2 | 36.4239 | 36.4239 | 50.0829 | 127.4837 | 264.0734 | C2 | 1764.1926 | 5199.3689 | 13484.3674 | 94.083 | 0 | 20542.0118 |  | 1979.7493 | 5199.3689 | 13224.938 | 0 | 0 | 20404.0562 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1510.3543 | 5120.6204 | 13581.3779 | 1011.2009 | 0 | 21223.5534 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628 |  | 1040.9228 | 4885.2854 | 10975.6153 | 6738.5345 | 6985.2701 | 30625.628
|  |  | 331.02 | 331.02 | C3 | 102.109 | 137.085 | 91.826 | 0 | 0 | 331.02 | 72.515 | 137.085 | 106.433 | 13.017 | 1.971 | 331.021 | 0 | 0 | 0 | 0 | 0 | 0 | 74.555 | 139.56 | 82.502 | 34.403 | 0 | 331.02 | 0 | 0 | 0 | 0 | 0 | 0 | 50.473 | 97.971 | 117.519 | 23.953 | 41.104 | 331.02 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C3 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | 682948.5 | C3 | 54.6359 | 54.6359 | 75.1243 | 191.2256 | 396.1101 | C3 | 3961.9208 | 7489.7596 | 7995.7083 | 2489.1834 | 780.7331 | 22717.3052 |  | 5578.8151 | 7489.7596 | 6898.3672 | 0 | 0 | 19966.9419 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 4073.378 | 7624.9834 | 6197.9079 | 6578.7336 | 0 | 24475.003 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424 |  | 2757.6368 | 5352.7318 | 8828.5367 | 4580.4263 | 16281.7108 | 37801.0424
|  |  | 3.344 | 3.344 | C4 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.344 | 0 | 0 | 3.344 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058 | C4 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | 1138247.5 | C4 | 91.0598 | 91.0598 | 125.2072 | 318.7093 | 660.1836 | C4 | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693 |  | 0 | 0 | 418.693 | 0 | 0 | 418.693
|  |  | 1089 | 1089 |  | 224.774 | 389.017 | 475.209 | 0 | 0 |  | 186.774 | 389.017 | 495.484 | 13.755 | 3.97 |  | 0 | 0 | 0 | 0 | 0 |  | 159.225 | 414.202 | 459.366 | 56.207 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 107.591 | 374.911 | 406.771 | 118.299 | 81.428 | [22 empty] | 7404.4111 | 15473.016 | 25981.8364 | 2583.2664 | 1150.251 | 52592.7808 |  | 9300.298 | 15473.016 | 24607.9576 | 0 | 0 | 49381.2715 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 6685.2936 | 16163.6463 | 23785.887 | 8827.8524 | 0 | 55462.6793 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373 |  | 4526.2366 | 13879.3857 | 22563.2835 | 15021.292 | 25831.2394 | 81821.4373
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 |  | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 |  | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 |  | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 |  | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 |  | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 332299.578 | 332299.578 |  | 42915.51 | 218898.204 | 23270.29 | 24840.303 | 22375.271 |  | 30404.083 | 218961.099 | 23937.221 | 26713.424 | 31755.268 |  | 0 | 0 | 0 | 0 | 0 |  | 27785.972 | 218257.399 | 21962.499 | 28848.12 | 29340.749 |  | 0 | 0 | 0 | 0 | 0 |  | 15031.894 | 219580.973 | 17776.627 | 35688.068 | 38116.177 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 |  | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 |  | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 |  | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 |  | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 |  | 4880649.1992 | 21500076.5901 | 4894531.1975 | 18852090.952 | 38733097.6504 | 88860445.5892
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 768154.2767 | 4810952.9894 | 1103636.8796 | 2041300.4252 | 3974740.9766 | 12698785.5474 | LV Network | 1064191.2893 | 4810249.9986 | 1081701.4169 | 1874337.8412 | 2357999.1135 | 11188479.6596 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 763391.3709 | 4821272.2842 | 1077420.8078 | 2176617.0415 | 3825121.5471 | 12663823.0516 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543 | LV Network | 445887.981 | 4858532.7817 | 1027156.8872 | 2517499.121 | 5380082.6835 | 14229159.4543
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 3761408.3337 | 12327123.192 | 1901370.7326 | 4601034.7082 | 13462305.3313 | 36053242.2977 | HV Network | 4462910.9227 | 12315319.5392 | 1849989.8713 | 4265741.624 | 9828438.2868 | 32722400.2441 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 3441375.4843 | 12693494.4254 | 1912363.7407 | 4970105.8377 | 12645578.7174 | 35662918.2055 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961 | HV Network | 2392666.8457 | 12990596.3292 | 1890802.9411 | 5804545.9416 | 16399431.9035 | 39478043.961
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 1174486.6466 | 1675393.3543 | 1810618.0629 | 3567424.162 | 5780196.5284 | 14008118.7543 | EHV Network | 1511629.6231 | 1670721.3625 | 1670280.8536 | 3344435.2078 | 4472767.511 | 12669834.558 | EHV Network | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 | EHV Network | 1246891.6658 | 1794338.8664 | 1205751.6105 | 3476960.8987 | 7721130.0381 | 15445073.0795 | EHV Network | 946376.7012 | 1939846.5948 | 759598.3376 | 3743900.5337 | 10656838.8377 | 18046561.005 | EHV Network | 946376.7012 | 1929100.888 | 759598.3376 | 3621095.7241 | 10656838.8377 | 17913010.4886
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1537644.2992 | 1576663.0801 | 1024206.0913 | 8486809.0536 | 1327476.098 | 13952798.6221 | 132kV Network | 1584801.6333 | 1576663.0801 | 1006392.822 | 7714562.166 | 1281224.1465 | 13163643.8478 | 132kV Network | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 | 132kV Network | 1343895.9872 | 1702755.6527 | 1103682.4945 | 6965290.0982 | 3896520.6787 | 15012144.9113 | 132kV Network | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853 | 132kV Network | 1095717.6713 | 1721846.5912 | 1216973.0316 | 6908950.1653 | 6296744.2258 | 17240231.6853
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 7241693.5561 | 20390132.6157 | 5839831.7664 | 18696568.349 | 24544718.9343 | 76712945.2216 | Total | 8623533.4683 | 20372953.9805 | 5608364.9637 | 17199076.8391 | 17940429.0578 | 69744358.3095 | Total | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 | Total | 6795554.5081 | 21011861.2287 | 5299218.6536 | 17588973.8762 | 28088350.9813 | 78783959.2479 | Total | 4880649.1992 | 21510822.2969 | 4894531.1975 | 18974895.7616 | 38733097.6504 | 88993996.1056 | Total | 4880649.1992 | 21500076.5901 | 4894531.1975 | 18852090.952 | 38733097.6504 | 88860445.5892
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality
Note on AK9: Forecast without any investment in RIIO-ED1 period

## SWALES - Ave. Cons. of Failure
Secondary deliverables RIIO-ED1 - Average Consequence of Asset Failure
SWALES
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period |  |  |  |  | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure
| LV Network | [5 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other |  |  |  |  | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 | LV UGB |  |  |  |  | 0
| LV OHL Support | 344 | 1405 | 278 | 2688 | 4715 | LV OHL Support | 344 | 1405 | 278 | 2688 | 4715
| LV Switchgear (at s/s) | 1107 | 675 | 491 | 3823 | 6096 | LV Switchgear (at s/s) | 1107 | 675 | 491 | 3823 | 6096
| LV UGB and LV Pillar OD (not at s/s) | 1273 | 782 | 494 | 2670 | 5219 | LV UGB and LV Pillar OD (not at s/s) | 1273 | 782 | 494 | 2670 | 5219
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| HV Network | [5 empty] | HV Network
| HV Switchgear (GM) - Primary | 37966 | 1198 | 1888 | 11397 | 52450 | HV Switchgear (GM) - Primary | 37966 | 1198 | 1888 | 11397 | 52450
| HV Switchgear (GM) - Distribution | 5682 | 1668 | 2423 | 4920 | 14693 | HV Switchgear (GM) - Distribution | 5682 | 1668 | 2423 | 4920 | 14693
| HV Transformer (GM) | 5679 | 1241 | 3666 | 4703 | 15289 | HV Transformer (GM) | 5679 | 1241 | 3666 | 4703 | 15289
| HV UG Cable | 19048 | 142 | 1102 | 10500 | 30792 | HV UG Cable | 19048 | 142 | 1102 | 10500 | 30792
| HV OHL Support - Poles | 1964 | 1475 | 478 | 2920 | 6837 | HV OHL Support - Poles | 1964 | 1475 | 478 | 2920 | 6837
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| EHV Network | [5 empty] | EHV Network
| EHV Switchgear (GM) | 101815 | 752 | 3572 | 18941 | 125080 | EHV Switchgear (GM) | 101815 | 752 | 3572 | 18941 | 125080
| EHV Transformer | 173351 | 951 | 18221 | 101562 | 294085 | EHV Transformer | 173351 | 951 | 18221 | 101562 | 294085
| EHV UG Cable (Gas) | 1726 | 7 | 390 | 6109 | 8232 | EHV UG Cable (Gas) | 1726 | 7 | 390 | 6109 | 8232
| EHV UG Cable (Oil) | 44728 | 708 | 3833 | 25805 | 75074 | EHV UG Cable (Oil) | 44728 | 708 | 3833 | 25805 | 75074
| EHV UG Cable (Non Pressurised) | 36497 | 142 | 1602 | 15000 | 53241 | EHV UG Cable (Non Pressurised) | 36497 | 142 | 1602 | 15000 | 53241
| EHV OHL Support - Towers | 175157 | 25436 | 2484 | 82888 | 285965 | EHV OHL Support - Towers | 175157 | 25436 | 2484 | 82888 | 285965
| EHV OHL Support - Poles | 6668 | 1467 | 478 | 4100 | 12713 | EHV OHL Support - Poles | 6668 | 1467 | 478 | 4100 | 12713
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| EHV OHL Fittings | 99549 | 12718 | 880 | 4000 | 117147 | EHV OHL Fittings | 99549 | 12718 | 880 | 4000 | 117147
| EHV OHL Conductor (Tower Lines) | 91579 | 12718 | 880 | 4000 | 109177 | EHV OHL Conductor (Tower Lines) | 91579 | 12718 | 880 | 4000 | 109177
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| 132kV Network | [5 empty] | 132kV Network
| 132kV CBs | 231710 | 796 | 5943 | 24834 | 263283 | 132kV CBs | 231710 | 796 | 5943 | 24834 | 263283
| 132kV Transformer | 949275 | 1277 | 52400 | 274907 | 1277859 | 132kV Transformer | 949275 | 1277 | 52400 | 274907 | 1277859
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) |  |  |  |  | 0
| 132kV UG Cable (Oil) | 48235 | 708 | 10706 | 25805 | 85454 | 132kV UG Cable (Oil) | 48235 | 708 | 10706 | 25805 | 85454
| 132kV UG Cable (Non Pressurised) | 224723 | 710 | 2501 | 225000 | 452934 | 132kV UG Cable (Non Pressurised) | 224723 | 710 | 2501 | 225000 | 452934
| 132kV OHL Support - Tower | 757448 | 25436 | 3901 | 137123 | 923908 | 132kV OHL Support - Tower | 757448 | 25436 | 3901 | 137123 | 923908
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| 132kV OHL Fittings | 429529 | 12718 | 880 | 4000 | 447127 | 132kV OHL Fittings | 429529 | 12718 | 880 | 4000 | 447127
| 132kV OHL Conductor (Tower Lines) | 437701 | 12718 | 880 | 4000 | 455299 | 132kV OHL Conductor (Tower Lines) | 437701 | 12718 | 880 | 4000 | 455299
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| Other | [5 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | Submarine Cables |  |  |  |  | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]

## SWALES - Probs. of Failure
Probabilities of Asset Failure
SWALES
Price base (2012/13)
Average Probabilities of Asset Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other
| LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | LV OHL Support | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV Switchgear (at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV UGB and LV Pillar OD (not at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | [10 empty] | HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Primary | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Distribution | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | HV Transformer (GM) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| HV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | [10 empty] | EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Switchgear (GM) | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV UG Cable (Gas) | 0.13141 | 0.13141 | 0.13141 | 0.13141 | 0.13141 | 8.7749 | 8.7749 | 13.1646 | 13.1646 | 34.6807 | EHV UG Cable (Gas) | 0.13141 | 0.13141 | 4.4531 | 10.8699 | 22.7759
| EHV UG Cable (Oil) | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.24174 | 0.24174 | 0.36267 | 0.36267 | 0.95542 | EHV UG Cable (Oil) | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Towers | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines)
| [Please insert new asset category as required] | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402 | EHV OHL Fittings | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391
| [Please insert new asset category as required] | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 0.00022516 | 0.00022516 | 0.0003378 | 0.0003378 | 0.0008899 | EHV OHL Conductor (Tower Lines) | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | [10 empty] | 132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV CBs | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.0036203 | 0.24174 | 0.24174 | 0.36267 | 0.36267 | 0.95542 | 132kV UG Cable (Oil) | 0.00362 | 0.00362 | 0.12268 | 0.29946 | 0.62746
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | 132kV OHL Support - Tower | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines)
| [Please insert new asset category as required] | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005 | 132kV OHL Fittings | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055
| [Please insert new asset category as required] | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 8.1493e-05 | 0.00022516 | 0.00022516 | 0.0003378 | 0.0003378 | 0.0008899 | 132kV OHL Conductor (Tower Lines) | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00058
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Other | [10 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 11188479.6596 | 12663823.0516 | 10075508.5923 | 14229159.4543 | 8989269.1461
HV Network | 32722400.2441 | 35662918.2055 | 28224060.6982 | 39478043.961 | 24394207.4593
EHV Network | 12669834.558 | 15445073.0795 | 12339982.0387 | 18046561.005 | 11281950.5927
132kV Network | 13163643.8478 | 15012144.9113 | 11333872.4738 | 17240231.6853 | 9101385.91
Other | 0 | 0 | 0 | 0 | 0
Total | 69744358.3095 | 78783959.2479 | 61973423.8031 | 88993996.1056 | 53766813.1081
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary Deliverables Target)
LV Network |  | 1475343.392 | -2588314.4593 | 3040679.7947 | -5239890.3082
HV Network |  | 2940517.9614 | -7438857.5072 | 6755643.7169 | -15083836.5017
EHV Network |  | 2775238.5215 | -3105091.0408 | 5376726.447 | -6764610.4123
132kV Network |  | 1848501.0635 | -3678272.4375 | 4076587.8375 | -8138845.7753
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 9039600.9384 | -16810535.4448 | 19249637.7961 | -35227182.9975