## EMID - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EMID | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | C1 | 42.9585 | 42.9585 | 59.7801 | 147.071 | 308.1488 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 11440 | 0 | -572 | -1716 | -9152 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 22524 | 0 | -1126 | -3379 | -18019 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4787 | 4787 | 4787 | 4787 | 4787 | C2 | 61.3693 | 61.3693 | 85.4001 | 210.1014 | 440.2125 | C2 | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | C3 | 92.054 | 92.054 | 128.1001 | 315.1521 | 660.3188 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | C4 | 153.4233 | 153.4233 | 213.5002 | 525.2536 | 1100.5313 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 11440 | 0 | -572 | -1716 | -9152 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 22524 | 0 | -1126 | -3379 | -18019 |  | 20323 | 38701 | 21750 | 7054 | 27617 | [22 empty] | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105
| LV Switchgear (at s/s) |  | 8 | 8 | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | C1 | 95.4965 | 95.4965 | 132.8107 | 326.7848 | 684.7228 | C1 | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861
|  |  | 17231 | 17231 | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 598 | -107 | -316 | -109 | -66 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 1190 | -207 | -96 | -619 | -268 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 7098 | 7098 | 7098 | 7098 | 7098 | C2 | 136.4236 | 136.4236 | 189.7295 | 466.8355 | 978.1754 | C2 | 1236133.8772 | 393036.2764 | 931572.0414 | 63489.6226 | 59668.6982 | 2683900.5157 |  | 1302572.1509 | 384441.5921 | 910701.792 | 21941.2666 | 17607.1568 | 2637263.9584 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 1173106.1924 | 430552.7554 | 1028144.3773 | 26609.6212 | 0 | 2658412.9463 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516 |  | 1050597.8356 | 544466.428 | 1036871.9361 | 34545.824 | 0 | 2666482.0237
|  |  | 1354 | 1354 | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 78 | -5 | -36 | -14 | -23 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 161 | -17 | -21 | -74 | -49 | 0 | 387 | 206 | 618 | 94 | 49 | 1354 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 10647 | 10647 | 10647 | 10647 | 10647 | C3 | 204.6353 | 204.6353 | 284.5943 | 700.2532 | 1467.2631 | C3 | 96997.1512 | 48089.3049 | 169049.0201 | 18906.8361 | 16139.8938 | 349182.2061 |  | 105182.5648 | 47475.3989 | 166772.2657 | 13304.8106 | 4401.7892 | 337136.8291 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 109684.5422 | 38880.7146 | 176163.8779 | 6302.2787 | 0 | 331031.4134 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305 |  | 112140.1663 | 38676.0793 | 169902.8031 | 14005.0638 | 0 | 334724.1125
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 17745 | 17745 | 17745 | 17745 | 17745 | C4 | 341.0589 | 341.0589 | 474.3238 | 1167.0886 | 2445.4384 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18593 | 18593 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 676 | -112 | -352 | -123 | -89 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 1351 | -224 | -117 | -693 | -317 |  | 6905 | 4404 | 6180 | 787 | 317 | [22 empty] | 1333799.5038 | 441125.5813 | 1100753.8722 | 82396.4587 | 75808.5919 | 3033884.0079 |  | 1408423.1911 | 431916.991 | 1077606.8683 | 35246.0772 | 22008.946 | 2975202.0737 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 1283459.2101 | 469433.47 | 1204441.0658 | 32911.8999 | 0 | 2990245.6458 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682 |  | 1163406.4773 | 583142.5072 | 1206907.5498 | 48550.8878 | 0 | 3002007.4222
| LV UGB and LV Pillar OD (not at s/s) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | C1 | 77.7776 | 77.7776 | 108.1683 | 266.1515 | 557.6757 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27987 | 27987 | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 731 | 0 | 0 | 0 | -731 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 1456 | 0 | 0 | 0 | -1456 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5781 | 5781 | 5781 | 5781 | 5781 | C2 | 111.1108 | 111.1108 | 154.5261 | 380.2164 | 796.6796 | C2 | 576776.2666 | 566331.8495 | 2504250.4628 | 216343.1145 | 658854.0375 | 4522555.7309 |  | 636331.6661 | 564554.0764 | 2496524.1563 | 216343.1145 | 361692.5429 | 4275445.5563 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 633776.1173 | 435776.636 | 2486943.5362 | 585913.4262 | 578389.3969 | 4720799.1126 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821 |  | 640998.3206 | 291554.7917 | 2031709.5572 | 1418967.4928 | 2162188.4615 | 6545418.6239
|  |  | 1022 | 1022 | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 21 | 0 | 0 | 0 | -21 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 48 | 0 | 0 | 0 | -48 | 0 | 48 | 116 | 557 | 157 | 144 | 1022 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | C3 | 166.6662 | 166.6662 | 231.7892 | 570.3246 | 1195.0194 | C3 | 14666.6282 | 39166.5641 | 152749.0795 | 9695.5174 | 22705.3689 | 238983.1581 |  | 17166.6217 | 38999.8978 | 152285.5011 | 9695.5174 | 13145.2136 | 231292.7516 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 15999.9581 | 33166.5798 | 150431.1876 | 29656.8769 | 31070.5048 | 260325.1071 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942 |  | 15999.9581 | 19333.2827 | 129106.5816 | 89540.9551 | 114721.8638 | 368702.6413
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | C4 | 277.7771 | 277.7771 | 386.3153 | 950.5409 | 1991.699 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29009 | 29009 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 752 | 0 | 0 | 0 | -752 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 1504 | 0 | 0 | 0 | -1504 |  | 4361 | 2740 | 13705 | 3889 | 4314 | [22 empty] | 591442.8949 | 605498.4136 | 2656999.5423 | 226038.632 | 681559.4064 | 4761538.8891 |  | 653498.2878 | 603553.9742 | 2648809.6574 | 226038.632 | 374837.7565 | 4506738.3079 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 649776.0754 | 468943.2158 | 2637374.7238 | 615570.303 | 609459.9017 | 4981124.2196 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764 |  | 656998.2787 | 310888.0744 | 2160816.1389 | 1508508.448 | 2276910.3254 | 6914121.2652
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 |  | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 4562727.3965 | 3313431.5131 | 5603107.0395 | 1420604.9582 | 4834619.6686 | 19734490.5759 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 |  | 4449896.867 | 3269085.4089 | 5129014.9386 | 2329182.0911 | 6502070.0923 | 21679249.3979
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 809 | 809 | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 34 | 0 | -9 | 0 | -25 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 91 | -18 | 0 | 0 | -73 | 0 | 196 | 168 | 215 | 121 | 109 | 809 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | C1 | 722.066 | 722.066 | 1004.8095 | 2472.034 | 5179.4999 | C1 | 186293.0249 | 113364.3601 | 366755.4514 | 61800.8506 | 15538.4996 | 743752.1867 |  | 197846.0807 | 111920.2281 | 356707.3569 | 61800.8506 | 0 | 728274.5164 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 192069.5528 | 120585.02 | 293404.3612 | 207650.8582 | 0 | 813709.7921 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655 |  | 207232.9386 | 108309.8982 | 216034.033 | 299116.1171 | 186461.9951 | 1017154.982
|  |  | 2623 | 2623 | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 195 | 0 | -43 | -96 | -56 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 397 | -85 | 0 | 0 | -312 | 0 | 744 | 464 | 728 | 364 | 323 | 2623 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 80462 | 80462 | 80462 | 80462 | 80462 | C2 | 1031.5228 | 1031.5228 | 1435.4421 | 3531.4772 | 7399.2855 | C2 | 926307.5103 | 340402.5372 | 1890477.2194 | 183636.8134 | 125787.8538 | 3466611.9341 |  | 989230.4036 | 338339.4915 | 1840236.7466 | 183636.8134 | 14798.571 | 3366242.026 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 1034617.4085 | 463153.7552 | 1444054.7325 | 582693.7347 | 0 | 3524519.6309 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414 |  | 1176967.5604 | 390947.1564 | 1045001.8342 | 1285457.6935 | 81392.1407 | 3979766.3853
|  |  | 880 | 880 | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 105 | 0 | -12 | -73 | -20 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 181 | -25 | 0 | -11 | -145 | 0 | 190 | 156 | 248 | 138 | 148 | 880 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 120693 | 120693 | 120693 | 120693 | 120693 | C3 | 1547.2843 | 1547.2843 | 2153.1631 | 5297.2158 | 11098.9283 | C3 | 331118.8316 | 188768.6797 | 1093806.865 | 100647.0996 | 133187.1394 | 1847528.6153 |  | 385273.7807 | 187221.3955 | 1057203.0919 | 100647.0996 | 0 | 1730345.3678 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 485847.2576 | 227450.7862 | 785904.5388 | 286049.6516 | 0 | 1785252.2342 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694 |  | 574042.4605 | 202694.2381 | 533984.4538 | 672746.4028 | 33296.7848 | 2016764.3399
|  |  | 20 | 20 | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 2 | 0 | 0 | -1 | -1 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 4 | 0 | 0 | -2 | -2 | 0 | 6 | 5 | 3 | 4 | 2 | 20 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 201155 | 201155 | 201155 | 201155 | 201155 | C4 | 2578.8071 | 2578.8071 | 3588.6052 | 8828.693 | 18498.2138 | C4 | 12894.0355 | 12894.0355 | 25120.2364 | 17657.3859 | 18498.2138 | 87063.9071 |  | 18051.6497 | 12894.0355 | 25120.2364 | 8828.693 | 0 | 64894.6145 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 20630.4568 | 12894.0355 | 25120.2364 | 0 | 0 | 58644.7287 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931 |  | 25788.071 | 12894.0355 | 10765.8156 | 17657.3859 | 0 | 67105.308
|  |  | 4332 | 4332 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 336 | 0 | -64 | -170 | -102 |  | 1255 | 768 | 1734 | 473 | 102 |  | 673 | -128 | 0 | -13 | -532 |  | 1136 | 793 | 1194 | 627 | 582 | [22 empty] | 1456613.4024 | 655429.6125 | 3376159.7722 | 363742.1495 | 293011.7066 | 6144956.6432 |  | 1590401.9147 | 650375.1506 | 3279267.4318 | 354913.4566 | 14798.571 | 5889756.5247 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1733164.6758 | 824083.5969 | 2548483.8688 | 1076394.2445 | 0 | 6182126.3859 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859 |  | 1984031.0305 | 714845.3281 | 1805786.1366 | 2274977.5994 | 301150.9207 | 7080791.0152
| HV Switchgear (GM) - Distribution |  | 9569 | 9434 | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 370 | -156 | -1 | -276 | 0 | -63 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 795 | -330 | 0 | -119 | -481 | -135 | 4321 | 2124 | 1640 | 1000 | 484 | 9569 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | C1 | 205.8277 | 205.8277 | 286.4248 | 704.6627 | 1476.4362 | C1 | 1190918.8639 | 207268.4576 | 765613.4049 | 125429.9656 | 160931.5449 | 2450162.2369 |  | 1286422.9 | 146137.6414 | 744704.3968 | 6341.9646 | 0 | 2183606.9028 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 1235171.8117 | 194507.1425 | 633858.0116 | 244517.9666 | 0 | 2308054.9323 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589 |  | 1053014.329 | 369254.8292 | 469736.6195 | 620807.8634 | 4429.3086 | 2517242.9497
|  |  | 12994 | 12774 | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 614 | -81 | 0 | -638 | 0 | -105 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 1288 | -146 | 0 | -411 | -951 | -220 | 3480 | 4503 | 2547 | 1510 | 954 | 12994 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 22936 | 22936 | 22936 | 22936 | 22936 | C2 | 294.0395 | 294.0395 | 409.1782 | 1006.661 | 2109.1946 | C2 | 1485781.6946 | 1000910.5261 | 1723049.5686 | 437897.5524 | 442930.8576 | 5090570.1993 |  | 1709839.8088 | 946219.1754 | 1613389.8003 | 18119.8987 | 0 | 4287568.6832 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1450202.9126 | 1213795.1386 | 1334739.4189 | 570776.8097 | 0 | 4569514.2798 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461 |  | 1401980.4314 | 1281130.1886 | 1042176.9773 | 1106320.483 | 6327.5837 | 4837935.6639
|  |  | 5187 | 5041 | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 483 | -10 | -41 | -515 | 0 | -83 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 860 | -18 | 0 | -616 | -372 | -146 | 1367 | 1486 | 991 | 971 | 372 | 5187 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 34404 | 34404 | 34404 | 34404 | 34404 | C3 | 441.0593 | 441.0593 | 613.7674 | 1509.9916 | 3163.7918 | C3 | 726865.6934 | 434884.4501 | 1477338.0355 | 472627.3583 | 578973.9067 | 3690689.444 |  | 978710.5423 | 426063.2645 | 1228762.2547 | 0 | 0 | 2633536.0615 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 963714.5268 | 585285.6646 | 964842.2899 | 30199.8312 | 0 | 2544042.3125 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488 |  | 982239.0166 | 647475.023 | 608243.4538 | 536047.0038 | 0 | 2774004.4972
|  |  | 143 | 140 | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 8 | -9 | 0 | 0 | 0 | -1 | 61 | 18 | 64 | 0 | 0 | 143 | 18 | -18 | 0 | -3 | 0 | -3 | 53 | 20 | 43 | 27 | 0 | 143 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 57340 | 57340 | 57340 | 57340 | 57340 | C4 | 735.0988 | 735.0988 | 1022.9456 | 2516.6526 | 5272.9864 | C4 | 38960.2364 | 14701.976 | 61376.736 | 30199.8312 | 47456.8776 | 192695.6572 |  | 52192.0148 | 13231.7784 | 55239.0624 | 0 | 0 | 120662.8556 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 50721.8172 | 6615.8892 | 65468.5184 | 0 | 0 | 122806.2248 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934 |  | 52192.0148 | 1470.1976 | 43986.6608 | 60399.6624 | 0 | 158048.5356
|  |  | 27893 | 27389 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 1475 | -256 | -42 | -1429 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 2961 | -512 | 0 | -1149 | -1804 |  | 9221 | 8133 | 5221 | 3508 | 1810 | [22 empty] | 3442526.4883 | 1657765.4098 | 4027377.745 | 1066154.7075 | 1230293.1868 | 11424117.5374 |  | 4027165.2659 | 1531651.8597 | 3642095.5142 | 24461.8633 | 0 | 9225374.5031 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 3699811.0683 | 2000203.8348 | 2998908.2388 | 845494.6075 | 0 | 9544417.7494 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472 |  | 3489425.7917 | 2299330.2385 | 2164143.7114 | 2323575.0125 | 10756.8923 | 10287231.6464
| HV Transformer (GM) |  | 3306 | 3306 | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 161 | 0 | 0 | -12 | -149 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 286 | 0 | 0 | -20 | -266 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 15848 | 15848 | 15848 | 15848 | 15848 | C1 | 304.5986 | 304.5986 | 423.617 | 1042.323 | 2184.0129 | C1 | 560461.3504 | 141333.7318 | 351178.5262 | 75047.2531 | 165984.9789 | 1294005.8404 |  | 575691.2784 | 140419.9362 | 349060.441 | 75047.2531 | 128856.7599 | 1269075.6686 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 550409.5979 | 157782.0541 | 381255.336 | 82343.5138 | 4368.0258 | 1176158.5276 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886 |  | 501064.6312 | 223575.343 | 344824.2706 | 112570.8797 | 10920.0644 | 1192955.1889
|  |  | 13028 | 13028 | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 436 | 0 | 0 | -93 | -343 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 895 | 0 | 0 | -213 | -682 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 22640 | 22640 | 22640 | 22640 | 22640 | C2 | 435.1408 | 435.1408 | 605.1672 | 1489.0328 | 3120.0184 | C2 | 3131708.3376 | 1113525.3072 | 1710202.5072 | 227822.0184 | 589683.4776 | 6772941.648 |  | 3214385.0896 | 1105692.7728 | 1701124.9992 | 227822.0184 | 424322.5024 | 6673347.3824 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2931108.4288 | 1218829.3808 | 2011575.7728 | 248668.4776 | 0 | 6410182.06 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888 |  | 2634342.4032 | 1486876.1136 | 2013996.4416 | 340988.5112 | 0 | 6476203.4696
|  |  | 3266 | 3266 | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 224 | 0 | 0 | -67 | -157 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 461 | 0 | 0 | -123 | -338 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 33960 | 33960 | 33960 | 33960 | 33960 | C3 | 652.7112 | 652.7112 | 907.7508 | 2233.5492 | 4680.0276 | C3 | 821110.6896 | 380530.6296 | 1130149.746 | 183151.0344 | 336961.9872 | 2851904.0868 |  | 855051.672 | 377919.7848 | 1124703.2412 | 183151.0344 | 262081.5456 | 2802907.278 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 875938.4304 | 358338.4488 | 1195507.8036 | 129545.8536 | 0 | 2559330.5364 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908 |  | 902046.8784 | 409249.9224 | 1059345.1836 | 198785.8788 | 4680.0276 | 2574107.8908
|  |  | 118 | 118 | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 16 | 0 | 0 | -6 | -10 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 33 | 0 | 0 | -7 | -26 | 0 | 31 | 27 | 25 | 9 | 26 | 118 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 56600 | 56600 | 56600 | 56600 | 56600 | C4 | 1087.852 | 1087.852 | 1512.918 | 3722.582 | 7800.046 | C4 | 55480.452 | 7614.964 | 78671.736 | 18612.91 | 23400.138 | 183780.2 |  | 57656.156 | 7614.964 | 78671.736 | 18612.91 | 7800.046 | 170355.812 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 67446.824 | 15229.928 | 52952.13 | 26058.074 | 0 | 161686.956 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8 |  | 69622.528 | 29372.004 | 37822.95 | 7445.164 | 0 | 144262.646
|  |  | 19718 | 19718 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 837 | 0 | 0 | -178 | -659 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 1675 | 0 | 0 | -363 | -1312 |  | 7470 | 4805 | 5334 | 791 | 1318 | [22 empty] | 4568760.8296 | 1643004.6326 | 3270202.5154 | 504633.2159 | 1116030.5817 | 11102631.7752 |  | 4702784.196 | 1631647.4578 | 3253560.4174 | 504633.2159 | 823060.8539 | 10915686.141 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 4424903.2811 | 1750179.8117 | 3641291.0424 | 486615.919 | 4368.0258 | 10307358.08 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828 |  | 4107076.4408 | 2149073.383 | 3455988.8458 | 659790.4337 | 15600.092 | 10387529.1953
| HV UG Cable |  | 3200.153 | 3200.153 | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 34503 | 34503 | 34503 | 34503 | 34503 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7275.757 | 7275.757 | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 49290 | 49290 | 49290 | 49290 | 49290 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3676.577 | 3676.577 | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 73935 | 73935 | 73935 | 73935 | 73935 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 123225 | 123225 | 123225 | 123225 | 123225 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14152.487 | 14152.487 |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | C1 | 72.5009 | 72.5009 | 100.8906 | 248.2111 | 520.0614 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 129615 | 129615 | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 11938 | 0 | -598 | -1790 | -9550 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 24132 | 0 | -1207 | -3620 | -19305 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 8079 | 8079 | 8079 | 8079 | 8079 | C2 | 103.5728 | 103.5728 | 144.1294 | 354.5873 | 742.9448 | C2 | 2343127.0019 | 5487907.3211 | 3641860.6685 | 1934273.776 | 16903480.9997 | 30310649.7672 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 2886159.0875 | 5488010.8939 | 3607846.1395 | 1683935.1352 | 14101836.008 | 27767787.2641 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362
|  |  | 18228 | 18228 | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 1680 | 0 | -83 | -252 | -1345 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 3394 | 0 | -170 | -509 | -2715 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | C3 | 155.3592 | 155.3592 | 216.194 | 531.881 | 1114.4173 | C3 | 494508.2381 | 1157581.1757 | 768137.4241 | 407952.7002 | 3565020.8147 | 6393200.3528 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944
|  |  | 253 | 253 | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 23 | 0 | -1 | -4 | -18 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 47 | 0 | -2 | -7 | -38 | 0 | 7 | 104 | 51 | 16 | 75 | 253 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | C4 | 258.9319 | 258.9319 | 360.3234 | 886.4683 | 1857.3621 | C4 | 11393.0058 | 26928.9228 | 17655.8466 | 9751.151 | 81723.9324 | 147452.8586 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 13982.3253 | 26669.9908 | 17655.8466 | 7978.2145 | 70579.7598 | 136866.137 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069
|  |  | 148096 | 148096 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 13641 | 0 | -682 | -2046 | -10913 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 27573 | 0 | -1379 | -4136 | -22058 |  | 4267 | 60541 | 29980 | 9562 | 43746 | [22 empty] | 2849028.2459 | 6672417.4195 | 4427653.9392 | 2351977.6272 | 20550225.7468 | 36851302.9787 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 3509149.3592 | 6672262.0604 | 4386505.0069 | 2047209.8343 | 17146795.4348 | 33761921.6955 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 |  | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 13367028.3844 | 11246729.3037 | 13575188.1569 | 4455714.6053 | 17151163.4605 | 59795823.9109 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 |  | 13089682.6222 | 11835666.3692 | 11812423.7007 | 7305552.8798 | 17473188.9224 | 61516514.4944
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 658 | 658 | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 42 | 0 | 0 | -33 | -9 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 81 | 0 | 0 | 0 | -81 | 0 | 274 | 205 | 49 | 13 | 117 | 658 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | C1 | 1418.4215 | 1418.4215 | 1973.8408 | 4856.0467 | 10174.5739 | C1 | 524815.9424 | 191486.8979 | 276337.7109 | 33992.3266 | 20349.1479 | 1046982.0257 |  | 547510.6859 | 185813.212 | 268442.3477 | 24280.2333 | 0 | 1026046.4789 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 536163.3141 | 224110.5916 | 102639.7212 | 301074.8927 | 81396.5916 | 1245385.1113 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395 |  | 503539.6204 | 290776.4005 | 96718.1988 | 63128.6065 | 366284.6621 | 1320447.4884
|  |  | 432 | 432 | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 45 | 0 | 0 | -43 | -2 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 125 | 0 | 0 | -20 | -105 | 0 | 165 | 91 | 21 | 49 | 106 | 432 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 158059 | 158059 | 158059 | 158059 | 158059 | C2 | 2026.3164 | 2026.3164 | 2819.7726 | 6937.2095 | 14535.1056 | C2 | 387026.4286 | 129684.2483 | 487820.6529 | 0 | 0 | 1004531.3298 |  | 431605.3889 | 121578.9828 | 448343.837 | 0 | 0 | 1001528.2088 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 453894.8691 | 162105.3104 | 222762.0322 | 339923.266 | 0 | 1178685.4778 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809 |  | 587631.7502 | 184394.7906 | 59215.2238 | 201179.0758 | 14535.1056 | 1046955.946
|  |  | 137 | 137 | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 18 | 0 | 0 | -13 | -5 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 37 | 0 | 0 | -4 | -33 | 0 | 62 | 16 | 14 | 12 | 33 | 137 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | C3 | 3039.4746 | 3039.4746 | 4229.6588 | 10405.8143 | 21802.6585 | C3 | 197565.847 | 45592.1185 | 215712.6008 | 0 | 43605.3169 | 502475.8834 |  | 227960.5927 | 45592.1185 | 198793.9655 | 0 | 0 | 472346.6768 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 243157.9656 | 54710.5423 | 148038.0594 | 41623.2571 | 0 | 487529.8243 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406 |  | 300907.9824 | 48631.5931 | 59215.2238 | 83246.5141 | 0 | 492001.3134
|  |  | 91 | 91 | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 37 | 0 | -14 | -23 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 40 | 0 | 0 | -11 | -29 | 0 | 17 | 24 | 7 | 14 | 29 | 91 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | C4 | 5065.7909 | 5065.7909 | 7049.4314 | 17343.0238 | 36337.7641 | C4 | 96250.028 | 116513.1918 | 345422.1386 | 0 | 0 | 558185.3585 |  | 141842.1466 | 91184.2371 | 317224.413 | 0 | 0 | 550250.7967 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 273552.7113 | 121578.9828 | 91642.6082 | 0 | 0 | 486774.3023 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405 |  | 288750.0841 | 121578.9828 | 49346.0198 | 52029.0713 | 0 | 511704.1581
|  |  | 1318 | 1318 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 142 | 0 | -14 | -112 | -16 |  | 594 | 280 | 193 | 227 | 24 |  | 283 | 0 | 0 | -35 | -248 |  | 518 | 336 | 91 | 88 | 285 | [22 empty] | 1205658.2461 | 483276.4566 | 1325293.1032 | 33992.3266 | 63954.4648 | 3112174.5973 |  | 1348918.8142 | 444168.5505 | 1232804.5632 | 24280.2333 | 0 | 3050172.1612 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 1506768.8602 | 562505.4271 | 565082.421 | 682621.4158 | 81396.5916 | 3398374.7156 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014 |  | 1680829.4372 | 645381.767 | 264494.6661 | 399583.2678 | 380819.7678 | 3371108.9059
| EHV Transformer |  | 234 | 234 | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 7 | 0 | 0 | 0 | -7 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 28 | 0 | 0 | 0 | -28 | 0 | 30 | 62 | 65 | 24 | 53 | 234 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | C1 | 4228.4321 | 4228.4321 | 5884.1833 | 14476.2782 | 30331.2496 | C1 | 215650.039 | 224106.9033 | 629607.6084 | 246096.7294 | 151656.2478 | 1467117.528 |  | 232563.7676 | 219878.4712 | 617839.2419 | 246096.7294 | 151656.2478 | 1468034.4579 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 224106.9033 | 224106.9033 | 482503.027 | 448764.6242 | 454968.7435 | 1834450.2013 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721 |  | 245249.064 | 262162.7926 | 382471.9116 | 347430.6768 | 758281.2391 | 1995595.6841
|  |  | 290 | 290 | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 26 | 0 | 0 | 0 | -26 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 38 | 0 | 0 | 0 | -38 | 0 | 50 | 47 | 78 | 72 | 43 | 290 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 471187 | 471187 | 471187 | 471187 | 471187 | C2 | 6040.6173 | 6040.6173 | 8405.9761 | 20680.3974 | 43330.3565 | C2 | 380558.8924 | 223502.8416 | 1361768.125 | 413607.9486 | 346642.8522 | 2726080.6597 |  | 416802.5965 | 211421.6069 | 1344956.1728 | 413607.9486 | 259982.1391 | 2646770.4639 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 531574.3259 | 241624.6936 | 1227272.5077 | 268845.1666 | 129991.0696 | 2399307.7634 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615 |  | 531574.3259 | 283909.015 | 655666.1342 | 1488988.615 | 216651.7826 | 3176789.8727
|  |  | 179 | 179 | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 15 | 0 | 0 | -7 | -8 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 28 | 0 | 0 | -4 | -24 | 0 | 30 | 38 | 56 | 29 | 26 | 179 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | C3 | 9060.926 | 9060.926 | 12608.9641 | 31020.5961 | 64995.5348 | C3 | 271827.7803 | 353376.1144 | 1273505.3761 | 248164.7692 | 64995.5348 | 2211869.5748 |  | 353376.1144 | 353376.1144 | 1172633.6632 | 248164.7692 | 0 | 2127550.6611 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 425863.5225 | 335254.2624 | 1059152.9861 | 341226.5576 | 0 | 2161497.3285 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519 |  | 525533.7086 | 344315.1884 | 706101.9907 | 775514.9036 | 129991.0696 | 2481456.8609
|  |  | 9 | 9 | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 1 | 4 | 2 | 2 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | C4 | 15101.5433 | 15101.5433 | 21014.9402 | 51700.9936 | 108325.8913 | C4 | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739 |  | 30203.0867 | 15101.5433 | 84059.7608 | 103401.9872 | 0 | 232766.378
|  |  | 712 | 712 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 48 | 0 | 0 | -7 | -41 |  | 140 | 131 | 318 | 64 | 59 |  | 96 | 0 | 0 | -4 | -92 |  | 110 | 148 | 203 | 127 | 124 | [22 empty] | 868036.7118 | 816087.4026 | 3433000.6311 | 907869.4472 | 563294.6348 | 6588288.8274 |  | 1002742.4784 | 799777.7358 | 3303548.5994 | 907869.4472 | 411638.3869 | 6425576.6478 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 1181544.7517 | 816087.4026 | 2895018.162 | 1162238.3356 | 584959.813 | 6639848.4649 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594 |  | 1332560.1852 | 905488.5393 | 1828299.7974 | 2715336.1826 | 1104924.0913 | 7886608.7957
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | C1 | 217.2993 | 217.2993 | 7366.0388 | 17980.3357 | 37674.4873 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132.569 | 132.569 | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 23253 | 23253 | 23253 | 23253 | 23253 | C2 | 310.4275 | 310.4275 | 10522.9126 | 25686.1939 | 53820.6962 | C2 | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369
|  |  | 20.77 | 20.77 | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | C3 | 465.6413 | 465.6413 | 15784.3689 | 38529.2909 | 80731.0443 | C3 | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229
|  |  | 7.371 | 7.371 | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | C4 | 776.0689 | 776.0689 | 26307.2815 | 64215.4848 | 134551.7405 | C4 | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457
|  |  | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0 | [22 empty] | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055
| EHV UG Cable (Non Pressurised) |  | 474.229 | 474.229 | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 929.677 | 929.677 | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 68614 | 68614 | 68614 | 68614 | 68614 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 292.451 | 292.451 | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 102921 | 102921 | 102921 | 102921 | 102921 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44.608 | 44.608 | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 171535 | 171535 | 171535 | 171535 | 171535 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1740.965 | 1740.965 |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 140 | 140 | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 2 | 2 | 0 | -2 | -2 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 4 | 4 | 0 | -4 | -4 | 0 | 22 | 81 | 10 | 23 | 4 | 140 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | C1 | 89.8543 | 89.8543 | 89.8543 | 4550.3597 | 15590.5765 | C1 | 0 | 8626.0171 | 628.9804 | 59154.6756 | 374173.837 | 442583.5101 |  | 2156.5043 | 8626.0171 | 628.9804 | 59154.6756 | 0 | 70566.1774 |  | 2156.5043 | 7637.6193 | 808.6891 | 91007.1932 | 31181.1531 | 132791.159 |  | 2336.213 | 7817.328 | 808.6891 | 81906.4739 | 0 | 92868.704 |  | 1976.7956 | 7278.2019 | 898.5434 | 104658.2722 | 62362.3062 | 177174.1193 |  | 2336.213 | 7637.6193 | 898.5434 | 86456.8335 | 0 | 97329.2093
|  |  | 557 | 557 | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 4 | 10 | 0 | -10 | -4 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 10 | 20 | 0 | -20 | -10 | 0 | 95 | 372 | 24 | 56 | 10 | 557 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 242195 | 242195 | 242195 | 242195 | 242195 | C2 | 128.3633 | 128.3633 | 128.3633 | 6500.5138 | 22272.2522 | C2 | 128.3633 | 49291.5264 | 2952.3571 | 338026.7176 | 2204952.9678 | 2595351.9322 |  | 12836.335 | 50061.7065 | 2695.6303 | 299023.6348 | 0 | 364617.3066 |  | 12836.335 | 47879.5295 | 2952.3571 | 351027.7452 | 155905.7654 | 570601.7322 |  | 13349.7884 | 49163.163 | 2952.3571 | 286022.6072 | 66816.7566 | 418304.6723 |  | 12194.5182 | 47751.1662 | 3080.7204 | 364028.7728 | 222722.522 | 649777.6996 |  | 13478.1517 | 50318.4332 | 3080.7204 | 234018.4968 | 0 | 300895.8022
|  |  | 441 | 441 | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 12 | 0 | -12 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 5 | 24 | 0 | -24 | -5 | 0 | 63 | 305 | 40 | 28 | 5 | 441 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | C3 | 192.545 | 192.545 | 192.545 | 9750.7707 | 33408.3783 | C3 | 0 | 60074.0478 | 7124.1659 | 312024.6624 | 2004502.698 | 2383725.5741 |  | 13093.0617 | 61229.3179 | 7124.1659 | 175513.8726 | 0 | 256960.4182 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 13093.0617 | 61614.408 | 7509.256 | 126760.0191 | 33408.3783 | 242385.1231 |  | 12130.3366 | 58726.2326 | 7701.801 | 273021.5796 | 167041.8915 | 518621.8413 |  | 13093.0617 | 63347.3132 | 7701.801 | 39003.0828 | 0 | 123145.2587
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | C4 | 320.9084 | 320.9084 | 320.9084 | 16251.2845 | 55680.6305 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1138 | 1138 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 6 | 24 | 0 | -24 | -6 |  | 192 | 766 | 71 | 99 | 10 |  | 19 | 48 | 0 | -48 | -19 |  | 180 | 758 | 74 | 107 | 19 | [22 empty] | 128.3633 | 117991.5913 | 10705.5034 | 709206.0556 | 4583629.5028 | 5421661.0164 |  | 28085.901 | 119917.0416 | 10448.7767 | 533692.183 | 0 | 692143.9022 |  | 28085.901 | 114821.0166 | 11270.3021 | 685804.2059 | 220495.2968 | 1060476.7224 |  | 28779.0631 | 118594.8991 | 11270.3021 | 494689.1002 | 100225.1349 | 753558.4993 |  | 26301.6504 | 113755.6008 | 11681.0648 | 741708.6246 | 452126.7197 | 1345573.6603 |  | 28907.4264 | 121303.3657 | 11681.0648 | 359478.4131 | 0 | 521370.2702
| EHV OHL Support - Poles |  | 3622 | 3622 | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 303 | 0 | -55 | -55 | -193 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 631 | 0 | -116 | -116 | -399 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | C1 | 124.8642 | 124.8642 | 173.758 | 427.4798 | 895.672 | C1 | 30716.6021 | 105510.2794 | 300080.1213 | 128243.9466 | 451418.692 | 1015969.6414 |  | 45450.5819 | 105510.2794 | 299037.5731 | 120549.3098 | 367225.5233 | 937773.2675 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 62556.9822 | 105510.2794 | 291913.4938 | 103450.1169 | 317067.8908 | 880498.7632 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951 |  | 81036.8892 | 105385.4152 | 284094.3823 | 84641.0048 | 265118.9144 | 820276.6058
|  |  | 21560 | 21560 | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 1811 | 0 | -335 | -336 | -1140 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 3769 | 0 | -696 | -697 | -2376 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 13914 | 13914 | 13914 | 13914 | 13914 | C2 | 178.3775 | 178.3775 | 248.2258 | 610.6855 | 1279.5314 | C2 | 261679.7632 | 896703.592 | 2551264.3613 | 1089462.8606 | 3843712.4458 | 8642823.0228 |  | 387079.1316 | 896703.592 | 2542576.4597 | 1025951.5728 | 3122056.7136 | 7974367.4696 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 532456.7778 | 896703.592 | 2481761.1485 | 876333.6351 | 2706208.9956 | 7493464.1489 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627 |  | 689607.3377 | 896881.9694 | 2416477.7736 | 715112.6737 | 2251975.3344 | 6970055.0888
|  |  | 2373 | 2373 | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 199 | 0 | -38 | -37 | -124 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 415 | 0 | -78 | -77 | -260 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 20871 | 20871 | 20871 | 20871 | 20871 | C3 | 267.5662 | 267.5662 | 372.3386 | 916.0282 | 1919.2972 | C3 | 43078.1614 | 147964.1197 | 421115.0018 | 181373.5816 | 633368.0628 | 1426898.9273 |  | 63948.3266 | 147964.1197 | 419625.6473 | 170381.2433 | 514371.6389 | 1316290.9757 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 87761.7202 | 147964.1197 | 409572.504 | 144732.454 | 449115.5354 | 1239146.3333 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942 |  | 113715.6435 | 147964.1197 | 398774.6834 | 118167.6365 | 374262.9462 | 1152885.0293
|  |  | 18 | 18 | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 4 | 0 | 0 | -1 | -3 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 3 | 0 | 0 | -2 | -1 | 0 | 0 | 4 | 9 | 2 | 3 | 18 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 34785 | 34785 | 34785 | 34785 | 34785 | C4 | 445.9437 | 445.9437 | 620.5644 | 1526.7136 | 3198.8286 | C4 | 445.9437 | 1783.7748 | 5585.0796 | 3053.4273 | 6397.6572 | 17265.8826 |  | 891.8874 | 1783.7748 | 5585.0796 | 1526.7136 | 6397.6572 | 16185.1126 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 1783.7748 | 1783.7748 | 5585.0796 | 1526.7136 | 0 | 10679.3429 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 1337.8311 | 1783.7748 | 5585.0796 | 0 | 6397.6572 | 15104.3427
|  |  | 27573 | 27573 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 2317 | 0 | -428 | -429 | -1460 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 4818 | 0 | -890 | -892 | -3036 |  | 125 | 6429 | 13340 | 2390 | 5289 | [22 empty] | 335920.4703 | 1151961.7658 | 3278044.564 | 1402133.8162 | 4934896.8578 | 11102957.4741 |  | 497369.9275 | 1151961.7658 | 3266824.7596 | 1318408.8396 | 4010051.533 | 10244616.8255 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 684559.255 | 1151961.7658 | 3188832.2258 | 1126042.9197 | 3472392.4219 | 9623788.5882 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195 |  | 885697.7014 | 1152015.2791 | 3104931.919 | 917921.3149 | 2897754.8522 | 8958321.0666
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 370 | 370 | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 8 | 0 | 0 | 0 | -8 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 77 | 0 | 0 | 0 | -77 | 0 | 51 | 71 | 96 | 75 | 77 | 370 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82320 | 82320 | 82320 | 82320 | 82320 | C1 | 274.1256 | 274.1256 | 381.9648 | 939.2712 | 1968.2712 | C1 | 13980.4056 | 44956.5984 | 30175.2192 | 57295.5432 | 31492.3392 | 177900.1056 |  | 13980.4056 | 44682.4728 | 30175.2192 | 57295.5432 | 31492.3392 | 177625.98 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 16173.4104 | 19462.9176 | 65315.9808 | 0 | 135810.7128 | 236763.0216 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664 |  | 35088.0768 | 19462.9176 | 36668.6208 | 70445.34 | 0 | 161664.9552
|  |  | 1902 | 1902 | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 558 | 0 | 0 | 0 | -558 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 807 | 0 | 0 | 0 | -807 | 0 | 75 | 38 | 408 | 574 | 807 | 1902 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117600 | 117600 | 117600 | 117600 | 117600 | C2 | 391.608 | 391.608 | 545.664 | 1341.816 | 2811.816 | C2 | 29370.6 | 152727.12 | 359592.576 | 42938.112 | 2117297.448 | 2701925.856 |  | 29370.6 | 151943.904 | 356864.256 | 42938.112 | 2117297.448 | 2698414.32 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 247887.864 | 70489.44 | 458357.76 | 29519.952 | 638282.232 | 1444537.248 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512 |  | 345398.256 | 14881.104 | 222630.912 | 770202.384 | 0 | 1353112.656
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 176400 | 176400 | 176400 | 176400 | 176400 | C3 | 587.412 | 587.412 | 818.496 | 2012.724 | 4217.724 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 294000 | 294000 | 294000 | 294000 | 294000 | C4 | 979.02 | 979.02 | 1364.16 | 3354.54 | 7029.54 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2272 | 2272 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 566 | 0 | 0 | 0 | -566 |  | 126 | 251 | 1011 | 22 | 862 |  | 884 | 0 | 0 | 0 | -884 |  | 126 | 109 | 504 | 649 | 884 | [22 empty] | 43351.0056 | 197683.7184 | 389767.7952 | 100233.6552 | 2148789.7872 | 2879825.9616 |  | 43351.0056 | 196626.3768 | 387039.4752 | 100233.6552 | 2148789.7872 | 2876040.3 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 264061.2744 | 89952.3576 | 523673.7408 | 29519.952 | 774092.9448 | 1681300.2696 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784 |  | 380486.3328 | 34344.0216 | 259299.5328 | 840647.724 | 0 | 1514777.6112
| EHV OHL Conductor (Tower Lines) |  | 155.606 | 155.606 | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 9 | 0 | 0 | -9 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 23 | 0 | 0 | 0 | -23 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | C1 | 5.7637 | 5.7637 | 7.4105 | 18.9379 | 39.5227 | C1 | 0 | 0 | 723.6651 | 0 | 1549.684 | 2273.349 |  | 334.2959 | 0 | 723.3094 | 0 | 0 | 1057.6053 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 386.1694 | 0 | 552.8678 | 265.1313 | 0 | 1204.1685 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019 |  | 466.8616 | 0 | 0 | 1412.8845 | 0 | 1879.746
|  |  | 705.644 | 705.644 | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 117627 | 117627 | 117627 | 117627 | 117627 | C2 | 8.2339 | 8.2339 | 10.5864 | 27.0542 | 56.461 | C2 | 0 | 550.6579 | 6767.0472 | 0 | 0 | 7317.7051 |  | 0 | 550.3038 | 6762.7173 | 0 | 0 | 7313.0212 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | C3 | 12.3508 | 12.3508 | 15.8796 | 40.5813 | 84.6914 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | C4 | 20.5847 | 20.5847 | 26.4661 | 67.6355 | 141.1524 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 861.25 | 861.25 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 9 | 0 | 0 | -9 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 23 | 0 | 0 | 0 | -23 |  | 58 | 0 | 66.834 | 713.416 | 23 | [22 empty] | 0 | 550.6579 | 7490.7123 | 0 | 1549.684 | 9591.0541 |  | 334.2959 | 550.3038 | 7486.0267 | 0 | 0 | 8370.6264 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 386.1694 | 0 | 8023.1186 | 265.1313 | 0 | 8674.4193 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352 |  | 466.8616 | 0 | 707.5335 | 18695.3844 | 0 | 19869.7794
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 |  | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 |  | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 |  | 3672957.6496 | 2763980.7578 | 8032833.271 | 3495376.8545 | 5013066.9062 | 22978215.4391 |  | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 |  | 4312112.7535 | 2880836.5713 | 6522847.5116 | 5251662.2868 | 4383498.7112 | 23350957.8344
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 115 | 115 | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 1 | 0 | 0 | 0 | -1 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 11 | 0 | 0 | 0 | -11 | 0 | 32 | 24 | 7 | 18 | 34 | 115 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | C1 | 2924.2407 | 2924.2407 | 4069.3022 | 10011.3046 | 20976.0668 | C1 | 111121.1473 | 52636.3329 | 118009.7643 | 260293.9199 | 41952.1336 | 584013.298 |  | 119893.8694 | 52636.3329 | 118009.7643 | 250282.6153 | 41952.1336 | 582774.7155 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 99424.1844 | 73106.0179 | 65108.8355 | 210237.3968 | 398545.2693 | 846421.7039 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501 |  | 125742.3509 | 70181.7772 | 28485.1155 | 180203.483 | 482449.5365 | 887062.2631
|  |  | 88 | 88 | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 4 | 0 | 0 | 0 | -4 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 16 | 0 | 0 | 0 | -16 | 0 | 34 | 22 | 0 | 16 | 16 | 88 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 325857 | 325857 | 325857 | 325857 | 325857 | C2 | 4177.4867 | 4177.4867 | 5813.2889 | 14301.8637 | 29965.8097 | C2 | 158744.4961 | 50129.8409 | 93012.6221 | 200226.0922 | 119863.2389 | 621976.2902 |  | 183809.4166 | 50129.8409 | 93012.6221 | 171622.3648 | 119863.2389 | 618437.4832 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 162921.9829 | 87727.2215 | 87199.3332 | 71509.3187 | 239726.4778 | 649084.334 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326 |  | 208874.337 | 91904.7083 | 0 | 228829.8197 | 0 | 529608.865
|  |  | 30 | 30 | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 16 | 0 | 0 | 0 | -16 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 17 | 0 | 0 | 0 | -17 | 0 | 8 | 1 | 0 | 4 | 17 | 30 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | C3 | 6266.2301 | 6266.2301 | 8719.9333 | 21452.7956 | 44948.7146 | C3 | 37597.3807 | 0 | 34879.7333 | 343244.7295 | 89897.4292 | 505619.2726 |  | 56396.071 | 0 | 34879.7333 | 321791.9339 | 89897.4292 | 502965.1674 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 150389.5226 | 6266.2301 | 34879.7333 | 21452.7956 | 0 | 212988.2816 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012 |  | 156655.7527 | 6266.2301 | 0 | 85811.1824 | 0 | 248733.1652
|  |  | 30 | 30 | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 3 | 18 | 5 | 1 | 3 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | C4 | 10443.7169 | 10443.7169 | 14533.2222 | 35754.6593 | 74914.5243 | C4 | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 52218.5842 | 198430.6202 | 72666.111 | 35754.6593 | 0 | 359069.9747 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971 |  | 62662.3011 | 187986.9033 | 72666.111 | 35754.6593 | 0 | 359069.9747
|  |  | 263 | 263 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 23 | 0 | 0 | 0 | -23 |  | 79 | 66 | 40 | 28 | 50 |  | 47 | 0 | 0 | 0 | -47 |  | 77 | 65 | 12 | 39 | 70 | [22 empty] | 349237.8915 | 332527.9445 | 274968.564 | 875274.0603 | 251712.8016 | 2083721.2619 |  | 401874.2244 | 332527.9445 | 274968.564 | 815206.2326 | 251712.8016 | 2076289.7672 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 464954.2742 | 365530.0898 | 259854.0129 | 338954.1704 | 638271.747 | 2067564.2943 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181 |  | 553934.7417 | 356339.6189 | 101151.2265 | 530599.1444 | 482449.5365 | 2024474.268
| 132kV Transformer |  | 63 | 63 | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 3 | 0 | 0 | 0 | -3 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 7 | 0 | 0 | 0 | -7 | 0 | 14 | 8 | 19 | 14 | 8 | 63 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | C1 | 19053.166 | 19053.166 | 26513.9222 | 65229.5989 | 136671.5405 | C1 | 400116.487 | 0 | 1007529.0427 | 65229.5989 | 410014.6216 | 1882889.7502 |  | 419169.6531 | 0 | 981015.1205 | 65229.5989 | 410014.6216 | 1875428.9941 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 323903.8228 | 152425.3284 | 901473.354 | 260918.3956 | 0 | 1638720.9008 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833 |  | 400116.487 | 152425.3284 | 503764.5213 | 913214.3845 | 136671.5405 | 2106192.2618
|  |  | 67 | 67 | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 9 | 0 | 0 | -9 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 23 | 0 | 0 | -11 | -12 | 0 | 22 | 4 | 15 | 14 | 12 | 67 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2123152 | 2123152 | 2123152 | 2123152 | 2123152 | C2 | 27218.8086 | 27218.8086 | 37877.0317 | 93185.1413 | 195245.0579 | C2 | 517157.3642 | 108875.2346 | 1628712.3622 | 0 | 390490.1158 | 2645235.0768 |  | 653251.4074 | 108875.2346 | 1477204.2355 | 0 | 0 | 2239330.8774 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 898220.6851 | 54437.6173 | 1174187.9821 | 93185.1413 | 0 | 2220031.4258 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728 |  | 1224846.3888 | 108875.2346 | 568155.4752 | 279555.4238 | 0 | 2181432.5224
|  |  | 54 | 54 | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 4 | 0 | 0 | -1 | -3 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 5 | 0 | 0 | -1 | -4 | 0 | 6 | 12 | 24 | 8 | 4 | 54 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3184728 | 3184728 | 3184728 | 3184728 | 3184728 | C3 | 40828.213 | 40828.213 | 56815.5475 | 139777.7119 | 292867.5869 | C3 | 244969.2778 | 571594.9814 | 1647650.8781 | 698888.5596 | 0 | 3163103.6969 |  | 326625.7037 | 571594.9814 | 1647650.8781 | 419333.1358 | 0 | 2965204.699 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 408282.1296 | 489938.5555 | 1818097.5206 | 0 | 0 | 2716318.2058 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166 |  | 449110.3426 | 489938.5555 | 1363573.1405 | 978443.9834 | 0 | 3281066.022
|  |  | 9 | 9 | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5307880 | 5307880 | 5307880 | 5307880 | 5307880 | C4 | 68047.0216 | 68047.0216 | 94692.5792 | 232962.8532 | 488112.6448 | C4 | 136094.0432 | 340235.108 | 94692.5792 | 0 | 488112.6448 | 1059134.3752 |  | 204141.0648 | 340235.108 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096
|  |  | 193 | 193 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 16 | 0 | 0 | -10 | -6 |  | 45 | 29 | 98 | 15 | 6 |  | 35 | 0 | 0 | -12 | -23 |  | 43 | 30 | 60 | 36 | 24 | [22 empty] | 1298337.1721 | 1020705.324 | 4378584.8622 | 764118.1585 | 1288617.3823 | 8750362.8991 |  | 1603187.8289 | 1020705.324 | 4200562.8133 | 484562.7347 | 410014.6216 | 7719033.3225 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1698453.6591 | 1173130.6524 | 3988451.4359 | 354103.5369 | 0 | 7214139.2843 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823 |  | 2142120.24 | 1159521.2481 | 2624878.2954 | 2171213.7918 | 136671.5405 | 8234405.1158
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 46.945 | 46.945 | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | C1 | 944.8823 | 944.8823 | 32029.7404 | 78183.8785 | 163819.9411 | C1 | 4653.5453 | 17734.4958 | 744723.4931 | 198899.787 | 0 | 966011.3211 |  | 4653.5453 | 17734.4958 | 744723.4931 | 0 | 0 | 767111.5342 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372
|  |  | 60.282 | 60.282 | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 101111 | 101111 | 101111 | 101111 | 101111 | C2 | 1349.8319 | 1349.8319 | 45756.7719 | 111691.255 | 234028.4873 | C2 | 3039.8213 | 43604.9681 | 1177184.4717 | 380755.4884 | 0 | 1604584.7495 |  | 3039.8213 | 43604.9681 | 1177138.7149 | 0 | 0 | 1223783.5043 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843
|  |  | 42.005 | 42.005 | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | C3 | 2024.7478 | 2024.7478 | 68635.1579 | 167536.8826 | 351042.7309 | C3 | 26141.5185 | 11640.275 | 1602287.7614 | 597436.5232 | 0 | 2237506.0781 |  | 26141.5185 | 11640.275 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834
|  |  | 0.038 | 0.038 | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | C4 | 3374.5796 | 3374.5796 | 114391.9299 | 279228.1376 | 585071.2182 | C4 | 16.8729 | 111.3611 | 0 | 896322.3217 | 0 | 896450.5557 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234
|  |  | 149.27 | 149.27 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0 | [22 empty] | 33851.7581 | 73091.1 | 3524195.7262 | 2073414.1203 | 0 | 5704552.7045 |  | 33851.7581 | 73091.1 | 3524149.9694 | 0 | 0 | 3631092.8274 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389
| 132kV UG Cable (Non Pressurised) |  | 28.233 | 28.233 | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 62.09 | 62.09 | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 636719 | 636719 | 636719 | 636719 | 636719 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 17.808 | 17.808 | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.269 | 3.269 | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 111.4 | 111.4 |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1441 | 1441 | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 3 | 26 | 0 | -26 | -3 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 6 | 48 | 0 | -48 | -6 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | C1 | 457.3005 | 457.3005 | 457.3005 | 23158.3894 | 79345.9572 | C1 | 33840.2397 | 526810.2175 | 63564.7745 | 694751.6822 | 3887951.9004 | 5206918.8143 |  | 50760.3595 | 530925.9223 | 63564.7745 | 694751.6822 | 0 | 1340002.7385 |  | 50760.3595 | 523609.1137 | 64479.3756 | 880018.7975 | 476075.7429 | 1994943.3892 |  | 52132.2611 | 535498.9277 | 64479.3756 | 277900.6729 | 238037.8715 | 1168049.1087 |  | 50760.3595 | 508518.196 | 64936.6761 | 1621087.2586 | 476075.7429 | 2721378.2331 |  | 53504.1627 | 530468.6218 | 64936.6761 | 509484.567 | 0 | 1158394.0276
|  |  | 1926 | 1926 | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 2 | 20 | 0 | -20 | -2 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 2 | 62 | 0 | -62 | -2 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 1232616 | 1232616 | 1232616 | 1232616 | 1232616 | C2 | 653.2865 | 653.2865 | 653.2865 | 33083.4134 | 113351.3674 | C2 | 50303.059 | 1040685.3626 | 140456.5932 | 926335.5763 | 2040324.6125 | 4198105.2036 |  | 59449.0697 | 1045258.368 | 140456.5932 | 661668.2688 | 0 | 1906832.2997 |  | 59449.0697 | 1038725.5032 | 145682.885 | 661668.2688 | 226702.7347 | 2132228.4614 |  | 60755.6426 | 1051791.2328 | 145682.885 | 0 | 0 | 1258229.7605 |  | 59449.0697 | 1011287.471 | 143723.0256 | 2150421.8736 | 226702.7347 | 3591584.1746 |  | 60755.6426 | 1051791.2328 | 143723.0256 | 99250.2403 | 0 | 1355520.1414
|  |  | 1045 | 1045 | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 40 | 0 | -40 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 7 | 66 | 0 | -66 | -7 | 0 | 89 | 828 | 53 | 68 | 7 | 1045 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1848924 | 1848924 | 1848924 | 1848924 | 1848924 | C3 | 979.9297 | 979.9297 | 979.9297 | 49625.1202 | 170027.051 | C3 | 18618.6647 | 842739.5592 | 40177.1185 | 1736879.2056 | 15642488.6957 | 18280903.2437 |  | 87213.7451 | 862338.1536 | 40177.1185 | 1736879.2056 | 0 | 2726608.2228 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 892715.9749 | 43116.9077 | 0 | 170027.051 | 1193073.6787 |  | 87213.7451 | 811381.8082 | 51936.2752 | 3374508.1709 | 1190189.3573 | 5515229.3566 |  | 94073.2531 | 876057.1697 | 51936.2752 | 99250.2403 | 0 | 1121316.9383
|  |  | 140 | 140 | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 6 | 0 | -6 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 8 | 0 | -8 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 3081540 | 3081540 | 3081540 | 3081540 | 3081540 | C4 | 1633.2162 | 1633.2162 | 1633.2162 | 82708.5336 | 283378.4184 | C4 | 1633.2162 | 129024.0798 | 81660.81 | 496251.2016 | 1133513.6736 | 1842082.9812 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 138823.377 | 81660.81 | 0 | 0 | 228650.268 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072 |  | 8166.081 | 142089.8094 | 78394.3776 | 0 | 0 | 228650.268
|  |  | 4552 | 4552 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 5 | 92 | 0 | -92 | -5 |  | 296 | 3685 | 458 | 104 | 9 |  | 15 | 184 | 0 | -184 | -15 |  | 296 | 3567 | 463 | 211 | 15 | [22 empty] | 104395.1795 | 2539259.2191 | 325859.2962 | 3854217.6658 | 22704278.8822 | 29528010.2428 |  | 205589.2553 | 2567546.5237 | 325859.2962 | 3589550.3582 | 0 | 6688545.4334 |  | 205589.2553 | 2544877.4828 | 334939.9783 | 4022943.0743 | 872805.5287 | 7981155.3194 |  | 208267.7298 | 2618829.5124 | 334939.9783 | 277900.6729 | 408064.9225 | 3848002.8159 |  | 205589.2553 | 2460211.555 | 338990.3545 | 7807685.5718 | 1892967.8349 | 12705444.5715 |  | 216499.1395 | 2600406.8336 | 338990.3545 | 707985.0476 | 0 | 3863881.3752
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 2763 | 2763 | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 564 | 0 | 0 | 0 | -564 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 1093 | 0 | 0 | 0 | -1093 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | C1 | 32.0252 | 32.0252 | 44.0347 | 104.082 | 220.1734 | C1 | 13514.6445 | 8838.9618 | 48306.0473 | 57661.4158 | 93573.7014 | 221894.7708 |  | 13418.5689 | 8774.9114 | 48041.8392 | 57661.4158 | 93573.7014 | 221470.4366 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 31480.7952 | 4579.607 | 43374.1628 | 24667.4288 | 91371.9672 | 195473.961 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542 |  | 48454.1639 | 3042.3963 | 28270.2665 | 53394.0547 | 0 | 133160.8814
|  |  | 3992 | 3992 | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 441 | 0 | 0 | -8 | -433 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 713 | 0 | 0 | 0 | -713 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 571879 | 571879 | 571879 | 571879 | 571879 | C2 | 45.7503 | 45.7503 | 62.9067 | 148.6885 | 314.5335 | C2 | 14823.1037 | 23332.6632 | 158461.9521 | 36726.0694 | 129273.248 | 362617.0363 |  | 14731.603 | 23195.4122 | 157581.2585 | 36726.0694 | 129273.248 | 361507.5911 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 34907.4942 | 10202.3214 | 160600.7796 | 30927.2163 | 77060.6953 | 313698.5067 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726 |  | 47397.3315 | 3705.7759 | 134620.3166 | 109286.0769 | 0 | 295009.5009
|  |  | 1996 | 1996 | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 388 | 0 | 0 | 0 | -388 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 767 | 0 | 0 | 0 | -767 | 0 | 94 | 22 | 867 | 246 | 767 | 1996 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | C3 | 68.6255 | 68.6255 | 94.36 | 223.0328 | 471.8002 | C3 | 6519.4206 | 7411.5518 | 97568.2762 | 87205.8287 | 177396.8658 | 376101.9431 |  | 6450.7951 | 7342.9264 | 97002.116 | 87205.8287 | 177396.8658 | 375398.532 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 33077.4814 | 2882.2702 | 101625.7577 | 3568.525 | 178812.2663 | 319966.3005 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115 |  | 59086.5383 | 1509.7606 | 81810.1503 | 54866.0713 | 0 | 197272.5204
|  |  | 333 | 333 | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 50 | 0 | 0 | 0 | -50 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 88 | 0 | 0 | 0 | -88 | 0 | 9 | 50 | 103 | 83 | 88 | 333 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | C4 | 114.3758 | 114.3758 | 157.2667 | 371.7213 | 786.3336 | C4 | 1029.3822 | 12123.8348 | 20759.2077 | 32711.4788 | 0 | 66623.9035 |  | 1029.3822 | 12009.459 | 20601.941 | 32711.4788 | 0 | 66352.261 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 6748.1722 | 5718.79 | 29251.6109 | 0 | 29880.6778 | 71599.2508 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759 |  | 11094.4526 | 5718.79 | 16198.4727 | 30852.872 | 0 | 63864.5873
|  |  | 9084 | 9084 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 1443 | 0 | 0 | -8 | -1435 |  | 844 | 458 | 4801 | 469 | 2512 |  | 2661 | 0 | 0 | 0 | -2661 |  | 846 | 248 | 3752 | 1577 | 2661 | [22 empty] | 35886.551 | 51707.0117 | 325095.4833 | 214304.7927 | 400243.8151 | 1027237.6538 |  | 35630.3492 | 51322.709 | 323227.1546 | 214304.7927 | 400243.8151 | 1024728.8206 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 106213.9429 | 23382.9886 | 334852.3109 | 59163.1701 | 377125.6066 | 900738.019 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142 |  | 166032.4863 | 13976.7228 | 260899.2061 | 248399.0749 | 0 | 689307.4901
| 132kV OHL Conductor (Tower Lines) |  | 679.807 | 679.808 | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 70.837 | 0 | 0 | 0 | -70.837 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 111.102 | 0 | 0 | -16.886 | -94.215 | 0.001 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 401324 | 401324 | 401324 | 401324 | 401324 | C1 | 28.0927 | 28.0927 | 36.1192 | 92.3045 | 192.6355 | C1 | 1047.7727 | 4017.8151 | 14675.6843 | 2569.9424 | 12785.99 | 35097.2045 |  | 1045.8624 | 4010.4829 | 14650.0397 | 2569.9424 | 12785.99 | 35062.3174 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 1990.0012 | 1045.8624 | 19196.5028 | 1558.6541 | 4503.4332 | 28294.4537 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047 |  | 3121.1529 | 1045.8624 | 8757.1265 | 26678.4062 | 0 | 39602.548
|  |  | 985.034 | 985.034 | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 52.059 | 0 | 0 | 0 | -52.059 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 114.72 | 0 | 0 | -19.967 | -94.753 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 573320 | 573320 | 573320 | 573320 | 573320 | C2 | 40.1324 | 40.1324 | 51.5988 | 131.8636 | 275.1936 | C2 | 605.317 | 2546.8824 | 42102.918 | 0 | 25348.3577 | 70603.4751 |  | 604.2334 | 2542.227 | 42028.3062 | 0 | 25348.3577 | 70523.1243 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 2089.2526 | 604.2334 | 44130.2865 | 2981.3041 | 11022.0541 | 60827.1307 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871 |  | 4603.9889 | 604.2334 | 11388.5259 | 83673.3881 | 0 | 100270.1363
|  |  | 492.36 | 492.36 | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 3.104 | 0 | 0 | 0 | -3.104 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 19.157 | 0 | 0 | -0.654 | -18.503 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 859980 | 859980 | 859980 | 859980 | 859980 | C3 | 60.1986 | 60.1986 | 77.3982 | 197.7954 | 412.7904 | C3 | 1699.8881 | 5135.7834 | 27953.9079 | 3047.2359 | 1277.9991 | 39114.8143 |  | 1696.8179 | 5126.3924 | 27903.0573 | 3047.2359 | 1277.9991 | 39051.5026 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 186.8565 | 1696.8179 | 34443.4374 | 129.3582 | 6356.5594 | 42813.0293 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646 |  | 1153.2246 | 1696.8179 | 10890.7007 | 60190.327 | 0 | 73931.0702
|  |  | 82.199 | 82.199 | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 23.021 | 0 | 0 | -23.021 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 1433300 | 1433300 | 1433300 | 1433300 | 1433300 | C4 | 100.331 | 100.331 | 128.997 | 329.659 | 687.984 | C4 | 0 | 50.3662 | 10552.5996 | 0 | 0 | 10602.9657 |  | 0 | 50.2658 | 10538.7969 | 0 | 0 | 10589.0627 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416 |  | 2309.72 | 0 | 408.9205 | 18463.5413 | 0 | 21182.1817
|  |  | 2239.4 | 2239.401 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 126 | 0 | 0 | 0 | -126 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 268 | 0 | 0 | -60.528 | -207.471 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471 | [22 empty] | 3352.9777 | 11750.847 | 95285.1098 | 5617.1784 | 39412.3468 | 155418.4597 |  | 3346.9137 | 11729.3681 | 95120.2 | 5617.1784 | 39412.3468 | 155226.007 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 4266.1102 | 3346.9137 | 105151.435 | 12903.8686 | 21882.0466 | 147550.3742 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298 |  | 11188.0864 | 3346.9137 | 31445.2736 | 189005.6625 | 0 | 234985.9363
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 |  | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 |  | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 |  | 2500367.7826 | 4251672.6042 | 9268695.1682 | 1043025.4188 | 1445344.3227 | 18509105.2965 |  | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 |  | 3096042.5031 | 4195209.0013 | 8205486.5216 | 3847202.7213 | 619121.077 | 19963061.8243
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 429606.482 | 429102.483 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 33858 | -252 | -2154 | -6353 | -25351 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 67410 | -632 | -3512 | -10968.528 | -52801.471 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 |  | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 |  | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 |  | 24103081.2131 | 21575814.1788 | 36479823.6357 | 10414721.8368 | 28444194.358 | 121017635.2224 |  | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 |  | 24947734.7457 | 22180797.3508 | 31669772.6725 | 18733599.9789 | 28977878.803 | 126509783.5511
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 | LV Network | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 4562727.3965 | 3313431.5131 | 5603107.0395 | 1420604.9582 | 4834619.6686 | 19734490.5759 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 | LV Network | 4449896.867 | 3269085.4089 | 5129014.9386 | 2329182.0911 | 6502070.0923 | 21679249.3979
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 | HV Network | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 13367028.3844 | 11246729.3037 | 13575188.1569 | 4455714.6053 | 17151163.4605 | 59795823.9109 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 | HV Network | 13089682.6222 | 11835666.3692 | 11812423.7007 | 7305552.8798 | 17473188.9224 | 61516514.4944
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 | EHV Network | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 | EHV Network | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 | EHV Network | 3672957.6496 | 2763980.7578 | 8032833.271 | 3495376.8545 | 5013066.9062 | 22978215.4391 | EHV Network | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 | EHV Network | 4312112.7535 | 2880836.5713 | 6522847.5116 | 5251662.2868 | 4383498.7112 | 23350957.8344
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 | 132kV Network | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 | 132kV Network | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 | 132kV Network | 2500367.7826 | 4251672.6042 | 9268695.1682 | 1043025.4188 | 1445344.3227 | 18509105.2965 | 132kV Network | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 | 132kV Network | 3096042.5031 | 4195209.0013 | 8205486.5216 | 3847202.7213 | 619121.077 | 19963061.8243
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 | Total | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 | Total | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 | Total | 24103081.2131 | 21575814.1788 | 36479823.6357 | 10414721.8368 | 28444194.358 | 121017635.2224 | Total | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 | Total | 24947734.7457 | 22180797.3508 | 31669772.6725 | 18733599.9789 | 28977878.803 | 126509783.5511
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EMID - Asset Rep
Secondary deliverables RIIO-ED1 - Asset replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EMID | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | C1 | 42.9585 | 42.9585 | 59.7801 | 147.071 | 308.1488 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 11440 | 0 | -572 | -1716 | -9152 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 22524 | 0 | -1126 | -3379 | -18019 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4787 | 4787 | 4787 | 4787 | 4787 | C2 | 61.3693 | 61.3693 | 85.4001 | 210.1014 | 440.2125 | C2 | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | C3 | 92.054 | 92.054 | 128.1001 | 315.1521 | 660.3188 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | C4 | 153.4233 | 153.4233 | 213.5002 | 525.2536 | 1100.5313 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 11440 | 0 | -572 | -1716 | -9152 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 22524 | 0 | -1126 | -3379 | -18019 |  | 20323 | 38701 | 21750 | 7054 | 27617 | [22 empty] | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105
| LV Switchgear (at s/s) |  | 8 | 8 | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | C1 | 95.4965 | 95.4965 | 132.8107 | 326.7848 | 684.7228 | C1 | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861
|  |  | 17231 | 17231 | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 598 | -107 | -316 | -109 | -66 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 1190 | -207 | -96 | -619 | -268 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 7098 | 7098 | 7098 | 7098 | 7098 | C2 | 136.4236 | 136.4236 | 189.7295 | 466.8355 | 978.1754 | C2 | 1236133.8772 | 393036.2764 | 931572.0414 | 63489.6226 | 59668.6982 | 2683900.5157 |  | 1302572.1509 | 384441.5921 | 910701.792 | 21941.2666 | 17607.1568 | 2637263.9584 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 1173106.1924 | 430552.7554 | 1028144.3773 | 26609.6212 | 0 | 2658412.9463 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516 |  | 1050597.8356 | 544466.428 | 1036871.9361 | 34545.824 | 0 | 2666482.0237
|  |  | 1354 | 1354 | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 78 | -5 | -36 | -14 | -23 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 161 | -17 | -21 | -74 | -49 | 0 | 387 | 206 | 618 | 94 | 49 | 1354 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 10647 | 10647 | 10647 | 10647 | 10647 | C3 | 204.6353 | 204.6353 | 284.5943 | 700.2532 | 1467.2631 | C3 | 96997.1512 | 48089.3049 | 169049.0201 | 18906.8361 | 16139.8938 | 349182.2061 |  | 105182.5648 | 47475.3989 | 166772.2657 | 13304.8106 | 4401.7892 | 337136.8291 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 109684.5422 | 38880.7146 | 176163.8779 | 6302.2787 | 0 | 331031.4134 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305 |  | 112140.1663 | 38676.0793 | 169902.8031 | 14005.0638 | 0 | 334724.1125
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 17745 | 17745 | 17745 | 17745 | 17745 | C4 | 341.0589 | 341.0589 | 474.3238 | 1167.0886 | 2445.4384 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18593 | 18593 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 676 | -112 | -352 | -123 | -89 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 1351 | -224 | -117 | -693 | -317 |  | 6905 | 4404 | 6180 | 787 | 317 | [22 empty] | 1333799.5038 | 441125.5813 | 1100753.8722 | 82396.4587 | 75808.5919 | 3033884.0079 |  | 1408423.1911 | 431916.991 | 1077606.8683 | 35246.0772 | 22008.946 | 2975202.0737 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 1283459.2101 | 469433.47 | 1204441.0658 | 32911.8999 | 0 | 2990245.6458 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682 |  | 1163406.4773 | 583142.5072 | 1206907.5498 | 48550.8878 | 0 | 3002007.4222
| LV UGB and LV Pillar OD (not at s/s) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | C1 | 77.7776 | 77.7776 | 108.1683 | 266.1515 | 557.6757 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27987 | 27987 | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 731 | 0 | 0 | 0 | -731 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 1456 | 0 | 0 | 0 | -1456 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5781 | 5781 | 5781 | 5781 | 5781 | C2 | 111.1108 | 111.1108 | 154.5261 | 380.2164 | 796.6796 | C2 | 576776.2666 | 566331.8495 | 2504250.4628 | 216343.1145 | 658854.0375 | 4522555.7309 |  | 636331.6661 | 564554.0764 | 2496524.1563 | 216343.1145 | 361692.5429 | 4275445.5563 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 633776.1173 | 435776.636 | 2486943.5362 | 585913.4262 | 578389.3969 | 4720799.1126 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821 |  | 640998.3206 | 291554.7917 | 2031709.5572 | 1418967.4928 | 2162188.4615 | 6545418.6239
|  |  | 1022 | 1022 | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 21 | 0 | 0 | 0 | -21 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 48 | 0 | 0 | 0 | -48 | 0 | 48 | 116 | 557 | 157 | 144 | 1022 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | C3 | 166.6662 | 166.6662 | 231.7892 | 570.3246 | 1195.0194 | C3 | 14666.6282 | 39166.5641 | 152749.0795 | 9695.5174 | 22705.3689 | 238983.1581 |  | 17166.6217 | 38999.8978 | 152285.5011 | 9695.5174 | 13145.2136 | 231292.7516 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 15999.9581 | 33166.5798 | 150431.1876 | 29656.8769 | 31070.5048 | 260325.1071 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942 |  | 15999.9581 | 19333.2827 | 129106.5816 | 89540.9551 | 114721.8638 | 368702.6413
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | C4 | 277.7771 | 277.7771 | 386.3153 | 950.5409 | 1991.699 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29009 | 29009 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 752 | 0 | 0 | 0 | -752 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 1504 | 0 | 0 | 0 | -1504 |  | 4361 | 2740 | 13705 | 3889 | 4314 | [22 empty] | 591442.8949 | 605498.4136 | 2656999.5423 | 226038.632 | 681559.4064 | 4761538.8891 |  | 653498.2878 | 603553.9742 | 2648809.6574 | 226038.632 | 374837.7565 | 4506738.3079 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 649776.0754 | 468943.2158 | 2637374.7238 | 615570.303 | 609459.9017 | 4981124.2196 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764 |  | 656998.2787 | 310888.0744 | 2160816.1389 | 1508508.448 | 2276910.3254 | 6914121.2652
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 |  | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 4562727.3965 | 3313431.5131 | 5603107.0395 | 1420604.9582 | 4834619.6686 | 19734490.5759 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 |  | 4449896.867 | 3269085.4089 | 5129014.9386 | 2329182.0911 | 6502070.0923 | 21679249.3979
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 809 | 809 | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 34 | 0 | -9 | 0 | -25 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 91 | -18 | 0 | 0 | -73 | 0 | 196 | 168 | 215 | 121 | 109 | 809 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | C1 | 722.066 | 722.066 | 1004.8095 | 2472.034 | 5179.4999 | C1 | 186293.0249 | 113364.3601 | 366755.4514 | 61800.8506 | 15538.4996 | 743752.1867 |  | 197846.0807 | 111920.2281 | 356707.3569 | 61800.8506 | 0 | 728274.5164 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 192069.5528 | 120585.02 | 293404.3612 | 207650.8582 | 0 | 813709.7921 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655 |  | 207232.9386 | 108309.8982 | 216034.033 | 299116.1171 | 186461.9951 | 1017154.982
|  |  | 2623 | 2623 | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 195 | 0 | -43 | -96 | -56 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 397 | -85 | 0 | 0 | -312 | 0 | 744 | 464 | 728 | 364 | 323 | 2623 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 80462 | 80462 | 80462 | 80462 | 80462 | C2 | 1031.5228 | 1031.5228 | 1435.4421 | 3531.4772 | 7399.2855 | C2 | 926307.5103 | 340402.5372 | 1890477.2194 | 183636.8134 | 125787.8538 | 3466611.9341 |  | 989230.4036 | 338339.4915 | 1840236.7466 | 183636.8134 | 14798.571 | 3366242.026 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 1034617.4085 | 463153.7552 | 1444054.7325 | 582693.7347 | 0 | 3524519.6309 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414 |  | 1176967.5604 | 390947.1564 | 1045001.8342 | 1285457.6935 | 81392.1407 | 3979766.3853
|  |  | 880 | 880 | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 105 | 0 | -12 | -73 | -20 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 181 | -25 | 0 | -11 | -145 | 0 | 190 | 156 | 248 | 138 | 148 | 880 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 120693 | 120693 | 120693 | 120693 | 120693 | C3 | 1547.2843 | 1547.2843 | 2153.1631 | 5297.2158 | 11098.9283 | C3 | 331118.8316 | 188768.6797 | 1093806.865 | 100647.0996 | 133187.1394 | 1847528.6153 |  | 385273.7807 | 187221.3955 | 1057203.0919 | 100647.0996 | 0 | 1730345.3678 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 485847.2576 | 227450.7862 | 785904.5388 | 286049.6516 | 0 | 1785252.2342 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694 |  | 574042.4605 | 202694.2381 | 533984.4538 | 672746.4028 | 33296.7848 | 2016764.3399
|  |  | 20 | 20 | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 2 | 0 | 0 | -1 | -1 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 4 | 0 | 0 | -2 | -2 | 0 | 6 | 5 | 3 | 4 | 2 | 20 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 201155 | 201155 | 201155 | 201155 | 201155 | C4 | 2578.8071 | 2578.8071 | 3588.6052 | 8828.693 | 18498.2138 | C4 | 12894.0355 | 12894.0355 | 25120.2364 | 17657.3859 | 18498.2138 | 87063.9071 |  | 18051.6497 | 12894.0355 | 25120.2364 | 8828.693 | 0 | 64894.6145 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 20630.4568 | 12894.0355 | 25120.2364 | 0 | 0 | 58644.7287 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931 |  | 25788.071 | 12894.0355 | 10765.8156 | 17657.3859 | 0 | 67105.308
|  |  | 4332 | 4332 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 336 | 0 | -64 | -170 | -102 |  | 1255 | 768 | 1734 | 473 | 102 |  | 673 | -128 | 0 | -13 | -532 |  | 1136 | 793 | 1194 | 627 | 582 | [22 empty] | 1456613.4024 | 655429.6125 | 3376159.7722 | 363742.1495 | 293011.7066 | 6144956.6432 |  | 1590401.9147 | 650375.1506 | 3279267.4318 | 354913.4566 | 14798.571 | 5889756.5247 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1733164.6758 | 824083.5969 | 2548483.8688 | 1076394.2445 | 0 | 6182126.3859 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859 |  | 1984031.0305 | 714845.3281 | 1805786.1366 | 2274977.5994 | 301150.9207 | 7080791.0152
| HV Switchgear (GM) - Distribution |  | 9569 | 9434 | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 370 | -156 | -1 | -276 | 0 | -63 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 795 | -330 | 0 | -119 | -481 | -135 | 4321 | 2124 | 1640 | 1000 | 484 | 9569 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | C1 | 205.8277 | 205.8277 | 286.4248 | 704.6627 | 1476.4362 | C1 | 1190918.8639 | 207268.4576 | 765613.4049 | 125429.9656 | 160931.5449 | 2450162.2369 |  | 1286422.9 | 146137.6414 | 744704.3968 | 6341.9646 | 0 | 2183606.9028 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 1235171.8117 | 194507.1425 | 633858.0116 | 244517.9666 | 0 | 2308054.9323 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589 |  | 1053014.329 | 369254.8292 | 469736.6195 | 620807.8634 | 4429.3086 | 2517242.9497
|  |  | 12994 | 12774 | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 614 | -81 | 0 | -638 | 0 | -105 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 1288 | -146 | 0 | -411 | -951 | -220 | 3480 | 4503 | 2547 | 1510 | 954 | 12994 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 22936 | 22936 | 22936 | 22936 | 22936 | C2 | 294.0395 | 294.0395 | 409.1782 | 1006.661 | 2109.1946 | C2 | 1485781.6946 | 1000910.5261 | 1723049.5686 | 437897.5524 | 442930.8576 | 5090570.1993 |  | 1709839.8088 | 946219.1754 | 1613389.8003 | 18119.8987 | 0 | 4287568.6832 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1450202.9126 | 1213795.1386 | 1334739.4189 | 570776.8097 | 0 | 4569514.2798 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461 |  | 1401980.4314 | 1281130.1886 | 1042176.9773 | 1106320.483 | 6327.5837 | 4837935.6639
|  |  | 5187 | 5041 | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 483 | -10 | -41 | -515 | 0 | -83 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 860 | -18 | 0 | -616 | -372 | -146 | 1367 | 1486 | 991 | 971 | 372 | 5187 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 34404 | 34404 | 34404 | 34404 | 34404 | C3 | 441.0593 | 441.0593 | 613.7674 | 1509.9916 | 3163.7918 | C3 | 726865.6934 | 434884.4501 | 1477338.0355 | 472627.3583 | 578973.9067 | 3690689.444 |  | 978710.5423 | 426063.2645 | 1228762.2547 | 0 | 0 | 2633536.0615 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 963714.5268 | 585285.6646 | 964842.2899 | 30199.8312 | 0 | 2544042.3125 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488 |  | 982239.0166 | 647475.023 | 608243.4538 | 536047.0038 | 0 | 2774004.4972
|  |  | 143 | 140 | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 8 | -9 | 0 | 0 | 0 | -1 | 61 | 18 | 64 | 0 | 0 | 143 | 18 | -18 | 0 | -3 | 0 | -3 | 53 | 20 | 43 | 27 | 0 | 143 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 57340 | 57340 | 57340 | 57340 | 57340 | C4 | 735.0988 | 735.0988 | 1022.9456 | 2516.6526 | 5272.9864 | C4 | 38960.2364 | 14701.976 | 61376.736 | 30199.8312 | 47456.8776 | 192695.6572 |  | 52192.0148 | 13231.7784 | 55239.0624 | 0 | 0 | 120662.8556 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 50721.8172 | 6615.8892 | 65468.5184 | 0 | 0 | 122806.2248 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934 |  | 52192.0148 | 1470.1976 | 43986.6608 | 60399.6624 | 0 | 158048.5356
|  |  | 27893 | 27389 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 1475 | -256 | -42 | -1429 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 2961 | -512 | 0 | -1149 | -1804 |  | 9221 | 8133 | 5221 | 3508 | 1810 | [22 empty] | 3442526.4883 | 1657765.4098 | 4027377.745 | 1066154.7075 | 1230293.1868 | 11424117.5374 |  | 4027165.2659 | 1531651.8597 | 3642095.5142 | 24461.8633 | 0 | 9225374.5031 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 3699811.0683 | 2000203.8348 | 2998908.2388 | 845494.6075 | 0 | 9544417.7494 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472 |  | 3489425.7917 | 2299330.2385 | 2164143.7114 | 2323575.0125 | 10756.8923 | 10287231.6464
| HV Transformer (GM) |  | 3306 | 3306 | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 161 | 0 | 0 | -12 | -149 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 286 | 0 | 0 | -20 | -266 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 15848 | 15848 | 15848 | 15848 | 15848 | C1 | 304.5986 | 304.5986 | 423.617 | 1042.323 | 2184.0129 | C1 | 560461.3504 | 141333.7318 | 351178.5262 | 75047.2531 | 165984.9789 | 1294005.8404 |  | 575691.2784 | 140419.9362 | 349060.441 | 75047.2531 | 128856.7599 | 1269075.6686 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 550409.5979 | 157782.0541 | 381255.336 | 82343.5138 | 4368.0258 | 1176158.5276 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886 |  | 501064.6312 | 223575.343 | 344824.2706 | 112570.8797 | 10920.0644 | 1192955.1889
|  |  | 13028 | 13028 | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 436 | 0 | 0 | -93 | -343 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 895 | 0 | 0 | -213 | -682 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 22640 | 22640 | 22640 | 22640 | 22640 | C2 | 435.1408 | 435.1408 | 605.1672 | 1489.0328 | 3120.0184 | C2 | 3131708.3376 | 1113525.3072 | 1710202.5072 | 227822.0184 | 589683.4776 | 6772941.648 |  | 3214385.0896 | 1105692.7728 | 1701124.9992 | 227822.0184 | 424322.5024 | 6673347.3824 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2931108.4288 | 1218829.3808 | 2011575.7728 | 248668.4776 | 0 | 6410182.06 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888 |  | 2634342.4032 | 1486876.1136 | 2013996.4416 | 340988.5112 | 0 | 6476203.4696
|  |  | 3266 | 3266 | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 224 | 0 | 0 | -67 | -157 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 461 | 0 | 0 | -123 | -338 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 33960 | 33960 | 33960 | 33960 | 33960 | C3 | 652.7112 | 652.7112 | 907.7508 | 2233.5492 | 4680.0276 | C3 | 821110.6896 | 380530.6296 | 1130149.746 | 183151.0344 | 336961.9872 | 2851904.0868 |  | 855051.672 | 377919.7848 | 1124703.2412 | 183151.0344 | 262081.5456 | 2802907.278 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 875938.4304 | 358338.4488 | 1195507.8036 | 129545.8536 | 0 | 2559330.5364 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908 |  | 902046.8784 | 409249.9224 | 1059345.1836 | 198785.8788 | 4680.0276 | 2574107.8908
|  |  | 118 | 118 | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 16 | 0 | 0 | -6 | -10 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 33 | 0 | 0 | -7 | -26 | 0 | 31 | 27 | 25 | 9 | 26 | 118 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 56600 | 56600 | 56600 | 56600 | 56600 | C4 | 1087.852 | 1087.852 | 1512.918 | 3722.582 | 7800.046 | C4 | 55480.452 | 7614.964 | 78671.736 | 18612.91 | 23400.138 | 183780.2 |  | 57656.156 | 7614.964 | 78671.736 | 18612.91 | 7800.046 | 170355.812 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 67446.824 | 15229.928 | 52952.13 | 26058.074 | 0 | 161686.956 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8 |  | 69622.528 | 29372.004 | 37822.95 | 7445.164 | 0 | 144262.646
|  |  | 19718 | 19718 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 837 | 0 | 0 | -178 | -659 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 1675 | 0 | 0 | -363 | -1312 |  | 7470 | 4805 | 5334 | 791 | 1318 | [22 empty] | 4568760.8296 | 1643004.6326 | 3270202.5154 | 504633.2159 | 1116030.5817 | 11102631.7752 |  | 4702784.196 | 1631647.4578 | 3253560.4174 | 504633.2159 | 823060.8539 | 10915686.141 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 4424903.2811 | 1750179.8117 | 3641291.0424 | 486615.919 | 4368.0258 | 10307358.08 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828 |  | 4107076.4408 | 2149073.383 | 3455988.8458 | 659790.4337 | 15600.092 | 10387529.1953
| HV UG Cable |  | 3200.153 | 3200.153 | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 34503 | 34503 | 34503 | 34503 | 34503 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7275.757 | 7275.757 | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 49290 | 49290 | 49290 | 49290 | 49290 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3676.577 | 3676.577 | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 73935 | 73935 | 73935 | 73935 | 73935 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 123225 | 123225 | 123225 | 123225 | 123225 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14152.487 | 14152.487 |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | C1 | 72.5009 | 72.5009 | 100.8906 | 248.2111 | 520.0614 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 129615 | 129615 | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 11938 | 0 | -598 | -1790 | -9550 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 24132 | 0 | -1207 | -3620 | -19305 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 8079 | 8079 | 8079 | 8079 | 8079 | C2 | 103.5728 | 103.5728 | 144.1294 | 354.5873 | 742.9448 | C2 | 2343127.0019 | 5487907.3211 | 3641860.6685 | 1934273.776 | 16903480.9997 | 30310649.7672 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 2886159.0875 | 5488010.8939 | 3607846.1395 | 1683935.1352 | 14101836.008 | 27767787.2641 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362
|  |  | 18228 | 18228 | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 1680 | 0 | -83 | -252 | -1345 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 3394 | 0 | -170 | -509 | -2715 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | C3 | 155.3592 | 155.3592 | 216.194 | 531.881 | 1114.4173 | C3 | 494508.2381 | 1157581.1757 | 768137.4241 | 407952.7002 | 3565020.8147 | 6393200.3528 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944
|  |  | 253 | 253 | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 23 | 0 | -1 | -4 | -18 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 47 | 0 | -2 | -7 | -38 | 0 | 7 | 104 | 51 | 16 | 75 | 253 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | C4 | 258.9319 | 258.9319 | 360.3234 | 886.4683 | 1857.3621 | C4 | 11393.0058 | 26928.9228 | 17655.8466 | 9751.151 | 81723.9324 | 147452.8586 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 13982.3253 | 26669.9908 | 17655.8466 | 7978.2145 | 70579.7598 | 136866.137 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069
|  |  | 148096 | 148096 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 13641 | 0 | -682 | -2046 | -10913 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 27573 | 0 | -1379 | -4136 | -22058 |  | 4267 | 60541 | 29980 | 9562 | 43746 | [22 empty] | 2849028.2459 | 6672417.4195 | 4427653.9392 | 2351977.6272 | 20550225.7468 | 36851302.9787 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 3509149.3592 | 6672262.0604 | 4386505.0069 | 2047209.8343 | 17146795.4348 | 33761921.6955 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 |  | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 13367028.3844 | 11246729.3037 | 13575188.1569 | 4455714.6053 | 17151163.4605 | 59795823.9109 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 |  | 13089682.6222 | 11835666.3692 | 11812423.7007 | 7305552.8798 | 17473188.9224 | 61516514.4944
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 658 | 658 | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 42 | 0 | 0 | -33 | -9 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 81 | 0 | 0 | 0 | -81 | 0 | 274 | 205 | 49 | 13 | 117 | 658 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | C1 | 1418.4215 | 1418.4215 | 1973.8408 | 4856.0467 | 10174.5739 | C1 | 524815.9424 | 191486.8979 | 276337.7109 | 33992.3266 | 20349.1479 | 1046982.0257 |  | 547510.6859 | 185813.212 | 268442.3477 | 24280.2333 | 0 | 1026046.4789 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 536163.3141 | 224110.5916 | 102639.7212 | 301074.8927 | 81396.5916 | 1245385.1113 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395 |  | 503539.6204 | 290776.4005 | 96718.1988 | 63128.6065 | 366284.6621 | 1320447.4884
|  |  | 432 | 432 | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 45 | 0 | 0 | -43 | -2 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 125 | 0 | 0 | -20 | -105 | 0 | 165 | 91 | 21 | 49 | 106 | 432 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 158059 | 158059 | 158059 | 158059 | 158059 | C2 | 2026.3164 | 2026.3164 | 2819.7726 | 6937.2095 | 14535.1056 | C2 | 387026.4286 | 129684.2483 | 487820.6529 | 0 | 0 | 1004531.3298 |  | 431605.3889 | 121578.9828 | 448343.837 | 0 | 0 | 1001528.2088 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 453894.8691 | 162105.3104 | 222762.0322 | 339923.266 | 0 | 1178685.4778 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809 |  | 587631.7502 | 184394.7906 | 59215.2238 | 201179.0758 | 14535.1056 | 1046955.946
|  |  | 137 | 137 | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 18 | 0 | 0 | -13 | -5 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 37 | 0 | 0 | -4 | -33 | 0 | 62 | 16 | 14 | 12 | 33 | 137 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | C3 | 3039.4746 | 3039.4746 | 4229.6588 | 10405.8143 | 21802.6585 | C3 | 197565.847 | 45592.1185 | 215712.6008 | 0 | 43605.3169 | 502475.8834 |  | 227960.5927 | 45592.1185 | 198793.9655 | 0 | 0 | 472346.6768 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 243157.9656 | 54710.5423 | 148038.0594 | 41623.2571 | 0 | 487529.8243 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406 |  | 300907.9824 | 48631.5931 | 59215.2238 | 83246.5141 | 0 | 492001.3134
|  |  | 91 | 91 | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 37 | 0 | -14 | -23 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 40 | 0 | 0 | -11 | -29 | 0 | 17 | 24 | 7 | 14 | 29 | 91 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | C4 | 5065.7909 | 5065.7909 | 7049.4314 | 17343.0238 | 36337.7641 | C4 | 96250.028 | 116513.1918 | 345422.1386 | 0 | 0 | 558185.3585 |  | 141842.1466 | 91184.2371 | 317224.413 | 0 | 0 | 550250.7967 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 273552.7113 | 121578.9828 | 91642.6082 | 0 | 0 | 486774.3023 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405 |  | 288750.0841 | 121578.9828 | 49346.0198 | 52029.0713 | 0 | 511704.1581
|  |  | 1318 | 1318 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 142 | 0 | -14 | -112 | -16 |  | 594 | 280 | 193 | 227 | 24 |  | 283 | 0 | 0 | -35 | -248 |  | 518 | 336 | 91 | 88 | 285 | [22 empty] | 1205658.2461 | 483276.4566 | 1325293.1032 | 33992.3266 | 63954.4648 | 3112174.5973 |  | 1348918.8142 | 444168.5505 | 1232804.5632 | 24280.2333 | 0 | 3050172.1612 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 1506768.8602 | 562505.4271 | 565082.421 | 682621.4158 | 81396.5916 | 3398374.7156 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014 |  | 1680829.4372 | 645381.767 | 264494.6661 | 399583.2678 | 380819.7678 | 3371108.9059
| EHV Transformer |  | 234 | 234 | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 7 | 0 | 0 | 0 | -7 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 28 | 0 | 0 | 0 | -28 | 0 | 30 | 62 | 65 | 24 | 53 | 234 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | C1 | 4228.4321 | 4228.4321 | 5884.1833 | 14476.2782 | 30331.2496 | C1 | 215650.039 | 224106.9033 | 629607.6084 | 246096.7294 | 151656.2478 | 1467117.528 |  | 232563.7676 | 219878.4712 | 617839.2419 | 246096.7294 | 151656.2478 | 1468034.4579 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 224106.9033 | 224106.9033 | 482503.027 | 448764.6242 | 454968.7435 | 1834450.2013 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721 |  | 245249.064 | 262162.7926 | 382471.9116 | 347430.6768 | 758281.2391 | 1995595.6841
|  |  | 290 | 290 | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 26 | 0 | 0 | 0 | -26 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 38 | 0 | 0 | 0 | -38 | 0 | 50 | 47 | 78 | 72 | 43 | 290 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 471187 | 471187 | 471187 | 471187 | 471187 | C2 | 6040.6173 | 6040.6173 | 8405.9761 | 20680.3974 | 43330.3565 | C2 | 380558.8924 | 223502.8416 | 1361768.125 | 413607.9486 | 346642.8522 | 2726080.6597 |  | 416802.5965 | 211421.6069 | 1344956.1728 | 413607.9486 | 259982.1391 | 2646770.4639 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 531574.3259 | 241624.6936 | 1227272.5077 | 268845.1666 | 129991.0696 | 2399307.7634 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615 |  | 531574.3259 | 283909.015 | 655666.1342 | 1488988.615 | 216651.7826 | 3176789.8727
|  |  | 179 | 179 | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 15 | 0 | 0 | -7 | -8 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 28 | 0 | 0 | -4 | -24 | 0 | 30 | 38 | 56 | 29 | 26 | 179 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | C3 | 9060.926 | 9060.926 | 12608.9641 | 31020.5961 | 64995.5348 | C3 | 271827.7803 | 353376.1144 | 1273505.3761 | 248164.7692 | 64995.5348 | 2211869.5748 |  | 353376.1144 | 353376.1144 | 1172633.6632 | 248164.7692 | 0 | 2127550.6611 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 425863.5225 | 335254.2624 | 1059152.9861 | 341226.5576 | 0 | 2161497.3285 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519 |  | 525533.7086 | 344315.1884 | 706101.9907 | 775514.9036 | 129991.0696 | 2481456.8609
|  |  | 9 | 9 | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 2 | 0 | 0 | 0 | -2 | 0 | 0 | 1 | 4 | 2 | 2 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | C4 | 15101.5433 | 15101.5433 | 21014.9402 | 51700.9936 | 108325.8913 | C4 | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739 |  | 30203.0867 | 15101.5433 | 84059.7608 | 103401.9872 | 0 | 232766.378
|  |  | 712 | 712 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 48 | 0 | 0 | -7 | -41 |  | 140 | 131 | 318 | 64 | 59 |  | 96 | 0 | 0 | -4 | -92 |  | 110 | 148 | 203 | 127 | 124 | [22 empty] | 868036.7118 | 816087.4026 | 3433000.6311 | 907869.4472 | 563294.6348 | 6588288.8274 |  | 1002742.4784 | 799777.7358 | 3303548.5994 | 907869.4472 | 411638.3869 | 6425576.6478 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 1181544.7517 | 816087.4026 | 2895018.162 | 1162238.3356 | 584959.813 | 6639848.4649 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594 |  | 1332560.1852 | 905488.5393 | 1828299.7974 | 2715336.1826 | 1104924.0913 | 7886608.7957
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | C1 | 217.2993 | 217.2993 | 7366.0388 | 17980.3357 | 37674.4873 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132.569 | 132.569 | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 23253 | 23253 | 23253 | 23253 | 23253 | C2 | 310.4275 | 310.4275 | 10522.9126 | 25686.1939 | 53820.6962 | C2 | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369
|  |  | 20.77 | 20.77 | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | C3 | 465.6413 | 465.6413 | 15784.3689 | 38529.2909 | 80731.0443 | C3 | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229
|  |  | 7.371 | 7.371 | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | C4 | 776.0689 | 776.0689 | 26307.2815 | 64215.4848 | 134551.7405 | C4 | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457
|  |  | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0 | [22 empty] | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055
| EHV UG Cable (Non Pressurised) |  | 474.229 | 474.229 | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 929.677 | 929.677 | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 68614 | 68614 | 68614 | 68614 | 68614 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 292.451 | 292.451 | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 102921 | 102921 | 102921 | 102921 | 102921 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44.608 | 44.608 | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 171535 | 171535 | 171535 | 171535 | 171535 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1740.965 | 1740.965 |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 140 | 140 | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 2 | 0 | 0 | 0 | -2 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 4 | 0 | 0 | 0 | -4 | 0 | 22 | 81 | 10 | 23 | 4 | 140 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | C1 | 89.8543 | 89.8543 | 89.8543 | 4550.3597 | 15590.5765 | C1 | 0 | 8626.0171 | 628.9804 | 59154.6756 | 374173.837 | 442583.5101 |  | 2156.5043 | 8626.0171 | 628.9804 | 59154.6756 | 0 | 70566.1774 |  | 2156.5043 | 7637.6193 | 808.6891 | 91007.1932 | 31181.1531 | 132791.159 |  | 2336.213 | 7637.6193 | 808.6891 | 91007.1932 | 0 | 101789.7146 |  | 1976.7956 | 7278.2019 | 898.5434 | 104658.2722 | 62362.3062 | 177174.1193 |  | 2336.213 | 7278.2019 | 898.5434 | 104658.2722 | 0 | 115171.2305
|  |  | 557 | 557 | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 4 | 0 | 0 | 0 | -4 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 10 | 0 | 0 | 0 | -10 | 0 | 95 | 372 | 24 | 56 | 10 | 557 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 242195 | 242195 | 242195 | 242195 | 242195 | C2 | 128.3633 | 128.3633 | 128.3633 | 6500.5138 | 22272.2522 | C2 | 128.3633 | 49291.5264 | 2952.3571 | 338026.7176 | 2204952.9678 | 2595351.9322 |  | 12836.335 | 50061.7065 | 2695.6303 | 299023.6348 | 0 | 364617.3066 |  | 12836.335 | 47879.5295 | 2952.3571 | 351027.7452 | 155905.7654 | 570601.7322 |  | 13349.7884 | 47879.5295 | 2952.3571 | 351027.7452 | 66816.7566 | 482026.1768 |  | 12194.5182 | 47751.1662 | 3080.7204 | 364028.7728 | 222722.522 | 649777.6996 |  | 13478.1517 | 47751.1662 | 3080.7204 | 364028.7728 | 0 | 428338.8111
|  |  | 441 | 441 | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 5 | 0 | 0 | 0 | -5 | 0 | 63 | 305 | 40 | 28 | 5 | 441 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | C3 | 192.545 | 192.545 | 192.545 | 9750.7707 | 33408.3783 | C3 | 0 | 60074.0478 | 7124.1659 | 312024.6624 | 2004502.698 | 2383725.5741 |  | 13093.0617 | 61229.3179 | 7124.1659 | 175513.8726 | 0 | 256960.4182 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 12130.3366 | 58726.2326 | 7701.801 | 273021.5796 | 167041.8915 | 518621.8413 |  | 13093.0617 | 58726.2326 | 7701.801 | 273021.5796 | 0 | 352542.6749
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | C4 | 320.9084 | 320.9084 | 320.9084 | 16251.2845 | 55680.6305 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1138 | 1138 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 6 | 0 | 0 | 0 | -6 |  | 192 | 766 | 71 | 99 | 10 |  | 19 | 0 | 0 | 0 | -19 |  | 180 | 758 | 74 | 107 | 19 | [22 empty] | 128.3633 | 117991.5913 | 10705.5034 | 709206.0556 | 4583629.5028 | 5421661.0164 |  | 28085.901 | 119917.0416 | 10448.7767 | 533692.183 | 0 | 692143.9022 |  | 28085.901 | 114821.0166 | 11270.3021 | 685804.2059 | 220495.2968 | 1060476.7224 |  | 28779.0631 | 114821.0166 | 11270.3021 | 685804.2059 | 100225.1349 | 940899.7226 |  | 26301.6504 | 113755.6008 | 11681.0648 | 741708.6246 | 452126.7197 | 1345573.6603 |  | 28907.4264 |  | 11681.0648 |  | 0 | 40588.4913
| EHV OHL Support - Poles |  | 3622 | 3622 | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 303 | 0 | -55 | -55 | -193 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 631 | 0 | -116 | -116 | -399 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | C1 | 124.8642 | 124.8642 | 173.758 | 427.4798 | 895.672 | C1 | 30716.6021 | 105510.2794 | 300080.1213 | 128243.9466 | 451418.692 | 1015969.6414 |  | 45450.5819 | 105510.2794 | 299037.5731 | 120549.3098 | 367225.5233 | 937773.2675 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 62556.9822 | 105510.2794 | 291913.4938 | 103450.1169 | 317067.8908 | 880498.7632 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951 |  | 81036.8892 | 105385.4152 | 284094.3823 | 84641.0048 | 265118.9144 | 820276.6058
|  |  | 21560 | 21560 | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 1811 | 0 | -335 | -336 | -1140 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 3769 | 0 | -696 | -697 | -2376 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 13914 | 13914 | 13914 | 13914 | 13914 | C2 | 178.3775 | 178.3775 | 248.2258 | 610.6855 | 1279.5314 | C2 | 261679.7632 | 896703.592 | 2551264.3613 | 1089462.8606 | 3843712.4458 | 8642823.0228 |  | 387079.1316 | 896703.592 | 2542576.4597 | 1025951.5728 | 3122056.7136 | 7974367.4696 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 532456.7778 | 896703.592 | 2481761.1485 | 876333.6351 | 2706208.9956 | 7493464.1489 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627 |  | 689607.3377 | 896881.9694 | 2416477.7736 | 715112.6737 | 2251975.3344 | 6970055.0888
|  |  | 2373 | 2373 | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 199 | 0 | -38 | -37 | -124 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 415 | 0 | -78 | -77 | -260 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 20871 | 20871 | 20871 | 20871 | 20871 | C3 | 267.5662 | 267.5662 | 372.3386 | 916.0282 | 1919.2972 | C3 | 43078.1614 | 147964.1197 | 421115.0018 | 181373.5816 | 633368.0628 | 1426898.9273 |  | 63948.3266 | 147964.1197 | 419625.6473 | 170381.2433 | 514371.6389 | 1316290.9757 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 87761.7202 | 147964.1197 | 409572.504 | 144732.454 | 449115.5354 | 1239146.3333 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942 |  | 113715.6435 | 147964.1197 | 398774.6834 | 118167.6365 | 374262.9462 | 1152885.0293
|  |  | 18 | 18 | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 4 | 0 | 0 | -1 | -3 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 3 | 0 | 0 | -2 | -1 | 0 | 0 | 4 | 9 | 2 | 3 | 18 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 34785 | 34785 | 34785 | 34785 | 34785 | C4 | 445.9437 | 445.9437 | 620.5644 | 1526.7136 | 3198.8286 | C4 | 445.9437 | 1783.7748 | 5585.0796 | 3053.4273 | 6397.6572 | 17265.8826 |  | 891.8874 | 1783.7748 | 5585.0796 | 1526.7136 | 6397.6572 | 16185.1126 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 1783.7748 | 1783.7748 | 5585.0796 | 1526.7136 | 0 | 10679.3429 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 1337.8311 | 1783.7748 | 5585.0796 | 0 | 6397.6572 | 15104.3427
|  |  | 27573 | 27573 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 2317 | 0 | -428 | -429 | -1460 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 4818 | 0 | -890 | -892 | -3036 |  | 125 | 6429 | 13340 | 2390 | 5289 | [22 empty] | 335920.4703 | 1151961.7658 | 3278044.564 | 1402133.8162 | 4934896.8578 | 11102957.4741 |  | 497369.9275 | 1151961.7658 | 3266824.7596 | 1318408.8396 | 4010051.533 | 10244616.8255 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 684559.255 | 1151961.7658 | 3188832.2258 | 1126042.9197 | 3472392.4219 | 9623788.5882 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195 |  | 885697.7014 | 1152015.2791 | 3104931.919 | 917921.3149 | 2897754.8522 | 8958321.0666
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 370 | 370 | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 8 | 0 | 0 | 0 | -8 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 77 | 0 | 0 | 0 | -77 | 0 | 51 | 71 | 96 | 75 | 77 | 370 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82320 | 82320 | 82320 | 82320 | 82320 | C1 | 274.1256 | 274.1256 | 381.9648 | 939.2712 | 1968.2712 | C1 | 13980.4056 | 44956.5984 | 30175.2192 | 57295.5432 | 31492.3392 | 177900.1056 |  | 13980.4056 | 44682.4728 | 30175.2192 | 57295.5432 | 31492.3392 | 177625.98 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 16173.4104 | 19462.9176 | 65315.9808 | 0 | 135810.7128 | 236763.0216 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664 |  | 35088.0768 | 19462.9176 | 36668.6208 | 70445.34 | 0 | 161664.9552
|  |  | 1902 | 1902 | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 558 | 0 | 0 | 0 | -558 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 807 | 0 | 0 | 0 | -807 | 0 | 75 | 38 | 408 | 574 | 807 | 1902 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117600 | 117600 | 117600 | 117600 | 117600 | C2 | 391.608 | 391.608 | 545.664 | 1341.816 | 2811.816 | C2 | 29370.6 | 152727.12 | 359592.576 | 42938.112 | 2117297.448 | 2701925.856 |  | 29370.6 | 151943.904 | 356864.256 | 42938.112 | 2117297.448 | 2698414.32 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 247887.864 | 70489.44 | 458357.76 | 29519.952 | 638282.232 | 1444537.248 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512 |  | 345398.256 | 14881.104 | 222630.912 | 770202.384 | 0 | 1353112.656
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 176400 | 176400 | 176400 | 176400 | 176400 | C3 | 587.412 | 587.412 | 818.496 | 2012.724 | 4217.724 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 294000 | 294000 | 294000 | 294000 | 294000 | C4 | 979.02 | 979.02 | 1364.16 | 3354.54 | 7029.54 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2272 | 2272 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 566 | 0 | 0 | 0 | -566 |  | 126 | 251 | 1011 | 22 | 862 |  | 884 | 0 | 0 | 0 | -884 |  | 126 | 109 | 504 | 649 | 884 | [22 empty] | 43351.0056 | 197683.7184 | 389767.7952 | 100233.6552 | 2148789.7872 | 2879825.9616 |  | 43351.0056 | 196626.3768 | 387039.4752 | 100233.6552 | 2148789.7872 | 2876040.3 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 264061.2744 | 89952.3576 | 523673.7408 | 29519.952 | 774092.9448 | 1681300.2696 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784 |  | 380486.3328 | 34344.0216 | 259299.5328 | 840647.724 | 0 | 1514777.6112
| EHV OHL Conductor (Tower Lines) |  | 155.606 | 155.606 | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 9 | 0 | 0 | -9 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 23 | 0 | 0 | 0 | -23 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | C1 | 5.7637 | 5.7637 | 7.4105 | 18.9379 | 39.5227 | C1 | 0 | 0 | 723.6651 | 0 | 1549.684 | 2273.349 |  | 334.2959 | 0 | 723.3094 | 0 | 0 | 1057.6053 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 386.1694 | 0 | 552.8678 | 265.1313 | 0 | 1204.1685 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019 |  | 466.8616 | 0 | 0 | 1412.8845 | 0 | 1879.746
|  |  | 705.644 | 705.644 | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 117627 | 117627 | 117627 | 117627 | 117627 | C2 | 8.2339 | 8.2339 | 10.5864 | 27.0542 | 56.461 | C2 | 0 | 550.6579 | 6767.0472 | 0 | 0 | 7317.7051 |  | 0 | 550.3038 | 6762.7173 | 0 | 0 | 7313.0212 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | C3 | 12.3508 | 12.3508 | 15.8796 | 40.5813 | 84.6914 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | C4 | 20.5847 | 20.5847 | 26.4661 | 67.6355 | 141.1524 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 861.25 | 861.25 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 9 | 0 | 0 | -9 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 23 | 0 | 0 | 0 | -23 |  | 58 | 0 | 66.834 | 713.416 | 23 | [22 empty] | 0 | 550.6579 | 7490.7123 | 0 | 1549.684 | 9591.0541 |  | 334.2959 | 550.3038 | 7486.0267 | 0 | 0 | 8370.6264 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 386.1694 | 0 | 8023.1186 | 265.1313 | 0 | 8674.4193 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352 |  | 466.8616 | 0 | 707.5335 | 18695.3844 | 0 | 19869.7794
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 |  | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 |  | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 |  | 3672957.6496 | 2760206.8753 | 8032833.271 | 3686491.9602 | 5013066.9062 | 23165556.6623 |  | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 |  | 4312112.7535 | 2759533.2056 | 6522847.5116 | 4892183.8736 | 4383498.7112 | 22870176.0555
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 115 | 115 | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 1 | 0 | 0 | 0 | -1 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 11 | 0 | 0 | 0 | -11 | 0 | 32 | 24 | 7 | 18 | 34 | 115 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | C1 | 2924.2407 | 2924.2407 | 4069.3022 | 10011.3046 | 20976.0668 | C1 | 111121.1473 | 52636.3329 | 118009.7643 | 260293.9199 | 41952.1336 | 584013.298 |  | 119893.8694 | 52636.3329 | 118009.7643 | 250282.6153 | 41952.1336 | 582774.7155 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 99424.1844 | 73106.0179 | 65108.8355 | 210237.3968 | 398545.2693 | 846421.7039 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501 |  | 125742.3509 | 70181.7772 | 28485.1155 | 180203.483 | 482449.5365 | 887062.2631
|  |  | 88 | 88 | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 4 | 0 | 0 | 0 | -4 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 16 | 0 | 0 | 0 | -16 | 0 | 34 | 22 | 0 | 16 | 16 | 88 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 325857 | 325857 | 325857 | 325857 | 325857 | C2 | 4177.4867 | 4177.4867 | 5813.2889 | 14301.8637 | 29965.8097 | C2 | 158744.4961 | 50129.8409 | 93012.6221 | 200226.0922 | 119863.2389 | 621976.2902 |  | 183809.4166 | 50129.8409 | 93012.6221 | 171622.3648 | 119863.2389 | 618437.4832 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 162921.9829 | 87727.2215 | 87199.3332 | 71509.3187 | 239726.4778 | 649084.334 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326 |  | 208874.337 | 91904.7083 | 0 | 228829.8197 | 0 | 529608.865
|  |  | 30 | 30 | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 16 | 0 | 0 | 0 | -16 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 17 | 0 | 0 | 0 | -17 | 0 | 8 | 1 | 0 | 4 | 17 | 30 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | C3 | 6266.2301 | 6266.2301 | 8719.9333 | 21452.7956 | 44948.7146 | C3 | 37597.3807 | 0 | 34879.7333 | 343244.7295 | 89897.4292 | 505619.2726 |  | 56396.071 | 0 | 34879.7333 | 321791.9339 | 89897.4292 | 502965.1674 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 150389.5226 | 6266.2301 | 34879.7333 | 21452.7956 | 0 | 212988.2816 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012 |  | 156655.7527 | 6266.2301 | 0 | 85811.1824 | 0 | 248733.1652
|  |  | 30 | 30 | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 3 | 18 | 5 | 1 | 3 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | C4 | 10443.7169 | 10443.7169 | 14533.2222 | 35754.6593 | 74914.5243 | C4 | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 52218.5842 | 198430.6202 | 72666.111 | 35754.6593 | 0 | 359069.9747 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971 |  | 62662.3011 | 187986.9033 | 72666.111 | 35754.6593 | 0 | 359069.9747
|  |  | 263 | 263 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 23 | 0 | 0 | 0 | -23 |  | 79 | 66 | 40 | 28 | 50 |  | 47 | 0 | 0 | 0 | -47 |  | 77 | 65 | 12 | 39 | 70 | [22 empty] | 349237.8915 | 332527.9445 | 274968.564 | 875274.0603 | 251712.8016 | 2083721.2619 |  | 401874.2244 | 332527.9445 | 274968.564 | 815206.2326 | 251712.8016 | 2076289.7672 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 464954.2742 | 365530.0898 | 259854.0129 | 338954.1704 | 638271.747 | 2067564.2943 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181 |  | 553934.7417 | 356339.6189 | 101151.2265 | 530599.1444 | 482449.5365 | 2024474.268
| 132kV Transformer |  | 63 | 63 | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 3 | 0 | 0 | 0 | -3 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 7 | 0 | 0 | 0 | -7 | 0 | 14 | 8 | 19 | 14 | 8 | 63 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | C1 | 19053.166 | 19053.166 | 26513.9222 | 65229.5989 | 136671.5405 | C1 | 400116.487 | 0 | 1007529.0427 | 65229.5989 | 410014.6216 | 1882889.7502 |  | 419169.6531 | 0 | 981015.1205 | 65229.5989 | 410014.6216 | 1875428.9941 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 323903.8228 | 152425.3284 | 901473.354 | 260918.3956 | 0 | 1638720.9008 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833 |  | 400116.487 | 152425.3284 | 503764.5213 | 913214.3845 | 136671.5405 | 2106192.2618
|  |  | 67 | 67 | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 9 | 0 | 0 | -9 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 23 | 0 | 0 | -11 | -12 | 0 | 22 | 4 | 15 | 14 | 12 | 67 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2123152 | 2123152 | 2123152 | 2123152 | 2123152 | C2 | 27218.8086 | 27218.8086 | 37877.0317 | 93185.1413 | 195245.0579 | C2 | 517157.3642 | 108875.2346 | 1628712.3622 | 0 | 390490.1158 | 2645235.0768 |  | 653251.4074 | 108875.2346 | 1477204.2355 | 0 | 0 | 2239330.8774 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 898220.6851 | 54437.6173 | 1174187.9821 | 93185.1413 | 0 | 2220031.4258 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728 |  | 1224846.3888 | 108875.2346 | 568155.4752 | 279555.4238 | 0 | 2181432.5224
|  |  | 54 | 54 | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 4 | 0 | 0 | -1 | -3 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 5 | 0 | 0 | -1 | -4 | 0 | 6 | 12 | 24 | 8 | 4 | 54 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3184728 | 3184728 | 3184728 | 3184728 | 3184728 | C3 | 40828.213 | 40828.213 | 56815.5475 | 139777.7119 | 292867.5869 | C3 | 244969.2778 | 571594.9814 | 1647650.8781 | 698888.5596 | 0 | 3163103.6969 |  | 326625.7037 | 571594.9814 | 1647650.8781 | 419333.1358 | 0 | 2965204.699 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 408282.1296 | 489938.5555 | 1818097.5206 | 0 | 0 | 2716318.2058 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166 |  | 449110.3426 | 489938.5555 | 1363573.1405 | 978443.9834 | 0 | 3281066.022
|  |  | 9 | 9 | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5307880 | 5307880 | 5307880 | 5307880 | 5307880 | C4 | 68047.0216 | 68047.0216 | 94692.5792 | 232962.8532 | 488112.6448 | C4 | 136094.0432 | 340235.108 | 94692.5792 | 0 | 488112.6448 | 1059134.3752 |  | 204141.0648 | 340235.108 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096
|  |  | 193 | 193 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 16 | 0 | 0 | -10 | -6 |  | 45 | 29 | 98 | 15 | 6 |  | 35 | 0 | 0 | -12 | -23 |  | 43 | 30 | 60 | 36 | 24 | [22 empty] | 1298337.1721 | 1020705.324 | 4378584.8622 | 764118.1585 | 1288617.3823 | 8750362.8991 |  | 1603187.8289 | 1020705.324 | 4200562.8133 | 484562.7347 | 410014.6216 | 7719033.3225 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1698453.6591 | 1173130.6524 | 3988451.4359 | 354103.5369 | 0 | 7214139.2843 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823 |  | 2142120.24 | 1159521.2481 | 2624878.2954 | 2171213.7918 | 136671.5405 | 8234405.1158
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 46.945 | 46.945 | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | C1 | 944.8823 | 944.8823 | 32029.7404 | 78183.8785 | 163819.9411 | C1 | 4653.5453 | 17734.4958 | 744723.4931 | 198899.787 | 0 | 966011.3211 |  | 4653.5453 | 17734.4958 | 744723.4931 | 0 | 0 | 767111.5342 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372
|  |  | 60.282 | 60.282 | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 101111 | 101111 | 101111 | 101111 | 101111 | C2 | 1349.8319 | 1349.8319 | 45756.7719 | 111691.255 | 234028.4873 | C2 | 3039.8213 | 43604.9681 | 1177184.4717 | 380755.4884 | 0 | 1604584.7495 |  | 3039.8213 | 43604.9681 | 1177138.7149 | 0 | 0 | 1223783.5043 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843
|  |  | 42.005 | 42.005 | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | C3 | 2024.7478 | 2024.7478 | 68635.1579 | 167536.8826 | 351042.7309 | C3 | 26141.5185 | 11640.275 | 1602287.7614 | 597436.5232 | 0 | 2237506.0781 |  | 26141.5185 | 11640.275 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834
|  |  | 0.038 | 0.038 | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | C4 | 3374.5796 | 3374.5796 | 114391.9299 | 279228.1376 | 585071.2182 | C4 | 16.8729 | 111.3611 | 0 | 896322.3217 | 0 | 896450.5557 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234
|  |  | 149.27 | 149.27 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0 | [22 empty] | 33851.7581 | 73091.1 | 3524195.7262 | 2073414.1203 | 0 | 5704552.7045 |  | 33851.7581 | 73091.1 | 3524149.9694 | 0 | 0 | 3631092.8274 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389
| 132kV UG Cable (Non Pressurised) |  | 28.233 | 28.233 | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 62.09 | 62.09 | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 636719 | 636719 | 636719 | 636719 | 636719 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 17.808 | 17.808 | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.269 | 3.269 | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 111.4 | 111.4 |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1441 | 1441 | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 3 | 0 | 0 | 0 | -3 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 6 | 0 | 0 | 0 | -6 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | C1 | 457.3005 | 457.3005 | 457.3005 | 23158.3894 | 79345.9572 | C1 | 33840.2397 | 526810.2175 | 63564.7745 | 694751.6822 | 3887951.9004 | 5206918.8143 |  | 50760.3595 | 530925.9223 | 63564.7745 | 694751.6822 | 0 | 1340002.7385 |  | 50760.3595 | 523609.1137 | 64479.3756 | 880018.7975 | 476075.7429 | 1994943.3892 |  | 52132.2611 | 523609.1137 | 64479.3756 | 880018.7975 | 238037.8715 | 1758277.4194 |  | 50760.3595 | 508518.196 | 64936.6761 | 1621087.2586 | 476075.7429 | 2721378.2331 |  | 53504.1627 | 508518.196 | 64936.6761 | 1621087.2586 | 0 | 2248046.2934
|  |  | 1926 | 1926 | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 2 | 0 | 0 | 0 | -2 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 2 | 0 | 0 | 0 | -2 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 1232616 | 1232616 | 1232616 | 1232616 | 1232616 | C2 | 653.2865 | 653.2865 | 653.2865 | 33083.4134 | 113351.3674 | C2 | 50303.059 | 1040685.3626 | 140456.5932 | 926335.5763 | 2040324.6125 | 4198105.2036 |  | 59449.0697 | 1045258.368 | 140456.5932 | 661668.2688 | 0 | 1906832.2997 |  | 59449.0697 | 1038725.5032 | 145682.885 | 661668.2688 | 226702.7347 | 2132228.4614 |  | 60755.6426 | 1038725.5032 | 145682.885 | 661668.2688 | 0 | 1906832.2997 |  | 59449.0697 | 1011287.471 | 143723.0256 | 2150421.8736 | 226702.7347 | 3591584.1746 |  | 60755.6426 | 1011287.471 | 143723.0256 | 2150421.8736 | 0 | 3366188.0129
|  |  | 1045 | 1045 | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 7 | 0 | 0 | 0 | -7 | 0 | 89 | 828 | 53 | 68 | 7 | 1045 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1848924 | 1848924 | 1848924 | 1848924 | 1848924 | C3 | 979.9297 | 979.9297 | 979.9297 | 49625.1202 | 170027.051 | C3 | 18618.6647 | 842739.5592 | 40177.1185 | 1736879.2056 | 15642488.6957 | 18280903.2437 |  | 87213.7451 | 862338.1536 | 40177.1185 | 1736879.2056 | 0 | 2726608.2228 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 811381.8082 | 51936.2752 | 3374508.1709 | 1190189.3573 | 5515229.3566 |  | 94073.2531 | 811381.8082 | 51936.2752 | 3374508.1709 | 0 | 4331899.5073
|  |  | 140 | 140 | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 3081540 | 3081540 | 3081540 | 3081540 | 3081540 | C4 | 1633.2162 | 1633.2162 | 1633.2162 | 82708.5336 | 283378.4184 | C4 | 1633.2162 | 129024.0798 | 81660.81 | 496251.2016 | 1133513.6736 | 1842082.9812 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072
|  |  | 4552 | 4552 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 5 | 0 | 0 | 0 | -5 |  | 296 | 3685 | 458 | 104 | 9 |  | 15 | 0 | 0 | 0 | -15 |  | 296 | 3567 | 463 | 211 | 15 | [22 empty] | 104395.1795 | 2539259.2191 | 325859.2962 | 3854217.6658 | 22704278.8822 | 29528010.2428 |  | 205589.2553 | 2567546.5237 | 325859.2962 | 3589550.3582 | 0 | 6688545.4334 |  | 205589.2553 | 2544877.4828 | 334939.9783 | 4022943.0743 | 872805.5287 | 7981155.3194 |  | 208267.7298 | 2544877.4828 | 334939.9783 | 4022943.0743 | 408064.9225 | 7519093.1878 |  | 205589.2553 | 2460211.555 | 338990.3545 | 7807685.5718 | 1892967.8349 | 12705444.5715 |  | 216499.1395 | 2460211.555 | 338990.3545 | 7807685.5718 | 0 | 10823386.6208
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 2763 | 2763 | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 564 | 0 | 0 | 0 | -564 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 1093 | 0 | 0 | 0 | -1093 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | C1 | 32.0252 | 32.0252 | 44.0347 | 104.082 | 220.1734 | C1 | 13514.6445 | 8838.9618 | 48306.0473 | 57661.4158 | 93573.7014 | 221894.7708 |  | 13418.5689 | 8774.9114 | 48041.8392 | 57661.4158 | 93573.7014 | 221470.4366 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 31480.7952 | 4579.607 | 43374.1628 | 24667.4288 | 91371.9672 | 195473.961 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542 |  | 48454.1639 | 3042.3963 | 28270.2665 | 53394.0547 | 0 | 133160.8814
|  |  | 3992 | 3992 | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 441 | 0 | 0 | -8 | -433 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 713 | 0 | 0 | 0 | -713 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 571879 | 571879 | 571879 | 571879 | 571879 | C2 | 45.7503 | 45.7503 | 62.9067 | 148.6885 | 314.5335 | C2 | 14823.1037 | 23332.6632 | 158461.9521 | 36726.0694 | 129273.248 | 362617.0363 |  | 14731.603 | 23195.4122 | 157581.2585 | 36726.0694 | 129273.248 | 361507.5911 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 34907.4942 | 10202.3214 | 160600.7796 | 30927.2163 | 77060.6953 | 313698.5067 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726 |  | 47397.3315 | 3705.7759 | 134620.3166 | 109286.0769 | 0 | 295009.5009
|  |  | 1996 | 1996 | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 388 | 0 | 0 | 0 | -388 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 767 | 0 | 0 | 0 | -767 | 0 | 94 | 22 | 867 | 246 | 767 | 1996 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | C3 | 68.6255 | 68.6255 | 94.36 | 223.0328 | 471.8002 | C3 | 6519.4206 | 7411.5518 | 97568.2762 | 87205.8287 | 177396.8658 | 376101.9431 |  | 6450.7951 | 7342.9264 | 97002.116 | 87205.8287 | 177396.8658 | 375398.532 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 33077.4814 | 2882.2702 | 101625.7577 | 3568.525 | 178812.2663 | 319966.3005 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115 |  | 59086.5383 | 1509.7606 | 81810.1503 | 54866.0713 | 0 | 197272.5204
|  |  | 333 | 333 | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 50 | 0 | 0 | 0 | -50 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 88 | 0 | 0 | 0 | -88 | 0 | 9 | 50 | 103 | 83 | 88 | 333 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | C4 | 114.3758 | 114.3758 | 157.2667 | 371.7213 | 786.3336 | C4 | 1029.3822 | 12123.8348 | 20759.2077 | 32711.4788 | 0 | 66623.9035 |  | 1029.3822 | 12009.459 | 20601.941 | 32711.4788 | 0 | 66352.261 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 6748.1722 | 5718.79 | 29251.6109 | 0 | 29880.6778 | 71599.2508 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759 |  | 11094.4526 | 5718.79 | 16198.4727 | 30852.872 | 0 | 63864.5873
|  |  | 9084 | 9084 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 1443 | 0 | 0 | -8 | -1435 |  | 844 | 458 | 4801 | 469 | 2512 |  | 2661 | 0 | 0 | 0 | -2661 |  | 846 | 248 | 3752 | 1577 | 2661 | [22 empty] | 35886.551 | 51707.0117 | 325095.4833 | 214304.7927 | 400243.8151 | 1027237.6538 |  | 35630.3492 | 51322.709 | 323227.1546 | 214304.7927 | 400243.8151 | 1024728.8206 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 106213.9429 | 23382.9886 | 334852.3109 | 59163.1701 | 377125.6066 | 900738.019 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142 |  | 166032.4863 | 13976.7228 | 260899.2061 | 248399.0749 | 0 | 689307.4901
| 132kV OHL Conductor (Tower Lines) |  | 679.807 | 679.808 | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 70.837 | 0 | 0 | 0 | -70.837 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 111.102 | 0 | 0 | -16.886 | -94.215 | 0.001 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 401324 | 401324 | 401324 | 401324 | 401324 | C1 | 28.0927 | 28.0927 | 36.1192 | 92.3045 | 192.6355 | C1 | 1047.7727 | 4017.8151 | 14675.6843 | 2569.9424 | 12785.99 | 35097.2045 |  | 1045.8624 | 4010.4829 | 14650.0397 | 2569.9424 | 12785.99 | 35062.3174 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 1990.0012 | 1045.8624 | 19196.5028 | 1558.6541 | 4503.4332 | 28294.4537 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047 |  | 3121.1529 | 1045.8624 | 8757.1265 | 26678.4062 | 0 | 39602.548
|  |  | 985.034 | 985.034 | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 52.059 | 0 | 0 | 0 | -52.059 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 114.72 | 0 | 0 | -19.967 | -94.753 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 573320 | 573320 | 573320 | 573320 | 573320 | C2 | 40.1324 | 40.1324 | 51.5988 | 131.8636 | 275.1936 | C2 | 605.317 | 2546.8824 | 42102.918 | 0 | 25348.3577 | 70603.4751 |  | 604.2334 | 2542.227 | 42028.3062 | 0 | 25348.3577 | 70523.1243 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 2089.2526 | 604.2334 | 44130.2865 | 2981.3041 | 11022.0541 | 60827.1307 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871 |  | 4603.9889 | 604.2334 | 11388.5259 | 83673.3881 | 0 | 100270.1363
|  |  | 492.36 | 492.36 | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 3.104 | 0 | 0 | 0 | -3.104 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 19.157 | 0 | 0 | -0.654 | -18.503 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 859980 | 859980 | 859980 | 859980 | 859980 | C3 | 60.1986 | 60.1986 | 77.3982 | 197.7954 | 412.7904 | C3 | 1699.8881 | 5135.7834 | 27953.9079 | 3047.2359 | 1277.9991 | 39114.8143 |  | 1696.8179 | 5126.3924 | 27903.0573 | 3047.2359 | 1277.9991 | 39051.5026 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 186.8565 | 1696.8179 | 34443.4374 | 129.3582 | 6356.5594 | 42813.0293 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646 |  | 1153.2246 | 1696.8179 | 10890.7007 | 60190.327 | 0 | 73931.0702
|  |  | 82.199 | 82.199 | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 23.021 | 0 | 0 | -23.021 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 1433300 | 1433300 | 1433300 | 1433300 | 1433300 | C4 | 100.331 | 100.331 | 128.997 | 329.659 | 687.984 | C4 | 0 | 50.3662 | 10552.5996 | 0 | 0 | 10602.9657 |  | 0 | 50.2658 | 10538.7969 | 0 | 0 | 10589.0627 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416 |  | 2309.72 | 0 | 408.9205 | 18463.5413 | 0 | 21182.1817
|  |  | 2239.4 | 2239.401 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 126 | 0 | 0 | 0 | -126 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 268 | 0 | 0 | -60.528 | -207.471 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471 | [22 empty] | 3352.9777 | 11750.847 | 95285.1098 | 5617.1784 | 39412.3468 | 155418.4597 |  | 3346.9137 | 11729.3681 | 95120.2 | 5617.1784 | 39412.3468 | 155226.007 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 4266.1102 | 3346.9137 | 105151.435 | 12903.8686 | 21882.0466 | 147550.3742 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298 |  | 11188.0864 | 3346.9137 | 31445.2736 | 189005.6625 | 0 | 234985.9363
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 |  | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 |  | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 |  | 2500367.7826 | 4177720.5746 | 9268695.1682 | 4788067.8202 | 1445344.3227 | 22180195.6684 |  | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 |  | 3096042.5031 | 4055013.7227 | 8205486.5216 | 10946903.2455 | 619121.077 | 26922567.07
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 429606.482 | 429102.483 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 33858 | -368 | -2154 | -6237 | -25351 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 67410 | -864 | -3512 | -10736.528 | -52801.471 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 |  | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 |  | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 |  | 24103081.2131 | 21498088.2668 | 36479823.6357 | 14350879.3439 | 28444194.358 | 124876066.8175 |  | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 |  | 24947734.7457 | 21919298.7065 | 31669772.6725 | 25473822.09 | 28977878.803 | 132988507.0178
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 | LV Network | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 4562727.3965 | 3313431.5131 | 5603107.0395 | 1420604.9582 | 4834619.6686 | 19734490.5759 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 | LV Network | 4449896.867 | 3269085.4089 | 5129014.9386 | 2329182.0911 | 6502070.0923 | 21679249.3979
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 | HV Network | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 13367028.3844 | 11246729.3037 | 13575188.1569 | 4455714.6053 | 17151163.4605 | 59795823.9109 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 | HV Network | 13089682.6222 | 11835666.3692 | 11812423.7007 | 7305552.8798 | 17473188.9224 | 61516514.4944
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 | EHV Network | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 | EHV Network | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 | EHV Network | 3672957.6496 | 2760206.8753 | 8032833.271 | 3686491.9602 | 5013066.9062 | 23165556.6623 | EHV Network | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 | EHV Network | 4312112.7535 | 2759533.2056 | 6522847.5116 | 4892183.8736 | 4383498.7112 | 22870176.0555
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 | 132kV Network | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 | 132kV Network | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 | 132kV Network | 2500367.7826 | 4177720.5746 | 9268695.1682 | 4788067.8202 | 1445344.3227 | 22180195.6684 | 132kV Network | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 | 132kV Network | 3096042.5031 | 4055013.7227 | 8205486.5216 | 10946903.2455 | 619121.077 | 26922567.07
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 | Total | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 | Total | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 | Total | 24103081.2131 | 21498088.2668 | 36479823.6357 | 14350879.3439 | 28444194.358 | 124876066.8175 | Total | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 | Total | 24947734.7457 | 21919298.7065 | 31669772.6725 | 25473822.09 | 28977878.803 | 132988507.0178
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EMID - Refurb
Secondary deliverables RIIO-ED1 - Refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EMID | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | C1 | 42.9585 | 42.9585 | 59.7801 | 147.071 | 308.1488 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 0 | 0 | 0 | 0 | 0 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 0 | 0 | 0 | 0 | 0 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4787 | 4787 | 4787 | 4787 | 4787 | C2 | 61.3693 | 61.3693 | 85.4001 | 210.1014 | 440.2125 | C2 | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | C3 | 92.054 | 92.054 | 128.1001 | 315.1521 | 660.3188 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | C4 | 153.4233 | 153.4233 | 213.5002 | 525.2536 | 1100.5313 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617 | [22 empty] | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162
| LV Switchgear (at s/s) |  | 8 | 8 | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | C1 | 95.4965 | 95.4965 | 132.8107 | 326.7848 | 684.7228 | C1 | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861
|  |  | 17231 | 17231 | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 0 | 0 | 0 | 0 | 0 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 0 | 0 | 0 | 0 | 0 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 7098 | 7098 | 7098 | 7098 | 7098 | C2 | 136.4236 | 136.4236 | 189.7295 | 466.8355 | 978.1754 | C2 | 1236133.8772 | 393036.2764 | 931572.0414 | 63489.6226 | 59668.6982 | 2683900.5157 |  | 1302572.1509 | 384441.5921 | 910701.792 | 21941.2666 | 17607.1568 | 2637263.9584 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516
|  |  | 1354 | 1354 | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 206 | 618 | 94 | 49 | 1354 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 10647 | 10647 | 10647 | 10647 | 10647 | C3 | 204.6353 | 204.6353 | 284.5943 | 700.2532 | 1467.2631 | C3 | 96997.1512 | 48089.3049 | 169049.0201 | 18906.8361 | 16139.8938 | 349182.2061 |  | 105182.5648 | 47475.3989 | 166772.2657 | 13304.8106 | 4401.7892 | 337136.8291 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 17745 | 17745 | 17745 | 17745 | 17745 | C4 | 341.0589 | 341.0589 | 474.3238 | 1167.0886 | 2445.4384 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18593 | 18593 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 0 | 0 | 0 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317 | [22 empty] | 1333799.5038 | 441125.5813 | 1100753.8722 | 82396.4587 | 75808.5919 | 3033884.0079 |  | 1408423.1911 | 431916.991 | 1077606.8683 | 35246.0772 | 22008.946 | 2975202.0737 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682
| LV UGB and LV Pillar OD (not at s/s) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | C1 | 77.7776 | 77.7776 | 108.1683 | 266.1515 | 557.6757 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27987 | 27987 | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 0 | 0 | 0 | 0 | 0 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 0 | 0 | 0 | 0 | 0 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5781 | 5781 | 5781 | 5781 | 5781 | C2 | 111.1108 | 111.1108 | 154.5261 | 380.2164 | 796.6796 | C2 | 576776.2666 | 566331.8495 | 2504250.4628 | 216343.1145 | 658854.0375 | 4522555.7309 |  | 636331.6661 | 564554.0764 | 2496524.1563 | 216343.1145 | 361692.5429 | 4275445.5563 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821
|  |  | 1022 | 1022 | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 116 | 557 | 157 | 144 | 1022 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | C3 | 166.6662 | 166.6662 | 231.7892 | 570.3246 | 1195.0194 | C3 | 14666.6282 | 39166.5641 | 152749.0795 | 9695.5174 | 22705.3689 | 238983.1581 |  | 17166.6217 | 38999.8978 | 152285.5011 | 9695.5174 | 13145.2136 | 231292.7516 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | C4 | 277.7771 | 277.7771 | 386.3153 | 950.5409 | 1991.699 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29009 | 29009 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 0 | 0 | 0 | 0 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 0 | 0 | 0 | 0 | 0 |  | 4361 | 2740 | 13705 | 3889 | 4314 | [22 empty] | 591442.8949 | 605498.4136 | 2656999.5423 | 226038.632 | 681559.4064 | 4761538.8891 |  | 653498.2878 | 603553.9742 | 2648809.6574 | 226038.632 | 374837.7565 | 4506738.3079 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 |  | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 809 | 809 | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 168 | 215 | 121 | 109 | 809 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | C1 | 722.066 | 722.066 | 1004.8095 | 2472.034 | 5179.4999 | C1 | 186293.0249 | 113364.3601 | 366755.4514 | 61800.8506 | 15538.4996 | 743752.1867 |  | 197846.0807 | 111920.2281 | 356707.3569 | 61800.8506 | 0 | 728274.5164 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655
|  |  | 2623 | 2623 | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 464 | 728 | 364 | 323 | 2623 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 80462 | 80462 | 80462 | 80462 | 80462 | C2 | 1031.5228 | 1031.5228 | 1435.4421 | 3531.4772 | 7399.2855 | C2 | 926307.5103 | 340402.5372 | 1890477.2194 | 183636.8134 | 125787.8538 | 3466611.9341 |  | 989230.4036 | 338339.4915 | 1840236.7466 | 183636.8134 | 14798.571 | 3366242.026 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414
|  |  | 880 | 880 | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 156 | 248 | 138 | 148 | 880 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 120693 | 120693 | 120693 | 120693 | 120693 | C3 | 1547.2843 | 1547.2843 | 2153.1631 | 5297.2158 | 11098.9283 | C3 | 331118.8316 | 188768.6797 | 1093806.865 | 100647.0996 | 133187.1394 | 1847528.6153 |  | 385273.7807 | 187221.3955 | 1057203.0919 | 100647.0996 | 0 | 1730345.3678 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694
|  |  | 20 | 20 | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 3 | 4 | 2 | 20 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 201155 | 201155 | 201155 | 201155 | 201155 | C4 | 2578.8071 | 2578.8071 | 3588.6052 | 8828.693 | 18498.2138 | C4 | 12894.0355 | 12894.0355 | 25120.2364 | 17657.3859 | 18498.2138 | 87063.9071 |  | 18051.6497 | 12894.0355 | 25120.2364 | 8828.693 | 0 | 64894.6145 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931
|  |  | 4332 | 4332 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582 | [22 empty] | 1456613.4024 | 655429.6125 | 3376159.7722 | 363742.1495 | 293011.7066 | 6144956.6432 |  | 1590401.9147 | 650375.1506 | 3279267.4318 | 354913.4566 | 14798.571 | 5889756.5247 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859
| HV Switchgear (GM) - Distribution |  | 9569 | 9569 | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 0 | 0 | 0 | 0 | 0 | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 0 | 0 | 0 | 0 | 0 | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | C1 | 205.8277 | 205.8277 | 286.4248 | 704.6627 | 1476.4362 | C1 | 1190918.8639 | 207268.4576 | 765613.4049 | 125429.9656 | 160931.5449 | 2450162.2369 |  | 1286422.9 | 146137.6414 | 744704.3968 | 6341.9646 | 0 | 2183606.9028 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589
|  |  | 12994 | 12994 | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 0 | 0 | 0 | 0 | 0 | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 22936 | 22936 | 22936 | 22936 | 22936 | C2 | 294.0395 | 294.0395 | 409.1782 | 1006.661 | 2109.1946 | C2 | 1485781.6946 | 1000910.5261 | 1723049.5686 | 437897.5524 | 442930.8576 | 5090570.1993 |  | 1709839.8088 | 946219.1754 | 1613389.8003 | 18119.8987 | 0 | 4287568.6832 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461
|  |  | 5187 | 5187 | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 0 | 0 | 0 | 0 | 0 | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 0 | 0 | 0 | 0 | 0 | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 34404 | 34404 | 34404 | 34404 | 34404 | C3 | 441.0593 | 441.0593 | 613.7674 | 1509.9916 | 3163.7918 | C3 | 726865.6934 | 434884.4501 | 1477338.0355 | 472627.3583 | 578973.9067 | 3690689.444 |  | 978710.5423 | 426063.2645 | 1228762.2547 | 0 | 0 | 2633536.0615 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488
|  |  | 143 | 143 | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 64 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 20 | 43 | 27 | 0 | 143 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 57340 | 57340 | 57340 | 57340 | 57340 | C4 | 735.0988 | 735.0988 | 1022.9456 | 2516.6526 | 5272.9864 | C4 | 38960.2364 | 14701.976 | 61376.736 | 30199.8312 | 47456.8776 | 192695.6572 |  | 52192.0148 | 13231.7784 | 55239.0624 | 0 | 0 | 120662.8556 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934
|  |  | 27893 | 27893 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 0 | 0 | 0 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810 | [22 empty] | 3442526.4883 | 1657765.4098 | 4027377.745 | 1066154.7075 | 1230293.1868 | 11424117.5374 |  | 4027165.2659 | 1531651.8597 | 3642095.5142 | 24461.8633 | 0 | 9225374.5031 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472
| HV Transformer (GM) |  | 3306 | 3306 | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 15848 | 15848 | 15848 | 15848 | 15848 | C1 | 304.5986 | 304.5986 | 423.617 | 1042.323 | 2184.0129 | C1 | 560461.3504 | 141333.7318 | 351178.5262 | 75047.2531 | 165984.9789 | 1294005.8404 |  | 575691.2784 | 140419.9362 | 349060.441 | 75047.2531 | 128856.7599 | 1269075.6686 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886
|  |  | 13028 | 13028 | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 0 | 0 | 0 | 0 | 0 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 22640 | 22640 | 22640 | 22640 | 22640 | C2 | 435.1408 | 435.1408 | 605.1672 | 1489.0328 | 3120.0184 | C2 | 3131708.3376 | 1113525.3072 | 1710202.5072 | 227822.0184 | 589683.4776 | 6772941.648 |  | 3214385.0896 | 1105692.7728 | 1701124.9992 | 227822.0184 | 424322.5024 | 6673347.3824 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888
|  |  | 3266 | 3266 | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 33960 | 33960 | 33960 | 33960 | 33960 | C3 | 652.7112 | 652.7112 | 907.7508 | 2233.5492 | 4680.0276 | C3 | 821110.6896 | 380530.6296 | 1130149.746 | 183151.0344 | 336961.9872 | 2851904.0868 |  | 855051.672 | 377919.7848 | 1124703.2412 | 183151.0344 | 262081.5456 | 2802907.278 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908
|  |  | 118 | 118 | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 27 | 25 | 9 | 26 | 118 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 56600 | 56600 | 56600 | 56600 | 56600 | C4 | 1087.852 | 1087.852 | 1512.918 | 3722.582 | 7800.046 | C4 | 55480.452 | 7614.964 | 78671.736 | 18612.91 | 23400.138 | 183780.2 |  | 57656.156 | 7614.964 | 78671.736 | 18612.91 | 7800.046 | 170355.812 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8
|  |  | 19718 | 19718 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 0 | 0 | 0 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 0 | 0 | 0 | 0 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318 | [22 empty] | 4568760.8296 | 1643004.6326 | 3270202.5154 | 504633.2159 | 1116030.5817 | 11102631.7752 |  | 4702784.196 | 1631647.4578 | 3253560.4174 | 504633.2159 | 823060.8539 | 10915686.141 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828
| HV UG Cable |  | 3200.153 | 3200.153 | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 34503 | 34503 | 34503 | 34503 | 34503 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7275.757 | 7275.757 | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 49290 | 49290 | 49290 | 49290 | 49290 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3676.577 | 3676.577 | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 73935 | 73935 | 73935 | 73935 | 73935 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 123225 | 123225 | 123225 | 123225 | 123225 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14152.487 | 14152.487 |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | C1 | 72.5009 | 72.5009 | 100.8906 | 248.2111 | 520.0614 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 129615 | 129615 | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 0 | 0 | 0 | 0 | 0 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 0 | 0 | 0 | 0 | 0 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 8079 | 8079 | 8079 | 8079 | 8079 | C2 | 103.5728 | 103.5728 | 144.1294 | 354.5873 | 742.9448 | C2 | 2343127.0019 | 5487907.3211 | 3641860.6685 | 1934273.776 | 16903480.9997 | 30310649.7672 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451
|  |  | 18228 | 18228 | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | C3 | 155.3592 | 155.3592 | 216.194 | 531.881 | 1114.4173 | C3 | 494508.2381 | 1157581.1757 | 768137.4241 | 407952.7002 | 3565020.8147 | 6393200.3528 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303
|  |  | 253 | 253 | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 104 | 51 | 16 | 75 | 253 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | C4 | 258.9319 | 258.9319 | 360.3234 | 886.4683 | 1857.3621 | C4 | 11393.0058 | 26928.9228 | 17655.8466 | 9751.151 | 81723.9324 | 147452.8586 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897
|  |  | 148096 | 148096 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746 | [22 empty] | 2849028.2459 | 6672417.4195 | 4427653.9392 | 2351977.6272 | 20550225.7468 | 36851302.9787 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 |  | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 658 | 658 | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 205 | 49 | 13 | 117 | 658 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | C1 | 1418.4215 | 1418.4215 | 1973.8408 | 4856.0467 | 10174.5739 | C1 | 524815.9424 | 191486.8979 | 276337.7109 | 33992.3266 | 20349.1479 | 1046982.0257 |  | 547510.6859 | 185813.212 | 268442.3477 | 24280.2333 | 0 | 1026046.4789 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395
|  |  | 432 | 432 | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 91 | 21 | 49 | 106 | 432 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 158059 | 158059 | 158059 | 158059 | 158059 | C2 | 2026.3164 | 2026.3164 | 2819.7726 | 6937.2095 | 14535.1056 | C2 | 387026.4286 | 129684.2483 | 487820.6529 | 0 | 0 | 1004531.3298 |  | 431605.3889 | 121578.9828 | 448343.837 | 0 | 0 | 1001528.2088 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809
|  |  | 137 | 137 | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 14 | 12 | 33 | 137 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | C3 | 3039.4746 | 3039.4746 | 4229.6588 | 10405.8143 | 21802.6585 | C3 | 197565.847 | 45592.1185 | 215712.6008 | 0 | 43605.3169 | 502475.8834 |  | 227960.5927 | 45592.1185 | 198793.9655 | 0 | 0 | 472346.6768 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406
|  |  | 91 | 91 | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | C4 | 5065.7909 | 5065.7909 | 7049.4314 | 17343.0238 | 36337.7641 | C4 | 96250.028 | 116513.1918 | 345422.1386 | 0 | 0 | 558185.3585 |  | 141842.1466 | 91184.2371 | 317224.413 | 0 | 0 | 550250.7967 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405
|  |  | 1318 | 1318 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285 | [22 empty] | 1205658.2461 | 483276.4566 | 1325293.1032 | 33992.3266 | 63954.4648 | 3112174.5973 |  | 1348918.8142 | 444168.5505 | 1232804.5632 | 24280.2333 | 0 | 3050172.1612 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014
| EHV Transformer |  | 234 | 234 | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | C1 | 4228.4321 | 4228.4321 | 5884.1833 | 14476.2782 | 30331.2496 | C1 | 215650.039 | 224106.9033 | 629607.6084 | 246096.7294 | 151656.2478 | 1467117.528 |  | 232563.7676 | 219878.4712 | 617839.2419 | 246096.7294 | 151656.2478 | 1468034.4579 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721
|  |  | 290 | 290 | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 47 | 78 | 72 | 43 | 290 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 471187 | 471187 | 471187 | 471187 | 471187 | C2 | 6040.6173 | 6040.6173 | 8405.9761 | 20680.3974 | 43330.3565 | C2 | 380558.8924 | 223502.8416 | 1361768.125 | 413607.9486 | 346642.8522 | 2726080.6597 |  | 416802.5965 | 211421.6069 | 1344956.1728 | 413607.9486 | 259982.1391 | 2646770.4639 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615
|  |  | 179 | 179 | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | C3 | 9060.926 | 9060.926 | 12608.9641 | 31020.5961 | 64995.5348 | C3 | 271827.7803 | 353376.1144 | 1273505.3761 | 248164.7692 | 64995.5348 | 2211869.5748 |  | 353376.1144 | 353376.1144 | 1172633.6632 | 248164.7692 | 0 | 2127550.6611 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519
|  |  | 9 | 9 | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | C4 | 15101.5433 | 15101.5433 | 21014.9402 | 51700.9936 | 108325.8913 | C4 | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739
|  |  | 712 | 712 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 0 | 0 | 0 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 0 | 0 | 0 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124 | [22 empty] | 868036.7118 | 816087.4026 | 3433000.6311 | 907869.4472 | 563294.6348 | 6588288.8274 |  | 1002742.4784 | 799777.7358 | 3303548.5994 | 907869.4472 | 411638.3869 | 6425576.6478 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | C1 | 217.2993 | 217.2993 | 7366.0388 | 17980.3357 | 37674.4873 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132.569 | 132.569 | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 23253 | 23253 | 23253 | 23253 | 23253 | C2 | 310.4275 | 310.4275 | 10522.9126 | 25686.1939 | 53820.6962 | C2 | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369
|  |  | 20.77 | 20.77 | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | C3 | 465.6413 | 465.6413 | 15784.3689 | 38529.2909 | 80731.0443 | C3 | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229
|  |  | 7.371 | 7.371 | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | C4 | 776.0689 | 776.0689 | 26307.2815 | 64215.4848 | 134551.7405 | C4 | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457
|  |  | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0 | [22 empty] | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055
| EHV UG Cable (Non Pressurised) |  | 474.229 | 474.229 | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 929.677 | 929.677 | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 68614 | 68614 | 68614 | 68614 | 68614 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 292.451 | 292.451 | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 102921 | 102921 | 102921 | 102921 | 102921 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44.608 | 44.608 | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 171535 | 171535 | 171535 | 171535 | 171535 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1740.965 | 1740.965 |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 140 | 140 | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 2 | 0 | -2 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 4 | 0 | -4 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | C1 | 89.8543 | 89.8543 | 89.8543 | 4550.3597 | 15590.5765 | C1 | 0 | 8626.0171 | 628.9804 | 59154.6756 | 374173.837 | 442583.5101 |  | 2156.5043 | 8626.0171 | 628.9804 | 59154.6756 | 0 | 70566.1774 |  | 2156.5043 | 7637.6193 | 808.6891 | 91007.1932 | 31181.1531 | 132791.159 |  | 2156.5043 | 7817.328 | 808.6891 | 81906.4739 | 31181.1531 | 123870.1484 |  | 1976.7956 | 7278.2019 | 898.5434 | 104658.2722 | 62362.3062 | 177174.1193 |  | 1976.7956 | 7637.6193 | 898.5434 | 86456.8335 | 62362.3062 | 159332.0981
|  |  | 557 | 557 | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 10 | 0 | -10 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 20 | 0 | -20 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 242195 | 242195 | 242195 | 242195 | 242195 | C2 | 128.3633 | 128.3633 | 128.3633 | 6500.5138 | 22272.2522 | C2 | 128.3633 | 49291.5264 | 2952.3571 | 338026.7176 | 2204952.9678 | 2595351.9322 |  | 12836.335 | 50061.7065 | 2695.6303 | 299023.6348 | 0 | 364617.3066 |  | 12836.335 | 47879.5295 | 2952.3571 | 351027.7452 | 155905.7654 | 570601.7322 |  | 12836.335 | 49163.163 | 2952.3571 | 286022.6072 | 155905.7654 | 506880.2277 |  | 12194.5182 | 47751.1662 | 3080.7204 | 364028.7728 | 222722.522 | 649777.6996 |  | 12194.5182 | 50318.4332 | 3080.7204 | 234018.4968 | 222722.522 | 522334.6907
|  |  | 441 | 441 | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 12 | 0 | -12 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 24 | 0 | -24 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | C3 | 192.545 | 192.545 | 192.545 | 9750.7707 | 33408.3783 | C3 | 0 | 60074.0478 | 7124.1659 | 312024.6624 | 2004502.698 | 2383725.5741 |  | 13093.0617 | 61229.3179 | 7124.1659 | 175513.8726 | 0 | 256960.4182 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 13093.0617 | 61614.408 | 7509.256 | 126760.0191 | 33408.3783 | 242385.1231 |  | 12130.3366 | 58726.2326 | 7701.801 | 273021.5796 | 167041.8915 | 518621.8413 |  | 12130.3366 | 63347.3132 | 7701.801 | 39003.0828 | 167041.8915 | 289224.4251
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | C4 | 320.9084 | 320.9084 | 320.9084 | 16251.2845 | 55680.6305 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1138 | 1138 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 24 | 0 | -24 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 48 | 0 | -48 | 0 |  | 180 | 758 | 74 | 107 | 19 | [22 empty] | 128.3633 | 117991.5913 | 10705.5034 | 709206.0556 | 4583629.5028 | 5421661.0164 |  | 28085.901 | 119917.0416 | 10448.7767 | 533692.183 | 0 | 692143.9022 |  | 28085.901 | 114821.0166 | 11270.3021 | 685804.2059 | 220495.2968 | 1060476.7224 |  | 28085.901 | 118594.8991 | 11270.3021 | 494689.1002 | 220495.2968 | 873135.4991 |  | 26301.6504 | 113755.6008 | 11681.0648 | 741708.6246 | 452126.7197 | 1345573.6603 |  | 26301.6504 |  | 11681.0648 |  | 452126.7197 | 490109.4349
| EHV OHL Support - Poles |  | 3622 | 3622 | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | C1 | 124.8642 | 124.8642 | 173.758 | 427.4798 | 895.672 | C1 | 30716.6021 | 105510.2794 | 300080.1213 | 128243.9466 | 451418.692 | 1015969.6414 |  | 45450.5819 | 105510.2794 | 299037.5731 | 120549.3098 | 367225.5233 | 937773.2675 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951
|  |  | 21560 | 21560 | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 13914 | 13914 | 13914 | 13914 | 13914 | C2 | 178.3775 | 178.3775 | 248.2258 | 610.6855 | 1279.5314 | C2 | 261679.7632 | 896703.592 | 2551264.3613 | 1089462.8606 | 3843712.4458 | 8642823.0228 |  | 387079.1316 | 896703.592 | 2542576.4597 | 1025951.5728 | 3122056.7136 | 7974367.4696 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627
|  |  | 2373 | 2373 | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 20871 | 20871 | 20871 | 20871 | 20871 | C3 | 267.5662 | 267.5662 | 372.3386 | 916.0282 | 1919.2972 | C3 | 43078.1614 | 147964.1197 | 421115.0018 | 181373.5816 | 633368.0628 | 1426898.9273 |  | 63948.3266 | 147964.1197 | 419625.6473 | 170381.2433 | 514371.6389 | 1316290.9757 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942
|  |  | 18 | 18 | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 34785 | 34785 | 34785 | 34785 | 34785 | C4 | 445.9437 | 445.9437 | 620.5644 | 1526.7136 | 3198.8286 | C4 | 445.9437 | 1783.7748 | 5585.0796 | 3053.4273 | 6397.6572 | 17265.8826 |  | 891.8874 | 1783.7748 | 5585.0796 | 1526.7136 | 6397.6572 | 16185.1126 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675
|  |  | 27573 | 27573 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 0 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 0 | 0 | 0 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289 | [22 empty] | 335920.4703 | 1151961.7658 | 3278044.564 | 1402133.8162 | 4934896.8578 | 11102957.4741 |  | 497369.9275 | 1151961.7658 | 3266824.7596 | 1318408.8396 | 4010051.533 | 10244616.8255 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 370 | 370 | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82320 | 82320 | 82320 | 82320 | 82320 | C1 | 274.1256 | 274.1256 | 381.9648 | 939.2712 | 1968.2712 | C1 | 13980.4056 | 44956.5984 | 30175.2192 | 57295.5432 | 31492.3392 | 177900.1056 |  | 13980.4056 | 44682.4728 | 30175.2192 | 57295.5432 | 31492.3392 | 177625.98 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664
|  |  | 1902 | 1902 | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117600 | 117600 | 117600 | 117600 | 117600 | C2 | 391.608 | 391.608 | 545.664 | 1341.816 | 2811.816 | C2 | 29370.6 | 152727.12 | 359592.576 | 42938.112 | 2117297.448 | 2701925.856 |  | 29370.6 | 151943.904 | 356864.256 | 42938.112 | 2117297.448 | 2698414.32 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 176400 | 176400 | 176400 | 176400 | 176400 | C3 | 587.412 | 587.412 | 818.496 | 2012.724 | 4217.724 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 294000 | 294000 | 294000 | 294000 | 294000 | C4 | 979.02 | 979.02 | 1364.16 | 3354.54 | 7029.54 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2272 | 2272 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884 | [22 empty] | 43351.0056 | 197683.7184 | 389767.7952 | 100233.6552 | 2148789.7872 | 2879825.9616 |  | 43351.0056 | 196626.3768 | 387039.4752 | 100233.6552 | 2148789.7872 | 2876040.3 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784
| EHV OHL Conductor (Tower Lines) |  | 155.606 | 155.606 | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | C1 | 5.7637 | 5.7637 | 7.4105 | 18.9379 | 39.5227 | C1 | 0 | 0 | 723.6651 | 0 | 1549.684 | 2273.349 |  | 334.2959 | 0 | 723.3094 | 0 | 0 | 1057.6053 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019
|  |  | 705.644 | 705.644 | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 117627 | 117627 | 117627 | 117627 | 117627 | C2 | 8.2339 | 8.2339 | 10.5864 | 27.0542 | 56.461 | C2 | 0 | 550.6579 | 6767.0472 | 0 | 0 | 7317.7051 |  | 0 | 550.3038 | 6762.7173 | 0 | 0 | 7313.0212 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | C3 | 12.3508 | 12.3508 | 15.8796 | 40.5813 | 84.6914 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | C4 | 20.5847 | 20.5847 | 26.4661 | 67.6355 | 141.1524 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 861.25 | 861.25 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23 | [22 empty] | 0 | 550.6579 | 7490.7123 | 0 | 1549.684 | 9591.0541 |  | 334.2959 | 550.3038 | 7486.0267 | 0 | 0 | 8370.6264 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 |  | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 |  | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 |  | 2320125.7008 | 2763980.7578 | 8238386.5002 | 4969527.6114 | 10685723.4023 | 28977743.9725 |  | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 |  | 1793644.7601 | 2759533.2056 | 6744810.9862 | 5936229.9899 | 19552965.3925 | 36787184.3343
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 115 | 115 | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 7 | 18 | 34 | 115 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | C1 | 2924.2407 | 2924.2407 | 4069.3022 | 10011.3046 | 20976.0668 | C1 | 111121.1473 | 52636.3329 | 118009.7643 | 260293.9199 | 41952.1336 | 584013.298 |  | 119893.8694 | 52636.3329 | 118009.7643 | 250282.6153 | 41952.1336 | 582774.7155 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501
|  |  | 88 | 88 | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22 | 0 | 16 | 16 | 88 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 325857 | 325857 | 325857 | 325857 | 325857 | C2 | 4177.4867 | 4177.4867 | 5813.2889 | 14301.8637 | 29965.8097 | C2 | 158744.4961 | 50129.8409 | 93012.6221 | 200226.0922 | 119863.2389 | 621976.2902 |  | 183809.4166 | 50129.8409 | 93012.6221 | 171622.3648 | 119863.2389 | 618437.4832 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326
|  |  | 30 | 30 | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 4 | 17 | 30 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | C3 | 6266.2301 | 6266.2301 | 8719.9333 | 21452.7956 | 44948.7146 | C3 | 37597.3807 | 0 | 34879.7333 | 343244.7295 | 89897.4292 | 505619.2726 |  | 56396.071 | 0 | 34879.7333 | 321791.9339 | 89897.4292 | 502965.1674 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012
|  |  | 30 | 30 | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | C4 | 10443.7169 | 10443.7169 | 14533.2222 | 35754.6593 | 74914.5243 | C4 | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971
|  |  | 263 | 263 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 79 | 66 | 40 | 28 | 50 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 65 | 12 | 39 | 70 | [22 empty] | 349237.8915 | 332527.9445 | 274968.564 | 875274.0603 | 251712.8016 | 2083721.2619 |  | 401874.2244 | 332527.9445 | 274968.564 | 815206.2326 | 251712.8016 | 2076289.7672 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181
| 132kV Transformer |  | 63 | 63 | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | C1 | 19053.166 | 19053.166 | 26513.9222 | 65229.5989 | 136671.5405 | C1 | 400116.487 | 0 | 1007529.0427 | 65229.5989 | 410014.6216 | 1882889.7502 |  | 419169.6531 | 0 | 981015.1205 | 65229.5989 | 410014.6216 | 1875428.9941 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833
|  |  | 67 | 67 | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 15 | 14 | 12 | 67 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2123152 | 2123152 | 2123152 | 2123152 | 2123152 | C2 | 27218.8086 | 27218.8086 | 37877.0317 | 93185.1413 | 195245.0579 | C2 | 517157.3642 | 108875.2346 | 1628712.3622 | 0 | 390490.1158 | 2645235.0768 |  | 653251.4074 | 108875.2346 | 1477204.2355 | 0 | 0 | 2239330.8774 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728
|  |  | 54 | 54 | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 24 | 8 | 4 | 54 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3184728 | 3184728 | 3184728 | 3184728 | 3184728 | C3 | 40828.213 | 40828.213 | 56815.5475 | 139777.7119 | 292867.5869 | C3 | 244969.2778 | 571594.9814 | 1647650.8781 | 698888.5596 | 0 | 3163103.6969 |  | 326625.7037 | 571594.9814 | 1647650.8781 | 419333.1358 | 0 | 2965204.699 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166
|  |  | 9 | 9 | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5307880 | 5307880 | 5307880 | 5307880 | 5307880 | C4 | 68047.0216 | 68047.0216 | 94692.5792 | 232962.8532 | 488112.6448 | C4 | 136094.0432 | 340235.108 | 94692.5792 | 0 | 488112.6448 | 1059134.3752 |  | 204141.0648 | 340235.108 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096
|  |  | 193 | 193 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24 | [22 empty] | 1298337.1721 | 1020705.324 | 4378584.8622 | 764118.1585 | 1288617.3823 | 8750362.8991 |  | 1603187.8289 | 1020705.324 | 4200562.8133 | 484562.7347 | 410014.6216 | 7719033.3225 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 46.945 | 46.945 | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | C1 | 944.8823 | 944.8823 | 32029.7404 | 78183.8785 | 163819.9411 | C1 | 4653.5453 | 17734.4958 | 744723.4931 | 198899.787 | 0 | 966011.3211 |  | 4653.5453 | 17734.4958 | 744723.4931 | 0 | 0 | 767111.5342 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372
|  |  | 60.282 | 60.282 | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 101111 | 101111 | 101111 | 101111 | 101111 | C2 | 1349.8319 | 1349.8319 | 45756.7719 | 111691.255 | 234028.4873 | C2 | 3039.8213 | 43604.9681 | 1177184.4717 | 380755.4884 | 0 | 1604584.7495 |  | 3039.8213 | 43604.9681 | 1177138.7149 | 0 | 0 | 1223783.5043 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843
|  |  | 42.005 | 42.005 | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | C3 | 2024.7478 | 2024.7478 | 68635.1579 | 167536.8826 | 351042.7309 | C3 | 26141.5185 | 11640.275 | 1602287.7614 | 597436.5232 | 0 | 2237506.0781 |  | 26141.5185 | 11640.275 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834
|  |  | 0.038 | 0.038 | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | C4 | 3374.5796 | 3374.5796 | 114391.9299 | 279228.1376 | 585071.2182 | C4 | 16.8729 | 111.3611 | 0 | 896322.3217 | 0 | 896450.5557 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234
|  |  | 149.27 | 149.27 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0 | [22 empty] | 33851.7581 | 73091.1 | 3524195.7262 | 2073414.1203 | 0 | 5704552.7045 |  | 33851.7581 | 73091.1 | 3524149.9694 | 0 | 0 | 3631092.8274 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389
| 132kV UG Cable (Non Pressurised) |  | 28.233 | 28.233 | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 62.09 | 62.09 | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 636719 | 636719 | 636719 | 636719 | 636719 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 17.808 | 17.808 | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.269 | 3.269 | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 111.4 | 111.4 |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1441 | 1441 | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 26 | 0 | -26 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 48 | 0 | -48 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | C1 | 457.3005 | 457.3005 | 457.3005 | 23158.3894 | 79345.9572 | C1 | 33840.2397 | 526810.2175 | 63564.7745 | 694751.6822 | 3887951.9004 | 5206918.8143 |  | 50760.3595 | 530925.9223 | 63564.7745 | 694751.6822 | 0 | 1340002.7385 |  | 50760.3595 | 523609.1137 | 64479.3756 | 880018.7975 | 476075.7429 | 1994943.3892 |  | 50760.3595 | 535498.9277 | 64479.3756 | 277900.6729 | 476075.7429 | 1404715.0785 |  | 50760.3595 | 508518.196 | 64936.6761 | 1621087.2586 | 476075.7429 | 2721378.2331 |  | 50760.3595 | 530468.6218 | 64936.6761 | 509484.567 | 476075.7429 | 1631725.9673
|  |  | 1926 | 1926 | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 20 | 0 | -20 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 0 | 62 | 0 | -62 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 1232616 | 1232616 | 1232616 | 1232616 | 1232616 | C2 | 653.2865 | 653.2865 | 653.2865 | 33083.4134 | 113351.3674 | C2 | 50303.059 | 1040685.3626 | 140456.5932 | 926335.5763 | 2040324.6125 | 4198105.2036 |  | 59449.0697 | 1045258.368 | 140456.5932 | 661668.2688 | 0 | 1906832.2997 |  | 59449.0697 | 1038725.5032 | 145682.885 | 661668.2688 | 226702.7347 | 2132228.4614 |  | 59449.0697 | 1051791.2328 | 145682.885 | 0 | 226702.7347 | 1483625.9222 |  | 59449.0697 | 1011287.471 | 143723.0256 | 2150421.8736 | 226702.7347 | 3591584.1746 |  | 59449.0697 | 1051791.2328 | 143723.0256 | 99250.2403 | 226702.7347 | 1580916.3031
|  |  | 1045 | 1045 | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 40 | 0 | -40 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 66 | 0 | -66 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1848924 | 1848924 | 1848924 | 1848924 | 1848924 | C3 | 979.9297 | 979.9297 | 979.9297 | 49625.1202 | 170027.051 | C3 | 18618.6647 | 842739.5592 | 40177.1185 | 1736879.2056 | 15642488.6957 | 18280903.2437 |  | 87213.7451 | 862338.1536 | 40177.1185 | 1736879.2056 | 0 | 2726608.2228 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 892715.9749 | 43116.9077 | 0 | 170027.051 | 1193073.6787 |  | 87213.7451 | 811381.8082 | 51936.2752 | 3374508.1709 | 1190189.3573 | 5515229.3566 |  | 87213.7451 | 876057.1697 | 51936.2752 | 99250.2403 | 1190189.3573 | 2304646.7875
|  |  | 140 | 140 | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 6 | 0 | -6 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 8 | 0 | -8 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 3081540 | 3081540 | 3081540 | 3081540 | 3081540 | C4 | 1633.2162 | 1633.2162 | 1633.2162 | 82708.5336 | 283378.4184 | C4 | 1633.2162 | 129024.0798 | 81660.81 | 496251.2016 | 1133513.6736 | 1842082.9812 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 138823.377 | 81660.81 | 0 | 0 | 228650.268 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072 |  | 8166.081 | 142089.8094 | 78394.3776 | 0 | 0 | 228650.268
|  |  | 4552 | 4552 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 92 | 0 | -92 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 0 | 184 | 0 | -184 | 0 |  | 296 | 3567 | 463 | 211 | 15 | [22 empty] | 104395.1795 | 2539259.2191 | 325859.2962 | 3854217.6658 | 22704278.8822 | 29528010.2428 |  | 205589.2553 | 2567546.5237 | 325859.2962 | 3589550.3582 | 0 | 6688545.4334 |  | 205589.2553 | 2544877.4828 | 334939.9783 | 4022943.0743 | 872805.5287 | 7981155.3194 |  | 205589.2553 | 2618829.5124 | 334939.9783 | 277900.6729 | 872805.5287 | 4310064.9475 |  | 205589.2553 | 2460211.555 | 338990.3545 | 7807685.5718 | 1892967.8349 | 12705444.5715 |  | 205589.2553 | 2600406.8336 | 338990.3545 | 707985.0476 | 1892967.8349 | 5745939.3259
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 2763 | 2763 | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | C1 | 32.0252 | 32.0252 | 44.0347 | 104.082 | 220.1734 | C1 | 13514.6445 | 8838.9618 | 48306.0473 | 57661.4158 | 93573.7014 | 221894.7708 |  | 13418.5689 | 8774.9114 | 48041.8392 | 57661.4158 | 93573.7014 | 221470.4366 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542
|  |  | 3992 | 3992 | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 571879 | 571879 | 571879 | 571879 | 571879 | C2 | 45.7503 | 45.7503 | 62.9067 | 148.6885 | 314.5335 | C2 | 14823.1037 | 23332.6632 | 158461.9521 | 36726.0694 | 129273.248 | 362617.0363 |  | 14731.603 | 23195.4122 | 157581.2585 | 36726.0694 | 129273.248 | 361507.5911 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726
|  |  | 1996 | 1996 | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 867 | 246 | 767 | 1996 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | C3 | 68.6255 | 68.6255 | 94.36 | 223.0328 | 471.8002 | C3 | 6519.4206 | 7411.5518 | 97568.2762 | 87205.8287 | 177396.8658 | 376101.9431 |  | 6450.7951 | 7342.9264 | 97002.116 | 87205.8287 | 177396.8658 | 375398.532 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115
|  |  | 333 | 333 | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | C4 | 114.3758 | 114.3758 | 157.2667 | 371.7213 | 786.3336 | C4 | 1029.3822 | 12123.8348 | 20759.2077 | 32711.4788 | 0 | 66623.9035 |  | 1029.3822 | 12009.459 | 20601.941 | 32711.4788 | 0 | 66352.261 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759
|  |  | 9084 | 9084 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 0 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 0 | 0 | 0 | 0 | 0 |  | 846 | 248 | 3752 | 1577 | 2661 | [22 empty] | 35886.551 | 51707.0117 | 325095.4833 | 214304.7927 | 400243.8151 | 1027237.6538 |  | 35630.3492 | 51322.709 | 323227.1546 | 214304.7927 | 400243.8151 | 1024728.8206 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142
| 132kV OHL Conductor (Tower Lines) |  | 679.807 | 679.807 | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 401324 | 401324 | 401324 | 401324 | 401324 | C1 | 28.0927 | 28.0927 | 36.1192 | 92.3045 | 192.6355 | C1 | 1047.7727 | 4017.8151 | 14675.6843 | 2569.9424 | 12785.99 | 35097.2045 |  | 1045.8624 | 4010.4829 | 14650.0397 | 2569.9424 | 12785.99 | 35062.3174 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047
|  |  | 985.034 | 985.034 | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 573320 | 573320 | 573320 | 573320 | 573320 | C2 | 40.1324 | 40.1324 | 51.5988 | 131.8636 | 275.1936 | C2 | 605.317 | 2546.8824 | 42102.918 | 0 | 25348.3577 | 70603.4751 |  | 604.2334 | 2542.227 | 42028.3062 | 0 | 25348.3577 | 70523.1243 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871
|  |  | 492.36 | 492.36 | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 859980 | 859980 | 859980 | 859980 | 859980 | C3 | 60.1986 | 60.1986 | 77.3982 | 197.7954 | 412.7904 | C3 | 1699.8881 | 5135.7834 | 27953.9079 | 3047.2359 | 1277.9991 | 39114.8143 |  | 1696.8179 | 5126.3924 | 27903.0573 | 3047.2359 | 1277.9991 | 39051.5026 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646
|  |  | 82.199 | 82.199 | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 1433300 | 1433300 | 1433300 | 1433300 | 1433300 | C4 | 100.331 | 100.331 | 128.997 | 329.659 | 687.984 | C4 | 0 | 50.3662 | 10552.5996 | 0 | 0 | 10602.9657 |  | 0 | 50.2658 | 10538.7969 | 0 | 0 | 10589.0627 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416
|  |  | 2239.4 | 2239.4 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471 | [22 empty] | 3352.9777 | 11750.847 | 95285.1098 | 5617.1784 | 39412.3468 | 155418.4597 |  | 3346.9137 | 11729.3681 | 95120.2 | 5617.1784 | 39412.3468 | 155226.007 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 |  | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 |  | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 |  | 1816616.6732 | 4251672.6042 | 9268695.1682 | 2022658.9106 | 4720549.3651 | 22080192.7213 |  | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 |  | 1743210.8469 | 4195209.0013 | 8205486.5216 | 5023926.9999 | 9630104.5706 | 28797937.9404
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 429606.482 | 429606.482 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 0 | 116 | 0 | -116 | 0 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 0 | 232 | 0 | -232 | 0 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 |  | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 |  | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 |  | 18407454.0913 | 21658387.4751 | 37030975.565 | 16733920.6879 | 53746775.951 | 147577513.7704 |  | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 |  | 13776347.1823 | 22362594.9429 | 32223524.9247 | 25356172.4712 | 92800076.9686 | 186518716.4897
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 | LV Network | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 | HV Network | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 | EHV Network | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 | EHV Network | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 | EHV Network | 2320125.7008 | 2763980.7578 | 8238386.5002 | 4969527.6114 | 10685723.4023 | 28977743.9725 | EHV Network | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 | EHV Network | 1793644.7601 | 2759533.2056 | 6744810.9862 | 5936229.9899 | 19552965.3925 | 36787184.3343
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 | 132kV Network | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 | 132kV Network | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 | 132kV Network | 1816616.6732 | 4251672.6042 | 9268695.1682 | 2022658.9106 | 4720549.3651 | 22080192.7213 | 132kV Network | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 | 132kV Network | 1743210.8469 | 4195209.0013 | 8205486.5216 | 5023926.9999 | 9630104.5706 | 28797937.9404
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 | Total | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 | Total | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 | Total | 18407454.0913 | 21658387.4751 | 37030975.565 | 16733920.6879 | 53746775.951 | 147577513.7704 | Total | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 | Total | 13776347.1823 | 22362594.9429 | 32223524.9247 | 25356172.4712 | 92800076.9686 | 186518716.4897
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EMID - HVP
Secondary deliverables RIIO-ED1 - HVP - Asset Replacement and Refurbishment driven | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
EMID | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | 3350.9 | C1 | 42.9585 | 42.9585 | 59.7801 | 147.071 | 308.1488 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 | C2 | 42847 | 38701 | 20624 | 3675 | 9598 | 115445 | 37247 | 38701 | 21004 | 4515 | 14078 | 115545 | 0 | 0 | 0 | 0 | 0 | 0 | 31407 | 38701 | 21196 | 5391 | 18750 | 115445 | 0 | 0 | 0 | 0 | 0 | 0 | 20323 | 38701 | 21750 | 7054 | 27617 | 115445 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4787 | 4787 | 4787 | 4787 | 4787 | C2 | 61.3693 | 61.3693 | 85.4001 | 210.1014 | 440.2125 | C2 | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | 7180.5 | C3 | 92.054 | 92.054 | 128.1001 | 315.1521 | 660.3188 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | 11967.5 | C4 | 153.4233 | 153.4233 | 213.5002 | 525.2536 | 1100.5313 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 115445 | 115445 |  | 42847 | 38701 | 20624 | 3675 | 9598 |  | 37247 | 38701 | 21004 | 4515 | 14078 |  | 0 | 0 | 0 | 0 | 0 |  | 31407 | 38701 | 21196 | 5391 | 18750 |  | 0 | 0 | 0 | 0 | 0 |  | 20323 | 38701 | 21750 | 7054 | 27617 | [22 empty] | 2285823.807 | 2375054.8273 | 1793743.2803 | 948607.9564 | 6197311.8566 | 13600541.7277 |  | 2629492.111 | 2375054.8273 | 1761291.2499 | 772122.7552 | 4225159.767 | 11763120.7105 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1927426.8614 | 2375054.8273 | 1810140.0957 | 1132656.8091 | 8253984.75 | 15499263.3435 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162 |  | 1247209.0968 | 2375054.8273 | 1857451.74 | 1482055.4872 | 12157349.1648 | 19119120.3162
| LV Switchgear (at s/s) |  | 8 | 8 | C1 | 7 | 0 | 1 | 0 | 0 | 8 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 0 | 1 | 0 | 0 | 8 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | 4968.6 | C1 | 95.4965 | 95.4965 | 132.8107 | 326.7848 | 684.7228 | C1 | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861 |  | 668.4754 | 0 | 132.8107 | 0 | 0 | 801.2861
|  |  | 17231 | 17231 | C2 | 9548 | 2818 | 4800 | 47 | 18 | 17231 | 9061 | 2881 | 4910 | 136 | 61 | 17049 | 0 | 0 | 0 | 0 | 0 | 0 | 8001 | 3263 | 5735 | 166 | 66 | 17231 | 0 | 0 | 0 | 0 | 0 | 0 | 6511 | 4198 | 5561 | 693 | 268 | 17231 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 7098 | 7098 | 7098 | 7098 | 7098 | C2 | 136.4236 | 136.4236 | 189.7295 | 466.8355 | 978.1754 | C2 | 1236133.8772 | 393036.2764 | 931572.0414 | 63489.6226 | 59668.6982 | 2683900.5157 |  | 1302572.1509 | 384441.5921 | 910701.792 | 21941.2666 | 17607.1568 | 2637263.9584 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 1091524.9036 | 445150.0763 | 1088098.9119 | 77494.6864 | 64559.5751 | 2766828.1532 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516 |  | 888253.7992 | 572706.1049 | 1055085.9719 | 323516.9738 | 262151.0018 | 3101713.8516
|  |  | 1354 | 1354 | C3 | 514 | 232 | 586 | 19 | 3 | 1354 | 474 | 235 | 594 | 27 | 11 | 1341 | 0 | 0 | 0 | 0 | 0 | 0 | 458 | 195 | 655 | 23 | 23 | 1354 | 0 | 0 | 0 | 0 | 0 | 0 | 387 | 206 | 618 | 94 | 49 | 1354 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 10647 | 10647 | 10647 | 10647 | 10647 | C3 | 204.6353 | 204.6353 | 284.5943 | 700.2532 | 1467.2631 | C3 | 96997.1512 | 48089.3049 | 169049.0201 | 18906.8361 | 16139.8938 | 349182.2061 |  | 105182.5648 | 47475.3989 | 166772.2657 | 13304.8106 | 4401.7892 | 337136.8291 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 93722.9857 | 39903.8913 | 186409.2731 | 16105.8234 | 33747.0506 | 369889.0241 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305 |  | 79193.8766 | 42154.88 | 175879.2836 | 65823.7999 | 71895.8904 | 434947.7305
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 17745 | 17745 | 17745 | 17745 | 17745 | C4 | 341.0589 | 341.0589 | 474.3238 | 1167.0886 | 2445.4384 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 18593 | 18593 |  | 10069 | 3050 | 5387 | 66 | 21 |  | 9542 | 3116 | 5505 | 163 | 72 |  | 0 | 0 | 0 | 0 | 0 |  | 8466 | 3458 | 6391 | 189 | 89 |  | 0 | 0 | 0 | 0 | 0 |  | 6905 | 4404 | 6180 | 787 | 317 | [22 empty] | 1333799.5038 | 441125.5813 | 1100753.8722 | 82396.4587 | 75808.5919 | 3033884.0079 |  | 1408423.1911 | 431916.991 | 1077606.8683 | 35246.0772 | 22008.946 | 2975202.0737 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 1185916.3647 | 485053.9676 | 1274640.9956 | 93600.5097 | 98306.6257 | 3137518.4634 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682 |  | 968116.1512 | 614860.9849 | 1231098.0662 | 389340.7736 | 334046.8923 | 3537462.8682
| LV UGB and LV Pillar OD (not at s/s) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | 4046.7 | C1 | 77.7776 | 77.7776 | 108.1683 | 266.1515 | 557.6757 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 27987 | 27987 | C2 | 5727 | 5081 | 16156 | 569 | 454 | 27987 | 5191 | 5097 | 16206 | 569 | 827 | 27890 | 0 | 0 | 0 | 0 | 0 | 0 | 4973 | 3922 | 16094 | 1541 | 1457 | 27987 | 0 | 0 | 0 | 0 | 0 | 0 | 4313 | 2624 | 13148 | 3732 | 4170 | 27987 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5781 | 5781 | 5781 | 5781 | 5781 | C2 | 111.1108 | 111.1108 | 154.5261 | 380.2164 | 796.6796 | C2 | 576776.2666 | 566331.8495 | 2504250.4628 | 216343.1145 | 658854.0375 | 4522555.7309 |  | 636331.6661 | 564554.0764 | 2496524.1563 | 216343.1145 | 361692.5429 | 4275445.5563 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 552554.1079 | 435776.636 | 2486943.5362 | 585913.4262 | 1160762.1918 | 5221949.8981 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821 |  | 479220.9667 | 291554.7917 | 2031709.5572 | 1418967.4928 | 3322153.9737 | 7543606.7821
|  |  | 1022 | 1022 | C3 | 103 | 234 | 657 | 17 | 11 | 1022 | 88 | 235 | 659 | 17 | 19 | 1018 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 199 | 649 | 52 | 47 | 1022 | 0 | 0 | 0 | 0 | 0 | 0 | 48 | 116 | 557 | 157 | 144 | 1022 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | 8671.5 | C3 | 166.6662 | 166.6662 | 231.7892 | 570.3246 | 1195.0194 | C3 | 14666.6282 | 39166.5641 | 152749.0795 | 9695.5174 | 22705.3689 | 238983.1581 |  | 17166.6217 | 38999.8978 | 152285.5011 | 9695.5174 | 13145.2136 | 231292.7516 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 12499.9673 | 33166.5798 | 150431.1876 | 29656.8769 | 56165.9125 | 281920.5239 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942 |  | 7999.979 | 19333.2827 | 129106.5816 | 89540.9551 | 172082.7958 | 418063.5942
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | 14452.5 | C4 | 277.7771 | 277.7771 | 386.3153 | 950.5409 | 1991.699 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29009 | 29009 |  | 5830 | 5315 | 16813 | 586 | 465 |  | 5279 | 5332 | 16865 | 586 | 846 |  | 0 | 0 | 0 | 0 | 0 |  | 5048 | 4121 | 16743 | 1593 | 1504 |  | 0 | 0 | 0 | 0 | 0 |  | 4361 | 2740 | 13705 | 3889 | 4314 | [22 empty] | 591442.8949 | 605498.4136 | 2656999.5423 | 226038.632 | 681559.4064 | 4761538.8891 |  | 653498.2878 | 603553.9742 | 2648809.6574 | 226038.632 | 374837.7565 | 4506738.3079 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 565054.0751 | 468943.2158 | 2637374.7238 | 615570.303 | 1216928.1043 | 5503870.422 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764 |  | 487220.9457 | 310888.0744 | 2160816.1389 | 1508508.448 | 3494236.7695 | 7961670.3764
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 |  | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 |  | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 809 | 809 | C1 | 274 | 155 | 355 | 25 | 0 | 809 | 258 | 157 | 365 | 25 | 3 | 808 | 0 | 0 | 0 | 0 | 0 | 0 | 232 | 167 | 301 | 84 | 25 | 809 | 0 | 0 | 0 | 0 | 0 | 0 | 196 | 168 | 215 | 121 | 109 | 809 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | 56323.4 | C1 | 722.066 | 722.066 | 1004.8095 | 2472.034 | 5179.4999 | C1 | 186293.0249 | 113364.3601 | 366755.4514 | 61800.8506 | 15538.4996 | 743752.1867 |  | 197846.0807 | 111920.2281 | 356707.3569 | 61800.8506 | 0 | 728274.5164 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 167519.3092 | 120585.02 | 302447.6463 | 207650.8582 | 129487.4966 | 927690.3303 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655 |  | 141524.9336 | 121307.086 | 216034.033 | 299116.1171 | 564565.4852 | 1342547.655
|  |  | 2623 | 2623 | C2 | 959 | 328 | 1282 | 52 | 2 | 2623 | 898 | 330 | 1317 | 52 | 17 | 2614 | 0 | 0 | 0 | 0 | 0 | 0 | 808 | 449 | 1049 | 261 | 56 | 2623 | 0 | 0 | 0 | 0 | 0 | 0 | 744 | 464 | 728 | 364 | 323 | 2623 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 80462 | 80462 | 80462 | 80462 | 80462 | C2 | 1031.5228 | 1031.5228 | 1435.4421 | 3531.4772 | 7399.2855 | C2 | 926307.5103 | 340402.5372 | 1890477.2194 | 183636.8134 | 125787.8538 | 3466611.9341 |  | 989230.4036 | 338339.4915 | 1840236.7466 | 183636.8134 | 14798.571 | 3366242.026 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 833470.4547 | 463153.7552 | 1505778.7419 | 921715.544 | 414359.9891 | 4138478.4849 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414 |  | 767452.993 | 478626.5978 | 1045001.8342 | 1285457.6935 | 2389969.223 | 5966508.3414
|  |  | 880 | 880 | C3 | 249 | 121 | 491 | 19 | 0 | 880 | 214 | 122 | 508 | 19 | 12 | 875 | 0 | 0 | 0 | 0 | 0 | 0 | 209 | 147 | 377 | 127 | 20 | 880 | 0 | 0 | 0 | 0 | 0 | 0 | 190 | 156 | 248 | 138 | 148 | 880 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 120693 | 120693 | 120693 | 120693 | 120693 | C3 | 1547.2843 | 1547.2843 | 2153.1631 | 5297.2158 | 11098.9283 | C3 | 331118.8316 | 188768.6797 | 1093806.865 | 100647.0996 | 133187.1394 | 1847528.6153 |  | 385273.7807 | 187221.3955 | 1057203.0919 | 100647.0996 | 0 | 1730345.3678 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 323382.4103 | 227450.7862 | 811742.4962 | 672746.4028 | 221978.5656 | 2257300.6612 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694 |  | 293984.0094 | 241376.3446 | 533984.4538 | 731015.7763 | 1642641.3854 | 3443001.9694
|  |  | 20 | 20 | C4 | 7 | 5 | 7 | 1 | 0 | 20 | 5 | 5 | 7 | 2 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 7 | 1 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 5 | 3 | 4 | 2 | 20 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 201155 | 201155 | 201155 | 201155 | 201155 | C4 | 2578.8071 | 2578.8071 | 3588.6052 | 8828.693 | 18498.2138 | C4 | 12894.0355 | 12894.0355 | 25120.2364 | 17657.3859 | 18498.2138 | 87063.9071 |  | 18051.6497 | 12894.0355 | 25120.2364 | 8828.693 | 0 | 64894.6145 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 15472.8426 | 12894.0355 | 25120.2364 | 8828.693 | 18498.2138 | 80814.0213 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931 |  | 15472.8426 | 12894.0355 | 10765.8156 | 35314.7718 | 36996.4276 | 111443.8931
|  |  | 4332 | 4332 |  | 1489 | 609 | 2135 | 97 | 2 |  | 1375 | 614 | 2197 | 98 | 33 |  | 0 | 0 | 0 | 0 | 0 |  | 1255 | 768 | 1734 | 473 | 102 |  | 0 | 0 | 0 | 0 | 0 |  | 1136 | 793 | 1194 | 627 | 582 | [22 empty] | 1456613.4024 | 655429.6125 | 3376159.7722 | 363742.1495 | 293011.7066 | 6144956.6432 |  | 1590401.9147 | 650375.1506 | 3279267.4318 | 354913.4566 | 14798.571 | 5889756.5247 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1339845.0169 | 824083.5969 | 2645089.1208 | 1810941.4979 | 784324.2651 | 7404283.4976 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859 |  | 1218434.7786 | 854204.0638 | 1805786.1366 | 2350904.3587 | 4634172.5212 | 10863501.859
| HV Switchgear (GM) - Distribution |  | 9569 | 9569 | C1 | 6250 | 710 | 2600 | 9 | 0 | 9569 | 5786 | 1007 | 2673 | 178 | 109 | 9753 | 0 | 0 | 0 | 0 | 0 | 0 | 5631 | 1101 | 2214 | 623 | 0 | 9569 | 0 | 0 | 0 | 0 | 0 | 0 | 4321 | 2124 | 1640 | 1000 | 484 | 9569 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | 16055.2 | C1 | 205.8277 | 205.8277 | 286.4248 | 704.6627 | 1476.4362 | C1 | 1190918.8639 | 207268.4576 | 765613.4049 | 125429.9656 | 160931.5449 | 2450162.2369 |  | 1286422.9 | 146137.6414 | 744704.3968 | 6341.9646 | 0 | 2183606.9028 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 1159015.576 | 226616.2581 | 634144.4364 | 439004.8795 | 0 | 2458781.1499 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589 |  | 889381.3361 | 437177.9583 | 469736.6195 | 704662.728 | 714595.1169 | 3215553.7589
|  |  | 12994 | 12994 | C2 | 5815 | 3218 | 3943 | 18 | 0 | 12994 | 5053 | 3404 | 4211 | 435 | 210 | 13313 | 0 | 0 | 0 | 0 | 0 | 0 | 4318 | 4209 | 3262 | 1205 | 0 | 12994 | 0 | 0 | 0 | 0 | 0 | 0 | 3480 | 4503 | 2547 | 1510 | 954 | 12994 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 22936 | 22936 | 22936 | 22936 | 22936 | C2 | 294.0395 | 294.0395 | 409.1782 | 1006.661 | 2109.1946 | C2 | 1485781.6946 | 1000910.5261 | 1723049.5686 | 437897.5524 | 442930.8576 | 5090570.1993 |  | 1709839.8088 | 946219.1754 | 1613389.8003 | 18119.8987 | 0 | 4287568.6832 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1269662.6474 | 1237612.3397 | 1334739.4189 | 1213026.5532 | 0 | 5055040.9591 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461 |  | 1023257.5296 | 1324059.9586 | 1042176.9773 | 1520058.1704 | 2012171.6102 | 6921724.2461
|  |  | 5187 | 5187 | C3 | 2219 | 966 | 2002 | 0 | 0 | 5187 | 1648 | 986 | 2407 | 313 | 183 | 5537 | 0 | 0 | 0 | 0 | 0 | 0 | 1702 | 1337 | 1613 | 535 | 0 | 5187 | 0 | 0 | 0 | 0 | 0 | 0 | 1367 | 1486 | 991 | 971 | 372 | 5187 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 34404 | 34404 | 34404 | 34404 | 34404 | C3 | 441.0593 | 441.0593 | 613.7674 | 1509.9916 | 3163.7918 | C3 | 726865.6934 | 434884.4501 | 1477338.0355 | 472627.3583 | 578973.9067 | 3690689.444 |  | 978710.5423 | 426063.2645 | 1228762.2547 | 0 | 0 | 2633536.0615 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 750682.8946 | 589696.2574 | 990006.7517 | 807845.4846 | 0 | 3138231.3882 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488 |  | 602928.0358 | 655414.0901 | 608243.4538 | 1466201.8048 | 1176930.5645 | 4509717.9488
|  |  | 143 | 143 | C4 | 71 | 18 | 54 | 0 | 0 | 143 | 53 | 20 | 60 | 12 | 9 | 154 | 0 | 0 | 0 | 0 | 0 | 0 | 61 | 18 | 64 | 0 | 0 | 143 | 0 | 0 | 0 | 0 | 0 | 0 | 53 | 20 | 43 | 27 | 0 | 143 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 57340 | 57340 | 57340 | 57340 | 57340 | C4 | 735.0988 | 735.0988 | 1022.9456 | 2516.6526 | 5272.9864 | C4 | 38960.2364 | 14701.976 | 61376.736 | 30199.8312 | 47456.8776 | 192695.6572 |  | 52192.0148 | 13231.7784 | 55239.0624 | 0 | 0 | 120662.8556 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 44841.0268 | 13231.7784 | 65468.5184 | 0 | 0 | 123541.3236 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934 |  | 38960.2364 | 14701.976 | 43986.6608 | 67949.6202 | 0 | 165598.4934
|  |  | 27893 | 27893 |  | 14355 | 4912 | 8599 | 27 | 0 |  | 12540 | 5417 | 9351 | 938 | 511 |  | 0 | 0 | 0 | 0 | 0 |  | 11712 | 6665 | 7153 | 2363 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 9221 | 8133 | 5221 | 3508 | 1810 | [22 empty] | 3442526.4883 | 1657765.4098 | 4027377.745 | 1066154.7075 | 1230293.1868 | 11424117.5374 |  | 4027165.2659 | 1531651.8597 | 3642095.5142 | 24461.8633 | 0 | 9225374.5031 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 3224202.1447 | 2067156.6335 | 3024359.1253 | 2459876.9173 | 0 | 10775594.8209 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472 |  | 2554527.1379 | 2431353.983 | 2164143.7114 | 3758872.3234 | 3903697.2916 | 14812594.4472
| HV Transformer (GM) |  | 3306 | 3306 | C1 | 1890 | 461 | 824 | 72 | 59 | 3306 | 1840 | 464 | 829 | 72 | 76 | 3281 | 0 | 0 | 0 | 0 | 0 | 0 | 1646 | 518 | 900 | 91 | 151 | 3306 | 0 | 0 | 0 | 0 | 0 | 0 | 1359 | 734 | 814 | 128 | 271 | 3306 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 15848 | 15848 | 15848 | 15848 | 15848 | C1 | 304.5986 | 304.5986 | 423.617 | 1042.323 | 2184.0129 | C1 | 560461.3504 | 141333.7318 | 351178.5262 | 75047.2531 | 165984.9789 | 1294005.8404 |  | 575691.2784 | 140419.9362 | 349060.441 | 75047.2531 | 128856.7599 | 1269075.6686 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 501369.2298 | 157782.0541 | 381255.336 | 94851.3894 | 329785.9449 | 1465043.9541 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886 |  | 413949.443 | 223575.343 | 344824.2706 | 133417.3389 | 591867.4905 | 1707633.886
|  |  | 13028 | 13028 | C2 | 7387 | 2541 | 2811 | 153 | 136 | 13028 | 7197 | 2559 | 2826 | 153 | 189 | 12924 | 0 | 0 | 0 | 0 | 0 | 0 | 6300 | 2801 | 3324 | 260 | 343 | 13028 | 0 | 0 | 0 | 0 | 0 | 0 | 5159 | 3417 | 3328 | 442 | 682 | 13028 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 22640 | 22640 | 22640 | 22640 | 22640 | C2 | 435.1408 | 435.1408 | 605.1672 | 1489.0328 | 3120.0184 | C2 | 3131708.3376 | 1113525.3072 | 1710202.5072 | 227822.0184 | 589683.4776 | 6772941.648 |  | 3214385.0896 | 1105692.7728 | 1701124.9992 | 227822.0184 | 424322.5024 | 6673347.3824 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2741387.04 | 1218829.3808 | 2011575.7728 | 387148.528 | 1070166.3112 | 7429107.0328 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888 |  | 2244891.3872 | 1486876.1136 | 2013996.4416 | 658152.4976 | 2127852.5488 | 8531768.9888
|  |  | 3266 | 3266 | C3 | 1310 | 579 | 1239 | 82 | 56 | 3266 | 1258 | 583 | 1245 | 82 | 72 | 3240 | 0 | 0 | 0 | 0 | 0 | 0 | 1118 | 549 | 1317 | 125 | 157 | 3266 | 0 | 0 | 0 | 0 | 0 | 0 | 921 | 627 | 1167 | 212 | 339 | 3266 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 33960 | 33960 | 33960 | 33960 | 33960 | C3 | 652.7112 | 652.7112 | 907.7508 | 2233.5492 | 4680.0276 | C3 | 821110.6896 | 380530.6296 | 1130149.746 | 183151.0344 | 336961.9872 | 2851904.0868 |  | 855051.672 | 377919.7848 | 1124703.2412 | 183151.0344 | 262081.5456 | 2802907.278 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 729731.1216 | 358338.4488 | 1195507.8036 | 279193.65 | 734764.3332 | 3297535.3572 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908 |  | 601147.0152 | 409249.9224 | 1059345.1836 | 473512.4304 | 1586529.3564 | 4129783.908
|  |  | 118 | 118 | C4 | 53 | 7 | 52 | 5 | 1 | 118 | 51 | 7 | 52 | 5 | 3 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 14 | 35 | 13 | 10 | 118 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 27 | 25 | 9 | 26 | 118 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 56600 | 56600 | 56600 | 56600 | 56600 | C4 | 1087.852 | 1087.852 | 1512.918 | 3722.582 | 7800.046 | C4 | 55480.452 | 7614.964 | 78671.736 | 18612.91 | 23400.138 | 183780.2 |  | 57656.156 | 7614.964 | 78671.736 | 18612.91 | 7800.046 | 170355.812 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 50041.192 | 15229.928 | 52952.13 | 48393.566 | 78000.46 | 244617.276 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8 |  | 33723.412 | 29372.004 | 37822.95 | 33503.238 | 202801.196 | 337222.8
|  |  | 19718 | 19718 |  | 10640 | 3588 | 4926 | 312 | 252 |  | 10346 | 3613 | 4952 | 312 | 340 |  | 0 | 0 | 0 | 0 | 0 |  | 9110 | 3882 | 5576 | 489 | 661 |  | 0 | 0 | 0 | 0 | 0 |  | 7470 | 4805 | 5334 | 791 | 1318 | [22 empty] | 4568760.8296 | 1643004.6326 | 3270202.5154 | 504633.2159 | 1116030.5817 | 11102631.7752 |  | 4702784.196 | 1631647.4578 | 3253560.4174 | 504633.2159 | 823060.8539 | 10915686.141 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 4022528.5834 | 1750179.8117 | 3641291.0424 | 809587.1334 | 2212717.0493 | 12436303.6201 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828 |  | 3293711.2574 | 2149073.383 | 3455988.8458 | 1298585.5049 | 4509050.5917 | 14706409.5828
| HV UG Cable |  | 3200.153 | 3200.153 | C1 | 2562.305 | 290.186 | 262.391 | 20.668 | 64.603 | 3200.153 | 2517.465 | 291.14 | 263.254 | 20.736 | 64.757 | 3157.352 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 34503 | 34503 | 34503 | 34503 | 34503 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 7275.757 | 7275.757 | C2 | 5044.187 | 742.954 | 1087.198 | 113.491 | 287.927 | 7275.757 | 4936.469 | 745.397 | 1090.77 | 113.864 | 292.906 | 7179.406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 49290 | 49290 | 49290 | 49290 | 49290 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3676.577 | 3676.577 | C3 | 2325.079 | 456.661 | 646.464 | 111.502 | 136.871 | 3676.577 | 2218.763 | 458.163 | 648.59 | 111.869 | 191.167 | 3628.552 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 73935 | 73935 | 73935 | 73935 | 73935 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 123225 | 123225 | 123225 | 123225 | 123225 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 14152.487 | 14152.487 |  | 9931.571 | 1489.801 | 1996.053 | 245.661 | 489.401 |  | 9672.697 | 1494.7 | 2002.614 | 246.469 | 548.83 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | 5655.3 | C1 | 72.5009 | 72.5009 | 100.8906 | 248.2111 | 520.0614 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 129615 | 129615 | C2 | 27866 | 52986 | 25032 | 4749 | 18982 | 129615 | 22623 | 52986 | 25268 | 5455 | 22752 | 129084 | 0 | 0 | 0 | 0 | 0 | 0 | 15928 | 52987 | 25630 | 6539 | 28531 | 129615 | 0 | 0 | 0 | 0 | 0 | 0 | 3734 | 52986 | 26239 | 8369 | 38287 | 129615 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 8079 | 8079 | 8079 | 8079 | 8079 | C2 | 103.5728 | 103.5728 | 144.1294 | 354.5873 | 742.9448 | C2 | 2343127.0019 | 5487907.3211 | 3641860.6685 | 1934273.776 | 16903480.9997 | 30310649.7672 |  | 2886159.0875 | 5487907.3211 | 3607846.1395 | 1683935.1352 | 14102578.9529 | 27768426.6362 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 1649707.2398 | 5488010.8939 | 3694035.4968 | 2318646.4201 | 21196959.23 | 34347359.2806 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451 |  | 386740.7605 | 5487907.3211 | 3781810.277 | 2967541.1974 | 28445129.0891 | 41069128.6451
|  |  | 18228 | 18228 | C3 | 3920 | 7451 | 3520 | 668 | 2669 | 18228 | 3183 | 7451 | 3553 | 767 | 3199 | 18153 | 0 | 0 | 0 | 0 | 0 | 0 | 2240 | 7451 | 3603 | 920 | 4014 | 18228 | 0 | 0 | 0 | 0 | 0 | 0 | 526 | 7451 | 3690 | 1177 | 5384 | 18228 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | 12118.5 | C3 | 155.3592 | 155.3592 | 216.194 | 531.881 | 1114.4173 | C3 | 494508.2381 | 1157581.1757 | 768137.4241 | 407952.7002 | 3565020.8147 | 6393200.3528 |  | 609007.9464 | 1157581.1757 | 761003.0208 | 355296.4846 | 2974379.6669 | 5857268.2944 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 348004.5408 | 1157581.1757 | 778947.1261 | 489330.4878 | 4473270.8816 | 7247134.212 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303 |  | 81718.9234 | 1157581.1757 | 797756.0076 | 626023.8958 | 6000022.5278 | 8663102.5303
|  |  | 253 | 253 | C4 | 54 | 104 | 49 | 9 | 37 | 253 | 44 | 104 | 49 | 11 | 44 | 252 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 103 | 50 | 13 | 56 | 253 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 104 | 51 | 16 | 75 | 253 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | 20197.5 | C4 | 258.9319 | 258.9319 | 360.3234 | 886.4683 | 1857.3621 | C4 | 11393.0058 | 26928.9228 | 17655.8466 | 9751.151 | 81723.9324 | 147452.8586 |  | 13982.3253 | 26928.9228 | 17655.8466 | 7978.2145 | 68722.3977 | 135267.7069 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 8026.8904 | 26669.9908 | 18016.17 | 11524.0876 | 104012.2776 | 168249.4165 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897 |  | 1812.5236 | 26928.9228 | 18376.4934 | 14183.4924 | 139302.1575 | 200603.5897
|  |  | 148096 | 148096 |  | 31840 | 60541 | 28601 | 5426 | 21688 |  | 25850 | 60541 | 28870 | 6233 | 25995 |  | 0 | 0 | 0 | 0 | 0 |  | 18199 | 60541 | 29283 | 7472 | 32601 |  | 0 | 0 | 0 | 0 | 0 |  | 4267 | 60541 | 29980 | 9562 | 43746 | [22 empty] | 2849028.2459 | 6672417.4195 | 4427653.9392 | 2351977.6272 | 20550225.7468 | 36851302.9787 |  | 3509149.3592 | 6672417.4195 | 4386505.0069 | 2047209.8343 | 17145681.0175 | 33760962.6375 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 2005738.6711 | 6672262.0604 | 4490998.7929 | 2819500.9955 | 25774242.3893 | 41762742.9091 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652 |  | 470272.2076 | 6672417.4195 | 4597942.778 | 3607748.5856 | 34584453.7744 | 49932834.7652
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 |  | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 |  | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 658 | 658 | C1 | 386 | 131 | 136 | 5 | 0 | 658 | 370 | 135 | 140 | 7 | 2 | 654 | 0 | 0 | 0 | 0 | 0 | 0 | 336 | 158 | 52 | 95 | 17 | 658 | 0 | 0 | 0 | 0 | 0 | 0 | 274 | 205 | 49 | 13 | 117 | 658 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | 110641.3 | C1 | 1418.4215 | 1418.4215 | 1973.8408 | 4856.0467 | 10174.5739 | C1 | 524815.9424 | 191486.8979 | 276337.7109 | 33992.3266 | 20349.1479 | 1046982.0257 |  | 547510.6859 | 185813.212 | 268442.3477 | 24280.2333 | 0 | 1026046.4789 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 476589.6126 | 224110.5916 | 102639.7212 | 461324.4324 | 172967.7571 | 1437632.1149 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395 |  | 388647.4817 | 290776.4005 | 96718.1988 | 63128.6065 | 1190425.1519 | 2029695.8395
|  |  | 432 | 432 | C2 | 213 | 60 | 159 | 0 | 0 | 432 | 191 | 64 | 173 | 0 | 0 | 428 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 80 | 79 | 92 | 2 | 432 | 0 | 0 | 0 | 0 | 0 | 0 | 165 | 91 | 21 | 49 | 106 | 432 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 158059 | 158059 | 158059 | 158059 | 158059 | C2 | 2026.3164 | 2026.3164 | 2819.7726 | 6937.2095 | 14535.1056 | C2 | 387026.4286 | 129684.2483 | 487820.6529 | 0 | 0 | 1004531.3298 |  | 431605.3889 | 121578.9828 | 448343.837 | 0 | 0 | 1001528.2088 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 362710.632 | 162105.3104 | 222762.0322 | 638223.2749 | 29070.2113 | 1414871.4609 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809 |  | 334342.2027 | 184394.7906 | 59215.2238 | 339923.266 | 1540721.1978 | 2458596.6809
|  |  | 137 | 137 | C3 | 75 | 15 | 47 | 0 | 0 | 137 | 65 | 15 | 51 | 0 | 2 | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 18 | 35 | 17 | 5 | 137 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 16 | 14 | 12 | 33 | 137 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | 237088.5 | C3 | 3039.4746 | 3039.4746 | 4229.6588 | 10405.8143 | 21802.6585 | C3 | 197565.847 | 45592.1185 | 215712.6008 | 0 | 43605.3169 | 502475.8834 |  | 227960.5927 | 45592.1185 | 198793.9655 | 0 | 0 | 472346.6768 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 188447.4233 | 54710.5423 | 148038.0594 | 176898.8425 | 109013.2923 | 677108.1598 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406 |  | 188447.4233 | 48631.5931 | 59215.2238 | 124869.7712 | 719487.7292 | 1140651.7406
|  |  | 91 | 91 | C4 | 28 | 18 | 45 | 0 | 0 | 91 | 19 | 23 | 49 | 0 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 27 | 23 | 0 | 91 | 0 | 0 | 0 | 0 | 0 | 0 | 17 | 24 | 7 | 14 | 29 | 91 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | 395147.5 | C4 | 5065.7909 | 5065.7909 | 7049.4314 | 17343.0238 | 36337.7641 | C4 | 96250.028 | 116513.1918 | 345422.1386 | 0 | 0 | 558185.3585 |  | 141842.1466 | 91184.2371 | 317224.413 | 0 | 0 | 550250.7967 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 86118.4461 | 121578.9828 | 190334.6478 | 398889.5468 | 0 | 796921.6236 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405 |  | 86118.4461 | 121578.9828 | 49346.0198 | 242802.3328 | 1053795.1589 | 1553640.9405
|  |  | 1318 | 1318 |  | 702 | 224 | 387 | 5 | 0 |  | 645 | 237 | 413 | 7 | 4 |  | 0 | 0 | 0 | 0 | 0 |  | 594 | 280 | 193 | 227 | 24 |  | 0 | 0 | 0 | 0 | 0 |  | 518 | 336 | 91 | 88 | 285 | [22 empty] | 1205658.2461 | 483276.4566 | 1325293.1032 | 33992.3266 | 63954.4648 | 3112174.5973 |  | 1348918.8142 | 444168.5505 | 1232804.5632 | 24280.2333 | 0 | 3050172.1612 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 1113866.1141 | 562505.4271 | 663774.4606 | 1675336.0967 | 311051.2607 | 4326533.3592 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014 |  | 997555.5539 | 645381.767 | 264494.6661 | 770723.9766 | 4504429.2378 | 7182585.2014
| EHV Transformer |  | 234 | 234 | C1 | 55 | 52 | 105 | 17 | 5 | 234 | 51 | 53 | 107 | 17 | 5 | 233 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 53 | 82 | 31 | 22 | 234 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 62 | 65 | 24 | 53 | 234 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | 329830.9 | C1 | 4228.4321 | 4228.4321 | 5884.1833 | 14476.2782 | 30331.2496 | C1 | 215650.039 | 224106.9033 | 629607.6084 | 246096.7294 | 151656.2478 | 1467117.528 |  | 232563.7676 | 219878.4712 | 617839.2419 | 246096.7294 | 151656.2478 | 1468034.4579 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 194507.8783 | 224106.9033 | 482503.027 | 448764.6242 | 667287.4904 | 2017169.9233 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721 |  | 126852.9641 | 262162.7926 | 382471.9116 | 347430.6768 | 1607556.2269 | 2726474.5721
|  |  | 290 | 290 | C2 | 69 | 35 | 160 | 20 | 6 | 290 | 63 | 37 | 162 | 20 | 8 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 62 | 40 | 146 | 13 | 29 | 290 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | 47 | 78 | 72 | 43 | 290 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 471187 | 471187 | 471187 | 471187 | 471187 | C2 | 6040.6173 | 6040.6173 | 8405.9761 | 20680.3974 | 43330.3565 | C2 | 380558.8924 | 223502.8416 | 1361768.125 | 413607.9486 | 346642.8522 | 2726080.6597 |  | 416802.5965 | 211421.6069 | 1344956.1728 | 413607.9486 | 259982.1391 | 2646770.4639 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 374518.2751 | 241624.6936 | 1227272.5077 | 268845.1666 | 1256580.3391 | 3368840.982 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615 |  | 302030.867 | 283909.015 | 655666.1342 | 1488988.615 | 1863205.3304 | 4593799.9615
|  |  | 179 | 179 | C3 | 39 | 39 | 93 | 8 | 0 | 179 | 30 | 39 | 101 | 8 | 1 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 37 | 84 | 18 | 8 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 30 | 38 | 56 | 29 | 26 | 179 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | 706780.5 | C3 | 9060.926 | 9060.926 | 12608.9641 | 31020.5961 | 64995.5348 | C3 | 271827.7803 | 353376.1144 | 1273505.3761 | 248164.7692 | 64995.5348 | 2211869.5748 |  | 353376.1144 | 353376.1144 | 1172633.6632 | 248164.7692 | 0 | 2127550.6611 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 289949.6323 | 335254.2624 | 1059152.9861 | 558370.7306 | 519964.2782 | 2762691.8896 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519 |  | 271827.7803 | 344315.1884 | 706101.9907 | 899597.2882 | 1689883.9043 | 3911726.1519
|  |  | 9 | 9 | C4 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 1 | 8 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 2 | 2 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | 1177967.5 | C4 | 15101.5433 | 15101.5433 | 21014.9402 | 51700.9936 | 108325.8913 | C4 | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 168119.5216 | 0 | 0 | 183221.0649 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 126089.6412 | 103401.9872 | 0 | 244593.1717 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739 |  | 0 | 15101.5433 | 84059.7608 | 103401.9872 | 216651.7826 | 419215.0739
|  |  | 712 | 712 |  | 163 | 127 | 366 | 45 | 11 |  | 144 | 130 | 378 | 45 | 14 |  | 0 | 0 | 0 | 0 | 0 |  | 140 | 131 | 318 | 64 | 59 |  | 0 | 0 | 0 | 0 | 0 |  | 110 | 148 | 203 | 127 | 124 | [22 empty] | 868036.7118 | 816087.4026 | 3433000.6311 | 907869.4472 | 563294.6348 | 6588288.8274 |  | 1002742.4784 | 799777.7358 | 3303548.5994 | 907869.4472 | 411638.3869 | 6425576.6478 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 858975.7857 | 816087.4026 | 2895018.162 | 1379382.5086 | 2443832.1077 | 8393295.9666 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594 |  | 700711.6114 | 905488.5393 | 1828299.7974 | 2839418.5671 | 5377297.2441 | 11651215.7594
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | 16277.1 | C1 | 217.2993 | 217.2993 | 7366.0388 | 17980.3357 | 37674.4873 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 132.569 | 132.569 | C2 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 14.405 | 94.132 | 24.032 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.744 | 64.209 | 57.616 | 0 | 0 | 132.569 | 0 | 0 | 0 | 0 | 0 | 0 | 10.168 | 55.724 | 66.677 | 0 | 0 | 132.569 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 23253 | 23253 | 23253 | 23253 | 23253 | C2 | 310.4275 | 310.4275 | 10522.9126 | 25686.1939 | 53820.6962 | C2 | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 4471.7089 | 29221.1661 | 252886.6361 | 0 | 0 | 286579.5111 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3335.2336 | 19932.2426 | 606288.1335 | 0 | 0 | 629555.6097 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369 |  | 3156.4273 | 17298.2648 | 701636.2448 | 0 | 0 | 722090.9369
|  |  | 20.77 | 20.77 | C3 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 7.566 | 4.544 | 8.66 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 7.566 | 2.71 | 10.494 | 0 | 0 | 20.77 | 0 | 0 | 0 | 0 | 0 | 0 | 0.018 | 9.146 | 11.606 | 0 | 0 | 20.77 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | 34879.5 | C3 | 465.6413 | 465.6413 | 15784.3689 | 38529.2909 | 80731.0443 | C3 | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 2115.8742 | 136692.6349 | 0 | 0 | 142331.5514 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 3523.0423 | 1261.888 | 165641.1676 | 0 | 0 | 170426.0978 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229 |  | 8.3815 | 4258.7556 | 183193.3858 | 0 | 0 | 187460.5229
|  |  | 7.371 | 7.371 | C4 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.748 | 2.623 | 0 | 0 | 7.371 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.962 | 6.409 | 0 | 0 | 7.371 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | 58132.5 | C4 | 776.0689 | 776.0689 | 26307.2815 | 64215.4848 | 134551.7405 | C4 | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 3684.775 | 69003.9995 | 0 | 0 | 72688.7745 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457 |  | 0 | 746.5783 | 168603.3675 | 0 | 0 | 169349.9457
|  |  | 160.71 | 160.71 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 21.971 | 103.424 | 35.315 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 18.31 | 71.667 | 70.733 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.186 | 65.832 | 84.692 | 0 | 0 | [22 empty] | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 7994.7511 | 35021.8153 | 458583.2705 | 0 | 0 | 501599.837 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 6858.2759 | 24878.9056 | 840933.3006 | 0 | 0 | 872670.482 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055 |  | 3164.8089 | 22303.5986 | 1053432.998 | 0 | 0 | 1078901.4055
| EHV UG Cable (Non Pressurised) |  | 474.229 | 474.229 | C1 | 263.375 | 107.026 | 75.278 | 3.595 | 24.955 | 474.229 | 222.225 | 107.026 | 75.278 | 3.595 | 24.955 | 433.079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | 48029.8 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 929.677 | 929.677 | C2 | 473.201 | 190.87 | 224.908 | 11.014 | 29.684 | 929.677 | 418.862 | 190.87 | 224.908 | 11.014 | 32.955 | 878.609 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 68614 | 68614 | 68614 | 68614 | 68614 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 292.451 | 292.451 | C3 | 207.863 | 46.708 | 27.008 | 0 | 10.872 | 292.451 | 194.267 | 46.708 | 27.008 | 0 | 14.601 | 282.584 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 102921 | 102921 | 102921 | 102921 | 102921 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 44.608 | 44.608 | C4 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 34.184 | 5.535 | 4.889 | 0 | 0 | 44.608 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 171535 | 171535 | 171535 | 171535 | 171535 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1740.965 | 1740.965 |  | 978.623 | 350.139 | 332.083 | 14.609 | 65.511 |  | 869.538 | 350.139 | 332.083 | 14.609 | 72.511 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 140 | 140 | C1 | 24 | 96 | 7 | 13 | 0 | 140 | 0 | 96 | 7 | 13 | 24 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 85 | 9 | 20 | 2 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 81 | 10 | 23 | 4 | 140 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | 169536.5 | C1 | 89.8543 | 89.8543 | 89.8543 | 4550.3597 | 15590.5765 | C1 | 0 | 8626.0171 | 628.9804 | 59154.6756 | 374173.837 | 442583.5101 |  | 2156.5043 | 8626.0171 | 628.9804 | 59154.6756 | 0 | 70566.1774 |  | 2156.5043 | 7637.6193 | 808.6891 | 91007.1932 | 31181.1531 | 132791.159 |  | 2156.5043 | 7637.6193 | 808.6891 | 91007.1932 | 31181.1531 | 132791.159 |  | 1976.7956 | 7278.2019 | 898.5434 | 104658.2722 | 62362.3062 | 177174.1193 |  | 1976.7956 | 7278.2019 | 898.5434 | 104658.2722 | 62362.3062 | 177174.1193
|  |  | 557 | 557 | C2 | 100 | 390 | 21 | 46 | 0 | 557 | 1 | 384 | 23 | 52 | 99 | 559 | 0 | 0 | 0 | 0 | 0 | 0 | 100 | 373 | 23 | 54 | 7 | 557 | 0 | 0 | 0 | 0 | 0 | 0 | 95 | 372 | 24 | 56 | 10 | 557 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 242195 | 242195 | 242195 | 242195 | 242195 | C2 | 128.3633 | 128.3633 | 128.3633 | 6500.5138 | 22272.2522 | C2 | 128.3633 | 49291.5264 | 2952.3571 | 338026.7176 | 2204952.9678 | 2595351.9322 |  | 12836.335 | 50061.7065 | 2695.6303 | 299023.6348 | 0 | 364617.3066 |  | 12836.335 | 47879.5295 | 2952.3571 | 351027.7452 | 155905.7654 | 570601.7322 |  | 12836.335 | 47879.5295 | 2952.3571 | 351027.7452 | 155905.7654 | 570601.7322 |  | 12194.5182 | 47751.1662 | 3080.7204 | 364028.7728 | 222722.522 | 649777.6996 |  | 12194.5182 | 47751.1662 | 3080.7204 | 364028.7728 | 222722.522 | 649777.6996
|  |  | 441 | 441 | C3 | 68 | 318 | 37 | 18 | 0 | 441 | 0 | 312 | 37 | 32 | 60 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 68 | 308 | 39 | 25 | 1 | 441 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 305 | 40 | 28 | 5 | 441 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | 363292.5 | C3 | 192.545 | 192.545 | 192.545 | 9750.7707 | 33408.3783 | C3 | 0 | 60074.0478 | 7124.1659 | 312024.6624 | 2004502.698 | 2383725.5741 |  | 13093.0617 | 61229.3179 | 7124.1659 | 175513.8726 | 0 | 256960.4182 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 13093.0617 | 59303.8677 | 7509.256 | 243769.2675 | 33408.3783 | 357083.8312 |  | 12130.3366 | 58726.2326 | 7701.801 | 273021.5796 | 167041.8915 | 518621.8413 |  | 12130.3366 | 58726.2326 | 7701.801 | 273021.5796 | 167041.8915 | 518621.8413
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | 605487.5 | C4 | 320.9084 | 320.9084 | 320.9084 | 16251.2845 | 55680.6305 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1138 | 1138 |  | 192 | 804 | 65 | 77 | 0 |  | 1 | 792 | 67 | 97 | 183 |  | 0 | 0 | 0 | 0 | 0 |  | 192 | 766 | 71 | 99 | 10 |  | 0 | 0 | 0 | 0 | 0 |  | 180 | 758 | 74 | 107 | 19 | [22 empty] | 128.3633 | 117991.5913 | 10705.5034 | 709206.0556 | 4583629.5028 | 5421661.0164 |  | 28085.901 | 119917.0416 | 10448.7767 | 533692.183 | 0 | 692143.9022 |  | 28085.901 | 114821.0166 | 11270.3021 | 685804.2059 | 220495.2968 | 1060476.7224 |  | 28085.901 | 114821.0166 | 11270.3021 | 685804.2059 | 220495.2968 | 1060476.7224 |  | 26301.6504 | 113755.6008 | 11681.0648 | 741708.6246 | 452126.7197 | 1345573.6603 |  | 26301.6504 |  | 11681.0648 |  | 452126.7197 | 490109.4349
| EHV OHL Support - Poles |  | 3622 | 3622 | C1 | 364 | 845 | 1721 | 282 | 410 | 3622 | 246 | 845 | 1727 | 300 | 504 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 198 | 845 | 1735 | 297 | 547 | 3622 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 844 | 1751 | 314 | 695 | 3622 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | 9739.8 | C1 | 124.8642 | 124.8642 | 173.758 | 427.4798 | 895.672 | C1 | 30716.6021 | 105510.2794 | 300080.1213 | 128243.9466 | 451418.692 | 1015969.6414 |  | 45450.5819 | 105510.2794 | 299037.5731 | 120549.3098 | 367225.5233 | 937773.2675 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 24723.1187 | 105510.2794 | 301470.1855 | 126961.5071 | 489932.5884 | 1048597.6792 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951 |  | 2247.5562 | 105385.4152 | 304250.314 | 134228.6641 | 622492.0456 | 1168603.9951
|  |  | 21560 | 21560 | C2 | 2170 | 5027 | 10243 | 1680 | 2440 | 21560 | 1467 | 5027 | 10278 | 1784 | 3004 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 1174 | 5027 | 10333 | 1771 | 3255 | 21560 | 0 | 0 | 0 | 0 | 0 | 0 | 97 | 5028 | 10431 | 1868 | 4136 | 21560 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 13914 | 13914 | 13914 | 13914 | 13914 | C2 | 178.3775 | 178.3775 | 248.2258 | 610.6855 | 1279.5314 | C2 | 261679.7632 | 896703.592 | 2551264.3613 | 1089462.8606 | 3843712.4458 | 8642823.0228 |  | 387079.1316 | 896703.592 | 2542576.4597 | 1025951.5728 | 3122056.7136 | 7974367.4696 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 209415.1615 | 896703.592 | 2564916.7781 | 1081523.9497 | 4164874.8372 | 8917434.3184 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627 |  | 17302.6156 | 896881.9694 | 2589242.9026 | 1140760.4393 | 5292142.0358 | 9936329.9627
|  |  | 2373 | 2373 | C3 | 239 | 553 | 1127 | 186 | 268 | 2373 | 161 | 553 | 1131 | 198 | 330 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 129 | 553 | 1138 | 195 | 358 | 2373 | 0 | 0 | 0 | 0 | 0 | 0 | 10 | 553 | 1149 | 206 | 455 | 2373 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 20871 | 20871 | 20871 | 20871 | 20871 | C3 | 267.5662 | 267.5662 | 372.3386 | 916.0282 | 1919.2972 | C3 | 43078.1614 | 147964.1197 | 421115.0018 | 181373.5816 | 633368.0628 | 1426898.9273 |  | 63948.3266 | 147964.1197 | 419625.6473 | 170381.2433 | 514371.6389 | 1316290.9757 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 34516.0424 | 147964.1197 | 423721.3723 | 178625.4971 | 687108.3833 | 1471935.4147 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942 |  | 2675.6622 | 147964.1197 | 427817.0974 | 188701.8071 | 873280.2078 | 1640438.8942
|  |  | 18 | 18 | C4 | 2 | 4 | 9 | 1 | 2 | 18 | 1 | 4 | 9 | 2 | 2 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 9 | 2 | 3 | 18 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 34785 | 34785 | 34785 | 34785 | 34785 | C4 | 445.9437 | 445.9437 | 620.5644 | 1526.7136 | 3198.8286 | C4 | 445.9437 | 1783.7748 | 5585.0796 | 3053.4273 | 6397.6572 | 17265.8826 |  | 891.8874 | 1783.7748 | 5585.0796 | 1526.7136 | 6397.6572 | 16185.1126 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675 |  | 0 | 1783.7748 | 5585.0796 | 3053.4273 | 9596.4858 | 20018.7675
|  |  | 27573 | 27573 |  | 2775 | 6429 | 13100 | 2149 | 3120 |  | 1875 | 6429 | 13145 | 2284 | 3840 |  | 0 | 0 | 0 | 0 | 0 |  | 1501 | 6429 | 13215 | 2265 | 4163 |  | 0 | 0 | 0 | 0 | 0 |  | 125 | 6429 | 13340 | 2390 | 5289 | [22 empty] | 335920.4703 | 1151961.7658 | 3278044.564 | 1402133.8162 | 4934896.8578 | 11102957.4741 |  | 497369.9275 | 1151961.7658 | 3266824.7596 | 1318408.8396 | 4010051.533 | 10244616.8255 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 268654.3226 | 1151961.7658 | 3295693.4155 | 1390164.3811 | 5351512.2947 | 11457986.1798 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195 |  | 22225.834 | 1152015.2791 | 3326895.3936 | 1466744.3378 | 6797510.775 | 12765391.6195
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 370 | 370 | C1 | 51 | 163 | 79 | 61 | 16 | 370 | 51 | 164 | 79 | 61 | 16 | 371 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 171 | 0 | 77 | 370 | 0 | 0 | 0 | 0 | 0 | 0 | 51 | 71 | 96 | 75 | 77 | 370 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 82320 | 82320 | 82320 | 82320 | 82320 | C1 | 274.1256 | 274.1256 | 381.9648 | 939.2712 | 1968.2712 | C1 | 13980.4056 | 44956.5984 | 30175.2192 | 57295.5432 | 31492.3392 | 177900.1056 |  | 13980.4056 | 44682.4728 | 30175.2192 | 57295.5432 | 31492.3392 | 177625.98 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 13980.4056 | 19462.9176 | 65315.9808 | 0 | 151556.8824 | 250316.1864 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664 |  | 13980.4056 | 19462.9176 | 36668.6208 | 70445.34 | 151556.8824 | 292114.1664
|  |  | 1902 | 1902 | C2 | 75 | 388 | 654 | 32 | 753 | 1902 | 75 | 390 | 659 | 32 | 753 | 1909 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 180 | 840 | 22 | 785 | 1902 | 0 | 0 | 0 | 0 | 0 | 0 | 75 | 38 | 408 | 574 | 807 | 1902 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 117600 | 117600 | 117600 | 117600 | 117600 | C2 | 391.608 | 391.608 | 545.664 | 1341.816 | 2811.816 | C2 | 29370.6 | 152727.12 | 359592.576 | 42938.112 | 2117297.448 | 2701925.856 |  | 29370.6 | 151943.904 | 356864.256 | 42938.112 | 2117297.448 | 2698414.32 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 29370.6 | 70489.44 | 458357.76 | 29519.952 | 2207275.56 | 2795013.312 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512 |  | 29370.6 | 14881.104 | 222630.912 | 770202.384 | 2269135.512 | 3306220.512
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 176400 | 176400 | 176400 | 176400 | 176400 | C3 | 587.412 | 587.412 | 818.496 | 2012.724 | 4217.724 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 294000 | 294000 | 294000 | 294000 | 294000 | C4 | 979.02 | 979.02 | 1364.16 | 3354.54 | 7029.54 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2272 | 2272 |  | 126 | 551 | 733 | 93 | 769 |  | 126 | 554 | 738 | 93 | 769 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 251 | 1011 | 22 | 862 |  | 0 | 0 | 0 | 0 | 0 |  | 126 | 109 | 504 | 649 | 884 | [22 empty] | 43351.0056 | 197683.7184 | 389767.7952 | 100233.6552 | 2148789.7872 | 2879825.9616 |  | 43351.0056 | 196626.3768 | 387039.4752 | 100233.6552 | 2148789.7872 | 2876040.3 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 43351.0056 | 89952.3576 | 523673.7408 | 29519.952 | 2358832.4424 | 3045329.4984 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784 |  | 43351.0056 | 34344.0216 | 259299.5328 | 840647.724 | 2420692.3944 | 3598334.6784
| EHV OHL Conductor (Tower Lines) |  | 155.606 | 155.606 | C1 | 58 | 0 | 97.606 | 0 | 0 | 155.606 | 0 | 0 | 97.654 | 0 | 39.21 | 136.864 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 74.606 | 23 | 0 | 155.606 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 0 | 0 | 74.606 | 23 | 155.606 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | 82338.9 | C1 | 5.7637 | 5.7637 | 7.4105 | 18.9379 | 39.5227 | C1 | 0 | 0 | 723.6651 | 0 | 1549.684 | 2273.349 |  | 334.2959 | 0 | 723.3094 | 0 | 0 | 1057.6053 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 334.2959 | 0 | 552.8678 | 435.5728 | 0 | 1322.7366 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019 |  | 334.2959 | 0 | 0 | 1412.8845 | 909.0215 | 2656.2019
|  |  | 705.644 | 705.644 | C2 | 0 | 66.834 | 638.81 | 0 | 0 | 705.644 | 0 | 66.877 | 639.219 | 0 | 0 | 706.096 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 705.644 | 0 | 0 | 705.644 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 66.834 | 638.81 | 0 | 705.644 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 117627 | 117627 | 117627 | 117627 | 117627 | C2 | 8.2339 | 8.2339 | 10.5864 | 27.0542 | 56.461 | C2 | 0 | 550.6579 | 6767.0472 | 0 | 0 | 7317.7051 |  | 0 | 550.3038 | 6762.7173 | 0 | 0 | 7313.0212 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 7470.2508 | 0 | 0 | 7470.2508 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334 |  | 0 | 0 | 707.5335 | 17282.4999 | 0 | 17990.0334
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | 176440.5 | C3 | 12.3508 | 12.3508 | 15.8796 | 40.5813 | 84.6914 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | 294067.5 | C4 | 20.5847 | 20.5847 | 26.4661 | 67.6355 | 141.1524 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 861.25 | 861.25 |  | 58 | 66.834 | 736.416 | 0 | 0 |  | 0 | 66.877 | 736.873 | 0 | 39.21 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 780.25 | 23 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 58 | 0 | 66.834 | 713.416 | 23 | [22 empty] | 0 | 550.6579 | 7490.7123 | 0 | 1549.684 | 9591.0541 |  | 334.2959 | 550.3038 | 7486.0267 | 0 | 0 | 8370.6264 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 334.2959 | 0 | 8023.1186 | 435.5728 | 0 | 8792.9874 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352 |  | 334.2959 | 0 | 707.5335 | 18695.3844 | 909.0215 | 20646.2352
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 |  | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 |  | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 |  | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 |  | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 |  | 1793644.7601 | 2759533.2056 | 6744810.9862 | 5936229.9899 | 19552965.3925 | 36787184.3343
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 115 | 115 | C1 | 41 | 18 | 29 | 25 | 2 | 115 | 38 | 18 | 29 | 26 | 2 | 113 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 25 | 16 | 21 | 20 | 115 | 0 | 0 | 0 | 0 | 0 | 0 | 32 | 24 | 7 | 18 | 34 | 115 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | 228099.9 | C1 | 2924.2407 | 2924.2407 | 4069.3022 | 10011.3046 | 20976.0668 | C1 | 111121.1473 | 52636.3329 | 118009.7643 | 260293.9199 | 41952.1336 | 584013.298 |  | 119893.8694 | 52636.3329 | 118009.7643 | 250282.6153 | 41952.1336 | 582774.7155 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 96499.9437 | 73106.0179 | 65108.8355 | 210237.3968 | 419521.3361 | 864473.53 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501 |  | 93575.703 | 70181.7772 | 28485.1155 | 180203.483 | 713186.2713 | 1085632.3501
|  |  | 88 | 88 | C2 | 44 | 12 | 16 | 12 | 4 | 88 | 38 | 12 | 16 | 14 | 4 | 84 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 21 | 15 | 5 | 12 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 22 | 0 | 16 | 16 | 88 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 325857 | 325857 | 325857 | 325857 | 325857 | C2 | 4177.4867 | 4177.4867 | 5813.2889 | 14301.8637 | 29965.8097 | C2 | 158744.4961 | 50129.8409 | 93012.6221 | 200226.0922 | 119863.2389 | 621976.2902 |  | 183809.4166 | 50129.8409 | 93012.6221 | 171622.3648 | 119863.2389 | 618437.4832 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 146212.0359 | 87727.2215 | 87199.3332 | 71509.3187 | 359589.7166 | 752237.6259 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326 |  | 142034.5492 | 91904.7083 | 0 | 228829.8197 | 479452.9555 | 942222.0326
|  |  | 30 | 30 | C3 | 9 | 0 | 4 | 15 | 2 | 30 | 6 | 0 | 4 | 16 | 2 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 4 | 1 | 16 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 8 | 1 | 0 | 4 | 17 | 30 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | 488785.5 | C3 | 6266.2301 | 6266.2301 | 8719.9333 | 21452.7956 | 44948.7146 | C3 | 37597.3807 | 0 | 34879.7333 | 343244.7295 | 89897.4292 | 505619.2726 |  | 56396.071 | 0 | 34879.7333 | 321791.9339 | 89897.4292 | 502965.1674 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 50129.8409 | 6266.2301 | 34879.7333 | 21452.7956 | 719179.4333 | 831908.0331 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012 |  | 50129.8409 | 6266.2301 | 0 | 85811.1824 | 764128.1479 | 906335.4012
|  |  | 30 | 30 | C4 | 4 | 22 | 2 | 2 | 0 | 30 | 4 | 22 | 2 | 2 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 19 | 5 | 1 | 2 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 18 | 5 | 1 | 3 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | 814642.5 | C4 | 10443.7169 | 10443.7169 | 14533.2222 | 35754.6593 | 74914.5243 | C4 | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 41774.8674 | 229761.7707 | 29066.4444 | 71509.3187 | 0 | 372112.4012 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 31331.1506 | 198430.6202 | 72666.111 | 35754.6593 | 149829.0486 | 488011.5896 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971 |  | 31331.1506 | 187986.9033 | 72666.111 | 35754.6593 | 224743.5729 | 552482.3971
|  |  | 263 | 263 |  | 98 | 52 | 51 | 54 | 8 |  | 86 | 52 | 51 | 58 | 8 |  | 0 | 0 | 0 | 0 | 0 |  | 79 | 66 | 40 | 28 | 50 |  | 0 | 0 | 0 | 0 | 0 |  | 77 | 65 | 12 | 39 | 70 | [22 empty] | 349237.8915 | 332527.9445 | 274968.564 | 875274.0603 | 251712.8016 | 2083721.2619 |  | 401874.2244 | 332527.9445 | 274968.564 | 815206.2326 | 251712.8016 | 2076289.7672 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 324172.971 | 365530.0898 | 259854.0129 | 338954.1704 | 1648119.5346 | 2936630.7787 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181 |  | 317071.2436 | 356339.6189 | 101151.2265 | 530599.1444 | 2181510.9476 | 3486672.181
| 132kV Transformer |  | 63 | 63 | C1 | 22 | 0 | 37 | 1 | 3 | 63 | 21 | 0 | 38 | 1 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 34 | 4 | 3 | 63 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 8 | 19 | 14 | 8 | 63 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | 1486206.4 | C1 | 19053.166 | 19053.166 | 26513.9222 | 65229.5989 | 136671.5405 | C1 | 400116.487 | 0 | 1007529.0427 | 65229.5989 | 410014.6216 | 1882889.7502 |  | 419169.6531 | 0 | 981015.1205 | 65229.5989 | 410014.6216 | 1875428.9941 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 266744.3247 | 152425.3284 | 901473.354 | 260918.3956 | 410014.6216 | 1991576.0243 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833 |  | 266744.3247 | 152425.3284 | 503764.5213 | 913214.3845 | 1093372.3244 | 2929520.8833
|  |  | 67 | 67 | C2 | 24 | 4 | 39 | 0 | 0 | 67 | 19 | 4 | 43 | 0 | 2 | 68 | 0 | 0 | 0 | 0 | 0 | 0 | 24 | 2 | 31 | 10 | 0 | 67 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 4 | 15 | 14 | 12 | 67 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2123152 | 2123152 | 2123152 | 2123152 | 2123152 | C2 | 27218.8086 | 27218.8086 | 37877.0317 | 93185.1413 | 195245.0579 | C2 | 517157.3642 | 108875.2346 | 1628712.3622 | 0 | 390490.1158 | 2645235.0768 |  | 653251.4074 | 108875.2346 | 1477204.2355 | 0 | 0 | 2239330.8774 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 653251.4074 | 54437.6173 | 1174187.9821 | 931851.4128 | 0 | 2813728.4195 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728 |  | 598813.7901 | 108875.2346 | 568155.4752 | 1304591.9779 | 2342940.695 | 4923377.1728
|  |  | 54 | 54 | C3 | 8 | 14 | 29 | 3 | 0 | 54 | 6 | 14 | 29 | 5 | 0 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 32 | 1 | 3 | 54 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 12 | 24 | 8 | 4 | 54 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3184728 | 3184728 | 3184728 | 3184728 | 3184728 | C3 | 40828.213 | 40828.213 | 56815.5475 | 139777.7119 | 292867.5869 | C3 | 244969.2778 | 571594.9814 | 1647650.8781 | 698888.5596 | 0 | 3163103.6969 |  | 326625.7037 | 571594.9814 | 1647650.8781 | 419333.1358 | 0 | 2965204.699 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 244969.2778 | 489938.5555 | 1818097.5206 | 139777.7119 | 878602.7606 | 3571385.8265 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166 |  | 244969.2778 | 489938.5555 | 1363573.1405 | 1118221.6954 | 1171470.3475 | 4388173.0166
|  |  | 9 | 9 | C4 | 3 | 5 | 1 | 0 | 0 | 9 | 2 | 5 | 1 | 0 | 1 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 7 | 1 | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 6 | 2 | 0 | 0 | 9 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5307880 | 5307880 | 5307880 | 5307880 | 5307880 | C4 | 68047.0216 | 68047.0216 | 94692.5792 | 232962.8532 | 488112.6448 | C4 | 136094.0432 | 340235.108 | 94692.5792 | 0 | 488112.6448 | 1059134.3752 |  | 204141.0648 | 340235.108 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 476329.1512 | 94692.5792 | 0 | 0 | 639068.752 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096 |  | 68047.0216 | 408282.1296 | 189385.1584 | 0 | 0 | 665714.3096
|  |  | 193 | 193 |  | 57 | 23 | 106 | 4 | 3 |  | 48 | 23 | 111 | 6 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 45 | 29 | 98 | 15 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 43 | 30 | 60 | 36 | 24 | [22 empty] | 1298337.1721 | 1020705.324 | 4378584.8622 | 764118.1585 | 1288617.3823 | 8750362.8991 |  | 1603187.8289 | 1020705.324 | 4200562.8133 | 484562.7347 | 410014.6216 | 7719033.3225 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1233012.0314 | 1173130.6524 | 3988451.4359 | 1332547.5203 | 1288617.3823 | 9015759.0223 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823 |  | 1178574.4141 | 1159521.2481 | 2624878.2954 | 3336028.0578 | 4607783.3669 | 12906785.3823
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 46.945 | 46.945 | C1 | 4.925 | 18.769 | 23.251 | 0 | 0 | 46.945 | 4.925 | 18.769 | 23.251 | 2.544 | 0 | 49.489 | 0 | 0 | 0 | 0 | 0 | 0 | 2.543 | 16.47 | 27.932 | 0 | 0 | 46.945 | 0 | 0 | 0 | 0 | 0 | 0 | 2.127 | 8.907 | 35.911 | 0 | 0 | 46.945 |  |  | C1 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C1 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | 70777.7 | C1 | 944.8823 | 944.8823 | 32029.7404 | 78183.8785 | 163819.9411 | C1 | 4653.5453 | 17734.4958 | 744723.4931 | 198899.787 | 0 | 966011.3211 |  | 4653.5453 | 17734.4958 | 744723.4931 | 0 | 0 | 767111.5342 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2402.8357 | 15562.2114 | 894654.7077 | 0 | 0 | 912619.7548 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372 |  | 2009.7646 | 8416.0666 | 1150220.006 | 0 | 0 | 1160645.8372
|  |  | 60.282 | 60.282 | C2 | 2.252 | 32.304 | 25.726 | 0 | 0 | 60.282 | 2.252 | 32.304 | 25.727 | 3.409 | 0 | 63.692 | 0 | 0 | 0 | 0 | 0 | 0 | 1.675 | 20.394 | 38.213 | 0 | 0 | 60.282 | 0 | 0 | 0 | 0 | 0 | 0 | 0.052 | 17.461 | 42.769 | 0 | 0 | 60.282 |  |  | C2 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C2 | 101111 | 101111 | 101111 | 101111 | 101111 | C2 | 1349.8319 | 1349.8319 | 45756.7719 | 111691.255 | 234028.4873 | C2 | 3039.8213 | 43604.9681 | 1177184.4717 | 380755.4884 | 0 | 1604584.7495 |  | 3039.8213 | 43604.9681 | 1177138.7149 | 0 | 0 | 1223783.5043 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 2260.9683 | 27528.4707 | 1748503.5261 | 0 | 0 | 1778292.9652 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843 |  | 70.1913 | 23569.4139 | 1956971.3791 | 0 | 0 | 1980610.9843
|  |  | 42.005 | 42.005 | C3 | 12.911 | 5.749 | 23.345 | 0 | 0 | 42.005 | 12.911 | 5.749 | 23.345 | 3.566 | 0 | 45.571 | 0 | 0 | 0 | 0 | 0 | 0 | 6.683 | 11.977 | 23.345 | 0 | 0 | 42.005 | 0 | 0 | 0 | 0 | 0 | 0 | 2.06 | 14.58 | 25.365 | 0 | 0 | 42.005 |  |  | C3 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C3 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | 151666.5 | C3 | 2024.7478 | 2024.7478 | 68635.1579 | 167536.8826 | 351042.7309 | C3 | 26141.5185 | 11640.275 | 1602287.7614 | 597436.5232 | 0 | 2237506.0781 |  | 26141.5185 | 11640.275 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 13531.3894 | 24250.4041 | 1602287.7614 | 0 | 0 | 1640069.5549 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834 |  | 4170.9804 | 29520.8226 | 1740930.7804 | 0 | 0 | 1774622.5834
|  |  | 0.038 | 0.038 | C4 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0.005 | 0.033 | 0 | 3.21 | 0 | 3.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 | 0 | 0 | 0 | 0 | 0 | 0 | 0.005 | 0.033 | 0 | 0 | 0 | 0.038 |  |  | C4 | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146 | C4 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | 252777.5 | C4 | 3374.5796 | 3374.5796 | 114391.9299 | 279228.1376 | 585071.2182 | C4 | 16.8729 | 111.3611 | 0 | 896322.3217 | 0 | 896450.5557 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234 |  | 16.8729 | 111.3611 | 0 | 0 | 0 | 128.234
|  |  | 149.27 | 149.27 |  | 20.093 | 56.855 | 72.322 | 0 | 0 |  | 20.093 | 56.855 | 72.323 | 12.729 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 10.906 | 48.874 | 89.49 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 4.244 | 40.981 | 104.045 | 0 | 0 | [22 empty] | 33851.7581 | 73091.1 | 3524195.7262 | 2073414.1203 | 0 | 5704552.7045 |  | 33851.7581 | 73091.1 | 3524149.9694 | 0 | 0 | 3631092.8274 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 18212.0663 | 67452.4474 | 4245445.9952 | 0 | 0 | 4331110.5089 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389 |  | 6267.8092 | 61617.6642 | 4848122.1655 | 0 | 0 | 4916007.6389
| 132kV UG Cable (Non Pressurised) |  | 28.233 | 28.233 | C1 | 28.233 | 0 | 0 | 0 | 0 | 28.233 | 11.581 | 0 | 0 | 0 | 0 | 11.581 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | 445703.3 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 62.09 | 62.09 | C2 | 62.09 | 0 | 0 | 0 | 0 | 62.09 | 46.471 | 0 | 0 | 0 | 0 | 46.471 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 636719 | 636719 | 636719 | 636719 | 636719 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 17.808 | 17.808 | C3 | 17.808 | 0 | 0 | 0 | 0 | 17.808 | 5.651 | 0 | 0 | 0 | 0 | 5.651 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | 955078.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 3.269 | 3.269 | C4 | 3.269 | 0 | 0 | 0 | 0 | 3.269 | 0.427 | 0 | 0 | 0 | 0 | 0.427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | 1591797.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 111.4 | 111.4 |  | 111.4 | 0 | 0 | 0 | 0 |  | 64.13 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1441 | 1441 | C1 | 111 | 1161 | 139 | 30 | 0 | 1441 | 74 | 1152 | 139 | 30 | 49 | 1444 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1145 | 141 | 38 | 6 | 1441 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 1112 | 142 | 70 | 6 | 1441 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | 862831.2 | C1 | 457.3005 | 457.3005 | 457.3005 | 23158.3894 | 79345.9572 | C1 | 33840.2397 | 526810.2175 | 63564.7745 | 694751.6822 | 3887951.9004 | 5206918.8143 |  | 50760.3595 | 530925.9223 | 63564.7745 | 694751.6822 | 0 | 1340002.7385 |  | 50760.3595 | 523609.1137 | 64479.3756 | 880018.7975 | 476075.7429 | 1994943.3892 |  | 50760.3595 | 523609.1137 | 64479.3756 | 880018.7975 | 476075.7429 | 1994943.3892 |  | 50760.3595 | 508518.196 | 64936.6761 | 1621087.2586 | 476075.7429 | 2721378.2331 |  | 50760.3595 | 508518.196 | 64936.6761 | 1621087.2586 | 476075.7429 | 2721378.2331
|  |  | 1926 | 1926 | C2 | 91 | 1600 | 215 | 20 | 0 | 1926 | 77 | 1593 | 215 | 28 | 18 | 1931 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1590 | 223 | 20 | 2 | 1926 | 0 | 0 | 0 | 0 | 0 | 0 | 91 | 1548 | 220 | 65 | 2 | 1926 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 1232616 | 1232616 | 1232616 | 1232616 | 1232616 | C2 | 653.2865 | 653.2865 | 653.2865 | 33083.4134 | 113351.3674 | C2 | 50303.059 | 1040685.3626 | 140456.5932 | 926335.5763 | 2040324.6125 | 4198105.2036 |  | 59449.0697 | 1045258.368 | 140456.5932 | 661668.2688 | 0 | 1906832.2997 |  | 59449.0697 | 1038725.5032 | 145682.885 | 661668.2688 | 226702.7347 | 2132228.4614 |  | 59449.0697 | 1038725.5032 | 145682.885 | 661668.2688 | 226702.7347 | 2132228.4614 |  | 59449.0697 | 1011287.471 | 143723.0256 | 2150421.8736 | 226702.7347 | 3591584.1746 |  | 59449.0697 | 1011287.471 | 143723.0256 | 2150421.8736 | 226702.7347 | 3591584.1746
|  |  | 1045 | 1045 | C3 | 89 | 880 | 41 | 35 | 0 | 1045 | 19 | 860 | 41 | 35 | 92 | 1047 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 871 | 44 | 40 | 1 | 1045 | 0 | 0 | 0 | 0 | 0 | 0 | 89 | 828 | 53 | 68 | 7 | 1045 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1848924 | 1848924 | 1848924 | 1848924 | 1848924 | C3 | 979.9297 | 979.9297 | 979.9297 | 49625.1202 | 170027.051 | C3 | 18618.6647 | 842739.5592 | 40177.1185 | 1736879.2056 | 15642488.6957 | 18280903.2437 |  | 87213.7451 | 862338.1536 | 40177.1185 | 1736879.2056 | 0 | 2726608.2228 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 853518.7861 | 43116.9077 | 1985004.8064 | 170027.051 | 3138881.2963 |  | 87213.7451 | 811381.8082 | 51936.2752 | 3374508.1709 | 1190189.3573 | 5515229.3566 |  | 87213.7451 | 811381.8082 | 51936.2752 | 3374508.1709 | 1190189.3573 | 5515229.3566
|  |  | 140 | 140 | C4 | 5 | 79 | 50 | 6 | 0 | 140 | 1 | 79 | 50 | 6 | 4 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 50 | 6 | 0 | 140 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 79 | 48 | 8 | 0 | 140 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 3081540 | 3081540 | 3081540 | 3081540 | 3081540 | C4 | 1633.2162 | 1633.2162 | 1633.2162 | 82708.5336 | 283378.4184 | C4 | 1633.2162 | 129024.0798 | 81660.81 | 496251.2016 | 1133513.6736 | 1842082.9812 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 81660.81 | 496251.2016 | 0 | 715102.1724 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072 |  | 8166.081 | 129024.0798 | 78394.3776 | 661668.2688 | 0 | 877252.8072
|  |  | 4552 | 4552 |  | 296 | 3720 | 445 | 91 | 0 |  | 171 | 3684 | 445 | 99 | 163 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3685 | 458 | 104 | 9 |  | 0 | 0 | 0 | 0 | 0 |  | 296 | 3567 | 463 | 211 | 15 | [22 empty] | 104395.1795 | 2539259.2191 | 325859.2962 | 3854217.6658 | 22704278.8822 | 29528010.2428 |  | 205589.2553 | 2567546.5237 | 325859.2962 | 3589550.3582 | 0 | 6688545.4334 |  | 205589.2553 | 2544877.4828 | 334939.9783 | 4022943.0743 | 872805.5287 | 7981155.3194 |  | 205589.2553 | 2544877.4828 | 334939.9783 | 4022943.0743 | 872805.5287 | 7981155.3194 |  | 205589.2553 | 2460211.555 | 338990.3545 | 7807685.5718 | 1892967.8349 | 12705444.5715 |  | 205589.2553 | 2460211.555 | 338990.3545 | 7807685.5718 | 1892967.8349 | 12705444.5715
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 2763 | 2763 | C1 | 419 | 274 | 1091 | 554 | 425 | 2763 | 422 | 276 | 1097 | 554 | 425 | 2774 | 0 | 0 | 0 | 0 | 0 | 0 | 419 | 143 | 985 | 237 | 979 | 2763 | 0 | 0 | 0 | 0 | 0 | 0 | 420 | 95 | 642 | 513 | 1093 | 2763 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | 400315.3 | C1 | 32.0252 | 32.0252 | 44.0347 | 104.082 | 220.1734 | C1 | 13514.6445 | 8838.9618 | 48306.0473 | 57661.4158 | 93573.7014 | 221894.7708 |  | 13418.5689 | 8774.9114 | 48041.8392 | 57661.4158 | 93573.7014 | 221470.4366 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 13418.5689 | 4579.607 | 43374.1628 | 24667.4288 | 215549.7733 | 301589.5407 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542 |  | 13450.5941 | 3042.3963 | 28270.2665 | 53394.0547 | 240649.5426 | 338806.8542
|  |  | 3992 | 3992 | C2 | 322 | 507 | 2505 | 247 | 411 | 3992 | 324 | 510 | 2519 | 247 | 411 | 4011 | 0 | 0 | 0 | 0 | 0 | 0 | 322 | 223 | 2553 | 216 | 678 | 3992 | 0 | 0 | 0 | 0 | 0 | 0 | 323 | 81 | 2140 | 735 | 713 | 3992 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 571879 | 571879 | 571879 | 571879 | 571879 | C2 | 45.7503 | 45.7503 | 62.9067 | 148.6885 | 314.5335 | C2 | 14823.1037 | 23332.6632 | 158461.9521 | 36726.0694 | 129273.248 | 362617.0363 |  | 14731.603 | 23195.4122 | 157581.2585 | 36726.0694 | 129273.248 | 361507.5911 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 14731.603 | 10202.3214 | 160600.7796 | 32116.7246 | 213253.6791 | 430905.1077 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726 |  | 14777.3534 | 3705.7759 | 134620.3166 | 109286.0769 | 224262.3498 | 486651.8726
|  |  | 1996 | 1996 | C3 | 94 | 107 | 1028 | 391 | 376 | 1996 | 95 | 108 | 1034 | 391 | 376 | 2004 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 42 | 1077 | 16 | 767 | 1996 | 0 | 0 | 0 | 0 | 0 | 0 | 94 | 22 | 867 | 246 | 767 | 1996 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | 857818.5 | C3 | 68.6255 | 68.6255 | 94.36 | 223.0328 | 471.8002 | C3 | 6519.4206 | 7411.5518 | 97568.2762 | 87205.8287 | 177396.8658 | 376101.9431 |  | 6450.7951 | 7342.9264 | 97002.116 | 87205.8287 | 177396.8658 | 375398.532 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 6450.7951 | 2882.2702 | 101625.7577 | 3568.525 | 361870.7342 | 476398.0822 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115 |  | 6450.7951 | 1509.7606 | 81810.1503 | 54866.0713 | 361870.7342 | 506507.5115
|  |  | 333 | 333 | C4 | 9 | 105 | 131 | 88 | 0 | 333 | 9 | 106 | 132 | 88 | 0 | 335 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 186 | 0 | 88 | 333 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 50 | 103 | 83 | 88 | 333 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | 1429697.5 | C4 | 114.3758 | 114.3758 | 157.2667 | 371.7213 | 786.3336 | C4 | 1029.3822 | 12123.8348 | 20759.2077 | 32711.4788 | 0 | 66623.9035 |  | 1029.3822 | 12009.459 | 20601.941 | 32711.4788 | 0 | 66352.261 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 1029.3822 | 5718.79 | 29251.6109 | 0 | 69197.359 | 105197.1421 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759 |  | 1029.3822 | 5718.79 | 16198.4727 | 30852.872 | 69197.359 | 122996.8759
|  |  | 9084 | 9084 |  | 844 | 993 | 4755 | 1280 | 1212 |  | 850 | 1000 | 4782 | 1280 | 1212 |  | 0 | 0 | 0 | 0 | 0 |  | 844 | 458 | 4801 | 469 | 2512 |  | 0 | 0 | 0 | 0 | 0 |  | 846 | 248 | 3752 | 1577 | 2661 | [22 empty] | 35886.551 | 51707.0117 | 325095.4833 | 214304.7927 | 400243.8151 | 1027237.6538 |  | 35630.3492 | 51322.709 | 323227.1546 | 214304.7927 | 400243.8151 | 1024728.8206 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 35630.3492 | 23382.9886 | 334852.3109 | 60352.6784 | 859871.5456 | 1314089.8726 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142 |  | 35708.1248 | 13976.7228 | 260899.2061 | 248399.0749 | 895979.9857 | 1454963.1142
| 132kV OHL Conductor (Tower Lines) |  | 679.807 | 679.807 | C1 | 37.229 | 142.759 | 405.603 | 27.842 | 66.374 | 679.807 | 37.297 | 143.02 | 406.313 | 27.842 | 66.374 | 680.846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 531.477 | 16.886 | 94.215 | 679.807 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.229 | 242.451 | 305.912 | 94.215 | 679.807 |  |  | C1 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C1 | 401324 | 401324 | 401324 | 401324 | 401324 | C1 | 28.0927 | 28.0927 | 36.1192 | 92.3045 | 192.6355 | C1 | 1047.7727 | 4017.8151 | 14675.6843 | 2569.9424 | 12785.99 | 35097.2045 |  | 1045.8624 | 4010.4829 | 14650.0397 | 2569.9424 | 12785.99 | 35062.3174 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 0 | 1045.8624 | 19196.5028 | 1558.6541 | 18149.1555 | 39950.1748 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047 |  | 0 | 1045.8624 | 8757.1265 | 28237.0603 | 18149.1555 | 56189.2047
|  |  | 985.034 | 985.034 | C2 | 15.056 | 63.346 | 814.521 | 0 | 92.111 | 985.034 | 15.083 | 63.462 | 815.967 | 0 | 92.111 | 986.623 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 855.258 | 22.609 | 92.111 | 985.034 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15.056 | 220.713 | 654.512 | 94.753 | 985.034 |  |  | C2 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C2 | 573320 | 573320 | 573320 | 573320 | 573320 | C2 | 40.1324 | 40.1324 | 51.5988 | 131.8636 | 275.1936 | C2 | 605.317 | 2546.8824 | 42102.918 | 0 | 25348.3577 | 70603.4751 |  | 604.2334 | 2542.227 | 42028.3062 | 0 | 25348.3577 | 70523.1243 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 0 | 604.2334 | 44130.2865 | 2981.3041 | 25348.3577 | 73064.1817 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871 |  | 0 | 604.2334 | 11388.5259 | 86306.3086 | 26075.4192 | 124374.4871
|  |  | 492.36 | 492.36 | C3 | 28.187 | 85.158 | 360.513 | 15.406 | 3.096 | 492.36 | 28.238 | 85.314 | 361.17 | 15.406 | 3.096 | 493.224 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 445.016 | 0.654 | 18.503 | 492.36 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.187 | 140.71 | 304.96 | 18.503 | 492.36 |  |  | C3 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C3 | 859980 | 859980 | 859980 | 859980 | 859980 | C3 | 60.1986 | 60.1986 | 77.3982 | 197.7954 | 412.7904 | C3 | 1699.8881 | 5135.7834 | 27953.9079 | 3047.2359 | 1277.9991 | 39114.8143 |  | 1696.8179 | 5126.3924 | 27903.0573 | 3047.2359 | 1277.9991 | 39051.5026 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 0 | 1696.8179 | 34443.4374 | 129.3582 | 7637.8608 | 43907.4743 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646 |  | 0 | 1696.8179 | 10890.7007 | 60319.6852 | 7637.8608 | 80545.0646
|  |  | 82.199 | 82.199 | C4 | 0 | 0.501 | 81.698 | 0 | 0 | 82.199 | 0 | 0.502 | 81.805 | 0 | 0 | 82.307 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 57.22 | 24.979 | 0 | 82.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.17 | 79.029 | 0 | 82.199 |  |  | C4 | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048 | C4 | 1433300 | 1433300 | 1433300 | 1433300 | 1433300 | C4 | 100.331 | 100.331 | 128.997 | 329.659 | 687.984 | C4 | 0 | 50.3662 | 10552.5996 | 0 | 0 | 10602.9657 |  | 0 | 50.2658 | 10538.7969 | 0 | 0 | 10589.0627 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 7381.2083 | 8234.5522 | 0 | 15615.7605 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416 |  | 0 | 0 | 408.9205 | 26052.6211 | 0 | 26461.5416
|  |  | 2239.4 | 2239.4 |  | 80.472 | 291.764 | 1662.335 | 43.248 | 161.581 |  | 80.618 | 292.298 | 1665.255 | 43.248 | 161.581 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 1888.971 | 65.128 | 204.829 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 80.472 | 607.044 | 1344.413 | 207.471 | [22 empty] | 3352.9777 | 11750.847 | 95285.1098 | 5617.1784 | 39412.3468 | 155418.4597 |  | 3346.9137 | 11729.3681 | 95120.2 | 5617.1784 | 39412.3468 | 155226.007 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 0 | 3346.9137 | 105151.435 | 12903.8686 | 51135.374 | 172537.5913 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298 |  | 0 | 3346.9137 | 31445.2736 | 200915.6752 | 51862.4355 | 287570.298
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 |  | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 |  | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 |  | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 |  | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 |  | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 429606.482 | 429606.482 |  | 133525.13 | 131997.817 | 111927.524 | 14290.518 | 37865.493 |  | 116854.047 | 132599.293 | 113718.463 | 17131.055 | 48896.132 |  | 0 | 0 | 0 | 0 | 0 |  | 89101.216 | 130432.013 | 111110.444 | 21351.128 | 61606.829 |  | 0 | 0 | 0 | 0 | 0 |  | 56076.43 | 131994.285 | 102725.615 | 33499.829 | 89305.471 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 |  | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 |  | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 |  | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 |  | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 |  | 13776347.1823 | 22222399.6643 | 32223524.9247 | 32455872.9954 | 92800076.9686 | 193478221.7353
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 4211066.2056 | 3421678.8222 | 5551496.6948 | 1257043.0471 | 6954679.8549 | 21395964.6246 | LV Network | 4691413.5899 | 3410525.7925 | 5487707.7757 | 1033407.4644 | 4622006.4695 | 19245061.092 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 3678397.3012 | 3329052.0107 | 5722155.8151 | 1841827.6219 | 9569219.48 | 24140652.2289 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608 | LV Network | 2702546.1937 | 3300803.8866 | 5249365.9451 | 3379904.7088 | 15985632.8266 | 30618253.5608
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 12316928.9661 | 10628617.0745 | 15101393.9717 | 4286507.7002 | 23189561.2219 | 65523008.9345 | HV Network | 13829500.7358 | 10486091.8876 | 14561428.3703 | 2931218.3701 | 17983540.4425 | 59791779.8062 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 10592314.416 | 11313682.1024 | 13801738.0814 | 7899906.5441 | 28771283.7037 | 72378924.8477 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542 | HV Network | 7536945.3815 | 12107048.8494 | 12023861.4718 | 11016110.7726 | 47631374.1789 | 90315340.6542
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2461089.5483 | 2802573.408 | 8902885.5796 | 3153435.3007 | 12296114.9313 | 29616098.7679 | EHV Network | 2928797.1737 | 2748023.5897 | 8666735.4714 | 2884484.3582 | 6570479.7071 | 23798520.3002 | EHV Network | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 | EHV Network | 2320125.7008 | 2760206.8753 | 8238386.5002 | 5160642.7171 | 10685723.4023 | 29165085.1957 | EHV Network | 1793644.7601 | 2873288.8064 | 6744810.9862 | 6677938.6145 | 19552965.3925 | 37642648.5597 | EHV Network | 1793644.7601 | 2759533.2056 | 6744810.9862 | 5936229.9899 | 19552965.3925 | 36787184.3343
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1825061.5299 | 4029041.4462 | 8923989.0417 | 7786945.9759 | 24684265.228 | 47249303.2217 | 132kV Network | 2283480.3295 | 4056922.9693 | 8743887.9975 | 5109241.2966 | 1101383.5852 | 21294916.1781 | 132kV Network | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 | 132kV Network | 1816616.6732 | 4177720.5746 | 9268695.1682 | 5767701.312 | 4720549.3651 | 25751283.0932 | 132kV Network | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186 | 132kV Network | 1743210.8469 | 4055013.7227 | 8205486.5216 | 12123627.5242 | 9630104.5706 | 35757443.186
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 20814146.2499 | 20881910.751 | 38479765.2879 | 16483932.0239 | 67124621.2361 | 163784375.5487 | Total | 23733191.829 | 20701564.2391 | 37459759.6149 | 11958351.4893 | 30277410.2043 | 124130277.3765 | Total | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 | Total | 18407454.0913 | 21580661.5631 | 37030975.565 | 20670078.195 | 53746775.951 | 151435945.3655 | Total | 13776347.1823 | 22336155.2651 | 32223524.9247 | 33197581.62 | 92800076.9686 | 194333685.9606 | Total | 13776347.1823 | 22222399.6643 | 32223524.9247 | 32455872.9954 | 92800076.9686 | 193478221.7353
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## EMID - Average Cons. of Failure
Secondary deliverables RIIO-ED1 - Average Consequence of Asset Failure
EMID
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period |  |  |  |  | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence Of Asset Failure |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence Of Asset Failure
| LV Network | [5 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other |  |  |  |  | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 | LV UGB |  |  |  |  | 0
| LV OHL Support | 416 | 1405 | 278 | 2688 | 4787 | LV OHL Support | 416 | 1405 | 278 | 2688 | 4787
| LV Switchgear (at s/s) | 1896 | 787 | 488 | 3927 | 7098 | LV Switchgear (at s/s) | 1896 | 787 | 488 | 3927 | 7098
| LV UGB and LV Pillar OD (not at s/s) | 2150 | 658 | 488 | 2485 | 5781 | LV UGB and LV Pillar OD (not at s/s) | 2150 | 658 | 488 | 2485 | 5781
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| HV Network | [5 empty] | HV Network
| HV Switchgear (GM) - Primary | 64745 | 1264 | 1985 | 12468 | 80462 | HV Switchgear (GM) - Primary | 64745 | 1264 | 1985 | 12468 | 80462
| HV Switchgear (GM) - Distribution | 14058 | 1629 | 2438 | 4811 | 22936 | HV Switchgear (GM) - Distribution | 14058 | 1629 | 2438 | 4811 | 22936
| HV Transformer (GM) | 13028 | 1236 | 3658 | 4718 | 22640 | HV Transformer (GM) | 13028 | 1236 | 3658 | 4718 | 22640
| HV UG Cable | 37546 | 142 | 1102 | 10500 | 49290 | HV UG Cable | 37546 | 142 | 1102 | 10500 | 49290
| HV OHL Support - Poles | 3217 | 1464 | 478 | 2920 | 8079 | HV OHL Support - Poles | 3217 | 1464 | 478 | 2920 | 8079
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| EHV Network | [5 empty] | EHV Network
| EHV Switchgear (GM) | 131429 | 841 | 3729 | 22060 | 158059 | EHV Switchgear (GM) | 131429 | 841 | 3729 | 22060 | 158059
| EHV Transformer | 292683 | 1178 | 24219 | 153107 | 471187 | EHV Transformer | 292683 | 1178 | 24219 | 153107 | 471187
| EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Gas) |  |  |  |  | 0
| EHV UG Cable (Oil) | 4735 | 710 | 8805 | 9003 | 23253 | EHV UG Cable (Oil) | 4735 | 710 | 8805 | 9003 | 23253
| EHV UG Cable (Non Pressurised) | 53870 | 142 | 1602 | 13000 | 68614 | EHV UG Cable (Non Pressurised) | 53870 | 142 | 1602 | 13000 | 68614
| EHV OHL Support - Towers | 151019 | 25436 | 2230 | 63510 | 242195 | EHV OHL Support - Towers | 151019 | 25436 | 2230 | 63510 | 242195
| EHV OHL Support - Poles | 7888 | 1448 | 478 | 4100 | 13914 | EHV OHL Support - Poles | 7888 | 1448 | 478 | 4100 | 13914
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| EHV OHL Fittings | 100002 | 12718 | 880 | 4000 | 117600 | EHV OHL Fittings | 100002 | 12718 | 880 | 4000 | 117600
| EHV OHL Conductor (Tower Lines) | 100029 | 12718 | 880 | 4000 | 117627 | EHV OHL Conductor (Tower Lines) | 100029 | 12718 | 880 | 4000 | 117627
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| 132kV Network | [5 empty] | 132kV Network
| 132kV CBs | 295844 | 1106 | 7395 | 21512 | 325857 | 132kV CBs | 295844 | 1106 | 7395 | 21512 | 325857
| 132kV Transformer | 1745086 | 1273 | 60737 | 316056 | 2123152 | 132kV Transformer | 1745086 | 1273 | 60737 | 316056 | 2123152
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) |  |  |  |  | 0
| 132kV UG Cable (Oil) | 73590 | 710 | 8805 | 18006 | 101111 | 132kV UG Cable (Oil) | 73590 | 710 | 8805 | 18006 | 101111
| 132kV UG Cable (Non Pressurised) | 408508 | 710 | 2501 | 225000 | 636719 | 132kV UG Cable (Non Pressurised) | 408508 | 710 | 2501 | 225000 | 636719
| 132kV OHL Support - Tower | 1067827 | 25436 | 2230 | 137123 | 1232616 | 132kV OHL Support - Tower | 1067827 | 25436 | 2230 | 137123 | 1232616
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| 132kV OHL Fittings | 554281 | 12718 | 880 | 4000 | 571879 | 132kV OHL Fittings | 554281 | 12718 | 880 | 4000 | 571879
| 132kV OHL Conductor (Tower Lines) | 555722 | 12718 | 880 | 4000 | 573320 | 132kV OHL Conductor (Tower Lines) | 555722 | 12718 | 880 | 4000 | 573320
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| Other | [5 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | Submarine Cables |  |  |  |  | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]

## EMID - Probs. of Failure
Probabilities of Asset Failure
EMID
Price base (2012/13)
Average Probabilities of Asset Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other | 0 | 0 | 0 | 0 | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB | 0 | 0 | 0 | 0 | 0
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | LV OHL Support | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV Switchgear (at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV UGB and LV Pillar OD (not at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | [10 empty] | HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Primary | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Distribution | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | HV Transformer (GM) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| HV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV UG Cable | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | [10 empty] | EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Switchgear (GM) | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.89173 | 0.89173 | 1.3378 | 1.3378 | 3.5244 | EHV UG Cable (Oil) | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Towers | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402 | EHV OHL Fittings | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391
| [Please insert new asset category as required] | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 0.00018655 | 0.00018655 | 0.00027988 | 0.00027988 | 0.00073732 | EHV OHL Conductor (Tower Lines) | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | [10 empty] | 132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV CBs | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.013355 | 0.89173 | 0.89173 | 1.3378 | 1.3378 | 3.5244 | 132kV UG Cable (Oil) | 0.01335 | 0.01335 | 0.45254 | 1.1046 | 2.3146
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | 132kV OHL Support - Tower | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005 | 132kV OHL Fittings | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055
| [Please insert new asset category as required] | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 6.752e-05 | 0.00018655 | 0.00018655 | 0.00027988 | 0.00027988 | 0.00073732 | 132kV OHL Conductor (Tower Lines) | 7e-05 | 7e-05 | 9e-05 | 0.00023 | 0.00048
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0
| Other | [10 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 19245061.092 | 24140652.2289 | 19734490.5759 | 30618253.5608 | 21679249.3979
HV Network | 59791779.8062 | 72378924.8477 | 59795823.9109 | 90315340.6542 | 61516514.4944
EHV Network | 23798520.3002 | 29165085.1957 | 22978215.4391 | 37642648.5597 | 23350957.8344
132kV Network | 21294916.1781 | 25751283.0932 | 18509105.2965 | 35757443.186 | 19963061.8243
Other | 0 | 0 | 0 | 0 | 0
Total | 124130277.3765 | 151435945.3655 | 121017635.2224 | 194333685.9606 | 126509783.5511
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary deliverables target)
LV Network |  | 4895591.1368 | -4406161.653 | 11373192.4687 | -8939004.1629
HV Network |  | 12587145.0414 | -12583100.9368 | 30523560.8479 | -28798826.1598
EHV Network |  | 5366564.8956 | -6186869.7567 | 13844128.2595 | -14291690.7252
132kV Network |  | 4456366.9151 | -7242177.7967 | 14462527.0079 | -15794381.3616
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 27305667.9889 | -30418310.1431 | 70203408.5841 | -67823902.4096