## SWEST - Total
Total Secondary deliverables RIIO-ED1 - Asset replacement, Refurbishment and HVP | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWEST | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | C1 | 43.7303 | 43.7303 | 60.854 | 149.7132 | 313.6848 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 14161 | 0 | -2266 | -3115 | -8780 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 28834 | 0 | -4614 | -6343 | -17877 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4873 | 4873 | 4873 | 4873 | 4873 | C2 | 62.4719 | 62.4719 | 86.9343 | 213.876 | 448.1211 | C2 | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 1742027.8161 | 8563580.0969 | 208729.3023 | 5454051.111 | 2542190.8868 | 18510579.2132 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 2017028.9438 | 8563580.0969 | 93889.0656 | 5171520.9546 | 1753497.786 | 17599516.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | C3 | 93.7078 | 93.7078 | 130.4015 | 320.814 | 672.1816 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | C4 | 156.1797 | 156.1797 | 217.3358 | 534.6899 | 1120.3027 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 14161 | 0 | -2266 | -3115 | -8780 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 28834 | 0 | -4614 | -6343 | -17877 |  | 3453 | 137079 | 5694 | 30523 | 21790 | [22 empty] | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 1742027.8161 | 8563580.0969 | 208729.3023 | 5454051.111 | 2542190.8868 | 18510579.2132 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 2017028.9438 | 8563580.0969 | 93889.0656 | 5171520.9546 | 1753497.786 | 17599516.847
| LV Switchgear (at s/s) |  | 857 | 857 | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 5 | 0 | 0 | 0 | -5 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 7 | 0 | 0 | 0 | -7 | 0 | 586 | 148 | 93 | 10 | 20 | 857 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | C1 | 76.19 | 76.19 | 105.9604 | 260.7189 | 546.2926 | C1 | 49066.3613 | 8304.7102 | 7629.1483 | 1564.3131 | 7648.0967 | 74212.6296 |  | 51733.0114 | 8228.5202 | 5721.8612 | 1564.3131 | 5462.9262 | 72710.6321 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 48380.6513 | 10818.9803 | 6463.584 | 2346.4697 | 5462.9262 | 73472.6115 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819 |  | 45180.6712 | 11276.1203 | 9854.3165 | 2607.1886 | 7101.8041 | 76020.1007
|  |  | 11264 | 11264 | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 474 | -25 | -59 | -92 | -298 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 954 | -56 | -82 | -122 | -694 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5663 | 5663 | 5663 | 5663 | 5663 | C2 | 108.8429 | 108.8429 | 151.372 | 372.4555 | 780.418 | C2 | 548568.0144 | 212352.4199 | 536916.4485 | 90134.2334 | 263000.8761 | 1650971.9923 |  | 610608.4446 | 209849.0341 | 515572.9979 | 87527.0448 | 66335.5325 | 1489893.054 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 543670.0857 | 256216.0924 | 548420.7198 | 84919.8563 | 49946.7539 | 1483173.5081 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721 |  | 515479.785 | 293549.1934 | 507550.2825 | 131104.3395 | 98332.6718 | 1546016.2721
|  |  | 107 | 107 | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 17 | 0 | -1 | -1 | -15 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 32 | 0 | -2 | -6 | -24 | 0 | 16 | 16 | 35 | 16 | 24 | 107 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | C3 | 163.2643 | 163.2643 | 227.058 | 558.6833 | 1170.627 | C3 | 1959.1715 | 2612.2286 | 13396.4211 | 6704.1992 | 9365.0164 | 34037.0368 |  | 3265.2858 | 2612.2286 | 12942.3051 | 6704.1992 | 2341.2541 | 27865.2729 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 5714.2502 | 2448.9644 | 11807.0152 | 2793.4163 | 0 | 22763.646 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681 |  | 7836.6859 | 2612.2286 | 7492.9135 | 5586.8327 | 0 | 23528.6607
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | C4 | 272.1071 | 272.1071 | 378.43 | 931.1388 | 1951.0451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12228 | 12228 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 496 | -25 | -60 | -93 | -318 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 993 | -56 | -84 | -128 | -725 |  | 4384 | 2917 | 3563 | 500 | 864 | [22 empty] | 599593.5472 | 223269.3587 | 557942.0179 | 98402.7457 | 280013.9892 | 1759221.6587 |  | 665606.7418 | 220689.7829 | 534237.1643 | 95795.5572 | 74139.7128 | 1590468.959 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 597764.9871 | 269484.0371 | 566691.319 | 90059.7423 | 55409.6801 | 1579409.7656 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592 |  | 568497.1421 | 307437.5424 | 524897.5125 | 139298.3607 | 105434.4759 | 1645565.0335
| LV UGB and LV Pillar OD (not at s/s) |  | 180 | 180 | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 1 | 0 | 0 | 0 | -1 | 0 | 179 | 0 | 0 | 0 | 1 | 180 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3269 | 3269 | 3269 | 3269 | 3269 | C1 | 62.8302 | 62.8302 | 87.3804 | 215.0021 | 450.5009 | C1 | 10618.3004 | 0 | 87.3804 | 0 | 0 | 10705.6808 |  | 11246.6022 | 0 | 87.3804 | 0 | 0 | 11333.9826 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031 |  | 11309.4324 | 0 | 0 | 0 | 0 | 11309.4324
|  |  | 11974 | 11974 | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 348 | 0 | 0 | -115 | -233 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 703 | 0 | 0 | 0 | -703 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 4670 | 4670 | 4670 | 4670 | 4670 | C2 | 89.7574 | 89.7574 | 124.8291 | 307.1459 | 643.5727 | C2 | 196927.7356 | 226727.1924 | 865065.663 | 921.4377 | 231686.172 | 1521328.2007 |  | 205364.9312 | 226727.1924 | 865065.663 | 921.4377 | 146091.0029 | 1444170.2272 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 204377.5998 | 188400.7826 | 868685.7069 | 192273.3334 | 8366.4451 | 1462103.8678 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959 |  | 189657.3862 | 137598.0942 | 773940.42 | 535969.5955 | 246488.3441 | 1883653.84
|  |  | 179 | 179 | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 16 | 0 | 0 | 0 | -16 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 24 | 0 | 0 | 0 | -24 | 0 | 14 | 9 | 114 | 18 | 24 | 179 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7005 | 7005 | 7005 | 7005 | 7005 | C3 | 134.6361 | 134.6361 | 187.2437 | 460.7188 | 965.359 | C3 | 942.4527 | 3904.4469 | 21720.2634 | 7371.5016 | 965.359 | 34904.0237 |  | 2423.4498 | 3904.4469 | 21720.2634 | 7371.5016 | 0 | 35419.6617 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 4173.7191 | 2154.1776 | 23405.4562 | 3225.0319 | 0 | 32958.3849 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629 |  | 5116.1718 | 1211.7249 | 21345.7761 | 8292.9393 | 0 | 35966.6121
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 11675 | 11675 | 11675 | 11675 | 11675 | C4 | 224.3935 | 224.3935 | 312.0727 | 767.8647 | 1608.9317 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12333 | 12333 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 364 | 0 | 0 | -115 | -249 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 728 | 0 | 0 | 0 | -728 |  | 1603 | 1542 | 6314 | 1763 | 1111 | [22 empty] | 208488.4887 | 230631.6393 | 886873.3068 | 8292.9393 | 232651.531 | 1566937.9051 |  | 219034.9832 | 230631.6393 | 886873.3068 | 8292.9393 | 146091.0029 | 1490923.8715 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 219797.9211 | 190554.9602 | 892091.1632 | 195713.3675 | 8366.4451 | 1506523.857 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619 |  | 206082.9904 | 138809.8191 | 795286.1961 | 544262.5348 | 246488.3441 | 1930929.8845
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 |  | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 2559590.7243 | 9023619.0942 | 1667511.7844 | 5739824.2208 | 2605967.0121 | 21596512.8358 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 |  | 2791609.0763 | 9009827.4584 | 1414072.7742 | 5855081.8501 | 2105420.606 | 21176011.765
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 700 | 700 | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 62 | 0 | -21 | -9 | -32 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 127 | 0 | -28 | -5 | -94 | 0 | 247 | 98 | 163 | 72 | 120 | 700 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | C1 | 564.9671 | 564.9671 | 786.1945 | 1934.1972 | 4052.6036 | C1 | 169490.1432 | 35592.9301 | 193403.8539 | 96709.8594 | 158051.5416 | 653248.3282 |  | 176834.7161 | 35592.9301 | 192617.6594 | 94775.6622 | 121578.109 | 621399.0767 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 198303.4675 | 34462.9958 | 154094.1275 | 114117.6341 | 133735.9199 | 634714.1448 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061 |  | 211297.7119 | 55366.7801 | 106136.2613 | 129591.2116 | 105367.6944 | 607759.6593
|  |  | 1868 | 1868 | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 184 | 0 | -33 | -22 | -129 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 386 | 0 | -73 | -19 | -294 | 0 | 574 | 255 | 417 | 253 | 369 | 1868 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 62956 | 62956 | 62956 | 62956 | 62956 | C2 | 807.0959 | 807.0959 | 1123.135 | 2763.1388 | 5789.4338 | C2 | 506856.2378 | 149312.7452 | 824381.1194 | 392365.7153 | 706310.9187 | 2579226.7363 |  | 573038.1032 | 149312.7452 | 822134.8493 | 384076.2988 | 590522.2435 | 2519084.24 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 681996.0524 | 159804.9922 | 621093.6771 | 580259.1564 | 358944.8931 | 2402098.7712 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133 |  | 774812.0832 | 205809.4596 | 386358.4538 | 646574.4886 | 434207.532 | 2447762.0171
|  |  | 455 | 455 | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 74 | 0 | -5 | -18 | -51 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 127 | 0 | -9 | -19 | -99 | 0 | 109 | 57 | 103 | 74 | 112 | 455 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 94434 | 94434 | 94434 | 94434 | 94434 | C3 | 1210.6439 | 1210.6439 | 1684.7026 | 4144.7083 | 8684.1506 | C3 | 116221.8125 | 56900.2624 | 338625.2146 | 116051.8313 | 477628.2852 | 1105427.4059 |  | 161015.636 | 56900.2624 | 338625.2146 | 116051.8313 | 399470.9294 | 1072063.8737 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 237286.2005 | 61742.8379 | 264498.3019 | 174077.7469 | 78157.3558 | 815762.443 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307 |  | 285711.9557 | 69006.7012 | 158362.0406 | 227958.9543 | 112893.9583 | 853933.6101
|  |  | 23 | 23 | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 1 | 0 | 0 | -1 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 5 | 0 | 0 | -4 | -1 | 0 | 6 | 4 | 6 | 6 | 1 | 23 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 157390 | 157390 | 157390 | 157390 | 157390 | C4 | 2017.7398 | 2017.7398 | 2807.8376 | 6907.8471 | 14473.5844 | C4 | 4035.4796 | 6053.2194 | 33694.0512 | 6907.8471 | 72367.922 | 123058.5193 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 16141.9184 | 6053.2194 | 33694.0512 | 0 | 0 | 55889.189 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906 |  | 22195.1378 | 8070.9592 | 16847.0256 | 13815.6942 | 0 | 60928.8168
|  |  | 3046 | 3046 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 321 | 0 | -59 | -50 | -212 |  | 1079 | 313 | 977 | 361 | 316 |  | 645 | 0 | -110 | -47 | -488 |  | 936 | 414 | 689 | 405 | 602 | [22 empty] | 796603.673 | 247859.157 | 1390104.239 | 612035.2531 | 1414358.6676 | 4460960.9897 |  | 925012.6339 | 247859.157 | 1387071.7744 | 601811.6394 | 1111571.2819 | 4273326.4866 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 1133727.6388 | 262064.0452 | 1073380.1577 | 868454.5374 | 570838.1687 | 3908464.5479 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407 |  | 1294016.8885 | 338253.9001 | 667703.7813 | 1017940.3487 | 652469.1848 | 3970384.1033
| HV Switchgear (GM) - Distribution |  | 669 | 666 | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 8 | -10 | 0 | 0 | 0 | -2 | 644 | 18 | 2 | 5 | 0 | 669 | 19 | -18 | -1 | 0 | -3 | -3 | 626 | 36 | 2 | 0 | 5 | 669 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | C1 | 136.001 | 136.001 | 189.2556 | 465.6071 | 975.5577 | C1 | 87040.6208 | 2856.0204 | 1324.7895 | 0 | 0 | 91221.4307 |  | 87584.6247 | 2448.0175 | 1324.7895 | 0 | 0 | 91357.4316 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 88672.6324 | 1088.0078 | 378.5113 | 2328.0353 | 0 | 92467.1868 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417 |  | 87720.6257 | 2448.0175 | 189.2556 | 0 | 1951.1153 | 92309.0141
|  |  | 14652 | 14304 | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 893 | -125 | -27 | 0 | -913 | -172 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 1806 | -107 | -185 | -43 | -1819 | -348 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 15155 | 15155 | 15155 | 15155 | 15155 | C2 | 194.2871 | 194.2871 | 270.3652 | 665.153 | 1393.6538 | C2 | 1117539.3992 | 665433.3175 | 904912.3244 | 580013.3724 | 1754610.1342 | 5022508.5477 |  | 1188065.6165 | 648724.6269 | 889771.8732 | 578683.0665 | 1445218.9906 | 4750464.1737 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 1117539.3992 | 770542.6386 | 767296.4376 | 817472.9756 | 968589.391 | 4441440.842 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762 |  | 1154065.374 | 761411.1449 | 750804.1604 | 750957.6806 | 751179.3982 | 4168417.7581
|  |  | 1431 | 1354 | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 202 | -11 | 0 | 0 | -230 | -39 | 82 | 398 | 360 | 235 | 356 | 1431 | 404 | 0 | -17 | -6 | -458 | -77 | 65 | 335 | 354 | 164 | 513 | 1431 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | C3 | 291.4307 | 291.4307 | 405.5478 | 997.7294 | 2090.4807 | C3 | 38760.2765 | 107246.4792 | 167896.7892 | 236461.8737 | 589515.5574 | 1139880.976 |  | 53040.3783 | 105789.3259 | 166274.598 | 236461.8737 | 499624.8873 | 1061191.0633 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 82766.3046 | 112783.6616 | 145997.208 | 234466.4149 | 263400.5682 | 839414.1572 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406 |  | 136680.9748 | 97629.2677 | 136669.6086 | 157641.2491 | 114976.4385 | 643597.5389
|  |  | 50 | 46 | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 1 | 25 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 0 | 26 | 50 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | C4 | 485.7177 | 485.7177 | 675.913 | 1662.8824 | 3484.1345 | C4 | 6800.0485 | 1457.1532 | 4055.478 | 8314.4119 | 76650.959 | 97278.0506 |  | 10200.0727 | 1457.1532 | 0 | 8314.4119 | 73166.8245 | 93138.4624 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 17000.1213 | 4371.4597 | 0 | 1662.8824 | 3484.1345 | 26518.5979 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723 |  | 17000.1213 | 4371.4597 | 0 | 0 | 6968.269 | 28339.85
|  |  | 16802 | 16370 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 1123 | -146 | -27 | 0 | -1167 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 2249 | -125 | -203 | -49 | -2304 |  | 4840 | 4406 | 3318 | 1336 | 2902 | [22 empty] | 1250140.345 | 776992.9703 | 1078189.3811 | 824789.658 | 2420776.6506 | 6350889.0049 |  | 1338890.6922 | 758419.1236 | 1057371.2607 | 823459.3521 | 2018010.7024 | 5996151.131 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 1305978.4575 | 888785.7677 | 913672.1569 | 1055930.3081 | 1235474.0937 | 5399840.7839 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469 |  | 1395467.0958 | 865859.8899 | 887663.0246 | 908598.9297 | 875075.221 | 4932664.161
| HV Transformer (GM) |  | 2220 | 2220 | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 151 | 0 | -1 | -18 | -132 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 275 | 0 | -1 | 0 | -274 | 0 | 822 | 319 | 682 | 114 | 283 | 2220 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | C1 | 219.1926 | 219.1926 | 304.8396 | 750.0674 | 1571.6404 | C1 | 204506.6659 | 89211.3752 | 183513.4464 | 54004.8519 | 311184.7921 | 842421.1316 |  | 223795.6119 | 88115.4123 | 181379.5691 | 54004.8519 | 204313.2473 | 751608.6927 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 232563.3146 | 78690.1319 | 200889.3043 | 52504.7172 | 111586.4658 | 676233.9339 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407 |  | 240454.2471 | 69922.4292 | 207595.7758 | 85507.6822 | 14144.7633 | 617624.8976
|  |  | 8983 | 8983 | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 536 | 0 | -4 | -121 | -411 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 1057 | 0 | -2 | -172 | -883 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 16292 | 16292 | 16292 | 16292 | 16292 | C2 | 313.1322 | 313.1322 | 435.4852 | 1071.5248 | 2245.2005 | C2 | 1133538.7088 | 600900.7686 | 1128777.5347 | 233592.4151 | 1356101.1141 | 4452910.5413 |  | 1234367.2901 | 592446.1981 | 1110051.6728 | 233592.4151 | 857666.5986 | 4028124.1748 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 1258165.3403 | 503516.6419 | 1271181.182 | 291454.7565 | 372703.2863 | 3697021.2071 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606 |  | 1261296.6627 | 496001.4682 | 1301665.1432 | 333244.2252 | 159409.2369 | 3551616.7363
|  |  | 1848 | 1848 | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 75 | 0 | 0 | -26 | -49 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 195 | 0 | 0 | -74 | -121 | 0 | 726 | 360 | 525 | 111 | 126 | 1848 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 24438 | 24438 | 24438 | 24438 | 24438 | C3 | 469.6984 | 469.6984 | 653.2277 | 1607.2873 | 3367.8008 | C3 | 427425.5076 | 154530.7604 | 327920.3255 | 43396.756 | 245849.4569 | 1199122.8065 |  | 456546.8059 | 151712.5703 | 316162.2262 | 43396.756 | 141447.6328 | 1109265.9911 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 439637.665 | 151712.5703 | 349476.8409 | 48218.6178 | 80827.2187 | 1069872.9127 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666 |  | 432592.1896 | 169091.4096 | 342944.5635 | 59469.6286 | 16839.0039 | 1020936.7952
|  |  | 14 | 14 | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 5 | 4 | 0 | 2 | 14 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 40730 | 40730 | 40730 | 40730 | 40730 | C4 | 782.8306 | 782.8306 | 1088.7129 | 2678.8121 | 5613.0013 | C4 | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 3914.153 | 4696.9836 | 3266.1387 | 0 | 0 | 11877.2753 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499 |  | 3914.153 | 3914.153 | 4354.8516 | 0 | 0 | 12183.1576
|  |  | 13065 | 13065 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 764 | 0 | -5 | -165 | -594 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 1529 | 0 | -3 | -246 | -1280 |  | 4522 | 2268 | 4202 | 708 | 1365 | [22 empty] | 1769385.0353 | 847774.2266 | 1643477.4453 | 333672.8352 | 1918748.3644 | 6513057.9068 |  | 1918623.8609 | 835405.5031 | 1610859.6068 | 333672.8352 | 1209040.48 | 5907602.2861 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1934280.4729 | 738616.3277 | 1824813.4659 | 392178.0914 | 565116.9709 | 5455005.3289 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669 |  | 1938257.2524 | 738929.46 | 1856560.3341 | 478221.5361 | 190393.0041 | 5202361.5866
| HV UG Cable |  | 1411.786 | 1411.786 | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 23093 | 23093 | 23093 | 23093 | 23093 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4500.517 | 4500.517 | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 32990 | 32990 | 32990 | 32990 | 32990 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1028.333 | 1028.333 | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 49485 | 49485 | 49485 | 49485 | 49485 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 82475 | 82475 | 82475 | 82475 | 82475 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6940.636 | 6940.636 |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | C1 | 61.436 | 61.436 | 85.4928 | 210.3297 | 440.6907 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 211011 | 211011 | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 15253 | 0 | -2442 | -3355 | -9456 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 31473 | 0 | -5037 | -6922 | -19514 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6846 | 6846 | 6846 | 6846 | 6846 | C2 | 87.7657 | 87.7657 | 122.1326 | 300.4709 | 629.5582 | C2 | 2581102.0595 | 12844337.5906 | 580984.9685 | 5771145.3446 | 7032164.6472 | 28809734.6103 |  | 3199411.5569 | 12844425.3563 | 538604.9424 | 5459556.9798 | 3543153.3245 | 25585152.1598 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 3601027.4916 | 12844337.5906 | 370916.8277 | 5047010.3792 | 2391691.4498 | 24254983.7389 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296 |  | 4028095.4851 | 12844425.3563 | 192603.1733 | 4608623.2777 | 1165312.1542 | 22839059.4466
|  |  | 2291 | 2291 | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 165 | 0 | -25 | -37 | -103 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 341 | 0 | -54 | -76 | -211 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10269 | 10269 | 10269 | 10269 | 10269 | C3 | 131.6486 | 131.6486 | 183.199 | 450.7064 | 944.3372 | C3 | 41995.897 | 209189.5936 | 9526.3459 | 94197.6397 | 113320.4688 | 468229.945 |  | 52132.8377 | 209189.5936 | 8793.5501 | 88789.1628 | 57604.5716 | 416509.7158 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 58583.6181 | 209321.2422 | 6045.5657 | 82028.5666 | 38717.8268 | 394696.8194 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377 |  | 65560.9928 | 209189.5936 | 3114.3823 | 74817.2641 | 19831.082 | 372513.3149
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17115 | 17115 | 17115 | 17115 | 17115 | C4 | 219.4143 | 219.4143 | 305.3316 | 751.1773 | 1573.8954 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 213302 | 213302 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 15418 | 0 | -2467 | -3392 | -9559 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 31814 | 0 | -5091 | -6998 | -19725 |  | 14580 | 147938 | 6685 | 22502 | 21597 | [22 empty] | 2623097.9565 | 13053527.1842 | 590511.3144 | 5865342.9843 | 7145485.116 | 29277964.5554 |  | 3251544.3946 | 13053614.9499 | 547398.4925 | 5548346.1426 | 3600757.8961 | 26001661.8756 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 3659611.1097 | 13053658.8328 | 376962.3934 | 5129038.9458 | 2430409.2767 | 24649680.5583 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673 |  | 4093656.478 | 13053614.9499 | 195717.5556 | 4683440.5418 | 1185143.2362 | 23211572.7614
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 |  | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 8033597.6789 | 14943124.9734 | 4188828.1739 | 7445601.8828 | 4801838.51 | 39412991.219 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 |  | 8721397.7146 | 14996658.1998 | 3607644.6956 | 7088201.3562 | 2903080.6461 | 37316982.6123
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 369 | 369 | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 16 | 0 | -2 | 0 | -14 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 30 | -2 | -2 | -1 | -25 | 0 | 210 | 80 | 31 | 12 | 36 | 369 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | C1 | 910.9866 | 910.9866 | 1267.7068 | 3118.8146 | 6534.6592 | C1 | 242322.4452 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 425963.7075 |  | 246877.3784 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 430518.6407 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 240500.4719 | 51926.2383 | 27889.5503 | 68613.9217 | 26138.6368 | 415068.819 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432 |  | 218636.7926 | 71056.9576 | 36763.4981 | 34306.9608 | 71881.2513 | 432645.4605
|  |  | 475 | 475 | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 52 | 0 | -2 | -13 | -37 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 85 | -1 | 0 | -3 | -81 | 0 | 157 | 91 | 69 | 36 | 122 | 475 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 101514 | 101514 | 101514 | 101514 | 101514 | C2 | 1301.4095 | 1301.4095 | 1811.0098 | 4455.4495 | 9335.2274 | C2 | 275898.8098 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 912299.212 |  | 282405.8572 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 918806.2594 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 307132.6373 | 98907.1205 | 146691.7906 | 325247.8106 | 84017.047 | 961996.4059 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527 |  | 314941.0942 | 117126.8532 | 124959.6734 | 147029.8322 | 382744.325 | 1086801.778
|  |  | 127 | 127 | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 11 | 0 | 0 | -1 | -10 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 41 | 0 | 0 | -6 | -35 | 0 | 33 | 21 | 9 | 24 | 40 | 127 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 152271 | 152271 | 152271 | 152271 | 152271 | C3 | 1952.1142 | 1952.1142 | 2716.5146 | 6683.1742 | 14002.8412 | C3 | 81988.7972 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 417338.266 |  | 91749.3683 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 427098.8371 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 107366.2821 | 31233.8275 | 73345.8953 | 167079.3547 | 56011.3646 | 435036.7243 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266 |  | 144456.4523 | 40994.3986 | 24448.6318 | 120297.1354 | 70014.2058 | 400210.8239
|  |  | 55 | 55 | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 7 | 0 | -1 | -3 | -3 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 14 | 0 | 0 | -4 | -10 | 0 | 9 | 16 | 8 | 9 | 13 | 55 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 253785 | 253785 | 253785 | 253785 | 253785 | C4 | 3253.5237 | 3253.5237 | 4527.5244 | 11138.6236 | 23338.0686 | C4 | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 84591.6162 | 32535.237 | 49802.7684 | 66831.7419 | 46676.1372 | 280437.5007 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924 |  | 74831.0451 | 52056.3792 | 36220.1952 | 55693.1182 | 70014.2058 | 288814.9435
|  |  | 1026 | 1026 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 86 | 0 | -5 | -17 | -64 |  | 495 | 159 | 146 | 143 | 83 |  | 170 | -3 | -2 | -14 | -151 |  | 409 | 208 | 117 | 81 | 211 | [22 empty] | 678294.621 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 1998176.502 |  | 699117.1727 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 2018999.0537 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 739591.0075 | 214602.4233 | 297730.0045 | 627772.8289 | 212843.1856 | 2092539.4498 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149 |  | 752865.3842 | 281234.5886 | 222391.9985 | 357327.0467 | 594653.9879 | 2208473.006
| EHV Transformer |  | 246 | 246 | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 16 | 0 | 0 | -1 | -15 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 34 | 0 | 0 | 0 | -34 | 0 | 105 | 39 | 36 | 16 | 50 | 246 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | C1 | 3379.4828 | 3379.4828 | 4702.806 | 11569.8517 | 24241.594 | C1 | 395399.4834 | 84487.0691 | 286871.164 | 300816.1436 | 363623.9099 | 1431197.77 |  | 425814.8283 | 84487.0691 | 277465.5521 | 266106.5886 | 315140.7219 | 1369014.76 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 429194.311 | 125040.8623 | 211626.2686 | 196687.4785 | 484831.8798 | 1447380.8002 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593 |  | 469748.1042 | 131799.8278 | 169301.0148 | 185117.6268 | 387865.5039 | 1343832.0776
|  |  | 248 | 248 | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 19 | 0 | 0 | -1 | -18 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 38 | 0 | 0 | 0 | -38 | 0 | 34 | 38 | 73 | 38 | 65 | 248 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 376586 | 376586 | 376586 | 376586 | 376586 | C2 | 4827.8325 | 4827.8325 | 6718.2942 | 16528.3595 | 34630.8486 | C2 | 241391.626 | 120695.813 | 866659.957 | 512379.1457 | 346308.4856 | 2087435.0273 |  | 265530.7886 | 120695.813 | 866659.957 | 512379.1457 | 277046.7885 | 2042312.4928 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 313809.1138 | 159318.4732 | 665111.1298 | 561964.2244 | 588724.4255 | 2288927.3666 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399 |  | 347603.9414 | 183457.6358 | 490435.4795 | 628077.6625 | 935032.9111 | 2584607.6304
|  |  | 73 | 73 | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 9 | 0 | 0 | 0 | -9 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 19 | 0 | 0 | 0 | -19 | 0 | 22 | 7 | 12 | 11 | 21 | 73 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 564879 | 564879 | 564879 | 564879 | 564879 | C3 | 7241.7488 | 7241.7488 | 10077.4414 | 24792.5393 | 51946.2728 | C3 | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 246219.4585 | 28966.9951 | 211626.2686 | 223132.8538 | 259731.3642 | 969676.9402 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673 |  | 296911.7 | 50692.2415 | 120929.2963 | 272717.9324 | 103892.5457 | 845143.7159
|  |  | 30 | 30 | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 3 | 0 | 0 | -2 | -1 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 18 | 4 | 2 | 1 | 5 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 941465 | 941465 | 941465 | 941465 | 941465 | C4 | 12069.5813 | 12069.5813 | 16795.7356 | 41320.8988 | 86577.1214 | C4 | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 301739.5325 | 0 | 50387.2068 | 82641.7977 | 0 | 434768.537 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656 |  | 253461.2073 | 48278.3252 | 33591.4712 | 41320.8988 | 173154.2428 | 549806.1454
|  |  | 597 | 597 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 47 | 0 | 0 | -4 | -43 |  | 204 | 74 | 168 | 66 | 85 |  | 94 | 0 | 0 | 0 | -94 |  | 179 | 88 | 123 | 66 | 141 | [22 empty] | 1083365.6175 | 234149.8772 | 1580142.8052 | 1110705.7611 | 865771.214 | 4874135.275 |  | 1137920.125 | 234149.8772 | 1570737.1933 | 1075996.2061 | 748026.3289 | 4766829.7304 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 1290962.4158 | 313326.3305 | 1138750.8737 | 1064426.3544 | 1333287.6696 | 5140753.644 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378 |  | 1367724.9529 | 414228.0302 | 814257.2619 | 1127234.1206 | 1599945.2035 | 5323389.5691
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C1 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | C1 | 553.5916 | 553.5916 | 18758.3105 | 45788.1803 | 95940.8181 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 0 | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | -17 | -17 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | -34 | -34 | 0 | 0 | 0 | 0 | 34 | 34 |  |  | C2 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C2 | 8424 | 8424 | 8424 | 8424 | 8424 | C2 | 790.8451 | 790.8451 | 26797.5864 | 65411.6861 | 137058.3115 | C2 | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 2329991.2958 | 2329991.2958 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C3 | 12636 | 12636 | 12636 | 12636 | 12636 | C3 | 1186.2677 | 1186.2677 | 40196.3796 | 98117.5291 | 205587.4673 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C4 | 21060 | 21060 | 21060 | 21060 | 21060 | C4 | 1977.1128 | 1977.1128 | 66993.966 | 163529.2152 | 342645.7788 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | -17 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | -34 |  | 0 | 0 | 0 | 0 | 34 | [22 empty] | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 2329991.2958 | 2329991.2958 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 21.926 | 21.926 | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | C1 | 301.5188 | 301.5188 | 10223.8139 | 24955.7384 | 52290.2374 | C1 | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936
|  |  | 29.901 | 15.501 | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | -7.2 | 0 | -7.2 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | -14.4 | -14.4 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 72272 | 72272 | 72272 | 72272 | 72272 | C2 | 430.7411 | 430.7411 | 14605.4485 | 35651.0549 | 74700.3392 | C2 | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 57.7193 | 1872.0009 | 155109.8629 | 270983.6681 | 0 | 428023.2512 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 29954.836 | 220614.036
|  |  | 8.451 | 8.451 | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 108408 | 108408 | 108408 | 108408 | 108408 | C3 | 646.1117 | 646.1117 | 21908.1727 | 53476.5823 | 112050.5088 | C3 | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 180680 | 180680 | 180680 | 180680 | 180680 | C4 | 1076.8528 | 1076.8528 | 36513.6212 | 89127.6372 | 186750.848 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 60.278 | 45.878 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | -7.2 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | -14.4 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801 | [22 empty] | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 239.1905 | 5938.0679 | 420398.8474 | 270983.6681 | 0 | 697559.774 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 29954.836 | 586211.133
| EHV UG Cable (Non Pressurised) |  | 241.211 | 241.211 | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 383.855 | 383.855 | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 50665 | 50665 | 50665 | 50665 | 50665 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 188.435 | 188.435 | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10.863 | 10.863 | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 824.364 | 824.364 |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 125 | 125 | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 2 | 0 | 0 | 0 | -2 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 4 | 7 | 0 | -7 | -4 | 0 | 27 | 69 | 18 | 7 | 4 | 125 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | C1 | 81.561 | 81.561 | 81.561 | 4130.3727 | 14151.6049 | C1 | 2528.3913 | 6524.8809 | 978.7321 | 24782.2362 | 0 | 34814.2406 |  | 2528.3913 | 6280.1978 | 897.1711 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2365.2693 | 5709.2708 | 1631.2202 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5627.7098 | 1468.0982 | 28912.609 | 56606.4194 | 94816.9836 |  | 2528.3913 | 6198.6368 | 1468.0982 | 0 | 0 | 10195.1264
|  |  | 299 | 299 | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 9 | 0 | -9 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 4 | 10 | 0 | -10 | -4 | 0 | 58 | 176 | 51 | 10 | 4 | 299 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 219841 | 219841 | 219841 | 219841 | 219841 | C2 | 116.5157 | 116.5157 | 116.5157 | 5900.5324 | 20216.5784 | C2 | 7690.0382 | 18759.0325 | 6874.4281 | 47204.2595 | 121299.4702 | 201827.2285 |  | 8389.1326 | 18992.064 | 6757.9123 | 35403.1946 | 0 | 69542.3035 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 8039.5854 | 20390.2527 | 6408.3651 | 0 | 0 | 34838.2033 |  | 6757.9123 | 20506.7685 | 5942.3022 | 59005.3244 | 80866.3134 | 173078.6209 |  | 7223.9753 | 21671.9258 | 5942.3022 | 0 | 0 | 34838.2033
|  |  | 65 | 65 | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 1 | 2 | 0 | -2 | -1 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 1 | 3 | 0 | -3 | -1 | 0 | 14 | 33 | 14 | 3 | 1 | 65 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | C3 | 174.7736 | 174.7736 | 174.7736 | 8850.7987 | 30324.8675 | C3 | 2796.3775 | 6990.9438 | 1048.6416 | 26552.396 | 0 | 37388.3589 |  | 2796.3775 | 7340.491 | 1048.6416 | 8850.7987 | 0 | 20036.3087 |  | 2796.3775 | 5942.3022 | 2097.2831 | 17701.5973 | 30324.8675 | 58862.4278 |  | 2971.1511 | 6291.8494 | 2097.2831 | 0 | 0 | 11360.2837 |  | 2446.8303 | 5767.5286 | 2446.8303 | 26552.396 | 30324.8675 | 67538.4528 |  | 2621.6039 | 6291.8494 | 2446.8303 | 0 | 0 | 11360.2837
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | C4 | 291.2893 | 291.2893 | 291.2893 | 14751.3311 | 50541.4459 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 3 | 11 | 0 | -11 | -3 |  | 112 | 270 | 87 | 17 | 3 |  | 9 | 20 | 0 | -20 | -9 |  | 99 | 278 | 83 | 20 | 9 | [22 empty] | 13014.807 | 32274.8572 | 8901.8018 | 98538.8917 | 121299.4702 | 274029.8279 |  | 13713.9014 | 32612.7528 | 8703.725 | 69036.2295 | 0 | 124066.6088 |  | 13038.1102 | 30993.1842 | 10136.8685 | 95588.6255 | 58628.0772 | 208384.8656 |  | 13376.0058 | 32391.3729 | 10136.8685 | 24782.2362 | 0 | 80686.4835 |  | 11406.89 | 31902.0069 | 9857.2308 | 114470.3293 | 167797.6004 | 335434.0573 |  | 12373.9705 | 34162.412 | 9857.2308 | 0 | 0 | 56393.6133
| EHV OHL Support - Poles |  | 4894 | 4894 | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 362 | 0 | -50 | -72 | -240 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 739 | 0 | -104 | -147 | -488 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | C1 | 112.0045 | 112.0045 | 155.8627 | 383.4538 | 803.4269 | C1 | 52418.1032 | 343181.7696 | 38653.9565 | 233906.7954 | 405730.6007 | 1073891.2254 |  | 66194.656 | 343181.7696 | 37718.7802 | 226621.1739 | 326191.3344 | 999907.7141 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 82435.3076 | 343181.7696 | 31016.6829 | 209749.2084 | 279592.5723 | 945975.5408 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472 |  | 99347.9862 | 343181.7696 | 23846.9974 | 192493.789 | 231386.9564 | 890257.4986
|  |  | 22777 | 22777 | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 1685 | 0 | -237 | -337 | -1111 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 3440 | 0 | -482 | -687 | -2271 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12481 | 12481 | 12481 | 12481 | 12481 | C2 | 160.0064 | 160.0064 | 222.661 | 547.7911 | 1147.7528 | C2 | 348493.9828 | 2281851.5556 | 257396.1622 | 1552439.9491 | 2698366.7388 | 7138548.3884 |  | 440337.6678 | 2281851.5556 | 250938.9921 | 1505329.9153 | 2168104.9636 | 6646563.0945 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 548181.9949 | 2281851.5556 | 205738.801 | 1394676.1151 | 1859359.4712 | 6289807.9378 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714 |  | 660506.5018 | 2281851.5556 | 158979.9826 | 1279092.1951 | 1536840.9456 | 5917271.1807
|  |  | 1936 | 1936 | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 143 | 0 | -20 | -29 | -94 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 293 | 0 | -41 | -59 | -193 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | C3 | 240.0096 | 240.0096 | 333.9916 | 821.6866 | 1721.6291 | C3 | 44401.7815 | 290891.6716 | 33065.1644 | 197204.7924 | 344325.828 | 909889.2379 |  | 56162.2534 | 290891.6716 | 32063.1898 | 191452.986 | 277182.2915 | 847752.3922 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 69842.8023 | 290891.6716 | 26385.3332 | 177484.3132 | 237584.8213 | 802188.9416 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804 |  | 84243.3801 | 290891.6716 | 20373.4852 | 162693.9537 | 196265.722 | 754468.2125
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | C4 | 400.0161 | 400.0161 | 556.6526 | 1369.4777 | 2869.3819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29607 | 29607 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 2190 | 0 | -307 | -438 | -1445 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 4472 | 0 | -627 | -893 | -2952 |  | 894 | 18537 | 1555 | 3928 | 4693 | [22 empty] | 445313.8675 | 2915924.9968 | 329115.2832 | 1983551.5369 | 3448423.1674 | 9122328.8518 |  | 562694.5772 | 2915924.9968 | 320720.962 | 1923404.0752 | 2771478.5896 | 8494223.2008 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 700460.1048 | 2915924.9968 | 263140.8171 | 1781909.6367 | 2376536.8649 | 8037972.4202 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416 |  | 844097.8681 | 2915924.9968 | 203200.4651 | 1634279.9379 | 1964493.624 | 7561996.8919
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 427 | 427 | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 17 | 0 | 0 | -12 | -5 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 137 | 0 | 0 | 0 | -137 | 0 | 0 | 290 | 0 | 0 | 137 | 427 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | C1 | 238.7737 | 238.7737 | 332.7056 | 818.1404 | 1714.4379 | C1 | 71632.0962 | 0 | 43917.1434 | 0 | 8572.1893 | 124121.4289 |  | 69244.3597 | 0 | 43917.1434 | 0 | 8572.1893 | 121733.6924 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 4059.1521 | 69244.3597 | 0 | 98176.843 | 0 | 171480.3547 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462 |  | 32711.9906 | 69244.3597 | 0 | 0 | 0 | 101956.3503
|  |  | 456 | 456 | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 102434 | 102434 | 102434 | 102434 | 102434 | C2 | 341.1052 | 341.1052 | 475.2938 | 1168.7719 | 2449.1969 | C2 | 99943.8295 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 431151.8764 |  | 96873.8825 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 428081.9294 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 98579.4086 | 56964.5717 | 0 | 0 | 0 | 155543.9803 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 98579.4086 | 56964.5717 | 0 | 0 | 0 | 155543.9803
|  |  | 55 | 55 | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 153651 | 153651 | 153651 | 153651 | 153651 | C3 | 511.6578 | 511.6578 | 712.9406 | 1753.1579 | 3673.7954 | C3 | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 27629.5228 | 511.6578 | 0 | 0 | 0 | 28141.1806 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 27629.5228 | 511.6578 | 0 | 0 | 0 | 28141.1806
|  |  | 87 | 87 | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 34 | 0 | 0 | 0 | -34 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 56 | 0 | 0 | 0 | -56 | 0 | 0 | 31 | 0 | 0 | 56 | 87 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 256085 | 256085 | 256085 | 256085 | 256085 | C4 | 852.7631 | 852.7631 | 1188.2344 | 2921.9298 | 6122.9924 | C4 | 27288.4176 | 0 | 26141.1568 | 99345.6149 | 0 | 152775.1893 |  | 26435.6545 | 0 | 26141.1568 | 99345.6149 | 0 | 151922.4263 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 28993.9437 | 26435.6545 | 11882.344 | 35063.1582 | 0 | 102375.1004 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262 |  | 47754.7308 | 26435.6545 | 0 | 0 | 0 | 74190.3853
|  |  | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 277 | 0 | 0 | -12 | -265 |  | 117 | 489 | 10 | 144 | 265 |  | 419 | 0 | 0 | 0 | -419 |  | 117 | 489 | 0 | 0 | 419 | [22 empty] | 199376.0011 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 906945.1046 |  | 193065.5545 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 900634.658 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 159262.0272 | 153156.2438 | 11882.344 | 133240.0012 | 0 | 457540.6162 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385 |  | 206675.6528 | 153156.2438 | 0 | 0 | 0 | 359831.8966
| EHV OHL Conductor (Tower Lines) |  | 40.481 | 40.481 | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | C1 | 5.8423 | 5.8423 | 8.0332 | 20.4481 | 43.0871 | C1 | 236.5143 | 0 | 3.7515 | 0 | 0 | 240.2658 |  | 233.8035 | 0 | 3.7113 | 0 | 0 | 237.5148 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505
|  |  | 52.696 | 52.696 | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 104327 | 104327 | 104327 | 104327 | 104327 | C2 | 8.3462 | 8.3462 | 11.476 | 29.2116 | 61.5529 | C2 | 232.0232 | 0 | 292.729 | 0 | 0 | 524.7523 |  | 229.3608 | 0 | 289.3666 | 0 | 0 | 518.7274 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996
|  |  | 6.374 | 6.374 | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | C3 | 12.5192 | 12.5192 | 17.214 | 43.8173 | 92.3294 | C3 | 1.6275 | 0 | 108.7406 | 0 | 0 | 110.3681 |  | 1.615 | 0 | 107.5011 | 0 | 0 | 109.1161 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543
|  |  | 8.199 | 8.199 | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | C4 | 20.8654 | 20.8654 | 28.6899 | 73.0289 | 153.8823 | C4 | 106.6639 | 66.4146 | 0 | 0 | 0 | 173.0785 |  | 105.4329 | 65.6425 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914
|  |  | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0 | [22 empty] | 576.829 | 66.4146 | 405.2211 | 0 | 0 | 1048.4646 |  | 570.2122 | 65.6425 | 400.5791 | 0 | 0 | 1036.4338 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 |  | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 |  | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 |  | 2903985.8729 | 3635880.177 | 2142208.7963 | 3903704.0658 | 6252659.0159 | 18838437.9279 |  | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 |  | 3184008.3905 | 3801648.5614 | 1780816.0837 | 3142388.1185 | 4189047.6514 | 16097908.8056
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 72 | 72 | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 4 | 0 | 0 | 0 | -4 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 7 | 0 | 0 | -1 | -6 | 0 | 34 | 19 | 9 | 4 | 6 | 72 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | C1 | 2255.4713 | 2255.4713 | 3138.659 | 7721.7345 | 16178.8722 | C1 | 110518.0945 | 11277.3566 | 37663.9079 | 30886.9379 | 32357.7445 | 222704.0414 |  | 112773.5658 | 11277.3566 | 37663.9079 | 30886.9379 | 16178.8722 | 208780.6405 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 115029.0371 | 18043.7705 | 34525.2489 | 7721.7345 | 16178.8722 | 191498.6633 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821 |  | 92474.324 | 42853.955 | 28247.9309 | 23165.2034 | 0 | 186741.4133
|  |  | 61 | 61 | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 1 | 0 | 0 | 0 | -1 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 6 | 0 | 0 | -1 | -5 | 0 | 35 | 16 | 2 | 3 | 5 | 61 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 251334 | 251334 | 251334 | 251334 | 251334 | C2 | 3222.1019 | 3222.1019 | 4483.7986 | 11031.0493 | 23112.6746 | C2 | 112773.5658 | 9666.3056 | 35870.3885 | 22062.0985 | 46225.3493 | 226597.7077 |  | 154660.8902 | 9666.3056 | 35870.3885 | 22062.0985 | 0 | 222259.6829 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 141772.4827 | 25776.815 | 17935.1942 | 44124.197 | 23112.6746 | 252721.3637 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314 |  | 132106.1771 | 51553.6301 | 8967.5971 | 22062.0985 | 0 | 214689.5028
|  |  | 26 | 26 | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 5 | 0 | 0 | -2 | -3 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 9 | 0 | 0 | 0 | -9 | 0 | 11 | 5 | 1 | 0 | 9 | 26 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 377001 | 377001 | 377001 | 377001 | 377001 | C3 | 4833.1528 | 4833.1528 | 6725.6978 | 16546.5739 | 34669.012 | C3 | 67664.1395 | 9666.3056 | 20177.0935 | 82732.8694 | 69338.0239 | 249578.432 |  | 72497.2923 | 9666.3056 | 20177.0935 | 82732.8694 | 34669.012 | 219742.5729 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 86996.7508 | 19332.6113 | 0 | 16546.5739 | 104007.0359 | 226882.9718 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506 |  | 96663.0564 | 24165.7641 | 6725.6978 | 0 | 0 | 127554.5183
|  |  | 7 | 7 | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 628335 | 628335 | 628335 | 628335 | 628335 | C4 | 8055.2547 | 8055.2547 | 11209.4964 | 27577.6231 | 57781.6866 | C4 | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829
|  |  | 166 | 166 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 10 | 0 | 0 | -2 | -8 |  | 107 | 23 | 15 | 8 | 13 |  | 22 | 0 | 0 | -2 | -20 |  | 82 | 45 | 12 | 7 | 20 | [22 empty] | 347342.5827 | 30609.9679 | 93711.3899 | 135681.9059 | 147921.1177 | 755266.964 |  | 396318.5312 | 30609.9679 | 93711.3899 | 135681.9059 | 50847.8842 | 707169.6791 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 376019.2894 | 87318.9609 | 52460.4432 | 68392.5054 | 143298.5828 | 727489.7817 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296 |  | 337354.0668 | 158849.6227 | 43941.2259 | 45227.302 | 0 | 585372.2174
| 132kV Transformer |  | 27 | 27 | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 4 | 8 | 2 | 1 | 27 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | C1 | 21313.7705 | 21313.7705 | 29659.7243 | 72968.9069 | 152887.2336 | C1 | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 298392.7869 | 85255.082 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697 |  | 277079.0164 | 85255.082 | 237277.7944 | 145937.8139 | 0 | 745549.7067
|  |  | 48 | 48 | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 1 | 0 | 0 | -1 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 6 | 0 | 0 | -3 | -3 | 0 | 16 | 5 | 14 | 9 | 4 | 48 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2375058 | 2375058 | 2375058 | 2375058 | 2375058 | C2 | 30448.2436 | 30448.2436 | 42371.0347 | 104241.2956 | 218410.3337 | C2 | 548068.3841 | 213137.7049 | 720307.5902 | 521206.4781 | 0 | 2002720.1573 |  | 608964.8712 | 213137.7049 | 720307.5902 | 416965.1825 | 0 | 1959375.3488 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 608964.8712 | 152241.2178 | 762678.625 | 416965.1825 | 218410.3337 | 2159260.2301 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961 |  | 669861.3583 | 152241.2178 | 593194.4861 | 625447.7737 | 218410.3337 | 2259155.1696
|  |  | 13 | 13 | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 1 | 0 | 0 | -1 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 3 | 0 | 0 | -1 | -2 | 0 | 4 | 3 | 2 | 2 | 2 | 13 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3562587 | 3562587 | 3562587 | 3562587 | 3562587 | C3 | 45672.3653 | 45672.3653 | 63556.5521 | 156361.9434 | 327615.5005 | C3 | 182689.4614 | 91344.7307 | 254226.2083 | 469085.8303 | 0 | 997346.2307 |  | 228361.8267 | 91344.7307 | 254226.2083 | 312723.8869 | 0 | 886656.6526 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 274034.192 | 91344.7307 | 190669.6562 | 312723.8869 | 0 | 868772.4658 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494 |  | 319706.5574 | 137017.096 | 127113.1042 | 156361.9434 | 0 | 740198.701
|  |  | 6 | 6 | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 2 | 0 | 0 | -1 | -1 | 0 | 0 | 1 | 2 | 2 | 1 | 6 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5937645 | 5937645 | 5937645 | 5937645 | 5937645 | C4 | 76120.6089 | 76120.6089 | 105927.5868 | 260603.2391 | 546025.8342 | C4 | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 76120.6089 | 76120.6089 | 317782.7604 | 260603.2391 | 0 | 730627.2172 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948 |  | 152241.2178 | 76120.6089 | 211855.1736 | 260603.2391 | 0 | 700820.2393
|  |  | 94 | 94 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 4 | 0 | -1 | -2 | -1 |  | 37 | 12 | 33 | 10 | 2 |  | 12 | 0 | 0 | -5 | -7 |  | 32 | 13 | 26 | 15 | 8 | [22 empty] | 1147898.7822 | 499351.1944 | 1529594.3534 | 1063261.2153 | 0 | 4240105.5453 |  | 1254467.6347 | 499351.1944 | 1529594.3534 | 802657.9763 | 0 | 4086071.1587 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 1257512.459 | 404961.6393 | 1508408.836 | 1063261.2153 | 218410.3337 | 4452554.4834 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101 |  | 1418888.1499 | 450634.0047 | 1169440.5583 | 1188350.7701 | 218410.3337 | 4445723.8166
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 24.121 | 24.121 | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | C1 | 687.9878 | 687.9878 | 23328.0975 | 56942.5365 | 119312.7891 | C1 | 2223.5767 | 11940.7168 | 82418.1684 | 168208.2529 | 0 | 264790.7147 |  | 2223.5767 | 11940.7168 | 82418.1684 | 0 | 0 | 96582.4619 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285
|  |  | 11.91 | 11.91 | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 164906 | 164906 | 164906 | 164906 | 164906 | C2 | 982.8398 | 982.8398 | 33325.8535 | 81346.4807 | 170446.8416 | C2 | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244
|  |  | 25.639 | 25.639 | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0.2 | 0 | 0 | 0 | -0.2 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0.4 | 0 | 0 | 0 | -0.4 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 247359 | 247359 | 247359 | 247359 | 247359 | C3 | 1474.2596 | 1474.2596 | 49988.7803 | 122019.7211 | 255670.2624 | C3 | 11561.1441 | 25647.695 | 0 | 78824.7398 | 0 | 116033.5789 |  | 11561.1441 | 25647.695 | 0 | 48807.8884 | 0 | 86016.7275 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 11855.996 | 931.7321 | 838061.9019 | 0 | 51134.0525 | 901983.6825 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308 |  | 8033.2408 | 4211.9598 | 866455.5291 | 0 | 0 | 878700.7297
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 412265 | 412265 | 412265 | 412265 | 412265 | C4 | 2457.0994 | 2457.0994 | 83314.6338 | 203366.2019 | 426117.104 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 61.67 | 61.67 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0.2 | 0 | 0 | 0 | -0.2 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0.4 | 0 | 0 | 0 | -0.4 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4 | [22 empty] | 15226.5467 | 47852.2074 | 82418.1684 | 247032.9927 | 0 | 392529.9152 |  | 15226.5467 | 47852.2074 | 82418.1684 | 48807.8884 | 0 | 194304.8109 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 14185.5228 | 18383.9194 | 1126917.07 | 0 | 51134.0525 | 1210620.5648 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837 |  | 8143.3188 | 12880.9013 | 1528386.9625 | 0 | 0 | 1549411.1826
| 132kV UG Cable (Non Pressurised) |  | 7.356 | 7.356 | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.671 | 9.671 | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 1610892 | 1610892 | 1610892 | 1610892 | 1610892 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2.775 | 2.775 | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 2416338 | 2416338 | 2416338 | 2416338 | 2416338 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.253 | 0.253 | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 4027230 | 4027230 | 4027230 | 4027230 | 4027230 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20.055 | 20.055 |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1148 | 1148 | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 1 | 17 | 0 | -17 | -1 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 3 | 43 | 0 | -43 | -3 | 0 | 267 | 705 | 125 | 48 | 3 | 1148 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | C1 | 293.7956 | 293.7956 | 293.7956 | 14878.2548 | 50976.3155 | C1 | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 87551.1013 | 198605.854 | 37605.8422 | 669521.4649 | 50976.3155 | 1044260.5779 |  | 87844.897 | 203600.3799 | 37605.8422 | 416591.1337 | 0 | 745642.2528 |  | 78443.4364 | 207125.9276 | 36724.4552 | 714156.2292 | 152928.9466 | 1189378.9952 |  | 79324.8233 | 219759.1402 | 36724.4552 | 74391.2739 | 0 | 410199.6927
|  |  | 1252 | 1252 | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 4 | 37 | 0 | -37 | -4 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 12 | 69 | 0 | -69 | -12 | 0 | 294 | 743 | 132 | 71 | 12 | 1252 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 791902 | 791902 | 791902 | 791902 | 791902 | C2 | 419.7081 | 419.7081 | 419.7081 | 21254.6497 | 72823.3079 | C2 | 125912.418 | 320237.2498 | 53302.9236 | 1254024.3311 | 218469.9238 | 1971946.8463 |  | 127171.5422 | 320237.2498 | 53302.9236 | 1254024.3311 | 0 | 1754736.0467 |  | 125073.0019 | 316879.5853 | 52463.5075 | 1487825.4776 | 291293.2317 | 2273534.804 |  | 126751.8341 | 332408.7835 | 52463.5075 | 701403.4394 | 0 | 1213027.5646 |  | 123394.1696 | 311843.0886 | 55401.4639 | 1509080.1273 | 873879.695 | 2873598.5445 |  | 128430.6664 | 340802.9447 | 55401.4639 | 42509.2994 | 0 | 567144.3744
|  |  | 501 | 501 | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 9 | 0 | -9 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 2 | 12 | 0 | -12 | -2 | 0 | 35 | 349 | 101 | 14 | 2 | 501 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1187853 | 1187853 | 1187853 | 1187853 | 1187853 | C3 | 629.5621 | 629.5621 | 629.5621 | 31881.9745 | 109234.9619 | C3 | 28330.2941 | 230419.7249 | 28330.2941 | 1434688.8534 | 0 | 1721769.1664 |  | 28330.2941 | 249306.5876 | 28330.2941 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 236085.7838 | 50994.5293 | 191291.8471 | 0 | 502925.0817 |  | 22034.6731 | 219717.1694 | 63585.7711 | 446347.6433 | 218469.9238 | 970155.1807 |  | 23293.7973 | 227271.9145 | 63585.7711 | 63763.949 | 0 | 377915.4319
|  |  | 187 | 187 | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 1979755 | 1979755 | 1979755 | 1979755 | 1979755 | C4 | 1049.2702 | 1049.2702 | 1049.2702 | 53136.6242 | 182058.2698 | C4 | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181
|  |  | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 5 | 63 | 0 | -63 | -5 |  | 698 | 1901 | 354 | 130 | 5 |  | 17 | 124 | 0 | -124 | -17 |  | 656 | 1891 | 391 | 133 | 17 | [22 empty] | 323720.8267 | 862122.326 | 122428.8411 | 3283843.3756 | 218469.9238 | 4810585.2931 |  | 324979.9509 | 881009.1887 | 122428.8411 | 2327384.14 | 0 | 3655802.1207 |  | 303281.0442 | 855029.2598 | 162049.282 | 2635576.5603 | 342269.5472 | 4298205.6935 |  | 305253.672 | 881219.0428 | 162049.282 | 1309286.4203 | 0 | 2657808.4171 |  | 286828.4882 | 837317.5797 | 190337.6052 | 2669583.9998 | 1245278.5654 | 5229346.2384 |  | 294005.496 | 886465.3935 | 190337.6052 | 180664.5223 | 0 | 1551473.017
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1974 | 1974 | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 258 | 0 | 0 | -256 | -2 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 459 | 0 | 0 | 0 | -459 | 0 | 873 | 153 | 489 | 0 | 459 | 1974 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | C1 | 24.2662 | 24.2662 | 33.366 | 78.8651 | 166.8301 | C1 | 16234.0878 | 15239.1736 | 14013.7305 | 3785.5272 | 34867.4961 | 84140.0152 |  | 21378.5222 | 15239.1736 | 14013.7305 | 3548.9318 | 0 | 54180.3581 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 27639.2018 | 4853.24 | 15181.5414 | 11435.4467 | 5839.0544 | 64948.4843 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348 |  | 32322.5784 | 3712.7286 | 16315.9862 | 0 | 0 | 52351.2932
|  |  | 1409 | 1409 | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 146 | 0 | 0 | -146 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 264 | 0 | 0 | 0 | -264 | 0 | 816 | 99 | 230 | 0 | 264 | 1409 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 433325 | 433325 | 433325 | 433325 | 433325 | C2 | 34.666 | 34.666 | 47.6658 | 112.6645 | 238.3288 | C2 | 26727.486 | 10607.796 | 11678.1088 | 4619.2445 | 10963.1225 | 64595.7578 |  | 28426.12 | 10607.796 | 11678.1088 | 4281.251 | 0 | 54993.2758 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 33487.356 | 3605.264 | 12440.7608 | 8787.831 | 0 | 58321.2118 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025 |  | 37439.28 | 3431.934 | 10963.1225 | 0 | 0 | 51834.3365
|  |  | 945 | 945 | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 68 | 0 | 0 | -68 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 175 | 0 | 0 | 0 | -175 | 0 | 507 | 32 | 231 | 0 | 175 | 945 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | C3 | 51.999 | 51.999 | 71.4986 | 168.9967 | 357.4931 | C3 | 24543.528 | 13623.738 | 11940.2704 | 1520.9707 | 12512.2594 | 64140.7665 |  | 26363.493 | 13623.738 | 11940.2704 | 1520.9707 | 0 | 53448.4721 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 29899.425 | 1715.967 | 18232.1494 | 13688.7368 | 357.4931 | 63893.7712 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402 |  | 35463.318 | 1663.968 | 16516.1824 | 0 | 0 | 53643.4684
|  |  | 436 | 436 | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 4 | 0 | 0 | -4 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 26 | 0 | 0 | 0 | -26 | 0 | 313 | 8 | 89 | 0 | 26 | 436 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | C4 | 86.665 | 86.665 | 119.1644 | 281.6612 | 595.8219 | C4 | 26779.485 | 8406.505 | 3098.2738 | 0 | 2383.2875 | 40667.5513 |  | 27126.145 | 8406.505 | 3098.2738 | 0 | 0 | 38630.9238 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27472.805 | 953.315 | 10963.1225 | 4506.58 | 0 | 43895.8225 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631 |  | 29379.435 | 693.32 | 10605.6294 | 0 | 0 | 40678.3844
|  |  | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 476 | 0 | 0 | -474 | -2 |  | 2521 | 348 | 1063 | 794 | 38 |  | 924 | 0 | 0 | 0 | -924 |  | 2509 | 292 | 1039 | 0 | 924 | [22 empty] | 94284.5868 | 47877.2126 | 40730.3834 | 9925.7424 | 60726.1655 | 253544.0907 |  | 103294.2802 | 47877.2126 | 40730.3834 | 9351.1535 | 0 | 201253.0297 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 118498.7878 | 11127.786 | 56817.574 | 38418.5945 | 6196.5475 | 231059.2898 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407 |  | 134604.6114 | 9501.9506 | 54400.9205 | 0 | 0 | 198507.4825
| 132kV OHL Conductor (Tower Lines) |  | 582.743 | 582.743 | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 40.805 | 0 | 0 | -32.346 | -8.459 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 66.899 | 0 | 0 | 0 | -66.899 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | C1 | 24.2866 | 24.2866 | 33.3941 | 85.003 | 179.1136 | C1 | 1808.5248 | 3592.0586 | 11976.176 | 286.1202 | 0 | 17662.8797 |  | 1802.8417 | 3580.7897 | 11945.2531 | 286.1202 | 0 | 17615.0047 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 2315.5801 | 2003.6675 | 12649.8009 | 2218.0694 | 0 | 19187.1178 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952 |  | 1878.203 | 2781.5425 | 11214.4243 | 4680.0126 | 0 | 20554.1823
|  |  | 372.373 | 372.373 | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 1.495 | 0 | 0 | -1.495 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 27.981 | 0 | 0 | 0 | -27.981 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 433689 | 433689 | 433689 | 433689 | 433689 | C2 | 34.6951 | 34.6951 | 47.7058 | 121.4329 | 255.8765 | C2 | 5409.4549 | 2529.3783 | 6900.1655 | 0 | 0 | 14838.9987 |  | 5392.489 | 2521.4332 | 6882.7051 | 0 | 0 | 14796.6273 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 5427.3576 | 752.8147 | 8003.0756 | 3216.2723 | 0 | 17399.5203 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577 |  | 1484.7777 | 5287.224 | 7678.2946 | 1971.5849 | 0 | 16421.8812
|  |  | 282.328 | 282.327 | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 3.72 | 0 | 0 | -2.99 | -0.731 | -0.001 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | C3 | 52.0427 | 52.0427 | 71.5587 | 182.1494 | 383.8148 | C3 | 1710.2786 | 5623.4197 | 10181.9422 | 0 | 0 | 17515.6405 |  | 1704.9182 | 5605.7773 | 10150.8141 | 0 | 0 | 17461.5096 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106 |  | 240.0729 | 4270.206 | 12569.4261 | 3644.8091 | 0 | 20724.5141
|  |  | 131.686 | 131.686 | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | C4 | 86.7378 | 86.7378 | 119.2645 | 303.5823 | 639.6913 | C4 | 8338.7119 | 1881.6031 | 1702.0233 | 0 | 0 | 11922.3383 |  | 8312.5171 | 1875.7049 | 1696.6564 | 0 | 0 | 11884.8784 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792
|  |  | 1369.13 | 1369.129 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 42.3 | 0 | 0 | -33.841 | -8.459 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 98.6 | 0 | 0 | -2.99 | -95.611 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611 | [22 empty] | 17266.9702 | 13626.4598 | 30760.307 | 286.1202 | 0 | 61939.8572 |  | 17212.766 | 13583.705 | 30675.4288 | 286.1202 | 0 | 61758.0201 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 16442.3574 | 9550.151 | 34183.6935 | 8169.8611 | 0 | 68346.063 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994 |  | 7283.4251 | 17592.4208 | 34883.6043 | 10296.4066 | 0 | 70055.8568
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 |  | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 |  | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 |  | 2087912.0885 | 1412561.4995 | 2940836.8987 | 2487528.5967 | 419039.5164 | 9347878.5998 |  | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 |  | 2200279.0681 | 1535924.2936 | 3021390.8766 | 1424539.0009 | 218410.3337 | 8400543.5729
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 519588.883 | 519108.482 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 35787.5 | -97 | -5197 | -7994.041 | -22740.659 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 73030 | -40 | -10734 | -14871.99 | -47864.411 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 |  | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 |  | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 |  | 15585086.3647 | 29015185.7441 | 10939385.6533 | 19576658.766 | 14079504.0544 | 89195820.5825 |  | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 |  | 16897294.2495 | 29344058.5132 | 9823924.4302 | 17510210.3258 | 9415959.2372 | 82991446.7559
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 | LV Network | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 2559590.7243 | 9023619.0942 | 1667511.7844 | 5739824.2208 | 2605967.0121 | 21596512.8358 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 | LV Network | 2791609.0763 | 9009827.4584 | 1414072.7742 | 5855081.8501 | 2105420.606 | 21176011.765
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 | HV Network | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 8033597.6789 | 14943124.9734 | 4188828.1739 | 7445601.8828 | 4801838.51 | 39412991.219 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 | HV Network | 8721397.7146 | 14996658.1998 | 3607644.6956 | 7088201.3562 | 2903080.6461 | 37316982.6123
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 | EHV Network | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 | EHV Network | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 | EHV Network | 2903985.8729 | 3635880.177 | 2142208.7963 | 3903704.0658 | 6252659.0159 | 18838437.9279 | EHV Network | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 | EHV Network | 3184008.3905 | 3801648.5614 | 1780816.0837 | 3142388.1185 | 4189047.6514 | 16097908.8056
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 | 132kV Network | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 | 132kV Network | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 | 132kV Network | 2087912.0885 | 1412561.4995 | 2940836.8987 | 2487528.5967 | 419039.5164 | 9347878.5998 | 132kV Network | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 | 132kV Network | 2200279.0681 | 1535924.2936 | 3021390.8766 | 1424539.0009 | 218410.3337 | 8400543.5729
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 | Total | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 | Total | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 | Total | 15585086.3647 | 29015185.7441 | 10939385.6533 | 19576658.766 | 14079504.0544 | 89195820.5825 | Total | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 | Total | 16897294.2495 | 29344058.5132 | 9823924.4302 | 17510210.3258 | 9415959.2372 | 82991446.7559
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWEST - Asset Rep
Secondary deliverables RIIO-ED1 - Asset Replacement | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWEST | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | C1 | 43.7303 | 43.7303 | 60.854 | 149.7132 | 313.6848 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 14161 | 0 | -2266 | -3115 | -8780 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 28834 | 0 | -4614 | -6343 | -17877 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4873 | 4873 | 4873 | 4873 | 4873 | C2 | 62.4719 | 62.4719 | 86.9343 | 213.876 | 448.1211 | C2 | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 1742027.8161 | 8563580.0969 | 208729.3023 | 5454051.111 | 2542190.8868 | 18510579.2132 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 2017028.9438 | 8563580.0969 | 93889.0656 | 5171520.9546 | 1753497.786 | 17599516.847
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | C3 | 93.7078 | 93.7078 | 130.4015 | 320.814 | 672.1816 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | C4 | 156.1797 | 156.1797 | 217.3358 | 534.6899 | 1120.3027 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 14161 | 0 | -2266 | -3115 | -8780 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 28834 | 0 | -4614 | -6343 | -17877 |  | 3453 | 137079 | 5694 | 30523 | 21790 | [22 empty] | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 1742027.8161 | 8563580.0969 | 208729.3023 | 5454051.111 | 2542190.8868 | 18510579.2132 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 2017028.9438 | 8563580.0969 | 93889.0656 | 5171520.9546 | 1753497.786 | 17599516.847
| LV Switchgear (at s/s) |  | 857 | 857 | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 5 | 0 | 0 | 0 | -5 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 7 | 0 | 0 | 0 | -7 | 0 | 586 | 148 | 93 | 10 | 20 | 857 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | C1 | 76.19 | 76.19 | 105.9604 | 260.7189 | 546.2926 | C1 | 49066.3613 | 8304.7102 | 7629.1483 | 1564.3131 | 7648.0967 | 74212.6296 |  | 51733.0114 | 8228.5202 | 5721.8612 | 1564.3131 | 5462.9262 | 72710.6321 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 48380.6513 | 10818.9803 | 6463.584 | 2346.4697 | 5462.9262 | 73472.6115 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819 |  | 45180.6712 | 11276.1203 | 9854.3165 | 2607.1886 | 7101.8041 | 76020.1007
|  |  | 11264 | 11264 | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 474 | -25 | -59 | -92 | -298 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 954 | -56 | -82 | -122 | -694 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5663 | 5663 | 5663 | 5663 | 5663 | C2 | 108.8429 | 108.8429 | 151.372 | 372.4555 | 780.418 | C2 | 548568.0144 | 212352.4199 | 536916.4485 | 90134.2334 | 263000.8761 | 1650971.9923 |  | 610608.4446 | 209849.0341 | 515572.9979 | 87527.0448 | 66335.5325 | 1489893.054 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 543670.0857 | 256216.0924 | 548420.7198 | 84919.8563 | 49946.7539 | 1483173.5081 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721 |  | 515479.785 | 293549.1934 | 507550.2825 | 131104.3395 | 98332.6718 | 1546016.2721
|  |  | 107 | 107 | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 17 | 0 | -1 | -1 | -15 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 32 | 0 | -2 | -6 | -24 | 0 | 16 | 16 | 35 | 16 | 24 | 107 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | C3 | 163.2643 | 163.2643 | 227.058 | 558.6833 | 1170.627 | C3 | 1959.1715 | 2612.2286 | 13396.4211 | 6704.1992 | 9365.0164 | 34037.0368 |  | 3265.2858 | 2612.2286 | 12942.3051 | 6704.1992 | 2341.2541 | 27865.2729 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 5714.2502 | 2448.9644 | 11807.0152 | 2793.4163 | 0 | 22763.646 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681 |  | 7836.6859 | 2612.2286 | 7492.9135 | 5586.8327 | 0 | 23528.6607
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | C4 | 272.1071 | 272.1071 | 378.43 | 931.1388 | 1951.0451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12228 | 12228 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 496 | -25 | -60 | -93 | -318 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 993 | -56 | -84 | -128 | -725 |  | 4384 | 2917 | 3563 | 500 | 864 | [22 empty] | 599593.5472 | 223269.3587 | 557942.0179 | 98402.7457 | 280013.9892 | 1759221.6587 |  | 665606.7418 | 220689.7829 | 534237.1643 | 95795.5572 | 74139.7128 | 1590468.959 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 597764.9871 | 269484.0371 | 566691.319 | 90059.7423 | 55409.6801 | 1579409.7656 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592 |  | 568497.1421 | 307437.5424 | 524897.5125 | 139298.3607 | 105434.4759 | 1645565.0335
| LV UGB and LV Pillar OD (not at s/s) |  | 180 | 180 | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 1 | 0 | 0 | 0 | -1 | 0 | 179 | 0 | 0 | 0 | 1 | 180 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3269 | 3269 | 3269 | 3269 | 3269 | C1 | 62.8302 | 62.8302 | 87.3804 | 215.0021 | 450.5009 | C1 | 10618.3004 | 0 | 87.3804 | 0 | 0 | 10705.6808 |  | 11246.6022 | 0 | 87.3804 | 0 | 0 | 11333.9826 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031 |  | 11309.4324 | 0 | 0 | 0 | 0 | 11309.4324
|  |  | 11974 | 11974 | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 348 | 0 | 0 | -115 | -233 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 703 | 0 | 0 | 0 | -703 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 4670 | 4670 | 4670 | 4670 | 4670 | C2 | 89.7574 | 89.7574 | 124.8291 | 307.1459 | 643.5727 | C2 | 196927.7356 | 226727.1924 | 865065.663 | 921.4377 | 231686.172 | 1521328.2007 |  | 205364.9312 | 226727.1924 | 865065.663 | 921.4377 | 146091.0029 | 1444170.2272 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 204377.5998 | 188400.7826 | 868685.7069 | 192273.3334 | 8366.4451 | 1462103.8678 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959 |  | 189657.3862 | 137598.0942 | 773940.42 | 535969.5955 | 246488.3441 | 1883653.84
|  |  | 179 | 179 | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 16 | 0 | 0 | 0 | -16 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 24 | 0 | 0 | 0 | -24 | 0 | 14 | 9 | 114 | 18 | 24 | 179 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7005 | 7005 | 7005 | 7005 | 7005 | C3 | 134.6361 | 134.6361 | 187.2437 | 460.7188 | 965.359 | C3 | 942.4527 | 3904.4469 | 21720.2634 | 7371.5016 | 965.359 | 34904.0237 |  | 2423.4498 | 3904.4469 | 21720.2634 | 7371.5016 | 0 | 35419.6617 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 4173.7191 | 2154.1776 | 23405.4562 | 3225.0319 | 0 | 32958.3849 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629 |  | 5116.1718 | 1211.7249 | 21345.7761 | 8292.9393 | 0 | 35966.6121
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 11675 | 11675 | 11675 | 11675 | 11675 | C4 | 224.3935 | 224.3935 | 312.0727 | 767.8647 | 1608.9317 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12333 | 12333 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 364 | 0 | 0 | -115 | -249 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 728 | 0 | 0 | 0 | -728 |  | 1603 | 1542 | 6314 | 1763 | 1111 | [22 empty] | 208488.4887 | 230631.6393 | 886873.3068 | 8292.9393 | 232651.531 | 1566937.9051 |  | 219034.9832 | 230631.6393 | 886873.3068 | 8292.9393 | 146091.0029 | 1490923.8715 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 219797.9211 | 190554.9602 | 892091.1632 | 195713.3675 | 8366.4451 | 1506523.857 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619 |  | 206082.9904 | 138809.8191 | 795286.1961 | 544262.5348 | 246488.3441 | 1930929.8845
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 |  | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 2559590.7243 | 9023619.0942 | 1667511.7844 | 5739824.2208 | 2605967.0121 | 21596512.8358 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 |  | 2791609.0763 | 9009827.4584 | 1414072.7742 | 5855081.8501 | 2105420.606 | 21176011.765
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 700 | 700 | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 62 | 0 | -21 | -9 | -32 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 127 | 0 | -28 | -5 | -94 | 0 | 247 | 98 | 163 | 72 | 120 | 700 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | C1 | 564.9671 | 564.9671 | 786.1945 | 1934.1972 | 4052.6036 | C1 | 169490.1432 | 35592.9301 | 193403.8539 | 96709.8594 | 158051.5416 | 653248.3282 |  | 176834.7161 | 35592.9301 | 192617.6594 | 94775.6622 | 121578.109 | 621399.0767 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 198303.4675 | 34462.9958 | 154094.1275 | 114117.6341 | 133735.9199 | 634714.1448 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061 |  | 211297.7119 | 55366.7801 | 106136.2613 | 129591.2116 | 105367.6944 | 607759.6593
|  |  | 1868 | 1868 | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 184 | 0 | -33 | -22 | -129 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 386 | 0 | -73 | -19 | -294 | 0 | 574 | 255 | 417 | 253 | 369 | 1868 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 62956 | 62956 | 62956 | 62956 | 62956 | C2 | 807.0959 | 807.0959 | 1123.135 | 2763.1388 | 5789.4338 | C2 | 506856.2378 | 149312.7452 | 824381.1194 | 392365.7153 | 706310.9187 | 2579226.7363 |  | 573038.1032 | 149312.7452 | 822134.8493 | 384076.2988 | 590522.2435 | 2519084.24 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 681996.0524 | 159804.9922 | 621093.6771 | 580259.1564 | 358944.8931 | 2402098.7712 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133 |  | 774812.0832 | 205809.4596 | 386358.4538 | 646574.4886 | 434207.532 | 2447762.0171
|  |  | 455 | 455 | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 74 | 0 | -5 | -18 | -51 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 127 | 0 | -9 | -19 | -99 | 0 | 109 | 57 | 103 | 74 | 112 | 455 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 94434 | 94434 | 94434 | 94434 | 94434 | C3 | 1210.6439 | 1210.6439 | 1684.7026 | 4144.7083 | 8684.1506 | C3 | 116221.8125 | 56900.2624 | 338625.2146 | 116051.8313 | 477628.2852 | 1105427.4059 |  | 161015.636 | 56900.2624 | 338625.2146 | 116051.8313 | 399470.9294 | 1072063.8737 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 237286.2005 | 61742.8379 | 264498.3019 | 174077.7469 | 78157.3558 | 815762.443 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307 |  | 285711.9557 | 69006.7012 | 158362.0406 | 227958.9543 | 112893.9583 | 853933.6101
|  |  | 23 | 23 | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 1 | 0 | 0 | -1 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 5 | 0 | 0 | -4 | -1 | 0 | 6 | 4 | 6 | 6 | 1 | 23 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 157390 | 157390 | 157390 | 157390 | 157390 | C4 | 2017.7398 | 2017.7398 | 2807.8376 | 6907.8471 | 14473.5844 | C4 | 4035.4796 | 6053.2194 | 33694.0512 | 6907.8471 | 72367.922 | 123058.5193 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 16141.9184 | 6053.2194 | 33694.0512 | 0 | 0 | 55889.189 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906 |  | 22195.1378 | 8070.9592 | 16847.0256 | 13815.6942 | 0 | 60928.8168
|  |  | 3046 | 3046 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 321 | 0 | -59 | -50 | -212 |  | 1079 | 313 | 977 | 361 | 316 |  | 645 | 0 | -110 | -47 | -488 |  | 936 | 414 | 689 | 405 | 602 | [22 empty] | 796603.673 | 247859.157 | 1390104.239 | 612035.2531 | 1414358.6676 | 4460960.9897 |  | 925012.6339 | 247859.157 | 1387071.7744 | 601811.6394 | 1111571.2819 | 4273326.4866 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 1133727.6388 | 262064.0452 | 1073380.1577 | 868454.5374 | 570838.1687 | 3908464.5479 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407 |  | 1294016.8885 | 338253.9001 | 667703.7813 | 1017940.3487 | 652469.1848 | 3970384.1033
| HV Switchgear (GM) - Distribution |  | 669 | 666 | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 8 | -10 | 0 | 0 | 0 | -2 | 644 | 18 | 2 | 5 | 0 | 669 | 19 | -18 | -1 | 0 | -3 | -3 | 626 | 36 | 2 | 0 | 5 | 669 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | C1 | 136.001 | 136.001 | 189.2556 | 465.6071 | 975.5577 | C1 | 87040.6208 | 2856.0204 | 1324.7895 | 0 | 0 | 91221.4307 |  | 87584.6247 | 2448.0175 | 1324.7895 | 0 | 0 | 91357.4316 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 88672.6324 | 1088.0078 | 378.5113 | 2328.0353 | 0 | 92467.1868 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417 |  | 87720.6257 | 2448.0175 | 189.2556 | 0 | 1951.1153 | 92309.0141
|  |  | 14652 | 14304 | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 893 | -125 | -27 | 0 | -913 | -172 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 1806 | -107 | -185 | -43 | -1819 | -348 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 15155 | 15155 | 15155 | 15155 | 15155 | C2 | 194.2871 | 194.2871 | 270.3652 | 665.153 | 1393.6538 | C2 | 1117539.3992 | 665433.3175 | 904912.3244 | 580013.3724 | 1754610.1342 | 5022508.5477 |  | 1188065.6165 | 648724.6269 | 889771.8732 | 578683.0665 | 1445218.9906 | 4750464.1737 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 1117539.3992 | 770542.6386 | 767296.4376 | 817472.9756 | 968589.391 | 4441440.842 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762 |  | 1154065.374 | 761411.1449 | 750804.1604 | 750957.6806 | 751179.3982 | 4168417.7581
|  |  | 1431 | 1354 | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 202 | -11 | 0 | 0 | -230 | -39 | 82 | 398 | 360 | 235 | 356 | 1431 | 404 | 0 | -17 | -6 | -458 | -77 | 65 | 335 | 354 | 164 | 513 | 1431 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | C3 | 291.4307 | 291.4307 | 405.5478 | 997.7294 | 2090.4807 | C3 | 38760.2765 | 107246.4792 | 167896.7892 | 236461.8737 | 589515.5574 | 1139880.976 |  | 53040.3783 | 105789.3259 | 166274.598 | 236461.8737 | 499624.8873 | 1061191.0633 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 82766.3046 | 112783.6616 | 145997.208 | 234466.4149 | 263400.5682 | 839414.1572 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406 |  | 136680.9748 | 97629.2677 | 136669.6086 | 157641.2491 | 114976.4385 | 643597.5389
|  |  | 50 | 46 | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 1 | 25 | 50 | 20 | 0 | 0 | 0 | -24 | -4 | 15 | 9 | 0 | 0 | 26 | 50 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | C4 | 485.7177 | 485.7177 | 675.913 | 1662.8824 | 3484.1345 | C4 | 6800.0485 | 1457.1532 | 4055.478 | 8314.4119 | 76650.959 | 97278.0506 |  | 10200.0727 | 1457.1532 | 0 | 8314.4119 | 73166.8245 | 93138.4624 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 17000.1213 | 4371.4597 | 0 | 1662.8824 | 3484.1345 | 26518.5979 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723 |  | 17000.1213 | 4371.4597 | 0 | 0 | 6968.269 | 28339.85
|  |  | 16802 | 16370 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 1123 | -146 | -27 | 0 | -1167 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 2249 | -125 | -203 | -49 | -2304 |  | 4840 | 4406 | 3318 | 1336 | 2902 | [22 empty] | 1250140.345 | 776992.9703 | 1078189.3811 | 824789.658 | 2420776.6506 | 6350889.0049 |  | 1338890.6922 | 758419.1236 | 1057371.2607 | 823459.3521 | 2018010.7024 | 5996151.131 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 1305978.4575 | 888785.7677 | 913672.1569 | 1055930.3081 | 1235474.0937 | 5399840.7839 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469 |  | 1395467.0958 | 865859.8899 | 887663.0246 | 908598.9297 | 875075.221 | 4932664.161
| HV Transformer (GM) |  | 2220 | 2220 | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 151 | 0 | -1 | -18 | -132 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 275 | 0 | -1 | 0 | -274 | 0 | 822 | 319 | 682 | 114 | 283 | 2220 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | C1 | 219.1926 | 219.1926 | 304.8396 | 750.0674 | 1571.6404 | C1 | 204506.6659 | 89211.3752 | 183513.4464 | 54004.8519 | 311184.7921 | 842421.1316 |  | 223795.6119 | 88115.4123 | 181379.5691 | 54004.8519 | 204313.2473 | 751608.6927 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 232563.3146 | 78690.1319 | 200889.3043 | 52504.7172 | 111586.4658 | 676233.9339 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407 |  | 240454.2471 | 69922.4292 | 207595.7758 | 85507.6822 | 14144.7633 | 617624.8976
|  |  | 8983 | 8983 | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 536 | 0 | -4 | -121 | -411 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 1057 | 0 | -2 | -172 | -883 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 16292 | 16292 | 16292 | 16292 | 16292 | C2 | 313.1322 | 313.1322 | 435.4852 | 1071.5248 | 2245.2005 | C2 | 1133538.7088 | 600900.7686 | 1128777.5347 | 233592.4151 | 1356101.1141 | 4452910.5413 |  | 1234367.2901 | 592446.1981 | 1110051.6728 | 233592.4151 | 857666.5986 | 4028124.1748 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 1258165.3403 | 503516.6419 | 1271181.182 | 291454.7565 | 372703.2863 | 3697021.2071 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606 |  | 1261296.6627 | 496001.4682 | 1301665.1432 | 333244.2252 | 159409.2369 | 3551616.7363
|  |  | 1848 | 1848 | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 75 | 0 | 0 | -26 | -49 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 195 | 0 | 0 | -74 | -121 | 0 | 726 | 360 | 525 | 111 | 126 | 1848 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 24438 | 24438 | 24438 | 24438 | 24438 | C3 | 469.6984 | 469.6984 | 653.2277 | 1607.2873 | 3367.8008 | C3 | 427425.5076 | 154530.7604 | 327920.3255 | 43396.756 | 245849.4569 | 1199122.8065 |  | 456546.8059 | 151712.5703 | 316162.2262 | 43396.756 | 141447.6328 | 1109265.9911 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 439637.665 | 151712.5703 | 349476.8409 | 48218.6178 | 80827.2187 | 1069872.9127 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666 |  | 432592.1896 | 169091.4096 | 342944.5635 | 59469.6286 | 16839.0039 | 1020936.7952
|  |  | 14 | 14 | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 2 | 0 | 0 | 0 | -2 | 0 | 3 | 5 | 4 | 0 | 2 | 14 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 40730 | 40730 | 40730 | 40730 | 40730 | C4 | 782.8306 | 782.8306 | 1088.7129 | 2678.8121 | 5613.0013 | C4 | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 3914.153 | 4696.9836 | 3266.1387 | 0 | 0 | 11877.2753 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499 |  | 3914.153 | 3914.153 | 4354.8516 | 0 | 0 | 12183.1576
|  |  | 13065 | 13065 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 764 | 0 | -5 | -165 | -594 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 1529 | 0 | -3 | -246 | -1280 |  | 4522 | 2268 | 4202 | 708 | 1365 | [22 empty] | 1769385.0353 | 847774.2266 | 1643477.4453 | 333672.8352 | 1918748.3644 | 6513057.9068 |  | 1918623.8609 | 835405.5031 | 1610859.6068 | 333672.8352 | 1209040.48 | 5907602.2861 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1934280.4729 | 738616.3277 | 1824813.4659 | 392178.0914 | 565116.9709 | 5455005.3289 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669 |  | 1938257.2524 | 738929.46 | 1856560.3341 | 478221.5361 | 190393.0041 | 5202361.5866
| HV UG Cable |  | 1411.786 | 1411.786 | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 23093 | 23093 | 23093 | 23093 | 23093 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4500.517 | 4500.517 | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 32990 | 32990 | 32990 | 32990 | 32990 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1028.333 | 1028.333 | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 49485 | 49485 | 49485 | 49485 | 49485 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 82475 | 82475 | 82475 | 82475 | 82475 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6940.636 | 6940.636 |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | C1 | 61.436 | 61.436 | 85.4928 | 210.3297 | 440.6907 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 211011 | 211011 | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 15253 | 0 | -2442 | -3355 | -9456 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 31473 | 0 | -5037 | -6922 | -19514 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6846 | 6846 | 6846 | 6846 | 6846 | C2 | 87.7657 | 87.7657 | 122.1326 | 300.4709 | 629.5582 | C2 | 2581102.0595 | 12844337.5906 | 580984.9685 | 5771145.3446 | 7032164.6472 | 28809734.6103 |  | 3199411.5569 | 12844425.3563 | 538604.9424 | 5459556.9798 | 3543153.3245 | 25585152.1598 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 3601027.4916 | 12844337.5906 | 370916.8277 | 5047010.3792 | 2391691.4498 | 24254983.7389 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296 |  | 4028095.4851 | 12844425.3563 | 192603.1733 | 4608623.2777 | 1165312.1542 | 22839059.4466
|  |  | 2291 | 2291 | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 165 | 0 | -25 | -37 | -103 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 341 | 0 | -54 | -76 | -211 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10269 | 10269 | 10269 | 10269 | 10269 | C3 | 131.6486 | 131.6486 | 183.199 | 450.7064 | 944.3372 | C3 | 41995.897 | 209189.5936 | 9526.3459 | 94197.6397 | 113320.4688 | 468229.945 |  | 52132.8377 | 209189.5936 | 8793.5501 | 88789.1628 | 57604.5716 | 416509.7158 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 58583.6181 | 209321.2422 | 6045.5657 | 82028.5666 | 38717.8268 | 394696.8194 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377 |  | 65560.9928 | 209189.5936 | 3114.3823 | 74817.2641 | 19831.082 | 372513.3149
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17115 | 17115 | 17115 | 17115 | 17115 | C4 | 219.4143 | 219.4143 | 305.3316 | 751.1773 | 1573.8954 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 213302 | 213302 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 15418 | 0 | -2467 | -3392 | -9559 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 31814 | 0 | -5091 | -6998 | -19725 |  | 14580 | 147938 | 6685 | 22502 | 21597 | [22 empty] | 2623097.9565 | 13053527.1842 | 590511.3144 | 5865342.9843 | 7145485.116 | 29277964.5554 |  | 3251544.3946 | 13053614.9499 | 547398.4925 | 5548346.1426 | 3600757.8961 | 26001661.8756 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 3659611.1097 | 13053658.8328 | 376962.3934 | 5129038.9458 | 2430409.2767 | 24649680.5583 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673 |  | 4093656.478 | 13053614.9499 | 195717.5556 | 4683440.5418 | 1185143.2362 | 23211572.7614
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 |  | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 8033597.6789 | 14943124.9734 | 4188828.1739 | 7445601.8828 | 4801838.51 | 39412991.219 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 |  | 8721397.7146 | 14996658.1998 | 3607644.6956 | 7088201.3562 | 2903080.6461 | 37316982.6123
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 369 | 369 | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 16 | 0 | -2 | 0 | -14 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 30 | -2 | -2 | -1 | -25 | 0 | 210 | 80 | 31 | 12 | 36 | 369 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | C1 | 910.9866 | 910.9866 | 1267.7068 | 3118.8146 | 6534.6592 | C1 | 242322.4452 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 425963.7075 |  | 246877.3784 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 430518.6407 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 240500.4719 | 51926.2383 | 27889.5503 | 68613.9217 | 26138.6368 | 415068.819 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432 |  | 218636.7926 | 71056.9576 | 36763.4981 | 34306.9608 | 71881.2513 | 432645.4605
|  |  | 475 | 475 | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 52 | 0 | -2 | -13 | -37 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 85 | -1 | 0 | -3 | -81 | 0 | 157 | 91 | 69 | 36 | 122 | 475 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 101514 | 101514 | 101514 | 101514 | 101514 | C2 | 1301.4095 | 1301.4095 | 1811.0098 | 4455.4495 | 9335.2274 | C2 | 275898.8098 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 912299.212 |  | 282405.8572 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 918806.2594 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 307132.6373 | 98907.1205 | 146691.7906 | 325247.8106 | 84017.047 | 961996.4059 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527 |  | 314941.0942 | 117126.8532 | 124959.6734 | 147029.8322 | 382744.325 | 1086801.778
|  |  | 127 | 127 | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 11 | 0 | 0 | -1 | -10 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 41 | 0 | 0 | -6 | -35 | 0 | 33 | 21 | 9 | 24 | 40 | 127 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 152271 | 152271 | 152271 | 152271 | 152271 | C3 | 1952.1142 | 1952.1142 | 2716.5146 | 6683.1742 | 14002.8412 | C3 | 81988.7972 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 417338.266 |  | 91749.3683 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 427098.8371 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 107366.2821 | 31233.8275 | 73345.8953 | 167079.3547 | 56011.3646 | 435036.7243 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266 |  | 144456.4523 | 40994.3986 | 24448.6318 | 120297.1354 | 70014.2058 | 400210.8239
|  |  | 55 | 55 | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 7 | 0 | -1 | -3 | -3 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 14 | 0 | 0 | -4 | -10 | 0 | 9 | 16 | 8 | 9 | 13 | 55 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 253785 | 253785 | 253785 | 253785 | 253785 | C4 | 3253.5237 | 3253.5237 | 4527.5244 | 11138.6236 | 23338.0686 | C4 | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 84591.6162 | 32535.237 | 49802.7684 | 66831.7419 | 46676.1372 | 280437.5007 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924 |  | 74831.0451 | 52056.3792 | 36220.1952 | 55693.1182 | 70014.2058 | 288814.9435
|  |  | 1026 | 1026 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 86 | 0 | -5 | -17 | -64 |  | 495 | 159 | 146 | 143 | 83 |  | 170 | -3 | -2 | -14 | -151 |  | 409 | 208 | 117 | 81 | 211 | [22 empty] | 678294.621 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 1998176.502 |  | 699117.1727 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 2018999.0537 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 739591.0075 | 214602.4233 | 297730.0045 | 627772.8289 | 212843.1856 | 2092539.4498 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149 |  | 752865.3842 | 281234.5886 | 222391.9985 | 357327.0467 | 594653.9879 | 2208473.006
| EHV Transformer |  | 246 | 246 | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 16 | 0 | 0 | -1 | -15 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 34 | 0 | 0 | 0 | -34 | 0 | 105 | 39 | 36 | 16 | 50 | 246 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | C1 | 3379.4828 | 3379.4828 | 4702.806 | 11569.8517 | 24241.594 | C1 | 395399.4834 | 84487.0691 | 286871.164 | 300816.1436 | 363623.9099 | 1431197.77 |  | 425814.8283 | 84487.0691 | 277465.5521 | 266106.5886 | 315140.7219 | 1369014.76 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 429194.311 | 125040.8623 | 211626.2686 | 196687.4785 | 484831.8798 | 1447380.8002 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593 |  | 469748.1042 | 131799.8278 | 169301.0148 | 185117.6268 | 387865.5039 | 1343832.0776
|  |  | 248 | 248 | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 19 | 0 | 0 | -1 | -18 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 38 | 0 | 0 | 0 | -38 | 0 | 34 | 38 | 73 | 38 | 65 | 248 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 376586 | 376586 | 376586 | 376586 | 376586 | C2 | 4827.8325 | 4827.8325 | 6718.2942 | 16528.3595 | 34630.8486 | C2 | 241391.626 | 120695.813 | 866659.957 | 512379.1457 | 346308.4856 | 2087435.0273 |  | 265530.7886 | 120695.813 | 866659.957 | 512379.1457 | 277046.7885 | 2042312.4928 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 313809.1138 | 159318.4732 | 665111.1298 | 561964.2244 | 588724.4255 | 2288927.3666 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399 |  | 347603.9414 | 183457.6358 | 490435.4795 | 628077.6625 | 935032.9111 | 2584607.6304
|  |  | 73 | 73 | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 9 | 0 | 0 | 0 | -9 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 19 | 0 | 0 | 0 | -19 | 0 | 22 | 7 | 12 | 11 | 21 | 73 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 564879 | 564879 | 564879 | 564879 | 564879 | C3 | 7241.7488 | 7241.7488 | 10077.4414 | 24792.5393 | 51946.2728 | C3 | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 246219.4585 | 28966.9951 | 211626.2686 | 223132.8538 | 259731.3642 | 969676.9402 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673 |  | 296911.7 | 50692.2415 | 120929.2963 | 272717.9324 | 103892.5457 | 845143.7159
|  |  | 30 | 30 | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 3 | 0 | 0 | -2 | -1 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 3 | 0 | 0 | 0 | -3 | 0 | 18 | 4 | 2 | 1 | 5 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 941465 | 941465 | 941465 | 941465 | 941465 | C4 | 12069.5813 | 12069.5813 | 16795.7356 | 41320.8988 | 86577.1214 | C4 | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 301739.5325 | 0 | 50387.2068 | 82641.7977 | 0 | 434768.537 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656 |  | 253461.2073 | 48278.3252 | 33591.4712 | 41320.8988 | 173154.2428 | 549806.1454
|  |  | 597 | 597 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 47 | 0 | 0 | -4 | -43 |  | 204 | 74 | 168 | 66 | 85 |  | 94 | 0 | 0 | 0 | -94 |  | 179 | 88 | 123 | 66 | 141 | [22 empty] | 1083365.6175 | 234149.8772 | 1580142.8052 | 1110705.7611 | 865771.214 | 4874135.275 |  | 1137920.125 | 234149.8772 | 1570737.1933 | 1075996.2061 | 748026.3289 | 4766829.7304 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 1290962.4158 | 313326.3305 | 1138750.8737 | 1064426.3544 | 1333287.6696 | 5140753.644 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378 |  | 1367724.9529 | 414228.0302 | 814257.2619 | 1127234.1206 | 1599945.2035 | 5323389.5691
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C1 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | C1 | 553.5916 | 553.5916 | 18758.3105 | 45788.1803 | 95940.8181 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 0 | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | -17 | -17 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | -34 | -34 | 0 | 0 | 0 | 0 | 34 | 34 |  |  | C2 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C2 | 8424 | 8424 | 8424 | 8424 | 8424 | C2 | 790.8451 | 790.8451 | 26797.5864 | 65411.6861 | 137058.3115 | C2 | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 2329991.2958 | 2329991.2958 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C3 | 12636 | 12636 | 12636 | 12636 | 12636 | C3 | 1186.2677 | 1186.2677 | 40196.3796 | 98117.5291 | 205587.4673 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C4 | 21060 | 21060 | 21060 | 21060 | 21060 | C4 | 1977.1128 | 1977.1128 | 66993.966 | 163529.2152 | 342645.7788 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 0 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | -17 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | -34 |  | 0 | 0 | 0 | 0 | 34 | [22 empty] | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 2329991.2958 | 2329991.2958 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV UG Cable (Oil) |  | 21.926 | 21.926 | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | C1 | 301.5188 | 301.5188 | 10223.8139 | 24955.7384 | 52290.2374 | C1 | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936
|  |  | 29.901 | 15.501 | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | -7.2 | 0 | -7.2 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | -14.4 | -14.4 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 72272 | 72272 | 72272 | 72272 | 72272 | C2 | 430.7411 | 430.7411 | 14605.4485 | 35651.0549 | 74700.3392 | C2 | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 57.7193 | 1872.0009 | 155109.8629 | 270983.6681 | 0 | 428023.2512 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 29954.836 | 220614.036
|  |  | 8.451 | 8.451 | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 108408 | 108408 | 108408 | 108408 | 108408 | C3 | 646.1117 | 646.1117 | 21908.1727 | 53476.5823 | 112050.5088 | C3 | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 180680 | 180680 | 180680 | 180680 | 180680 | C4 | 1076.8528 | 1076.8528 | 36513.6212 | 89127.6372 | 186750.848 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 60.278 | 45.878 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | -7.2 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | -14.4 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801 | [22 empty] | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 239.1905 | 5938.0679 | 420398.8474 | 270983.6681 | 0 | 697559.774 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 29954.836 | 586211.133
| EHV UG Cable (Non Pressurised) |  | 241.211 | 241.211 | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 383.855 | 383.855 | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 50665 | 50665 | 50665 | 50665 | 50665 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 188.435 | 188.435 | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10.863 | 10.863 | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 824.364 | 824.364 |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 125 | 125 | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 2 | 0 | 0 | 0 | -2 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 4 | 0 | 0 | 0 | -4 | 0 | 27 | 69 | 18 | 7 | 4 | 125 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | C1 | 81.561 | 81.561 | 81.561 | 4130.3727 | 14151.6049 | C1 | 2528.3913 | 6524.8809 | 978.7321 | 24782.2362 | 0 | 34814.2406 |  | 2528.3913 | 6280.1978 | 897.1711 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2365.2693 | 5709.2708 | 1631.2202 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5627.7098 | 1468.0982 | 28912.609 | 56606.4194 | 94816.9836 |  | 2528.3913 | 5627.7098 | 1468.0982 | 28912.609 | 0 | 38536.8083
|  |  | 299 | 299 | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 4 | 0 | 0 | 0 | -4 | 0 | 58 | 176 | 51 | 10 | 4 | 299 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 219841 | 219841 | 219841 | 219841 | 219841 | C2 | 116.5157 | 116.5157 | 116.5157 | 5900.5324 | 20216.5784 | C2 | 7690.0382 | 18759.0325 | 6874.4281 | 47204.2595 | 121299.4702 | 201827.2285 |  | 8389.1326 | 18992.064 | 6757.9123 | 35403.1946 | 0 | 69542.3035 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 6757.9123 | 20506.7685 | 5942.3022 | 59005.3244 | 80866.3134 | 173078.6209 |  | 7223.9753 | 20506.7685 | 5942.3022 | 59005.3244 | 0 | 92678.3704
|  |  | 65 | 65 | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 1 | 0 | 0 | 0 | -1 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 1 | 0 | 0 | 0 | -1 | 0 | 14 | 33 | 14 | 3 | 1 | 65 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | C3 | 174.7736 | 174.7736 | 174.7736 | 8850.7987 | 30324.8675 | C3 | 2796.3775 | 6990.9438 | 1048.6416 | 26552.396 | 0 | 37388.3589 |  | 2796.3775 | 7340.491 | 1048.6416 | 8850.7987 | 0 | 20036.3087 |  | 2796.3775 | 5942.3022 | 2097.2831 | 17701.5973 | 30324.8675 | 58862.4278 |  | 2971.1511 | 5942.3022 | 2097.2831 | 17701.5973 | 0 | 28712.3338 |  | 2446.8303 | 5767.5286 | 2446.8303 | 26552.396 | 30324.8675 | 67538.4528 |  | 2621.6039 | 5767.5286 | 2446.8303 | 26552.396 | 0 | 37388.3589
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | C4 | 291.2893 | 291.2893 | 291.2893 | 14751.3311 | 50541.4459 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 3 | 0 | 0 | 0 | -3 |  | 112 | 270 | 87 | 17 | 3 |  | 9 | 0 | 0 | 0 | -9 |  | 99 | 278 | 83 | 20 | 9 | [22 empty] | 13014.807 | 32274.8572 | 8901.8018 | 98538.8917 | 121299.4702 | 274029.8279 |  | 13713.9014 | 32612.7528 | 8703.725 | 69036.2295 | 0 | 124066.6088 |  | 13038.1102 | 30993.1842 | 10136.8685 | 95588.6255 | 58628.0772 | 208384.8656 |  | 13376.0058 | 30993.1842 | 10136.8685 | 95588.6255 | 0 | 150094.684 |  | 11406.89 | 31902.0069 | 9857.2308 | 114470.3293 | 167797.6004 | 335434.0573 |  | 12373.9705 |  | 9857.2308 |  | 0 | 22231.2013
| EHV OHL Support - Poles |  | 4894 | 4894 | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 362 | 0 | -50 | -72 | -240 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 739 | 0 | -104 | -147 | -488 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | C1 | 112.0045 | 112.0045 | 155.8627 | 383.4538 | 803.4269 | C1 | 52418.1032 | 343181.7696 | 38653.9565 | 233906.7954 | 405730.6007 | 1073891.2254 |  | 66194.656 | 343181.7696 | 37718.7802 | 226621.1739 | 326191.3344 | 999907.7141 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 82435.3076 | 343181.7696 | 31016.6829 | 209749.2084 | 279592.5723 | 945975.5408 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472 |  | 99347.9862 | 343181.7696 | 23846.9974 | 192493.789 | 231386.9564 | 890257.4986
|  |  | 22777 | 22777 | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 1685 | 0 | -237 | -337 | -1111 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 3440 | 0 | -482 | -687 | -2271 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12481 | 12481 | 12481 | 12481 | 12481 | C2 | 160.0064 | 160.0064 | 222.661 | 547.7911 | 1147.7528 | C2 | 348493.9828 | 2281851.5556 | 257396.1622 | 1552439.9491 | 2698366.7388 | 7138548.3884 |  | 440337.6678 | 2281851.5556 | 250938.9921 | 1505329.9153 | 2168104.9636 | 6646563.0945 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 548181.9949 | 2281851.5556 | 205738.801 | 1394676.1151 | 1859359.4712 | 6289807.9378 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714 |  | 660506.5018 | 2281851.5556 | 158979.9826 | 1279092.1951 | 1536840.9456 | 5917271.1807
|  |  | 1936 | 1936 | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 143 | 0 | -20 | -29 | -94 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 293 | 0 | -41 | -59 | -193 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | C3 | 240.0096 | 240.0096 | 333.9916 | 821.6866 | 1721.6291 | C3 | 44401.7815 | 290891.6716 | 33065.1644 | 197204.7924 | 344325.828 | 909889.2379 |  | 56162.2534 | 290891.6716 | 32063.1898 | 191452.986 | 277182.2915 | 847752.3922 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 69842.8023 | 290891.6716 | 26385.3332 | 177484.3132 | 237584.8213 | 802188.9416 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804 |  | 84243.3801 | 290891.6716 | 20373.4852 | 162693.9537 | 196265.722 | 754468.2125
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | C4 | 400.0161 | 400.0161 | 556.6526 | 1369.4777 | 2869.3819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29607 | 29607 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 2190 | 0 | -307 | -438 | -1445 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 4472 | 0 | -627 | -893 | -2952 |  | 894 | 18537 | 1555 | 3928 | 4693 | [22 empty] | 445313.8675 | 2915924.9968 | 329115.2832 | 1983551.5369 | 3448423.1674 | 9122328.8518 |  | 562694.5772 | 2915924.9968 | 320720.962 | 1923404.0752 | 2771478.5896 | 8494223.2008 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 700460.1048 | 2915924.9968 | 263140.8171 | 1781909.6367 | 2376536.8649 | 8037972.4202 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416 |  | 844097.8681 | 2915924.9968 | 203200.4651 | 1634279.9379 | 1964493.624 | 7561996.8919
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 427 | 427 | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 17 | 0 | 0 | -12 | -5 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 137 | 0 | 0 | 0 | -137 | 0 | 0 | 290 | 0 | 0 | 137 | 427 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | C1 | 238.7737 | 238.7737 | 332.7056 | 818.1404 | 1714.4379 | C1 | 71632.0962 | 0 | 43917.1434 | 0 | 8572.1893 | 124121.4289 |  | 69244.3597 | 0 | 43917.1434 | 0 | 8572.1893 | 121733.6924 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 4059.1521 | 69244.3597 | 0 | 98176.843 | 0 | 171480.3547 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462 |  | 32711.9906 | 69244.3597 | 0 | 0 | 0 | 101956.3503
|  |  | 456 | 456 | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 172 | 0 | 0 | 0 | -172 | 0 | 117 | 167 | 0 | 0 | 172 | 456 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 102434 | 102434 | 102434 | 102434 | 102434 | C2 | 341.1052 | 341.1052 | 475.2938 | 1168.7719 | 2449.1969 | C2 | 99943.8295 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 431151.8764 |  | 96873.8825 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 428081.9294 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 98579.4086 | 56964.5717 | 0 | 0 | 0 | 155543.9803 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 98579.4086 | 56964.5717 | 0 | 0 | 0 | 155543.9803
|  |  | 55 | 55 | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 54 | 0 | 0 | 0 | -54 | 0 | 0 | 1 | 0 | 0 | 54 | 55 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 153651 | 153651 | 153651 | 153651 | 153651 | C3 | 511.6578 | 511.6578 | 712.9406 | 1753.1579 | 3673.7954 | C3 | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 27629.5228 | 511.6578 | 0 | 0 | 0 | 28141.1806 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 27629.5228 | 511.6578 | 0 | 0 | 0 | 28141.1806
|  |  | 87 | 87 | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 34 | 0 | 0 | 0 | -34 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 56 | 0 | 0 | 0 | -56 | 0 | 0 | 31 | 0 | 0 | 56 | 87 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 256085 | 256085 | 256085 | 256085 | 256085 | C4 | 852.7631 | 852.7631 | 1188.2344 | 2921.9298 | 6122.9924 | C4 | 27288.4176 | 0 | 26141.1568 | 99345.6149 | 0 | 152775.1893 |  | 26435.6545 | 0 | 26141.1568 | 99345.6149 | 0 | 151922.4263 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 28993.9437 | 26435.6545 | 11882.344 | 35063.1582 | 0 | 102375.1004 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262 |  | 47754.7308 | 26435.6545 | 0 | 0 | 0 | 74190.3853
|  |  | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 277 | 0 | 0 | -12 | -265 |  | 117 | 489 | 10 | 144 | 265 |  | 419 | 0 | 0 | 0 | -419 |  | 117 | 489 | 0 | 0 | 419 | [22 empty] | 199376.0011 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 906945.1046 |  | 193065.5545 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 900634.658 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 159262.0272 | 153156.2438 | 11882.344 | 133240.0012 | 0 | 457540.6162 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385 |  | 206675.6528 | 153156.2438 | 0 | 0 | 0 | 359831.8966
| EHV OHL Conductor (Tower Lines) |  | 40.481 | 40.481 | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | C1 | 5.8423 | 5.8423 | 8.0332 | 20.4481 | 43.0871 | C1 | 236.5143 | 0 | 3.7515 | 0 | 0 | 240.2658 |  | 233.8035 | 0 | 3.7113 | 0 | 0 | 237.5148 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505
|  |  | 52.696 | 52.696 | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 104327 | 104327 | 104327 | 104327 | 104327 | C2 | 8.3462 | 8.3462 | 11.476 | 29.2116 | 61.5529 | C2 | 232.0232 | 0 | 292.729 | 0 | 0 | 524.7523 |  | 229.3608 | 0 | 289.3666 | 0 | 0 | 518.7274 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996
|  |  | 6.374 | 6.374 | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | C3 | 12.5192 | 12.5192 | 17.214 | 43.8173 | 92.3294 | C3 | 1.6275 | 0 | 108.7406 | 0 | 0 | 110.3681 |  | 1.615 | 0 | 107.5011 | 0 | 0 | 109.1161 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543
|  |  | 8.199 | 8.199 | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | C4 | 20.8654 | 20.8654 | 28.6899 | 73.0289 | 153.8823 | C4 | 106.6639 | 66.4146 | 0 | 0 | 0 | 173.0785 |  | 105.4329 | 65.6425 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914
|  |  | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0 | [22 empty] | 576.829 | 66.4146 | 405.2211 | 0 | 0 | 1048.4646 |  | 570.2122 | 65.6425 | 400.5791 | 0 | 0 | 1036.4338 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 |  | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 |  | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 |  | 2903985.8729 | 3634481.9883 | 2142208.7963 | 3974510.4551 | 6252659.0159 | 18907846.1284 |  | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 |  | 3184008.3905 | 3767486.1494 | 1780816.0837 | 3142388.1185 | 4189047.6514 | 16063746.3936
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 72 | 72 | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 4 | 0 | 0 | 0 | -4 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 7 | 0 | 0 | -1 | -6 | 0 | 34 | 19 | 9 | 4 | 6 | 72 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | C1 | 2255.4713 | 2255.4713 | 3138.659 | 7721.7345 | 16178.8722 | C1 | 110518.0945 | 11277.3566 | 37663.9079 | 30886.9379 | 32357.7445 | 222704.0414 |  | 112773.5658 | 11277.3566 | 37663.9079 | 30886.9379 | 16178.8722 | 208780.6405 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 115029.0371 | 18043.7705 | 34525.2489 | 7721.7345 | 16178.8722 | 191498.6633 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821 |  | 92474.324 | 42853.955 | 28247.9309 | 23165.2034 | 0 | 186741.4133
|  |  | 61 | 61 | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 1 | 0 | 0 | 0 | -1 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 6 | 0 | 0 | -1 | -5 | 0 | 35 | 16 | 2 | 3 | 5 | 61 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 251334 | 251334 | 251334 | 251334 | 251334 | C2 | 3222.1019 | 3222.1019 | 4483.7986 | 11031.0493 | 23112.6746 | C2 | 112773.5658 | 9666.3056 | 35870.3885 | 22062.0985 | 46225.3493 | 226597.7077 |  | 154660.8902 | 9666.3056 | 35870.3885 | 22062.0985 | 0 | 222259.6829 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 141772.4827 | 25776.815 | 17935.1942 | 44124.197 | 23112.6746 | 252721.3637 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314 |  | 132106.1771 | 51553.6301 | 8967.5971 | 22062.0985 | 0 | 214689.5028
|  |  | 26 | 26 | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 5 | 0 | 0 | -2 | -3 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 9 | 0 | 0 | 0 | -9 | 0 | 11 | 5 | 1 | 0 | 9 | 26 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 377001 | 377001 | 377001 | 377001 | 377001 | C3 | 4833.1528 | 4833.1528 | 6725.6978 | 16546.5739 | 34669.012 | C3 | 67664.1395 | 9666.3056 | 20177.0935 | 82732.8694 | 69338.0239 | 249578.432 |  | 72497.2923 | 9666.3056 | 20177.0935 | 82732.8694 | 34669.012 | 219742.5729 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 86996.7508 | 19332.6113 | 0 | 16546.5739 | 104007.0359 | 226882.9718 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506 |  | 96663.0564 | 24165.7641 | 6725.6978 | 0 | 0 | 127554.5183
|  |  | 7 | 7 | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 628335 | 628335 | 628335 | 628335 | 628335 | C4 | 8055.2547 | 8055.2547 | 11209.4964 | 27577.6231 | 57781.6866 | C4 | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829
|  |  | 166 | 166 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 10 | 0 | 0 | -2 | -8 |  | 107 | 23 | 15 | 8 | 13 |  | 22 | 0 | 0 | -2 | -20 |  | 82 | 45 | 12 | 7 | 20 | [22 empty] | 347342.5827 | 30609.9679 | 93711.3899 | 135681.9059 | 147921.1177 | 755266.964 |  | 396318.5312 | 30609.9679 | 93711.3899 | 135681.9059 | 50847.8842 | 707169.6791 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 376019.2894 | 87318.9609 | 52460.4432 | 68392.5054 | 143298.5828 | 727489.7817 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296 |  | 337354.0668 | 158849.6227 | 43941.2259 | 45227.302 | 0 | 585372.2174
| 132kV Transformer |  | 27 | 27 | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 1 | 0 | 0 | 0 | -1 | 0 | 12 | 4 | 8 | 2 | 1 | 27 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | C1 | 21313.7705 | 21313.7705 | 29659.7243 | 72968.9069 | 152887.2336 | C1 | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 298392.7869 | 85255.082 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697 |  | 277079.0164 | 85255.082 | 237277.7944 | 145937.8139 | 0 | 745549.7067
|  |  | 48 | 48 | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 1 | 0 | 0 | -1 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 6 | 0 | 0 | -3 | -3 | 0 | 16 | 5 | 14 | 9 | 4 | 48 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2375058 | 2375058 | 2375058 | 2375058 | 2375058 | C2 | 30448.2436 | 30448.2436 | 42371.0347 | 104241.2956 | 218410.3337 | C2 | 548068.3841 | 213137.7049 | 720307.5902 | 521206.4781 | 0 | 2002720.1573 |  | 608964.8712 | 213137.7049 | 720307.5902 | 416965.1825 | 0 | 1959375.3488 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 608964.8712 | 152241.2178 | 762678.625 | 416965.1825 | 218410.3337 | 2159260.2301 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961 |  | 669861.3583 | 152241.2178 | 593194.4861 | 625447.7737 | 218410.3337 | 2259155.1696
|  |  | 13 | 13 | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 1 | 0 | 0 | -1 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 3 | 0 | 0 | -1 | -2 | 0 | 4 | 3 | 2 | 2 | 2 | 13 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3562587 | 3562587 | 3562587 | 3562587 | 3562587 | C3 | 45672.3653 | 45672.3653 | 63556.5521 | 156361.9434 | 327615.5005 | C3 | 182689.4614 | 91344.7307 | 254226.2083 | 469085.8303 | 0 | 997346.2307 |  | 228361.8267 | 91344.7307 | 254226.2083 | 312723.8869 | 0 | 886656.6526 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 274034.192 | 91344.7307 | 190669.6562 | 312723.8869 | 0 | 868772.4658 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494 |  | 319706.5574 | 137017.096 | 127113.1042 | 156361.9434 | 0 | 740198.701
|  |  | 6 | 6 | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 0 | -1 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 2 | 0 | 0 | -1 | -1 | 0 | 0 | 1 | 2 | 2 | 1 | 6 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5937645 | 5937645 | 5937645 | 5937645 | 5937645 | C4 | 76120.6089 | 76120.6089 | 105927.5868 | 260603.2391 | 546025.8342 | C4 | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 76120.6089 | 76120.6089 | 317782.7604 | 260603.2391 | 0 | 730627.2172 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948 |  | 152241.2178 | 76120.6089 | 211855.1736 | 260603.2391 | 0 | 700820.2393
|  |  | 94 | 94 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 4 | 0 | -1 | -2 | -1 |  | 37 | 12 | 33 | 10 | 2 |  | 12 | 0 | 0 | -5 | -7 |  | 32 | 13 | 26 | 15 | 8 | [22 empty] | 1147898.7822 | 499351.1944 | 1529594.3534 | 1063261.2153 | 0 | 4240105.5453 |  | 1254467.6347 | 499351.1944 | 1529594.3534 | 802657.9763 | 0 | 4086071.1587 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 1257512.459 | 404961.6393 | 1508408.836 | 1063261.2153 | 218410.3337 | 4452554.4834 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101 |  | 1418888.1499 | 450634.0047 | 1169440.5583 | 1188350.7701 | 218410.3337 | 4445723.8166
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 24.121 | 24.121 | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | C1 | 687.9878 | 687.9878 | 23328.0975 | 56942.5365 | 119312.7891 | C1 | 2223.5767 | 11940.7168 | 82418.1684 | 168208.2529 | 0 | 264790.7147 |  | 2223.5767 | 11940.7168 | 82418.1684 | 0 | 0 | 96582.4619 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285
|  |  | 11.91 | 11.91 | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 164906 | 164906 | 164906 | 164906 | 164906 | C2 | 982.8398 | 982.8398 | 33325.8535 | 81346.4807 | 170446.8416 | C2 | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244
|  |  | 25.639 | 25.639 | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0.2 | 0 | 0 | 0 | -0.2 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0.4 | 0 | 0 | 0 | -0.4 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 247359 | 247359 | 247359 | 247359 | 247359 | C3 | 1474.2596 | 1474.2596 | 49988.7803 | 122019.7211 | 255670.2624 | C3 | 11561.1441 | 25647.695 | 0 | 78824.7398 | 0 | 116033.5789 |  | 11561.1441 | 25647.695 | 0 | 48807.8884 | 0 | 86016.7275 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 11855.996 | 931.7321 | 838061.9019 | 0 | 51134.0525 | 901983.6825 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308 |  | 8033.2408 | 4211.9598 | 866455.5291 | 0 | 0 | 878700.7297
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 412265 | 412265 | 412265 | 412265 | 412265 | C4 | 2457.0994 | 2457.0994 | 83314.6338 | 203366.2019 | 426117.104 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 61.67 | 61.67 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0.2 | 0 | 0 | 0 | -0.2 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0.4 | 0 | 0 | 0 | -0.4 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4 | [22 empty] | 15226.5467 | 47852.2074 | 82418.1684 | 247032.9927 | 0 | 392529.9152 |  | 15226.5467 | 47852.2074 | 82418.1684 | 48807.8884 | 0 | 194304.8109 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 14185.5228 | 18383.9194 | 1126917.07 | 0 | 51134.0525 | 1210620.5648 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837 |  | 8143.3188 | 12880.9013 | 1528386.9625 | 0 | 0 | 1549411.1826
| 132kV UG Cable (Non Pressurised) |  | 7.356 | 7.356 | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.671 | 9.671 | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 1610892 | 1610892 | 1610892 | 1610892 | 1610892 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2.775 | 2.775 | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 2416338 | 2416338 | 2416338 | 2416338 | 2416338 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.253 | 0.253 | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 4027230 | 4027230 | 4027230 | 4027230 | 4027230 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20.055 | 20.055 |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1148 | 1148 | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 1 | 0 | 0 | 0 | -1 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 3 | 0 | 0 | 0 | -3 | 0 | 267 | 705 | 125 | 48 | 3 | 1148 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | C1 | 293.7956 | 293.7956 | 293.7956 | 14878.2548 | 50976.3155 | C1 | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 87551.1013 | 198605.854 | 37605.8422 | 669521.4649 | 50976.3155 | 1044260.5779 |  | 87844.897 | 198605.854 | 37605.8422 | 669521.4649 | 0 | 993578.058 |  | 78443.4364 | 207125.9276 | 36724.4552 | 714156.2292 | 152928.9466 | 1189378.9952 |  | 79324.8233 | 207125.9276 | 36724.4552 | 714156.2292 | 0 | 1037331.4354
|  |  | 1252 | 1252 | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 4 | 0 | 0 | 0 | -4 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 12 | 0 | 0 | 0 | -12 | 0 | 294 | 743 | 132 | 71 | 12 | 1252 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 791902 | 791902 | 791902 | 791902 | 791902 | C2 | 419.7081 | 419.7081 | 419.7081 | 21254.6497 | 72823.3079 | C2 | 125912.418 | 320237.2498 | 53302.9236 | 1254024.3311 | 218469.9238 | 1971946.8463 |  | 127171.5422 | 320237.2498 | 53302.9236 | 1254024.3311 | 0 | 1754736.0467 |  | 125073.0019 | 316879.5853 | 52463.5075 | 1487825.4776 | 291293.2317 | 2273534.804 |  | 126751.8341 | 316879.5853 | 52463.5075 | 1487825.4776 | 0 | 1983920.4045 |  | 123394.1696 | 311843.0886 | 55401.4639 | 1509080.1273 | 873879.695 | 2873598.5445 |  | 128430.6664 | 311843.0886 | 55401.4639 | 1509080.1273 | 0 | 2004755.3461
|  |  | 501 | 501 | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 2 | 0 | 0 | 0 | -2 | 0 | 35 | 349 | 101 | 14 | 2 | 501 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1187853 | 1187853 | 1187853 | 1187853 | 1187853 | C3 | 629.5621 | 629.5621 | 629.5621 | 31881.9745 | 109234.9619 | C3 | 28330.2941 | 230419.7249 | 28330.2941 | 1434688.8534 | 0 | 1721769.1664 |  | 28330.2941 | 249306.5876 | 28330.2941 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 22034.6731 | 219717.1694 | 63585.7711 | 446347.6433 | 218469.9238 | 970155.1807 |  | 23293.7973 | 219717.1694 | 63585.7711 | 446347.6433 | 0 | 752944.3811
|  |  | 187 | 187 | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 1979755 | 1979755 | 1979755 | 1979755 | 1979755 | C4 | 1049.2702 | 1049.2702 | 1049.2702 | 53136.6242 | 182058.2698 | C4 | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181
|  |  | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 5 | 0 | 0 | 0 | -5 |  | 698 | 1901 | 354 | 130 | 5 |  | 17 | 0 | 0 | 0 | -17 |  | 656 | 1891 | 391 | 133 | 17 | [22 empty] | 323720.8267 | 862122.326 | 122428.8411 | 3283843.3756 | 218469.9238 | 4810585.2931 |  | 324979.9509 | 881009.1887 | 122428.8411 | 2327384.14 | 0 | 3655802.1207 |  | 303281.0442 | 855029.2598 | 162049.282 | 2635576.5603 | 342269.5472 | 4298205.6935 |  | 305253.672 | 855029.2598 | 162049.282 | 2635576.5603 | 0 | 3957908.7742 |  | 286828.4882 | 837317.5797 | 190337.6052 | 2669583.9998 | 1245278.5654 | 5229346.2384 |  | 294005.496 | 837317.5797 | 190337.6052 | 2669583.9998 | 0 | 3991244.6807
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1974 | 1974 | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 258 | 0 | 0 | -256 | -2 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 459 | 0 | 0 | 0 | -459 | 0 | 873 | 153 | 489 | 0 | 459 | 1974 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | C1 | 24.2662 | 24.2662 | 33.366 | 78.8651 | 166.8301 | C1 | 16234.0878 | 15239.1736 | 14013.7305 | 3785.5272 | 34867.4961 | 84140.0152 |  | 21378.5222 | 15239.1736 | 14013.7305 | 3548.9318 | 0 | 54180.3581 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 27639.2018 | 4853.24 | 15181.5414 | 11435.4467 | 5839.0544 | 64948.4843 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348 |  | 32322.5784 | 3712.7286 | 16315.9862 | 0 | 0 | 52351.2932
|  |  | 1409 | 1409 | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 146 | 0 | 0 | -146 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 264 | 0 | 0 | 0 | -264 | 0 | 816 | 99 | 230 | 0 | 264 | 1409 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 433325 | 433325 | 433325 | 433325 | 433325 | C2 | 34.666 | 34.666 | 47.6658 | 112.6645 | 238.3288 | C2 | 26727.486 | 10607.796 | 11678.1088 | 4619.2445 | 10963.1225 | 64595.7578 |  | 28426.12 | 10607.796 | 11678.1088 | 4281.251 | 0 | 54993.2758 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 33487.356 | 3605.264 | 12440.7608 | 8787.831 | 0 | 58321.2118 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025 |  | 37439.28 | 3431.934 | 10963.1225 | 0 | 0 | 51834.3365
|  |  | 945 | 945 | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 68 | 0 | 0 | -68 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 175 | 0 | 0 | 0 | -175 | 0 | 507 | 32 | 231 | 0 | 175 | 945 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | C3 | 51.999 | 51.999 | 71.4986 | 168.9967 | 357.4931 | C3 | 24543.528 | 13623.738 | 11940.2704 | 1520.9707 | 12512.2594 | 64140.7665 |  | 26363.493 | 13623.738 | 11940.2704 | 1520.9707 | 0 | 53448.4721 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 29899.425 | 1715.967 | 18232.1494 | 13688.7368 | 357.4931 | 63893.7712 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402 |  | 35463.318 | 1663.968 | 16516.1824 | 0 | 0 | 53643.4684
|  |  | 436 | 436 | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 4 | 0 | 0 | -4 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 26 | 0 | 0 | 0 | -26 | 0 | 313 | 8 | 89 | 0 | 26 | 436 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | C4 | 86.665 | 86.665 | 119.1644 | 281.6612 | 595.8219 | C4 | 26779.485 | 8406.505 | 3098.2738 | 0 | 2383.2875 | 40667.5513 |  | 27126.145 | 8406.505 | 3098.2738 | 0 | 0 | 38630.9238 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27472.805 | 953.315 | 10963.1225 | 4506.58 | 0 | 43895.8225 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631 |  | 29379.435 | 693.32 | 10605.6294 | 0 | 0 | 40678.3844
|  |  | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 476 | 0 | 0 | -474 | -2 |  | 2521 | 348 | 1063 | 794 | 38 |  | 924 | 0 | 0 | 0 | -924 |  | 2509 | 292 | 1039 | 0 | 924 | [22 empty] | 94284.5868 | 47877.2126 | 40730.3834 | 9925.7424 | 60726.1655 | 253544.0907 |  | 103294.2802 | 47877.2126 | 40730.3834 | 9351.1535 | 0 | 201253.0297 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 118498.7878 | 11127.786 | 56817.574 | 38418.5945 | 6196.5475 | 231059.2898 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407 |  | 134604.6114 | 9501.9506 | 54400.9205 | 0 | 0 | 198507.4825
| 132kV OHL Conductor (Tower Lines) |  | 582.743 | 582.743 | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 40.805 | 0 | 0 | -32.346 | -8.459 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 66.899 | 0 | 0 | 0 | -66.899 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | C1 | 24.2866 | 24.2866 | 33.3941 | 85.003 | 179.1136 | C1 | 1808.5248 | 3592.0586 | 11976.176 | 286.1202 | 0 | 17662.8797 |  | 1802.8417 | 3580.7897 | 11945.2531 | 286.1202 | 0 | 17615.0047 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 2315.5801 | 2003.6675 | 12649.8009 | 2218.0694 | 0 | 19187.1178 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952 |  | 1878.203 | 2781.5425 | 11214.4243 | 4680.0126 | 0 | 20554.1823
|  |  | 372.373 | 372.373 | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 1.495 | 0 | 0 | -1.495 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 27.981 | 0 | 0 | 0 | -27.981 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 433689 | 433689 | 433689 | 433689 | 433689 | C2 | 34.6951 | 34.6951 | 47.7058 | 121.4329 | 255.8765 | C2 | 5409.4549 | 2529.3783 | 6900.1655 | 0 | 0 | 14838.9987 |  | 5392.489 | 2521.4332 | 6882.7051 | 0 | 0 | 14796.6273 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 5427.3576 | 752.8147 | 8003.0756 | 3216.2723 | 0 | 17399.5203 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577 |  | 1484.7777 | 5287.224 | 7678.2946 | 1971.5849 | 0 | 16421.8812
|  |  | 282.328 | 282.327 | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 3.72 | 0 | 0 | -2.99 | -0.731 | -0.001 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | C3 | 52.0427 | 52.0427 | 71.5587 | 182.1494 | 383.8148 | C3 | 1710.2786 | 5623.4197 | 10181.9422 | 0 | 0 | 17515.6405 |  | 1704.9182 | 5605.7773 | 10150.8141 | 0 | 0 | 17461.5096 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106 |  | 240.0729 | 4270.206 | 12569.4261 | 3644.8091 | 0 | 20724.5141
|  |  | 131.686 | 131.686 | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | C4 | 86.7378 | 86.7378 | 119.2645 | 303.5823 | 639.6913 | C4 | 8338.7119 | 1881.6031 | 1702.0233 | 0 | 0 | 11922.3383 |  | 8312.5171 | 1875.7049 | 1696.6564 | 0 | 0 | 11884.8784 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792
|  |  | 1369.13 | 1369.129 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 42.3 | 0 | 0 | -33.841 | -8.459 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 98.6 | 0 | 0 | -2.99 | -95.611 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611 | [22 empty] | 17266.9702 | 13626.4598 | 30760.307 | 286.1202 | 0 | 61939.8572 |  | 17212.766 | 13583.705 | 30675.4288 | 286.1202 | 0 | 61758.0201 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 16442.3574 | 9550.151 | 34183.6935 | 8169.8611 | 0 | 68346.063 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994 |  | 7283.4251 | 17592.4208 | 34883.6043 | 10296.4066 | 0 | 70055.8568
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 |  | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 |  | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 |  | 2087912.0885 | 1386371.7165 | 2940836.8987 | 3813818.7367 | 419039.5164 | 10647978.9569 |  | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 |  | 2200279.0681 | 1486776.4798 | 3021390.8766 | 3913458.4784 | 218410.3337 | 10840315.2366
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 519588.883 | 519108.482 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 35787.5 | -171 | -5197 | -7920.041 | -22740.659 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 73030 | -184 | -10734 | -14727.99 | -47864.411 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 |  | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 |  | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 |  | 15585086.3647 | 28987597.7724 | 10939385.6533 | 20973755.2953 | 14079504.0544 | 90565329.1401 |  | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 |  | 16897294.2495 | 29260748.2874 | 9823924.4302 | 19999129.8033 | 9415959.2372 | 85397056.0076
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 | LV Network | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 2559590.7243 | 9023619.0942 | 1667511.7844 | 5739824.2208 | 2605967.0121 | 21596512.8358 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 | LV Network | 2791609.0763 | 9009827.4584 | 1414072.7742 | 5855081.8501 | 2105420.606 | 21176011.765
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 | HV Network | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 8033597.6789 | 14943124.9734 | 4188828.1739 | 7445601.8828 | 4801838.51 | 39412991.219 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 | HV Network | 8721397.7146 | 14996658.1998 | 3607644.6956 | 7088201.3562 | 2903080.6461 | 37316982.6123
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 | EHV Network | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 | EHV Network | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 | EHV Network | 2903985.8729 | 3634481.9883 | 2142208.7963 | 3974510.4551 | 6252659.0159 | 18907846.1284 | EHV Network | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 | EHV Network | 3184008.3905 | 3767486.1494 | 1780816.0837 | 3142388.1185 | 4189047.6514 | 16063746.3936
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 | 132kV Network | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 | 132kV Network | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 | 132kV Network | 2087912.0885 | 1386371.7165 | 2940836.8987 | 3813818.7367 | 419039.5164 | 10647978.9569 | 132kV Network | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 | 132kV Network | 2200279.0681 | 1486776.4798 | 3021390.8766 | 3913458.4784 | 218410.3337 | 10840315.2366
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 | Total | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 | Total | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 | Total | 15585086.3647 | 28987597.7724 | 10939385.6533 | 20973755.2953 | 14079504.0544 | 90565329.1401 | Total | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 | Total | 16897294.2495 | 29260748.2874 | 9823924.4302 | 19999129.8033 | 9415959.2372 | 85397056.0076
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWEST - Refurb
Secondary deliverables RIIO-ED1 - Refurbishment | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWEST | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | C1 | 43.7303 | 43.7303 | 60.854 | 149.7132 | 313.6848 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 0 | 0 | 0 | 0 | 0 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4873 | 4873 | 4873 | 4873 | 4873 | C2 | 62.4719 | 62.4719 | 86.9343 | 213.876 | 448.1211 | C2 | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | C3 | 93.7078 | 93.7078 | 130.4015 | 320.814 | 672.1816 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | C4 | 156.1797 | 156.1797 | 217.3358 | 534.6899 | 1120.3027 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790 | [22 empty] | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131
| LV Switchgear (at s/s) |  | 857 | 857 | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 148 | 93 | 10 | 20 | 857 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | C1 | 76.19 | 76.19 | 105.9604 | 260.7189 | 546.2926 | C1 | 49066.3613 | 8304.7102 | 7629.1483 | 1564.3131 | 7648.0967 | 74212.6296 |  | 51733.0114 | 8228.5202 | 5721.8612 | 1564.3131 | 5462.9262 | 72710.6321 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819
|  |  | 11264 | 11264 | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 0 | 0 | 0 | 0 | 0 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 0 | 0 | 0 | 0 | 0 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5663 | 5663 | 5663 | 5663 | 5663 | C2 | 108.8429 | 108.8429 | 151.372 | 372.4555 | 780.418 | C2 | 548568.0144 | 212352.4199 | 536916.4485 | 90134.2334 | 263000.8761 | 1650971.9923 |  | 610608.4446 | 209849.0341 | 515572.9979 | 87527.0448 | 66335.5325 | 1489893.054 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721
|  |  | 107 | 107 | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 35 | 16 | 24 | 107 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | C3 | 163.2643 | 163.2643 | 227.058 | 558.6833 | 1170.627 | C3 | 1959.1715 | 2612.2286 | 13396.4211 | 6704.1992 | 9365.0164 | 34037.0368 |  | 3265.2858 | 2612.2286 | 12942.3051 | 6704.1992 | 2341.2541 | 27865.2729 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | C4 | 272.1071 | 272.1071 | 378.43 | 931.1388 | 1951.0451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12228 | 12228 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864 | [22 empty] | 599593.5472 | 223269.3587 | 557942.0179 | 98402.7457 | 280013.9892 | 1759221.6587 |  | 665606.7418 | 220689.7829 | 534237.1643 | 95795.5572 | 74139.7128 | 1590468.959 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592
| LV UGB and LV Pillar OD (not at s/s) |  | 180 | 180 | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1 | 180 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3269 | 3269 | 3269 | 3269 | 3269 | C1 | 62.8302 | 62.8302 | 87.3804 | 215.0021 | 450.5009 | C1 | 10618.3004 | 0 | 87.3804 | 0 | 0 | 10705.6808 |  | 11246.6022 | 0 | 87.3804 | 0 | 0 | 11333.9826 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031
|  |  | 11974 | 11974 | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 0 | 0 | 0 | 0 | 0 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 4670 | 4670 | 4670 | 4670 | 4670 | C2 | 89.7574 | 89.7574 | 124.8291 | 307.1459 | 643.5727 | C2 | 196927.7356 | 226727.1924 | 865065.663 | 921.4377 | 231686.172 | 1521328.2007 |  | 205364.9312 | 226727.1924 | 865065.663 | 921.4377 | 146091.0029 | 1444170.2272 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959
|  |  | 179 | 179 | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 114 | 18 | 24 | 179 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7005 | 7005 | 7005 | 7005 | 7005 | C3 | 134.6361 | 134.6361 | 187.2437 | 460.7188 | 965.359 | C3 | 942.4527 | 3904.4469 | 21720.2634 | 7371.5016 | 965.359 | 34904.0237 |  | 2423.4498 | 3904.4469 | 21720.2634 | 7371.5016 | 0 | 35419.6617 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 11675 | 11675 | 11675 | 11675 | 11675 | C4 | 224.3935 | 224.3935 | 312.0727 | 767.8647 | 1608.9317 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12333 | 12333 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111 | [22 empty] | 208488.4887 | 230631.6393 | 886873.3068 | 8292.9393 | 232651.531 | 1566937.9051 |  | 219034.9832 | 230631.6393 | 886873.3068 | 8292.9393 | 146091.0029 | 1490923.8715 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 |  | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 700 | 700 | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 98 | 163 | 72 | 120 | 700 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | C1 | 564.9671 | 564.9671 | 786.1945 | 1934.1972 | 4052.6036 | C1 | 169490.1432 | 35592.9301 | 193403.8539 | 96709.8594 | 158051.5416 | 653248.3282 |  | 176834.7161 | 35592.9301 | 192617.6594 | 94775.6622 | 121578.109 | 621399.0767 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061
|  |  | 1868 | 1868 | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 255 | 417 | 253 | 369 | 1868 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 62956 | 62956 | 62956 | 62956 | 62956 | C2 | 807.0959 | 807.0959 | 1123.135 | 2763.1388 | 5789.4338 | C2 | 506856.2378 | 149312.7452 | 824381.1194 | 392365.7153 | 706310.9187 | 2579226.7363 |  | 573038.1032 | 149312.7452 | 822134.8493 | 384076.2988 | 590522.2435 | 2519084.24 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133
|  |  | 455 | 455 | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 57 | 103 | 74 | 112 | 455 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 94434 | 94434 | 94434 | 94434 | 94434 | C3 | 1210.6439 | 1210.6439 | 1684.7026 | 4144.7083 | 8684.1506 | C3 | 116221.8125 | 56900.2624 | 338625.2146 | 116051.8313 | 477628.2852 | 1105427.4059 |  | 161015.636 | 56900.2624 | 338625.2146 | 116051.8313 | 399470.9294 | 1072063.8737 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307
|  |  | 23 | 23 | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 6 | 6 | 1 | 23 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 157390 | 157390 | 157390 | 157390 | 157390 | C4 | 2017.7398 | 2017.7398 | 2807.8376 | 6907.8471 | 14473.5844 | C4 | 4035.4796 | 6053.2194 | 33694.0512 | 6907.8471 | 72367.922 | 123058.5193 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906
|  |  | 3046 | 3046 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602 | [22 empty] | 796603.673 | 247859.157 | 1390104.239 | 612035.2531 | 1414358.6676 | 4460960.9897 |  | 925012.6339 | 247859.157 | 1387071.7744 | 601811.6394 | 1111571.2819 | 4273326.4866 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407
| HV Switchgear (GM) - Distribution |  | 669 | 669 | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 18 | 2 | 5 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 36 | 2 | 0 | 5 | 669 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | C1 | 136.001 | 136.001 | 189.2556 | 465.6071 | 975.5577 | C1 | 87040.6208 | 2856.0204 | 1324.7895 | 0 | 0 | 91221.4307 |  | 87584.6247 | 2448.0175 | 1324.7895 | 0 | 0 | 91357.4316 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417
|  |  | 14652 | 14652 | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 0 | 0 | 0 | 0 | 0 | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 0 | 0 | 0 | 0 | 0 | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 15155 | 15155 | 15155 | 15155 | 15155 | C2 | 194.2871 | 194.2871 | 270.3652 | 665.153 | 1393.6538 | C2 | 1117539.3992 | 665433.3175 | 904912.3244 | 580013.3724 | 1754610.1342 | 5022508.5477 |  | 1188065.6165 | 648724.6269 | 889771.8732 | 578683.0665 | 1445218.9906 | 4750464.1737 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762
|  |  | 1431 | 1431 | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 335 | 354 | 164 | 513 | 1431 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | C3 | 291.4307 | 291.4307 | 405.5478 | 997.7294 | 2090.4807 | C3 | 38760.2765 | 107246.4792 | 167896.7892 | 236461.8737 | 589515.5574 | 1139880.976 |  | 53040.3783 | 105789.3259 | 166274.598 | 236461.8737 | 499624.8873 | 1061191.0633 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406
|  |  | 50 | 50 | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 1 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 26 | 50 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | C4 | 485.7177 | 485.7177 | 675.913 | 1662.8824 | 3484.1345 | C4 | 6800.0485 | 1457.1532 | 4055.478 | 8314.4119 | 76650.959 | 97278.0506 |  | 10200.0727 | 1457.1532 | 0 | 8314.4119 | 73166.8245 | 93138.4624 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723
|  |  | 16802 | 16802 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 0 | 0 | 0 | 0 | 0 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 0 | 0 | 0 | 0 | 0 |  | 4840 | 4406 | 3318 | 1336 | 2902 | [22 empty] | 1250140.345 | 776992.9703 | 1078189.3811 | 824789.658 | 2420776.6506 | 6350889.0049 |  | 1338890.6922 | 758419.1236 | 1057371.2607 | 823459.3521 | 2018010.7024 | 5996151.131 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469
| HV Transformer (GM) |  | 2220 | 2220 | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 319 | 682 | 114 | 283 | 2220 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | C1 | 219.1926 | 219.1926 | 304.8396 | 750.0674 | 1571.6404 | C1 | 204506.6659 | 89211.3752 | 183513.4464 | 54004.8519 | 311184.7921 | 842421.1316 |  | 223795.6119 | 88115.4123 | 181379.5691 | 54004.8519 | 204313.2473 | 751608.6927 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407
|  |  | 8983 | 8983 | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 0 | 0 | 0 | 0 | 0 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 16292 | 16292 | 16292 | 16292 | 16292 | C2 | 313.1322 | 313.1322 | 435.4852 | 1071.5248 | 2245.2005 | C2 | 1133538.7088 | 600900.7686 | 1128777.5347 | 233592.4151 | 1356101.1141 | 4452910.5413 |  | 1234367.2901 | 592446.1981 | 1110051.6728 | 233592.4151 | 857666.5986 | 4028124.1748 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606
|  |  | 1848 | 1848 | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 360 | 525 | 111 | 126 | 1848 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 24438 | 24438 | 24438 | 24438 | 24438 | C3 | 469.6984 | 469.6984 | 653.2277 | 1607.2873 | 3367.8008 | C3 | 427425.5076 | 154530.7604 | 327920.3255 | 43396.756 | 245849.4569 | 1199122.8065 |  | 456546.8059 | 151712.5703 | 316162.2262 | 43396.756 | 141447.6328 | 1109265.9911 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666
|  |  | 14 | 14 | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 4 | 0 | 2 | 14 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 40730 | 40730 | 40730 | 40730 | 40730 | C4 | 782.8306 | 782.8306 | 1088.7129 | 2678.8121 | 5613.0013 | C4 | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499
|  |  | 13065 | 13065 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 0 | 0 | 0 | 0 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 0 | 0 | 0 | 0 | 0 |  | 4522 | 2268 | 4202 | 708 | 1365 | [22 empty] | 1769385.0353 | 847774.2266 | 1643477.4453 | 333672.8352 | 1918748.3644 | 6513057.9068 |  | 1918623.8609 | 835405.5031 | 1610859.6068 | 333672.8352 | 1209040.48 | 5907602.2861 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669
| HV UG Cable |  | 1411.786 | 1411.786 | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 23093 | 23093 | 23093 | 23093 | 23093 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4500.517 | 4500.517 | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 32990 | 32990 | 32990 | 32990 | 32990 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1028.333 | 1028.333 | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 49485 | 49485 | 49485 | 49485 | 49485 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 82475 | 82475 | 82475 | 82475 | 82475 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6940.636 | 6940.636 |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | C1 | 61.436 | 61.436 | 85.4928 | 210.3297 | 440.6907 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 211011 | 211011 | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 0 | 0 | 0 | 0 | 0 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 0 | 0 | 0 | 0 | 0 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6846 | 6846 | 6846 | 6846 | 6846 | C2 | 87.7657 | 87.7657 | 122.1326 | 300.4709 | 629.5582 | C2 | 2581102.0595 | 12844337.5906 | 580984.9685 | 5771145.3446 | 7032164.6472 | 28809734.6103 |  | 3199411.5569 | 12844425.3563 | 538604.9424 | 5459556.9798 | 3543153.3245 | 25585152.1598 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296
|  |  | 2291 | 2291 | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10269 | 10269 | 10269 | 10269 | 10269 | C3 | 131.6486 | 131.6486 | 183.199 | 450.7064 | 944.3372 | C3 | 41995.897 | 209189.5936 | 9526.3459 | 94197.6397 | 113320.4688 | 468229.945 |  | 52132.8377 | 209189.5936 | 8793.5501 | 88789.1628 | 57604.5716 | 416509.7158 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17115 | 17115 | 17115 | 17115 | 17115 | C4 | 219.4143 | 219.4143 | 305.3316 | 751.1773 | 1573.8954 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 213302 | 213302 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597 | [22 empty] | 2623097.9565 | 13053527.1842 | 590511.3144 | 5865342.9843 | 7145485.116 | 29277964.5554 |  | 3251544.3946 | 13053614.9499 | 547398.4925 | 5548346.1426 | 3600757.8961 | 26001661.8756 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 |  | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 369 | 369 | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 80 | 31 | 12 | 36 | 369 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | C1 | 910.9866 | 910.9866 | 1267.7068 | 3118.8146 | 6534.6592 | C1 | 242322.4452 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 425963.7075 |  | 246877.3784 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 430518.6407 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432
|  |  | 475 | 475 | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 91 | 69 | 36 | 122 | 475 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 101514 | 101514 | 101514 | 101514 | 101514 | C2 | 1301.4095 | 1301.4095 | 1811.0098 | 4455.4495 | 9335.2274 | C2 | 275898.8098 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 912299.212 |  | 282405.8572 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 918806.2594 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527
|  |  | 127 | 127 | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 152271 | 152271 | 152271 | 152271 | 152271 | C3 | 1952.1142 | 1952.1142 | 2716.5146 | 6683.1742 | 14002.8412 | C3 | 81988.7972 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 417338.266 |  | 91749.3683 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 427098.8371 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266
|  |  | 55 | 55 | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 253785 | 253785 | 253785 | 253785 | 253785 | C4 | 3253.5237 | 3253.5237 | 4527.5244 | 11138.6236 | 23338.0686 | C4 | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924
|  |  | 1026 | 1026 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 0 | 0 | 0 | 0 | 0 |  | 409 | 208 | 117 | 81 | 211 | [22 empty] | 678294.621 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 1998176.502 |  | 699117.1727 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 2018999.0537 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149
| EHV Transformer |  | 246 | 246 | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | C1 | 3379.4828 | 3379.4828 | 4702.806 | 11569.8517 | 24241.594 | C1 | 395399.4834 | 84487.0691 | 286871.164 | 300816.1436 | 363623.9099 | 1431197.77 |  | 425814.8283 | 84487.0691 | 277465.5521 | 266106.5886 | 315140.7219 | 1369014.76 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593
|  |  | 248 | 248 | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 376586 | 376586 | 376586 | 376586 | 376586 | C2 | 4827.8325 | 4827.8325 | 6718.2942 | 16528.3595 | 34630.8486 | C2 | 241391.626 | 120695.813 | 866659.957 | 512379.1457 | 346308.4856 | 2087435.0273 |  | 265530.7886 | 120695.813 | 866659.957 | 512379.1457 | 277046.7885 | 2042312.4928 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399
|  |  | 73 | 73 | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 564879 | 564879 | 564879 | 564879 | 564879 | C3 | 7241.7488 | 7241.7488 | 10077.4414 | 24792.5393 | 51946.2728 | C3 | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673
|  |  | 30 | 30 | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 941465 | 941465 | 941465 | 941465 | 941465 | C4 | 12069.5813 | 12069.5813 | 16795.7356 | 41320.8988 | 86577.1214 | C4 | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656
|  |  | 597 | 597 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 0 | 0 | 0 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 179 | 88 | 123 | 66 | 141 | [22 empty] | 1083365.6175 | 234149.8772 | 1580142.8052 | 1110705.7611 | 865771.214 | 4874135.275 |  | 1137920.125 | 234149.8772 | 1570737.1933 | 1075996.2061 | 748026.3289 | 4766829.7304 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C1 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | C1 | 553.5916 | 553.5916 | 18758.3105 | 45788.1803 | 95940.8181 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 34 | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 |  |  | C2 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C2 | 8424 | 8424 | 8424 | 8424 | 8424 | C2 | 790.8451 | 790.8451 | 26797.5864 | 65411.6861 | 137058.3115 | C2 | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C3 | 12636 | 12636 | 12636 | 12636 | 12636 | C3 | 1186.2677 | 1186.2677 | 40196.3796 | 98117.5291 | 205587.4673 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C4 | 21060 | 21060 | 21060 | 21060 | 21060 | C4 | 1977.1128 | 1977.1128 | 66993.966 | 163529.2152 | 342645.7788 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 34 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 | [22 empty] | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917
| EHV UG Cable (Oil) |  | 21.926 | 21.926 | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | C1 | 301.5188 | 301.5188 | 10223.8139 | 24955.7384 | 52290.2374 | C1 | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936
|  |  | 29.901 | 29.901 | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 72272 | 72272 | 72272 | 72272 | 72272 | C2 | 430.7411 | 430.7411 | 14605.4485 | 35651.0549 | 74700.3392 | C2 | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205
|  |  | 8.451 | 8.451 | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 108408 | 108408 | 108408 | 108408 | 108408 | C3 | 646.1117 | 646.1117 | 21908.1727 | 53476.5823 | 112050.5088 | C3 | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 180680 | 180680 | 180680 | 180680 | 180680 | C4 | 1076.8528 | 1076.8528 | 36513.6212 | 89127.6372 | 186750.848 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 60.278 | 60.278 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801 | [22 empty] | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175
| EHV UG Cable (Non Pressurised) |  | 241.211 | 241.211 | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 383.855 | 383.855 | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 50665 | 50665 | 50665 | 50665 | 50665 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 188.435 | 188.435 | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10.863 | 10.863 | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 824.364 | 824.364 |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 125 | 125 | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 7 | 0 | -7 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | C1 | 81.561 | 81.561 | 81.561 | 4130.3727 | 14151.6049 | C1 | 2528.3913 | 6524.8809 | 978.7321 | 24782.2362 | 0 | 34814.2406 |  | 2528.3913 | 6280.1978 | 897.1711 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2202.1473 | 5627.7098 | 1468.0982 | 28912.609 | 56606.4194 | 94816.9836 |  | 2202.1473 | 6198.6368 | 1468.0982 | 0 | 56606.4194 | 66475.3017
|  |  | 299 | 299 | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 9 | 0 | -9 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 10 | 0 | -10 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 219841 | 219841 | 219841 | 219841 | 219841 | C2 | 116.5157 | 116.5157 | 116.5157 | 5900.5324 | 20216.5784 | C2 | 7690.0382 | 18759.0325 | 6874.4281 | 47204.2595 | 121299.4702 | 201827.2285 |  | 8389.1326 | 18992.064 | 6757.9123 | 35403.1946 | 0 | 69542.3035 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 8039.5854 | 20390.2527 | 6408.3651 | 0 | 0 | 34838.2033 |  | 6757.9123 | 20506.7685 | 5942.3022 | 59005.3244 | 80866.3134 | 173078.6209 |  | 6757.9123 | 21671.9258 | 5942.3022 | 0 | 80866.3134 | 115238.4538
|  |  | 65 | 65 | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 2 | 0 | -2 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 3 | 0 | -3 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | C3 | 174.7736 | 174.7736 | 174.7736 | 8850.7987 | 30324.8675 | C3 | 2796.3775 | 6990.9438 | 1048.6416 | 26552.396 | 0 | 37388.3589 |  | 2796.3775 | 7340.491 | 1048.6416 | 8850.7987 | 0 | 20036.3087 |  | 2796.3775 | 5942.3022 | 2097.2831 | 17701.5973 | 30324.8675 | 58862.4278 |  | 2796.3775 | 6291.8494 | 2097.2831 | 0 | 30324.8675 | 41510.3776 |  | 2446.8303 | 5767.5286 | 2446.8303 | 26552.396 | 30324.8675 | 67538.4528 |  | 2446.8303 | 6291.8494 | 2446.8303 | 0 | 30324.8675 | 41510.3776
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | C4 | 291.2893 | 291.2893 | 291.2893 | 14751.3311 | 50541.4459 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 11 | 0 | -11 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 20 | 0 | -20 | 0 |  | 99 | 278 | 83 | 20 | 9 | [22 empty] | 13014.807 | 32274.8572 | 8901.8018 | 98538.8917 | 121299.4702 | 274029.8279 |  | 13713.9014 | 32612.7528 | 8703.725 | 69036.2295 | 0 | 124066.6088 |  | 13038.1102 | 30993.1842 | 10136.8685 | 95588.6255 | 58628.0772 | 208384.8656 |  | 13038.1102 | 32391.3729 | 10136.8685 | 24782.2362 | 58628.0772 | 138976.6651 |  | 11406.89 | 31902.0069 | 9857.2308 | 114470.3293 | 167797.6004 | 335434.0573 |  | 11406.89 |  | 9857.2308 |  | 167797.6004 | 189061.7211
| EHV OHL Support - Poles |  | 4894 | 4894 | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | C1 | 112.0045 | 112.0045 | 155.8627 | 383.4538 | 803.4269 | C1 | 52418.1032 | 343181.7696 | 38653.9565 | 233906.7954 | 405730.6007 | 1073891.2254 |  | 66194.656 | 343181.7696 | 37718.7802 | 226621.1739 | 326191.3344 | 999907.7141 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472
|  |  | 22777 | 22777 | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 0 | 0 | 0 | 0 | 0 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12481 | 12481 | 12481 | 12481 | 12481 | C2 | 160.0064 | 160.0064 | 222.661 | 547.7911 | 1147.7528 | C2 | 348493.9828 | 2281851.5556 | 257396.1622 | 1552439.9491 | 2698366.7388 | 7138548.3884 |  | 440337.6678 | 2281851.5556 | 250938.9921 | 1505329.9153 | 2168104.9636 | 6646563.0945 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714
|  |  | 1936 | 1936 | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | C3 | 240.0096 | 240.0096 | 333.9916 | 821.6866 | 1721.6291 | C3 | 44401.7815 | 290891.6716 | 33065.1644 | 197204.7924 | 344325.828 | 909889.2379 |  | 56162.2534 | 290891.6716 | 32063.1898 | 191452.986 | 277182.2915 | 847752.3922 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | C4 | 400.0161 | 400.0161 | 556.6526 | 1369.4777 | 2869.3819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29607 | 29607 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 0 | 0 | 0 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 0 | 0 | 0 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693 | [22 empty] | 445313.8675 | 2915924.9968 | 329115.2832 | 1983551.5369 | 3448423.1674 | 9122328.8518 |  | 562694.5772 | 2915924.9968 | 320720.962 | 1923404.0752 | 2771478.5896 | 8494223.2008 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 427 | 427 | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | C1 | 238.7737 | 238.7737 | 332.7056 | 818.1404 | 1714.4379 | C1 | 71632.0962 | 0 | 43917.1434 | 0 | 8572.1893 | 124121.4289 |  | 69244.3597 | 0 | 43917.1434 | 0 | 8572.1893 | 121733.6924 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462
|  |  | 456 | 456 | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 102434 | 102434 | 102434 | 102434 | 102434 | C2 | 341.1052 | 341.1052 | 475.2938 | 1168.7719 | 2449.1969 | C2 | 99943.8295 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 431151.8764 |  | 96873.8825 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 428081.9294 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562
|  |  | 55 | 55 | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 153651 | 153651 | 153651 | 153651 | 153651 | C3 | 511.6578 | 511.6578 | 712.9406 | 1753.1579 | 3673.7954 | C3 | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61
|  |  | 87 | 87 | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 256085 | 256085 | 256085 | 256085 | 256085 | C4 | 852.7631 | 852.7631 | 1188.2344 | 2921.9298 | 6122.9924 | C4 | 27288.4176 | 0 | 26141.1568 | 99345.6149 | 0 | 152775.1893 |  | 26435.6545 | 0 | 26141.1568 | 99345.6149 | 0 | 151922.4263 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262
|  |  | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419 | [22 empty] | 199376.0011 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 906945.1046 |  | 193065.5545 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 900634.658 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385
| EHV OHL Conductor (Tower Lines) |  | 40.481 | 40.481 | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | C1 | 5.8423 | 5.8423 | 8.0332 | 20.4481 | 43.0871 | C1 | 236.5143 | 0 | 3.7515 | 0 | 0 | 240.2658 |  | 233.8035 | 0 | 3.7113 | 0 | 0 | 237.5148 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505
|  |  | 52.696 | 52.696 | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 104327 | 104327 | 104327 | 104327 | 104327 | C2 | 8.3462 | 8.3462 | 11.476 | 29.2116 | 61.5529 | C2 | 232.0232 | 0 | 292.729 | 0 | 0 | 524.7523 |  | 229.3608 | 0 | 289.3666 | 0 | 0 | 518.7274 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996
|  |  | 6.374 | 6.374 | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | C3 | 12.5192 | 12.5192 | 17.214 | 43.8173 | 92.3294 | C3 | 1.6275 | 0 | 108.7406 | 0 | 0 | 110.3681 |  | 1.615 | 0 | 107.5011 | 0 | 0 | 109.1161 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543
|  |  | 8.199 | 8.199 | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | C4 | 20.8654 | 20.8654 | 28.6899 | 73.0289 | 153.8823 | C4 | 106.6639 | 66.4146 | 0 | 0 | 0 | 173.0785 |  | 105.4329 | 65.6425 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914
|  |  | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0 | [22 empty] | 576.829 | 66.4146 | 405.2211 | 0 | 0 | 1048.4646 |  | 570.2122 | 65.6425 | 400.5791 | 0 | 0 | 1036.4338 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 |  | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 |  | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 |  | 2066135.4127 | 3635880.177 | 2220137.3879 | 4615012.423 | 13295492.0857 | 25832657.4863 |  | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 |  | 1577061.3003 | 3770609.5321 | 1920577.4963 | 3724706.5147 | 19650715.4154 | 30643670.2588
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 72 | 72 | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | C1 | 2255.4713 | 2255.4713 | 3138.659 | 7721.7345 | 16178.8722 | C1 | 110518.0945 | 11277.3566 | 37663.9079 | 30886.9379 | 32357.7445 | 222704.0414 |  | 112773.5658 | 11277.3566 | 37663.9079 | 30886.9379 | 16178.8722 | 208780.6405 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821
|  |  | 61 | 61 | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 2 | 3 | 5 | 61 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 251334 | 251334 | 251334 | 251334 | 251334 | C2 | 3222.1019 | 3222.1019 | 4483.7986 | 11031.0493 | 23112.6746 | C2 | 112773.5658 | 9666.3056 | 35870.3885 | 22062.0985 | 46225.3493 | 226597.7077 |  | 154660.8902 | 9666.3056 | 35870.3885 | 22062.0985 | 0 | 222259.6829 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314
|  |  | 26 | 26 | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 377001 | 377001 | 377001 | 377001 | 377001 | C3 | 4833.1528 | 4833.1528 | 6725.6978 | 16546.5739 | 34669.012 | C3 | 67664.1395 | 9666.3056 | 20177.0935 | 82732.8694 | 69338.0239 | 249578.432 |  | 72497.2923 | 9666.3056 | 20177.0935 | 82732.8694 | 34669.012 | 219742.5729 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506
|  |  | 7 | 7 | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 628335 | 628335 | 628335 | 628335 | 628335 | C4 | 8055.2547 | 8055.2547 | 11209.4964 | 27577.6231 | 57781.6866 | C4 | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829
|  |  | 166 | 166 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 45 | 12 | 7 | 20 | [22 empty] | 347342.5827 | 30609.9679 | 93711.3899 | 135681.9059 | 147921.1177 | 755266.964 |  | 396318.5312 | 30609.9679 | 93711.3899 | 135681.9059 | 50847.8842 | 707169.6791 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296
| 132kV Transformer |  | 27 | 27 | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | C1 | 21313.7705 | 21313.7705 | 29659.7243 | 72968.9069 | 152887.2336 | C1 | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697
|  |  | 48 | 48 | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 14 | 9 | 4 | 48 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2375058 | 2375058 | 2375058 | 2375058 | 2375058 | C2 | 30448.2436 | 30448.2436 | 42371.0347 | 104241.2956 | 218410.3337 | C2 | 548068.3841 | 213137.7049 | 720307.5902 | 521206.4781 | 0 | 2002720.1573 |  | 608964.8712 | 213137.7049 | 720307.5902 | 416965.1825 | 0 | 1959375.3488 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961
|  |  | 13 | 13 | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3562587 | 3562587 | 3562587 | 3562587 | 3562587 | C3 | 45672.3653 | 45672.3653 | 63556.5521 | 156361.9434 | 327615.5005 | C3 | 182689.4614 | 91344.7307 | 254226.2083 | 469085.8303 | 0 | 997346.2307 |  | 228361.8267 | 91344.7307 | 254226.2083 | 312723.8869 | 0 | 886656.6526 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494
|  |  | 6 | 6 | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5937645 | 5937645 | 5937645 | 5937645 | 5937645 | C4 | 76120.6089 | 76120.6089 | 105927.5868 | 260603.2391 | 546025.8342 | C4 | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948
|  |  | 94 | 94 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8 | [22 empty] | 1147898.7822 | 499351.1944 | 1529594.3534 | 1063261.2153 | 0 | 4240105.5453 |  | 1254467.6347 | 499351.1944 | 1529594.3534 | 802657.9763 | 0 | 4086071.1587 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 24.121 | 24.121 | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | C1 | 687.9878 | 687.9878 | 23328.0975 | 56942.5365 | 119312.7891 | C1 | 2223.5767 | 11940.7168 | 82418.1684 | 168208.2529 | 0 | 264790.7147 |  | 2223.5767 | 11940.7168 | 82418.1684 | 0 | 0 | 96582.4619 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285
|  |  | 11.91 | 11.91 | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 164906 | 164906 | 164906 | 164906 | 164906 | C2 | 982.8398 | 982.8398 | 33325.8535 | 81346.4807 | 170446.8416 | C2 | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244
|  |  | 25.639 | 25.639 | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 247359 | 247359 | 247359 | 247359 | 247359 | C3 | 1474.2596 | 1474.2596 | 49988.7803 | 122019.7211 | 255670.2624 | C3 | 11561.1441 | 25647.695 | 0 | 78824.7398 | 0 | 116033.5789 |  | 11561.1441 | 25647.695 | 0 | 48807.8884 | 0 | 86016.7275 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 412265 | 412265 | 412265 | 412265 | 412265 | C4 | 2457.0994 | 2457.0994 | 83314.6338 | 203366.2019 | 426117.104 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 61.67 | 61.67 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4 | [22 empty] | 15226.5467 | 47852.2074 | 82418.1684 | 247032.9927 | 0 | 392529.9152 |  | 15226.5467 | 47852.2074 | 82418.1684 | 48807.8884 | 0 | 194304.8109 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837
| 132kV UG Cable (Non Pressurised) |  | 7.356 | 7.356 | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.671 | 9.671 | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 1610892 | 1610892 | 1610892 | 1610892 | 1610892 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2.775 | 2.775 | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 2416338 | 2416338 | 2416338 | 2416338 | 2416338 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.253 | 0.253 | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 4027230 | 4027230 | 4027230 | 4027230 | 4027230 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20.055 | 20.055 |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1148 | 1148 | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 17 | 0 | -17 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 43 | 0 | -43 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | C1 | 293.7956 | 293.7956 | 293.7956 | 14878.2548 | 50976.3155 | C1 | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 87551.1013 | 198605.854 | 37605.8422 | 669521.4649 | 50976.3155 | 1044260.5779 |  | 87551.1013 | 203600.3799 | 37605.8422 | 416591.1337 | 50976.3155 | 796324.7727 |  | 78443.4364 | 207125.9276 | 36724.4552 | 714156.2292 | 152928.9466 | 1189378.9952 |  | 78443.4364 | 219759.1402 | 36724.4552 | 74391.2739 | 152928.9466 | 562247.2524
|  |  | 1252 | 1252 | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 37 | 0 | -37 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 69 | 0 | -69 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 791902 | 791902 | 791902 | 791902 | 791902 | C2 | 419.7081 | 419.7081 | 419.7081 | 21254.6497 | 72823.3079 | C2 | 125912.418 | 320237.2498 | 53302.9236 | 1254024.3311 | 218469.9238 | 1971946.8463 |  | 127171.5422 | 320237.2498 | 53302.9236 | 1254024.3311 | 0 | 1754736.0467 |  | 125073.0019 | 316879.5853 | 52463.5075 | 1487825.4776 | 291293.2317 | 2273534.804 |  | 125073.0019 | 332408.7835 | 52463.5075 | 701403.4394 | 291293.2317 | 1502641.964 |  | 123394.1696 | 311843.0886 | 55401.4639 | 1509080.1273 | 873879.695 | 2873598.5445 |  | 123394.1696 | 340802.9447 | 55401.4639 | 42509.2994 | 873879.695 | 1435987.5727
|  |  | 501 | 501 | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 9 | 0 | -9 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 12 | 0 | -12 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1187853 | 1187853 | 1187853 | 1187853 | 1187853 | C3 | 629.5621 | 629.5621 | 629.5621 | 31881.9745 | 109234.9619 | C3 | 28330.2941 | 230419.7249 | 28330.2941 | 1434688.8534 | 0 | 1721769.1664 |  | 28330.2941 | 249306.5876 | 28330.2941 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 236085.7838 | 50994.5293 | 191291.8471 | 0 | 502925.0817 |  | 22034.6731 | 219717.1694 | 63585.7711 | 446347.6433 | 218469.9238 | 970155.1807 |  | 22034.6731 | 227271.9145 | 63585.7711 | 63763.949 | 218469.9238 | 595126.2315
|  |  | 187 | 187 | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 1979755 | 1979755 | 1979755 | 1979755 | 1979755 | C4 | 1049.2702 | 1049.2702 | 1049.2702 | 53136.6242 | 182058.2698 | C4 | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181
|  |  | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 63 | 0 | -63 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 124 | 0 | -124 | 0 |  | 656 | 1891 | 391 | 133 | 17 | [22 empty] | 323720.8267 | 862122.326 | 122428.8411 | 3283843.3756 | 218469.9238 | 4810585.2931 |  | 324979.9509 | 881009.1887 | 122428.8411 | 2327384.14 | 0 | 3655802.1207 |  | 303281.0442 | 855029.2598 | 162049.282 | 2635576.5603 | 342269.5472 | 4298205.6935 |  | 303281.0442 | 881219.0428 | 162049.282 | 1309286.4203 | 342269.5472 | 2998105.3364 |  | 286828.4882 | 837317.5797 | 190337.6052 | 2669583.9998 | 1245278.5654 | 5229346.2384 |  | 286828.4882 | 886465.3935 | 190337.6052 | 180664.5223 | 1245278.5654 | 2789574.5747
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1974 | 1974 | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | C1 | 24.2662 | 24.2662 | 33.366 | 78.8651 | 166.8301 | C1 | 16234.0878 | 15239.1736 | 14013.7305 | 3785.5272 | 34867.4961 | 84140.0152 |  | 21378.5222 | 15239.1736 | 14013.7305 | 3548.9318 | 0 | 54180.3581 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348
|  |  | 1409 | 1409 | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 433325 | 433325 | 433325 | 433325 | 433325 | C2 | 34.666 | 34.666 | 47.6658 | 112.6645 | 238.3288 | C2 | 26727.486 | 10607.796 | 11678.1088 | 4619.2445 | 10963.1225 | 64595.7578 |  | 28426.12 | 10607.796 | 11678.1088 | 4281.251 | 0 | 54993.2758 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025
|  |  | 945 | 945 | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | C3 | 51.999 | 51.999 | 71.4986 | 168.9967 | 357.4931 | C3 | 24543.528 | 13623.738 | 11940.2704 | 1520.9707 | 12512.2594 | 64140.7665 |  | 26363.493 | 13623.738 | 11940.2704 | 1520.9707 | 0 | 53448.4721 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402
|  |  | 436 | 436 | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | C4 | 86.665 | 86.665 | 119.1644 | 281.6612 | 595.8219 | C4 | 26779.485 | 8406.505 | 3098.2738 | 0 | 2383.2875 | 40667.5513 |  | 27126.145 | 8406.505 | 3098.2738 | 0 | 0 | 38630.9238 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631
|  |  | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924 | [22 empty] | 94284.5868 | 47877.2126 | 40730.3834 | 9925.7424 | 60726.1655 | 253544.0907 |  | 103294.2802 | 47877.2126 | 40730.3834 | 9351.1535 | 0 | 201253.0297 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407
| 132kV OHL Conductor (Tower Lines) |  | 582.743 | 582.743 | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | C1 | 24.2866 | 24.2866 | 33.3941 | 85.003 | 179.1136 | C1 | 1808.5248 | 3592.0586 | 11976.176 | 286.1202 | 0 | 17662.8797 |  | 1802.8417 | 3580.7897 | 11945.2531 | 286.1202 | 0 | 17615.0047 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952
|  |  | 372.373 | 372.373 | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 433689 | 433689 | 433689 | 433689 | 433689 | C2 | 34.6951 | 34.6951 | 47.7058 | 121.4329 | 255.8765 | C2 | 5409.4549 | 2529.3783 | 6900.1655 | 0 | 0 | 14838.9987 |  | 5392.489 | 2521.4332 | 6882.7051 | 0 | 0 | 14796.6273 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577
|  |  | 282.328 | 282.328 | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | C3 | 52.0427 | 52.0427 | 71.5587 | 182.1494 | 383.8148 | C3 | 1710.2786 | 5623.4197 | 10181.9422 | 0 | 0 | 17515.6405 |  | 1704.9182 | 5605.7773 | 10150.8141 | 0 | 0 | 17461.5096 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106
|  |  | 131.686 | 131.686 | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | C4 | 86.7378 | 86.7378 | 119.2645 | 303.5823 | 639.6913 | C4 | 8338.7119 | 1881.6031 | 1702.0233 | 0 | 0 | 11922.3383 |  | 8312.5171 | 1875.7049 | 1696.6564 | 0 | 0 | 11884.8784 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792
|  |  | 1369.13 | 1369.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611 | [22 empty] | 17266.9702 | 13626.4598 | 30760.307 | 286.1202 | 0 | 61939.8572 |  | 17212.766 | 13583.705 | 30675.4288 | 286.1202 | 0 | 61758.0201 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 |  | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 |  | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 |  | 1859432.4783 | 1412561.4995 | 3046764.4855 | 2833412.9536 | 1159014.331 | 10311185.7479 |  | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 |  | 1586199.249 | 1535924.2936 | 3021390.8766 | 2173525.4806 | 4336959.0383 | 12653998.9381
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 519588.883 | 519588.883 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 0 | 74 | 0 | -74 | 0 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 0 | 144 | 0 | -144 | 0 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 |  | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 |  | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 |  | 11429503.3005 | 29046758.4499 | 11703564.5821 | 22739632.2485 | 36728167.1884 | 111647625.7694 |  | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 |  | 8379358.875 | 29342351.4213 | 11180183.8339 | 22867416.6374 | 59909425.7855 | 131678736.553
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 | LV Network | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 | HV Network | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 | EHV Network | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 | EHV Network | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 | EHV Network | 2066135.4127 | 3635880.177 | 2220137.3879 | 4615012.423 | 13295492.0857 | 25832657.4863 | EHV Network | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 | EHV Network | 1577061.3003 | 3770609.5321 | 1920577.4963 | 3724706.5147 | 19650715.4154 | 30643670.2588
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 | 132kV Network | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 | 132kV Network | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 | 132kV Network | 1859432.4783 | 1412561.4995 | 3046764.4855 | 2833412.9536 | 1159014.331 | 10311185.7479 | 132kV Network | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 | 132kV Network | 1586199.249 | 1535924.2936 | 3021390.8766 | 2173525.4806 | 4336959.0383 | 12653998.9381
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 | Total | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 | Total | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 | Total | 11429503.3005 | 29046758.4499 | 11703564.5821 | 22739632.2485 | 36728167.1884 | 111647625.7694 | Total | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 | Total | 8379358.875 | 29342351.4213 | 11180183.8339 | 22867416.6374 | 59909425.7855 | 131678736.553
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWEST - HVP
Secondary deliverables RIIO-ED1 - HVP - Asset Replacement and Refurbishment driven | [50 empty] | Criticality weightings C1 to C4 | Criticality Rating Boundaries
SWEST | [49 empty] | C1 | 0.7 | Below 75% of average
[50 empty] | C2 | 1 | 75%-125%
[50 empty] | C3 | 1.5 | 125%-200%
[50 empty] | C4 | 2.5 | Over 200% of average
Price base (2012/13)
| ASSET CATEGORIES |  | ASSET REGISTER |  |  | End of DPCR5 (31 March 2015) with investment | [5 empty] | End of DPCR5 (31 March 2015) without investment | [5 empty] | Mid-Period Review (31 March 2019) planned investment | [5 empty] | Mid-Period Review (31 March 2019) without investment | [5 empty] | End of RIIO-ED1 (31 March 2023) planned investment | [5 empty] | End of RIIO-ED1 (31 March 2023) without investment | [8 empty] | Probability of Asset Failure | [5 empty] | Consequence of Asset Failure | [5 empty] | Probability of Asset Failure x Consequence of Asset Failure
Is it your current intention to have a health index for this asset category in the RIIO-ED1 control period.
|  |  | as at 31st March 2015 | as at 31st March 2023 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  |  |  |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | HI 1 | HI 2 | HI 3 | HI 4 | HI 5 |  | End of DPCR5 (without investment) | [6 empty] | Position at Beginning of RIIO-ED1 | [6 empty] | Mid Period (Without Investment) | [6 empty] | Mid Period (With Investment) | [6 empty] | End of RIIO-ED1 (Without Investment) | [6 empty] | End of RIIO-ED1 (With Investment)
| LV Network | [61 empty] | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total |  | 1 | 2 | 3 | 4 | 5 | Total
| LV Switchgear and Other |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Yes |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | No |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV UGB |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| LV OHL Support |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | 3411.1 | C1 | 43.7303 | 43.7303 | 60.854 | 149.7132 | 313.6848 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 | C2 | 23637 | 137079 | 3676 | 26775 | 7372 | 198539 | 16806 | 137079 | 4016 | 27795 | 12812 | 198508 | 0 | 0 | 0 | 0 | 0 | 0 | 13724 | 137079 | 4667 | 28616 | 14453 | 198539 | 0 | 0 | 0 | 0 | 0 | 0 | 3453 | 137079 | 5694 | 30523 | 21790 | 198539 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 4873 | 4873 | 4873 | 4873 | 4873 | C2 | 62.4719 | 62.4719 | 86.9343 | 213.876 | 448.1211 | C2 | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | 7309.5 | C3 | 93.7078 | 93.7078 | 130.4015 | 320.814 | 672.1816 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | 12182.5 | C4 | 156.1797 | 156.1797 | 217.3358 | 534.6899 | 1120.3027 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 198539 | 198539 |  | 23637 | 137079 | 3676 | 26775 | 7372 |  | 16806 | 137079 | 4016 | 27795 | 12812 |  | 0 | 0 | 0 | 0 | 0 |  | 13724 | 137079 | 4667 | 28616 | 14453 |  | 0 | 0 | 0 | 0 | 0 |  | 3453 | 137079 | 5694 | 30523 | 21790 | [22 empty] | 1049902.0792 | 8563580.0969 | 349128.2291 | 5944682.5861 | 5741327.277 | 21648620.2683 |  | 1476647.3548 | 8563580.0969 | 319570.5603 | 5726529.0967 | 3303548.6018 | 19389875.7106 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 857363.8066 | 8563580.0969 | 405722.4714 | 6120274.7575 | 6476693.9692 | 22423635.1018 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131 |  | 215715.3326 | 8563580.0969 | 495004.0181 | 6528136.2323 | 9764558.3332 | 25566994.0131
| LV Switchgear (at s/s) |  | 857 | 857 | C1 | 679 | 108 | 54 | 6 | 10 | 857 | 644 | 109 | 72 | 6 | 14 | 845 | 0 | 0 | 0 | 0 | 0 | 0 | 630 | 142 | 61 | 9 | 15 | 857 | 0 | 0 | 0 | 0 | 0 | 0 | 586 | 148 | 93 | 10 | 20 | 857 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | 3964.1 | C1 | 76.19 | 76.19 | 105.9604 | 260.7189 | 546.2926 | C1 | 49066.3613 | 8304.7102 | 7629.1483 | 1564.3131 | 7648.0967 | 74212.6296 |  | 51733.0114 | 8228.5202 | 5721.8612 | 1564.3131 | 5462.9262 | 72710.6321 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 47999.7013 | 10818.9803 | 6463.584 | 2346.4697 | 8194.3893 | 75823.1245 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819 |  | 44647.3412 | 11276.1203 | 9854.3165 | 2607.1886 | 10925.8524 | 79310.819
|  |  | 11264 | 11264 | C2 | 5610 | 1928 | 3406 | 235 | 85 | 11264 | 5040 | 1951 | 3547 | 242 | 337 | 11117 | 0 | 0 | 0 | 0 | 0 | 0 | 4521 | 2379 | 3682 | 320 | 362 | 11264 | 0 | 0 | 0 | 0 | 0 | 0 | 3782 | 2753 | 3435 | 474 | 820 | 11264 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 5663 | 5663 | 5663 | 5663 | 5663 | C2 | 108.8429 | 108.8429 | 151.372 | 372.4555 | 780.418 | C2 | 548568.0144 | 212352.4199 | 536916.4485 | 90134.2334 | 263000.8761 | 1650971.9923 |  | 610608.4446 | 209849.0341 | 515572.9979 | 87527.0448 | 66335.5325 | 1489893.054 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 492078.5701 | 258937.1639 | 557351.6672 | 119185.7632 | 282511.3269 | 1710064.4912 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721 |  | 411643.6965 | 299644.3936 | 519962.7857 | 176543.9117 | 639942.7846 | 2047737.5721
|  |  | 107 | 107 | C3 | 20 | 16 | 57 | 12 | 2 | 107 | 12 | 16 | 59 | 12 | 8 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 15 | 53 | 6 | 15 | 107 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 16 | 35 | 16 | 24 | 107 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | 8494.5 | C3 | 163.2643 | 163.2643 | 227.058 | 558.6833 | 1170.627 | C3 | 1959.1715 | 2612.2286 | 13396.4211 | 6704.1992 | 9365.0164 | 34037.0368 |  | 3265.2858 | 2612.2286 | 12942.3051 | 6704.1992 | 2341.2541 | 27865.2729 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 2938.7572 | 2448.9644 | 12034.0732 | 3352.0996 | 17559.4057 | 38333.3 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681 |  | 2612.2286 | 2612.2286 | 7947.0295 | 8938.9322 | 28095.0491 | 50205.4681
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | 14157.5 | C4 | 272.1071 | 272.1071 | 378.43 | 931.1388 | 1951.0451 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12228 | 12228 |  | 6309 | 2052 | 3517 | 253 | 97 |  | 5696 | 2076 | 3678 | 260 | 359 |  | 0 | 0 | 0 | 0 | 0 |  | 5169 | 2536 | 3796 | 335 | 392 |  | 0 | 0 | 0 | 0 | 0 |  | 4384 | 2917 | 3563 | 500 | 864 | [22 empty] | 599593.5472 | 223269.3587 | 557942.0179 | 98402.7457 | 280013.9892 | 1759221.6587 |  | 665606.7418 | 220689.7829 | 534237.1643 | 95795.5572 | 74139.7128 | 1590468.959 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 543017.0285 | 272205.1086 | 575849.3244 | 124884.3325 | 308265.1218 | 1824220.9158 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592 |  | 458903.2663 | 313532.7425 | 537764.1317 | 188090.0325 | 678963.6861 | 2177253.8592
| LV UGB and LV Pillar OD (not at s/s) |  | 180 | 180 | C1 | 179 | 0 | 1 | 0 | 0 | 180 | 169 | 0 | 1 | 0 | 0 | 170 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 1 | 0 | 180 | 0 | 0 | 0 | 0 | 0 | 0 | 179 | 0 | 0 | 0 | 1 | 180 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 3269 | 3269 | 3269 | 3269 | 3269 | C1 | 62.8302 | 62.8302 | 87.3804 | 215.0021 | 450.5009 | C1 | 10618.3004 | 0 | 87.3804 | 0 | 0 | 10705.6808 |  | 11246.6022 | 0 | 87.3804 | 0 | 0 | 11333.9826 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 215.0021 | 0 | 11461.6044 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031 |  | 11246.6022 | 0 | 0 | 0 | 450.5009 | 11697.1031
|  |  | 11974 | 11974 | C2 | 2288 | 2526 | 6930 | 3 | 227 | 11974 | 2194 | 2526 | 6930 | 3 | 360 | 12013 | 0 | 0 | 0 | 0 | 0 | 0 | 1929 | 2099 | 6959 | 741 | 246 | 11974 | 0 | 0 | 0 | 0 | 0 | 0 | 1410 | 1533 | 6200 | 1745 | 1086 | 11974 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 4670 | 4670 | 4670 | 4670 | 4670 | C2 | 89.7574 | 89.7574 | 124.8291 | 307.1459 | 643.5727 | C2 | 196927.7356 | 226727.1924 | 865065.663 | 921.4377 | 231686.172 | 1521328.2007 |  | 205364.9312 | 226727.1924 | 865065.663 | 921.4377 | 146091.0029 | 1444170.2272 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 173142.0246 | 188400.7826 | 868685.7069 | 227595.1119 | 158318.8842 | 1616142.5102 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959 |  | 126557.934 | 137598.0942 | 773940.42 | 535969.5955 | 698919.9522 | 2272985.9959
|  |  | 179 | 179 | C3 | 18 | 29 | 116 | 16 | 0 | 179 | 7 | 29 | 116 | 16 | 1 | 169 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 16 | 125 | 7 | 16 | 179 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 9 | 114 | 18 | 24 | 179 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 7005 | 7005 | 7005 | 7005 | 7005 | C3 | 134.6361 | 134.6361 | 187.2437 | 460.7188 | 965.359 | C3 | 942.4527 | 3904.4469 | 21720.2634 | 7371.5016 | 965.359 | 34904.0237 |  | 2423.4498 | 3904.4469 | 21720.2634 | 7371.5016 | 0 | 35419.6617 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 2019.5415 | 2154.1776 | 23405.4562 | 3225.0319 | 15445.7448 | 46249.9521 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629 |  | 1884.9054 | 1211.7249 | 21345.7761 | 8292.9393 | 23168.6172 | 55903.9629
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 11675 | 11675 | 11675 | 11675 | 11675 | C4 | 224.3935 | 224.3935 | 312.0727 | 767.8647 | 1608.9317 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 12333 | 12333 |  | 2485 | 2555 | 7047 | 19 | 227 |  | 2370 | 2555 | 7047 | 19 | 361 |  | 0 | 0 | 0 | 0 | 0 |  | 2123 | 2115 | 7084 | 749 | 262 |  | 0 | 0 | 0 | 0 | 0 |  | 1603 | 1542 | 6314 | 1763 | 1111 | [22 empty] | 208488.4887 | 230631.6393 | 886873.3068 | 8292.9393 | 232651.531 | 1566937.9051 |  | 219034.9832 | 230631.6393 | 886873.3068 | 8292.9393 | 146091.0029 | 1490923.8715 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 186408.1683 | 190554.9602 | 892091.1632 | 231035.146 | 173764.629 | 1673854.0667 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619 |  | 139689.4416 | 138809.8191 | 795286.1961 | 544262.5348 | 722539.0703 | 2340587.0619
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 |  | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 |  | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342
| HV Network | [73 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| HV Switchgear (GM) - Primary |  | 700 | 700 | C1 | 313 | 63 | 245 | 49 | 30 | 700 | 300 | 63 | 246 | 50 | 39 | 698 | 0 | 0 | 0 | 0 | 0 | 0 | 289 | 61 | 217 | 68 | 65 | 700 | 0 | 0 | 0 | 0 | 0 | 0 | 247 | 98 | 163 | 72 | 120 | 700 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | 44069.2 | C1 | 564.9671 | 564.9671 | 786.1945 | 1934.1972 | 4052.6036 | C1 | 169490.1432 | 35592.9301 | 193403.8539 | 96709.8594 | 158051.5416 | 653248.3282 |  | 176834.7161 | 35592.9301 | 192617.6594 | 94775.6622 | 121578.109 | 621399.0767 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 163275.5046 | 34462.9958 | 170604.2126 | 131525.4088 | 263419.2361 | 763287.3578 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061 |  | 139546.8846 | 55366.7801 | 128149.7081 | 139262.1975 | 486312.4358 | 948638.0061
|  |  | 1868 | 1868 | C2 | 710 | 185 | 732 | 139 | 102 | 1868 | 628 | 185 | 734 | 142 | 122 | 1811 | 0 | 0 | 0 | 0 | 0 | 0 | 661 | 198 | 586 | 232 | 191 | 1868 | 0 | 0 | 0 | 0 | 0 | 0 | 574 | 255 | 417 | 253 | 369 | 1868 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 62956 | 62956 | 62956 | 62956 | 62956 | C2 | 807.0959 | 807.0959 | 1123.135 | 2763.1388 | 5789.4338 | C2 | 506856.2378 | 149312.7452 | 824381.1194 | 392365.7153 | 706310.9187 | 2579226.7363 |  | 573038.1032 | 149312.7452 | 822134.8493 | 384076.2988 | 590522.2435 | 2519084.24 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 533490.4031 | 159804.9922 | 658157.1334 | 641048.2109 | 1105781.8482 | 3098282.5878 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133 |  | 463273.0581 | 205809.4596 | 468347.3117 | 699074.1265 | 2136301.0574 | 3972805.0133
|  |  | 455 | 455 | C3 | 133 | 47 | 201 | 28 | 46 | 455 | 96 | 47 | 201 | 28 | 55 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 122 | 51 | 162 | 60 | 60 | 455 | 0 | 0 | 0 | 0 | 0 | 0 | 109 | 57 | 103 | 74 | 112 | 455 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 94434 | 94434 | 94434 | 94434 | 94434 | C3 | 1210.6439 | 1210.6439 | 1684.7026 | 4144.7083 | 8684.1506 | C3 | 116221.8125 | 56900.2624 | 338625.2146 | 116051.8313 | 477628.2852 | 1105427.4059 |  | 161015.636 | 56900.2624 | 338625.2146 | 116051.8313 | 399470.9294 | 1072063.8737 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 147698.5534 | 61742.8379 | 272921.8147 | 248682.4956 | 521049.0384 | 1252094.74 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307 |  | 131960.1829 | 69006.7012 | 173524.3637 | 306708.4112 | 972624.8717 | 1653824.5307
|  |  | 23 | 23 | C4 | 7 | 3 | 12 | 1 | 0 | 23 | 2 | 3 | 12 | 1 | 5 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 7 | 3 | 12 | 1 | 0 | 23 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 4 | 6 | 6 | 1 | 23 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 157390 | 157390 | 157390 | 157390 | 157390 | C4 | 2017.7398 | 2017.7398 | 2807.8376 | 6907.8471 | 14473.5844 | C4 | 4035.4796 | 6053.2194 | 33694.0512 | 6907.8471 | 72367.922 | 123058.5193 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 14124.1786 | 6053.2194 | 33694.0512 | 6907.8471 | 0 | 60779.2963 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906 |  | 12106.4388 | 8070.9592 | 16847.0256 | 41447.0826 | 14473.5844 | 92945.0906
|  |  | 3046 | 3046 |  | 1163 | 298 | 1190 | 217 | 178 |  | 1026 | 298 | 1193 | 221 | 221 |  | 0 | 0 | 0 | 0 | 0 |  | 1079 | 313 | 977 | 361 | 316 |  | 0 | 0 | 0 | 0 | 0 |  | 936 | 414 | 689 | 405 | 602 | [22 empty] | 796603.673 | 247859.157 | 1390104.239 | 612035.2531 | 1414358.6676 | 4460960.9897 |  | 925012.6339 | 247859.157 | 1387071.7744 | 601811.6394 | 1111571.2819 | 4273326.4866 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 858588.6397 | 262064.0452 | 1135377.2119 | 1028163.9624 | 1890250.1226 | 5174443.9819 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407 |  | 746886.5644 | 338253.9001 | 786868.409 | 1186491.8179 | 3609711.9494 | 6668212.6407
| HV Switchgear (GM) - Distribution |  | 669 | 669 | C1 | 644 | 18 | 7 | 0 | 0 | 669 | 640 | 21 | 7 | 0 | 0 | 668 | 0 | 0 | 0 | 0 | 0 | 0 | 644 | 18 | 2 | 5 | 0 | 669 | 0 | 0 | 0 | 0 | 0 | 0 | 626 | 36 | 2 | 0 | 5 | 669 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | 10608.5 | C1 | 136.001 | 136.001 | 189.2556 | 465.6071 | 975.5577 | C1 | 87040.6208 | 2856.0204 | 1324.7895 | 0 | 0 | 91221.4307 |  | 87584.6247 | 2448.0175 | 1324.7895 | 0 | 0 | 91357.4316 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 87584.6247 | 2448.0175 | 378.5113 | 2328.0353 | 0 | 92739.1887 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417 |  | 85136.6072 | 4896.0349 | 378.5113 | 0 | 4877.7883 | 95288.9417
|  |  | 14652 | 14652 | C2 | 6115 | 3339 | 3291 | 870 | 1037 | 14652 | 5752 | 3425 | 3347 | 872 | 1259 | 14655 | 0 | 0 | 0 | 0 | 0 | 0 | 4859 | 4091 | 2865 | 1229 | 1608 | 14652 | 0 | 0 | 0 | 0 | 0 | 0 | 4134 | 4026 | 2962 | 1172 | 2358 | 14652 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 15155 | 15155 | 15155 | 15155 | 15155 | C2 | 194.2871 | 194.2871 | 270.3652 | 665.153 | 1393.6538 | C2 | 1117539.3992 | 665433.3175 | 904912.3244 | 580013.3724 | 1754610.1342 | 5022508.5477 |  | 1188065.6165 | 648724.6269 | 889771.8732 | 578683.0665 | 1445218.9906 | 4750464.1737 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 944041.0189 | 794828.5261 | 774596.298 | 817472.9756 | 2240995.3104 | 5571934.1289 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762 |  | 803182.8714 | 782199.8646 | 800821.7224 | 779559.2574 | 3286235.6604 | 6451999.3762
|  |  | 1431 | 1431 | C3 | 182 | 363 | 410 | 237 | 239 | 1431 | 133 | 368 | 414 | 237 | 282 | 1434 | 0 | 0 | 0 | 0 | 0 | 0 | 82 | 398 | 360 | 235 | 356 | 1431 | 0 | 0 | 0 | 0 | 0 | 0 | 65 | 335 | 354 | 164 | 513 | 1431 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | 22732.5 | C3 | 291.4307 | 291.4307 | 405.5478 | 997.7294 | 2090.4807 | C3 | 38760.2765 | 107246.4792 | 167896.7892 | 236461.8737 | 589515.5574 | 1139880.976 |  | 53040.3783 | 105789.3259 | 166274.598 | 236461.8737 | 499624.8873 | 1061191.0633 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 23897.3133 | 115989.3987 | 145997.208 | 234466.4149 | 744211.1292 | 1264561.4641 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406 |  | 18942.9922 | 97629.2677 | 143563.9212 | 163627.6257 | 1072416.5991 | 1496180.406
|  |  | 50 | 50 | C4 | 21 | 3 | 0 | 5 | 21 | 50 | 14 | 3 | 6 | 5 | 22 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 1 | 25 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 15 | 9 | 0 | 0 | 26 | 50 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | 37887.5 | C4 | 485.7177 | 485.7177 | 675.913 | 1662.8824 | 3484.1345 | C4 | 6800.0485 | 1457.1532 | 4055.478 | 8314.4119 | 76650.959 | 97278.0506 |  | 10200.0727 | 1457.1532 | 0 | 8314.4119 | 73166.8245 | 93138.4624 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 7285.7662 | 4371.4597 | 0 | 1662.8824 | 87103.3625 | 100423.4709 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723 |  | 7285.7662 | 4371.4597 | 0 | 0 | 90587.497 | 102244.723
|  |  | 16802 | 16802 |  | 6962 | 3723 | 3708 | 1112 | 1297 |  | 6539 | 3817 | 3774 | 1114 | 1563 |  | 0 | 0 | 0 | 0 | 0 |  | 5600 | 4516 | 3227 | 1470 | 1989 |  | 0 | 0 | 0 | 0 | 0 |  | 4840 | 4406 | 3318 | 1336 | 2902 | [22 empty] | 1250140.345 | 776992.9703 | 1078189.3811 | 824789.658 | 2420776.6506 | 6350889.0049 |  | 1338890.6922 | 758419.1236 | 1057371.2607 | 823459.3521 | 2018010.7024 | 5996151.131 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 1062808.7231 | 917637.402 | 920972.0173 | 1055930.3081 | 3072309.8021 | 7029658.2526 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469 |  | 914548.2371 | 889096.627 | 944764.1549 | 943186.8831 | 4454117.5448 | 8145713.4469
| HV Transformer (GM) |  | 2220 | 2220 | C1 | 1021 | 402 | 595 | 72 | 130 | 2220 | 933 | 407 | 602 | 72 | 198 | 2212 | 0 | 0 | 0 | 0 | 0 | 0 | 910 | 359 | 660 | 88 | 203 | 2220 | 0 | 0 | 0 | 0 | 0 | 0 | 822 | 319 | 682 | 114 | 283 | 2220 |  |  | C1 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C1 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | 11404.4 | C1 | 219.1926 | 219.1926 | 304.8396 | 750.0674 | 1571.6404 | C1 | 204506.6659 | 89211.3752 | 183513.4464 | 54004.8519 | 311184.7921 | 842421.1316 |  | 223795.6119 | 88115.4123 | 181379.5691 | 54004.8519 | 204313.2473 | 751608.6927 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 199465.2369 | 78690.1319 | 201194.1439 | 66005.9301 | 319042.9939 | 864398.4367 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407 |  | 180176.2909 | 69922.4292 | 207900.6154 | 85507.6822 | 444774.223 | 988281.2407
|  |  | 8983 | 8983 | C2 | 3942 | 1892 | 2549 | 218 | 382 | 8983 | 3620 | 1919 | 2592 | 218 | 604 | 8953 | 0 | 0 | 0 | 0 | 0 | 0 | 3482 | 1608 | 2923 | 393 | 577 | 8983 | 0 | 0 | 0 | 0 | 0 | 0 | 2971 | 1584 | 2991 | 483 | 954 | 8983 |  |  | C2 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C2 | 16292 | 16292 | 16292 | 16292 | 16292 | C2 | 313.1322 | 313.1322 | 435.4852 | 1071.5248 | 2245.2005 | C2 | 1133538.7088 | 600900.7686 | 1128777.5347 | 233592.4151 | 1356101.1141 | 4452910.5413 |  | 1234367.2901 | 592446.1981 | 1110051.6728 | 233592.4151 | 857666.5986 | 4028124.1748 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 1090326.4597 | 503516.6419 | 1272923.1227 | 421109.2621 | 1295480.7 | 4583356.1864 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606 |  | 930315.885 | 496001.4682 | 1302536.1136 | 517546.4977 | 2141921.2961 | 5388321.2606
|  |  | 1848 | 1848 | C3 | 972 | 323 | 484 | 27 | 42 | 1848 | 910 | 329 | 502 | 27 | 73 | 1841 | 0 | 0 | 0 | 0 | 0 | 0 | 861 | 323 | 535 | 56 | 73 | 1848 | 0 | 0 | 0 | 0 | 0 | 0 | 726 | 360 | 525 | 111 | 126 | 1848 |  |  | C3 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C3 | 24438 | 24438 | 24438 | 24438 | 24438 | C3 | 469.6984 | 469.6984 | 653.2277 | 1607.2873 | 3367.8008 | C3 | 427425.5076 | 154530.7604 | 327920.3255 | 43396.756 | 245849.4569 | 1199122.8065 |  | 456546.8059 | 151712.5703 | 316162.2262 | 43396.756 | 141447.6328 | 1109265.9911 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 404410.288 | 151712.5703 | 349476.8409 | 90008.0866 | 245849.4569 | 1241457.2426 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666 |  | 341001.0094 | 169091.4096 | 342944.5635 | 178408.8859 | 424342.8983 | 1455788.7666
|  |  | 14 | 14 | C4 | 5 | 4 | 3 | 1 | 1 | 14 | 5 | 4 | 3 | 1 | 1 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 6 | 3 | 0 | 2 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | 3 | 5 | 4 | 0 | 2 | 14 |  |  | C4 | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781 | C4 | 40730 | 40730 | 40730 | 40730 | 40730 | C4 | 782.8306 | 782.8306 | 1088.7129 | 2678.8121 | 5613.0013 | C4 | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 3914.153 | 3131.3224 | 3266.1387 | 2678.8121 | 5613.0013 | 18603.4275 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 2348.4918 | 4696.9836 | 3266.1387 | 0 | 11226.0026 | 21537.6167 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499 |  | 2348.4918 | 3914.153 | 4354.8516 | 0 | 11226.0026 | 21843.499
|  |  | 13065 | 13065 |  | 5940 | 2621 | 3631 | 318 | 555 |  | 5468 | 2659 | 3699 | 318 | 876 |  | 0 | 0 | 0 | 0 | 0 |  | 5256 | 2296 | 4121 | 537 | 855 |  | 0 | 0 | 0 | 0 | 0 |  | 4522 | 2268 | 4202 | 708 | 1365 | [22 empty] | 1769385.0353 | 847774.2266 | 1643477.4453 | 333672.8352 | 1918748.3644 | 6513057.9068 |  | 1918623.8609 | 835405.5031 | 1610859.6068 | 333672.8352 | 1209040.48 | 5907602.2861 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1696550.4763 | 738616.3277 | 1826860.2462 | 577123.2788 | 1871599.1535 | 6710749.4825 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669 |  | 1453841.6771 | 738929.46 | 1857736.144 | 781463.0658 | 3022264.42 | 7854234.7669
| HV UG Cable |  | 1411.786 | 1411.786 | C1 | 851.313 | 326.427 | 176.622 | 13.984 | 43.44 | 1411.786 | 831.106 | 328.51 | 177.749 | 14.073 | 44.835 | 1396.273 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 23093 | 23093 | 23093 | 23093 | 23093 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 4500.517 | 4500.517 | C2 | 2442.282 | 1088.194 | 778.959 | 68.822 | 122.26 | 4500.517 | 2373.354 | 1095.137 | 783.93 | 69.261 | 129.428 | 4451.11 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 32990 | 32990 | 32990 | 32990 | 32990 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 1028.333 | 1028.333 | C3 | 568.948 | 259.816 | 173.533 | 11.485 | 14.551 | 1028.333 | 546.655 | 261.474 | 174.64 | 11.558 | 22.716 | 1017.043 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 49485 | 49485 | 49485 | 49485 | 49485 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 82475 | 82475 | 82475 | 82475 | 82475 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 6940.636 | 6940.636 |  | 3862.543 | 1674.437 | 1129.114 | 94.291 | 180.251 |  | 3751.115 | 1685.121 | 1136.319 | 94.892 | 196.979 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| HV OHL Support - Poles |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | 4792.2 | C1 | 61.436 | 61.436 | 85.4928 | 210.3297 | 440.6907 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 211011 | 211011 | C2 | 36454 | 146349 | 4410 | 18170 | 5628 | 211011 | 29409 | 146348 | 4757 | 19207 | 11170 | 210891 | 0 | 0 | 0 | 0 | 0 | 0 | 25777 | 146348 | 5479 | 20152 | 13255 | 211011 | 0 | 0 | 0 | 0 | 0 | 0 | 14423 | 146349 | 6614 | 22260 | 21365 | 211011 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 6846 | 6846 | 6846 | 6846 | 6846 | C2 | 87.7657 | 87.7657 | 122.1326 | 300.4709 | 629.5582 | C2 | 2581102.0595 | 12844337.5906 | 580984.9685 | 5771145.3446 | 7032164.6472 | 28809734.6103 |  | 3199411.5569 | 12844425.3563 | 538604.9424 | 5459556.9798 | 3543153.3245 | 25585152.1598 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 2262336.9644 | 12844337.5906 | 669164.7346 | 6055090.3829 | 8344793.4108 | 30175723.0832 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296 |  | 1265844.9796 | 12844425.3563 | 807785.281 | 6688483.1244 | 13450510.0884 | 35057048.8296
|  |  | 2291 | 2291 | C3 | 396 | 1589 | 48 | 197 | 61 | 2291 | 319 | 1589 | 52 | 209 | 120 | 2289 | 0 | 0 | 0 | 0 | 0 | 0 | 280 | 1590 | 58 | 219 | 144 | 2291 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 1589 | 71 | 242 | 232 | 2291 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 10269 | 10269 | 10269 | 10269 | 10269 | C3 | 131.6486 | 131.6486 | 183.199 | 450.7064 | 944.3372 | C3 | 41995.897 | 209189.5936 | 9526.3459 | 94197.6397 | 113320.4688 | 468229.945 |  | 52132.8377 | 209189.5936 | 8793.5501 | 88789.1628 | 57604.5716 | 416509.7158 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 36861.6024 | 209321.2422 | 10625.5397 | 98704.7038 | 135984.5626 | 491497.6506 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377 |  | 20668.8271 | 209189.5936 | 13007.1262 | 109070.9512 | 219086.2397 | 571022.7377
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 17115 | 17115 | 17115 | 17115 | 17115 | C4 | 219.4143 | 219.4143 | 305.3316 | 751.1773 | 1573.8954 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 213302 | 213302 |  | 36850 | 147938 | 4458 | 18367 | 5689 |  | 29728 | 147937 | 4809 | 19416 | 11290 |  | 0 | 0 | 0 | 0 | 0 |  | 26057 | 147938 | 5537 | 20371 | 13399 |  | 0 | 0 | 0 | 0 | 0 |  | 14580 | 147938 | 6685 | 22502 | 21597 | [22 empty] | 2623097.9565 | 13053527.1842 | 590511.3144 | 5865342.9843 | 7145485.116 | 29277964.5554 |  | 3251544.3946 | 13053614.9499 | 547398.4925 | 5548346.1426 | 3600757.8961 | 26001661.8756 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 2299198.5668 | 13053658.8328 | 679790.2742 | 6153795.0867 | 8480777.9734 | 30667220.7339 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673 |  | 1286513.8066 | 13053614.9499 | 820792.4071 | 6797554.0756 | 13669596.3281 | 35628071.5673
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 |  | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 |  | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219
| EHV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| EHV Switchgear (GM) |  | 369 | 369 | C1 | 271 | 39 | 36 | 14 | 9 | 369 | 266 | 39 | 36 | 14 | 9 | 364 | 0 | 0 | 0 | 0 | 0 | 0 | 248 | 57 | 24 | 22 | 18 | 369 | 0 | 0 | 0 | 0 | 0 | 0 | 210 | 80 | 31 | 12 | 36 | 369 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | 71059.8 | C1 | 910.9866 | 910.9866 | 1267.7068 | 3118.8146 | 6534.6592 | C1 | 242322.4452 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 425963.7075 |  | 246877.3784 | 35528.4788 | 45637.446 | 43663.4047 | 58811.9329 | 430518.6407 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 225924.6857 | 51926.2383 | 30424.964 | 68613.9217 | 117623.8657 | 494513.6754 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432 |  | 191307.1936 | 72878.9309 | 39298.9118 | 37425.7755 | 235247.7315 | 576158.5432
|  |  | 475 | 475 | C2 | 217 | 52 | 156 | 37 | 13 | 475 | 212 | 52 | 156 | 37 | 13 | 470 | 0 | 0 | 0 | 0 | 0 | 0 | 184 | 76 | 83 | 86 | 46 | 475 | 0 | 0 | 0 | 0 | 0 | 0 | 157 | 91 | 69 | 36 | 122 | 475 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 101514 | 101514 | 101514 | 101514 | 101514 | C2 | 1301.4095 | 1301.4095 | 1811.0098 | 4455.4495 | 9335.2274 | C2 | 275898.8098 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 912299.212 |  | 282405.8572 | 67673.293 | 282517.5226 | 164851.63 | 121357.9567 | 918806.2594 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 239459.3443 | 98907.1205 | 150313.8101 | 383168.6536 | 429420.4622 | 1301269.3907 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527 |  | 204321.2884 | 118428.2627 | 124959.6734 | 160396.1806 | 1138897.7477 | 1747003.1527
|  |  | 127 | 127 | C3 | 47 | 14 | 52 | 4 | 10 | 127 | 42 | 14 | 52 | 4 | 10 | 122 | 0 | 0 | 0 | 0 | 0 | 0 | 44 | 16 | 27 | 26 | 14 | 127 | 0 | 0 | 0 | 0 | 0 | 0 | 33 | 21 | 9 | 24 | 40 | 127 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 152271 | 152271 | 152271 | 152271 | 152271 | C3 | 1952.1142 | 1952.1142 | 2716.5146 | 6683.1742 | 14002.8412 | C3 | 81988.7972 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 417338.266 |  | 91749.3683 | 27329.5991 | 141258.7613 | 26732.6968 | 140028.4116 | 427098.8371 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 85893.0257 | 31233.8275 | 73345.8953 | 173762.5289 | 196039.7762 | 560275.0537 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266 |  | 64419.7693 | 40994.3986 | 24448.6318 | 160396.1806 | 560113.6464 | 850372.6266
|  |  | 55 | 55 | C4 | 24 | 7 | 19 | 5 | 0 | 55 | 24 | 7 | 19 | 5 | 0 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 10 | 12 | 9 | 5 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 9 | 16 | 8 | 9 | 13 | 55 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 253785 | 253785 | 253785 | 253785 | 253785 | C4 | 3253.5237 | 3253.5237 | 4527.5244 | 11138.6236 | 23338.0686 | C4 | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 78084.5688 | 22774.6659 | 86022.9636 | 55693.1182 | 0 | 242575.3165 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 61816.9503 | 32535.237 | 54330.2928 | 100247.6128 | 116690.343 | 365620.4359 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924 |  | 29281.7133 | 52056.3792 | 36220.1952 | 100247.6128 | 303394.8918 | 521200.7924
|  |  | 1026 | 1026 |  | 559 | 112 | 263 | 60 | 32 |  | 544 | 112 | 263 | 60 | 32 |  | 0 | 0 | 0 | 0 | 0 |  | 495 | 159 | 146 | 143 | 83 |  | 0 | 0 | 0 | 0 | 0 |  | 409 | 208 | 117 | 81 | 211 | [22 empty] | 678294.621 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 1998176.502 |  | 699117.1727 | 153306.0367 | 555436.6934 | 290940.8497 | 320198.3012 | 2018999.0537 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 613094.006 | 214602.4233 | 308414.9621 | 725792.717 | 859774.4472 | 2721678.5557 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149 |  | 489329.9645 | 284357.9714 | 224927.4122 | 458465.7494 | 2237654.0174 | 3694735.1149
| EHV Transformer |  | 246 | 246 | C1 | 126 | 25 | 59 | 23 | 13 | 246 | 117 | 25 | 61 | 26 | 15 | 244 | 0 | 0 | 0 | 0 | 0 | 0 | 111 | 37 | 45 | 18 | 35 | 246 | 0 | 0 | 0 | 0 | 0 | 0 | 105 | 39 | 36 | 16 | 50 | 246 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | 263610.2 | C1 | 3379.4828 | 3379.4828 | 4702.806 | 11569.8517 | 24241.594 | C1 | 395399.4834 | 84487.0691 | 286871.164 | 300816.1436 | 363623.9099 | 1431197.77 |  | 425814.8283 | 84487.0691 | 277465.5521 | 266106.5886 | 315140.7219 | 1369014.76 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 375122.5868 | 125040.8623 | 211626.2686 | 208257.3302 | 848455.7897 | 1768502.8376 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593 |  | 354845.6902 | 131799.8278 | 169301.0148 | 185117.6268 | 1212079.6996 | 2053143.8593
|  |  | 248 | 248 | C2 | 55 | 25 | 129 | 31 | 8 | 248 | 50 | 25 | 129 | 31 | 10 | 245 | 0 | 0 | 0 | 0 | 0 | 0 | 46 | 33 | 99 | 35 | 35 | 248 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 38 | 73 | 38 | 65 | 248 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 376586 | 376586 | 376586 | 376586 | 376586 | C2 | 4827.8325 | 4827.8325 | 6718.2942 | 16528.3595 | 34630.8486 | C2 | 241391.626 | 120695.813 | 866659.957 | 512379.1457 | 346308.4856 | 2087435.0273 |  | 265530.7886 | 120695.813 | 866659.957 | 512379.1457 | 277046.7885 | 2042312.4928 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 222080.2959 | 159318.4732 | 665111.1298 | 578492.5839 | 1212079.6996 | 2837082.1823 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399 |  | 164146.3057 | 183457.6358 | 490435.4795 | 628077.6625 | 2251005.1564 | 3717122.2399
|  |  | 73 | 73 | C3 | 25 | 4 | 29 | 12 | 3 | 73 | 25 | 4 | 29 | 12 | 3 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 25 | 4 | 21 | 9 | 14 | 73 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 7 | 12 | 11 | 21 | 73 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 564879 | 564879 | 564879 | 564879 | 564879 | C3 | 7241.7488 | 7241.7488 | 10077.4414 | 24792.5393 | 51946.2728 | C3 | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 292245.7994 | 297510.4717 | 155838.8185 | 955605.8043 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 181043.7195 | 28966.9951 | 211626.2686 | 223132.8538 | 727247.8198 | 1372017.6567 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673 |  | 159318.4732 | 50692.2415 | 120929.2963 | 272717.9324 | 1090871.7296 | 1694529.673
|  |  | 30 | 30 | C4 | 22 | 0 | 8 | 0 | 0 | 30 | 22 | 0 | 8 | 0 | 0 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 22 | 0 | 3 | 4 | 1 | 30 | 0 | 0 | 0 | 0 | 0 | 0 | 18 | 4 | 2 | 1 | 5 | 30 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 941465 | 941465 | 941465 | 941465 | 941465 | C4 | 12069.5813 | 12069.5813 | 16795.7356 | 41320.8988 | 86577.1214 | C4 | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 134365.8848 | 0 | 0 | 399896.6734 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 265530.7886 | 0 | 50387.2068 | 165283.5954 | 86577.1214 | 567778.7122 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656 |  | 217252.4634 | 48278.3252 | 33591.4712 | 41320.8988 | 432885.607 | 773328.7656
|  |  | 597 | 597 |  | 228 | 54 | 225 | 66 | 24 |  | 214 | 54 | 227 | 69 | 28 |  | 0 | 0 | 0 | 0 | 0 |  | 204 | 74 | 168 | 66 | 85 |  | 0 | 0 | 0 | 0 | 0 |  | 179 | 88 | 123 | 66 | 141 | [22 empty] | 1083365.6175 | 234149.8772 | 1580142.8052 | 1110705.7611 | 865771.214 | 4874135.275 |  | 1137920.125 | 234149.8772 | 1570737.1933 | 1075996.2061 | 748026.3289 | 4766829.7304 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 1043777.3908 | 313326.3305 | 1138750.8737 | 1175166.3633 | 2874360.4305 | 6545381.3888 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378 |  | 895562.9325 | 414228.0302 | 814257.2619 | 1127234.1206 | 4986842.1926 | 8238124.5378
| EHV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C1 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | 5896.8 | C1 | 553.5916 | 553.5916 | 18758.3105 | 45788.1803 | 95940.8181 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 34 | C2 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 32.735 | 1.265 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 34 |  |  | C2 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C2 | 8424 | 8424 | 8424 | 8424 | 8424 | C2 | 790.8451 | 790.8451 | 26797.5864 | 65411.6861 | 137058.3115 | C2 | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C3 | 12636 | 12636 | 12636 | 12636 | 12636 | C3 | 1186.2677 | 1186.2677 | 40196.3796 | 98117.5291 | 205587.4673 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27 | C4 | 21060 | 21060 | 21060 | 21060 | 21060 | C4 | 1977.1128 | 1977.1128 | 66993.966 | 163529.2152 | 342645.7788 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 34 | 34 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 32.735 | 1.265 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 34 | [22 empty] | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 2141251.5438 | 173378.7641 | 2314630.3079 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917 |  | 0 | 0 | 0 | 0 | 4659982.5917 | 4659982.5917
| EHV UG Cable (Oil) |  | 21.926 | 21.926 | C1 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0.244 | 18.122 | 3.56 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.244 | 10.376 | 11.306 | 0 | 0 | 21.926 | 0 | 0 | 0 | 0 | 0 | 0 | 0.224 | 3.824 | 17.878 | 0 | 0 | 21.926 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | 50590.4 | C1 | 301.5188 | 301.5188 | 10223.8139 | 24955.7384 | 52290.2374 | C1 | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 5464.1234 | 36396.7776 | 0 | 0 | 41934.4716 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 73.5706 | 3128.5589 | 115590.4404 | 0 | 0 | 118792.5698 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936 |  | 67.5402 | 1153.0078 | 182781.3455 | 0 | 0 | 184001.8936
|  |  | 29.901 | 29.901 | C2 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0.327 | 4.177 | 25.397 | 0 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0.134 | 4.346 | 10.62 | 14.801 | 0 | 29.901 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.051 | 11.414 | 0.635 | 14.801 | 29.901 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 72272 | 72272 | 72272 | 72272 | 72272 | C2 | 430.7411 | 430.7411 | 14605.4485 | 35651.0549 | 74700.3392 | C2 | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 140.8523 | 1799.2057 | 370934.575 | 0 | 0 | 372874.6331 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 57.7193 | 1872.0009 | 155109.8629 | 527671.2633 | 0 | 684710.8464 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205 |  | 0 | 1314.1912 | 166706.589 | 22638.4198 | 1105639.7205 | 1296298.9205
|  |  | 8.451 | 8.451 | C3 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0.167 | 6.477 | 1.807 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 1.451 | 6.833 | 0 | 0 | 8.451 | 0 | 0 | 0 | 0 | 0 | 0 | 0.167 | 0 | 8.284 | 0 | 0 | 8.451 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 108408 | 108408 | 108408 | 108408 | 108408 | C3 | 646.1117 | 646.1117 | 21908.1727 | 53476.5823 | 112050.5088 | C3 | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 4184.8654 | 39588.0681 | 0 | 0 | 43880.8341 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 937.508 | 149698.5442 | 0 | 0 | 150743.9529 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035 |  | 107.9007 | 0 | 181487.3028 | 0 | 0 | 181595.2035
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 180680 | 180680 | 180680 | 180680 | 180680 | C4 | 1076.8528 | 1076.8528 | 36513.6212 | 89127.6372 | 186750.848 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 60.278 | 60.278 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0.738 | 28.776 | 30.764 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.545 | 16.173 | 28.759 | 14.801 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0.391 | 6.875 | 37.576 | 0.635 | 14.801 | [22 empty] | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 322.3236 | 11448.1944 | 446919.4208 | 0 | 0 | 458689.9388 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 239.1905 | 5938.0679 | 420398.8474 | 527671.2633 | 0 | 954247.3691 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175 |  | 175.4409 | 2467.199 | 530975.2373 | 22638.4198 | 1105639.7205 | 1661896.0175
| EHV UG Cable (Non Pressurised) |  | 241.211 | 241.211 | C1 | 102.041 | 79.473 | 38.332 | 6.567 | 14.798 | 241.211 | 98.486 | 79.494 | 38.342 | 6.569 | 14.798 | 237.689 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | 35465.5 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 383.855 | 383.855 | C2 | 187.889 | 71.424 | 84.157 | 6.573 | 33.812 | 383.855 | 182.232 | 71.443 | 84.179 | 6.575 | 33.815 | 378.244 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 50665 | 50665 | 50665 | 50665 | 50665 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 188.435 | 188.435 | C3 | 71.85 | 50.635 | 53.553 | 0.613 | 11.784 | 188.435 | 69.137 | 50.648 | 53.567 | 0.613 | 11.784 | 185.749 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | 75997.5 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 10.863 | 10.863 | C4 | 7.449 | 1.64 | 1.774 | 0 | 0 | 10.863 | 7.33 | 1.64 | 1.774 | 0 | 0 | 10.744 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | 126662.5 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 824.364 | 824.364 |  | 369.229 | 203.172 | 177.816 | 13.753 | 60.394 |  | 357.185 | 203.225 | 177.862 | 13.757 | 60.397 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Support - Towers |  | 125 | 125 | C1 | 31 | 77 | 11 | 6 | 0 | 125 | 31 | 80 | 12 | 6 | 0 | 129 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 70 | 20 | 6 | 2 | 125 | 0 | 0 | 0 | 0 | 0 | 0 | 27 | 69 | 18 | 7 | 4 | 125 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | 153888.7 | C1 | 81.561 | 81.561 | 81.561 | 4130.3727 | 14151.6049 | C1 | 2528.3913 | 6524.8809 | 978.7321 | 24782.2362 | 0 | 34814.2406 |  | 2528.3913 | 6280.1978 | 897.1711 | 24782.2362 | 0 | 34487.9966 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2202.1473 | 5709.2708 | 1631.2202 | 24782.2362 | 28303.2097 | 62628.0842 |  | 2202.1473 | 5627.7098 | 1468.0982 | 28912.609 | 56606.4194 | 94816.9836 |  | 2202.1473 | 5627.7098 | 1468.0982 | 28912.609 | 56606.4194 | 94816.9836
|  |  | 299 | 299 | C2 | 72 | 163 | 58 | 6 | 0 | 299 | 66 | 161 | 59 | 8 | 6 | 300 | 0 | 0 | 0 | 0 | 0 | 0 | 69 | 166 | 55 | 9 | 0 | 299 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 176 | 51 | 10 | 4 | 299 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 219841 | 219841 | 219841 | 219841 | 219841 | C2 | 116.5157 | 116.5157 | 116.5157 | 5900.5324 | 20216.5784 | C2 | 7690.0382 | 18759.0325 | 6874.4281 | 47204.2595 | 121299.4702 | 201827.2285 |  | 8389.1326 | 18992.064 | 6757.9123 | 35403.1946 | 0 | 69542.3035 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 8039.5854 | 19341.6112 | 6408.3651 | 53104.792 | 0 | 86894.3537 |  | 6757.9123 | 20506.7685 | 5942.3022 | 59005.3244 | 80866.3134 | 173078.6209 |  | 6757.9123 | 20506.7685 | 5942.3022 | 59005.3244 | 80866.3134 | 173078.6209
|  |  | 65 | 65 | C3 | 16 | 42 | 6 | 1 | 0 | 65 | 16 | 40 | 6 | 3 | 0 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 34 | 12 | 2 | 1 | 65 | 0 | 0 | 0 | 0 | 0 | 0 | 14 | 33 | 14 | 3 | 1 | 65 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | 329761.5 | C3 | 174.7736 | 174.7736 | 174.7736 | 8850.7987 | 30324.8675 | C3 | 2796.3775 | 6990.9438 | 1048.6416 | 26552.396 | 0 | 37388.3589 |  | 2796.3775 | 7340.491 | 1048.6416 | 8850.7987 | 0 | 20036.3087 |  | 2796.3775 | 5942.3022 | 2097.2831 | 17701.5973 | 30324.8675 | 58862.4278 |  | 2796.3775 | 5942.3022 | 2097.2831 | 17701.5973 | 30324.8675 | 58862.4278 |  | 2446.8303 | 5767.5286 | 2446.8303 | 26552.396 | 30324.8675 | 67538.4528 |  | 2446.8303 | 5767.5286 | 2446.8303 | 26552.396 | 30324.8675 | 67538.4528
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | 549602.5 | C4 | 291.2893 | 291.2893 | 291.2893 | 14751.3311 | 50541.4459 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 489 | 489 |  | 119 | 282 | 75 | 13 | 0 |  | 113 | 281 | 77 | 17 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 112 | 270 | 87 | 17 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 99 | 278 | 83 | 20 | 9 | [22 empty] | 13014.807 | 32274.8572 | 8901.8018 | 98538.8917 | 121299.4702 | 274029.8279 |  | 13713.9014 | 32612.7528 | 8703.725 | 69036.2295 | 0 | 124066.6088 |  | 13038.1102 | 30993.1842 | 10136.8685 | 95588.6255 | 58628.0772 | 208384.8656 |  | 13038.1102 | 30993.1842 | 10136.8685 | 95588.6255 | 58628.0772 | 208384.8656 |  | 11406.89 | 31902.0069 | 9857.2308 | 114470.3293 | 167797.6004 | 335434.0573 |  | 11406.89 |  | 9857.2308 |  | 167797.6004 | 189061.7211
| EHV OHL Support - Poles |  | 4894 | 4894 | C1 | 591 | 3064 | 242 | 591 | 406 | 4894 | 468 | 3064 | 248 | 610 | 505 | 4895 | 0 | 0 | 0 | 0 | 0 | 0 | 374 | 3064 | 249 | 619 | 588 | 4894 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 3064 | 257 | 649 | 776 | 4894 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | 8736.7 | C1 | 112.0045 | 112.0045 | 155.8627 | 383.4538 | 803.4269 | C1 | 52418.1032 | 343181.7696 | 38653.9565 | 233906.7954 | 405730.6007 | 1073891.2254 |  | 66194.656 | 343181.7696 | 37718.7802 | 226621.1739 | 326191.3344 | 999907.7141 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 41889.6808 | 343181.7696 | 38809.8193 | 237357.8793 | 472415.036 | 1133654.185 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472 |  | 16576.6651 | 343181.7696 | 40056.7211 | 248861.4922 | 623459.2992 | 1272135.9472
|  |  | 22777 | 22777 | C2 | 2752 | 14261 | 1127 | 2748 | 1889 | 22777 | 2178 | 14261 | 1156 | 2834 | 2351 | 22780 | 0 | 0 | 0 | 0 | 0 | 0 | 1741 | 14261 | 1161 | 2883 | 2731 | 22777 | 0 | 0 | 0 | 0 | 0 | 0 | 688 | 14261 | 1196 | 3022 | 3610 | 22777 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 12481 | 12481 | 12481 | 12481 | 12481 | C2 | 160.0064 | 160.0064 | 222.661 | 547.7911 | 1147.7528 | C2 | 348493.9828 | 2281851.5556 | 257396.1622 | 1552439.9491 | 2698366.7388 | 7138548.3884 |  | 440337.6678 | 2281851.5556 | 250938.9921 | 1505329.9153 | 2168104.9636 | 6646563.0945 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 278571.1772 | 2281851.5556 | 258509.4674 | 1579281.7125 | 3134512.7876 | 7532726.7003 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714 |  | 110084.417 | 2281851.5556 | 266302.6038 | 1655424.674 | 4143387.4636 | 8457050.714
|  |  | 1936 | 1936 | C3 | 234 | 1212 | 96 | 233 | 161 | 1936 | 185 | 1212 | 99 | 240 | 200 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 148 | 1212 | 99 | 245 | 232 | 1936 | 0 | 0 | 0 | 0 | 0 | 0 | 58 | 1212 | 102 | 257 | 307 | 1936 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | 18721.5 | C3 | 240.0096 | 240.0096 | 333.9916 | 821.6866 | 1721.6291 | C3 | 44401.7815 | 290891.6716 | 33065.1644 | 197204.7924 | 344325.828 | 909889.2379 |  | 56162.2534 | 290891.6716 | 32063.1898 | 191452.986 | 277182.2915 | 847752.3922 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 35521.4252 | 290891.6716 | 33065.1644 | 201313.2256 | 399417.9605 | 960209.4473 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804 |  | 13920.5585 | 290891.6716 | 34067.1391 | 211173.4652 | 528540.146 | 1078592.9804
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | 31202.5 | C4 | 400.0161 | 400.0161 | 556.6526 | 1369.4777 | 2869.3819 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 29607 | 29607 |  | 3577 | 18537 | 1465 | 3572 | 2456 |  | 2831 | 18537 | 1503 | 3684 | 3056 |  | 0 | 0 | 0 | 0 | 0 |  | 2263 | 18537 | 1509 | 3747 | 3551 |  | 0 | 0 | 0 | 0 | 0 |  | 894 | 18537 | 1555 | 3928 | 4693 | [22 empty] | 445313.8675 | 2915924.9968 | 329115.2832 | 1983551.5369 | 3448423.1674 | 9122328.8518 |  | 562694.5772 | 2915924.9968 | 320720.962 | 1923404.0752 | 2771478.5896 | 8494223.2008 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 355982.2832 | 2915924.9968 | 330384.4512 | 2017952.8173 | 4006345.7841 | 9626590.3326 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416 |  | 140581.6406 | 2915924.9968 | 340426.4641 | 2115459.6314 | 5295386.9088 | 10807779.6416
| EHV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| EHV OHL Fittings |  | 427 | 427 | C1 | 290 | 0 | 132 | 0 | 5 | 427 | 300 | 0 | 132 | 0 | 5 | 437 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 132 | 5 | 427 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 290 | 0 | 0 | 137 | 427 |  |  | C1 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C1 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | 71703.8 | C1 | 238.7737 | 238.7737 | 332.7056 | 818.1404 | 1714.4379 | C1 | 71632.0962 | 0 | 43917.1434 | 0 | 8572.1893 | 124121.4289 |  | 69244.3597 | 0 | 43917.1434 | 0 | 8572.1893 | 121733.6924 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 0 | 69244.3597 | 0 | 107994.5273 | 8572.1893 | 185811.0762 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462 |  | 0 | 69244.3597 | 0 | 0 | 234877.9865 | 304122.3462
|  |  | 456 | 456 | C2 | 284 | 0 | 32 | 21 | 119 | 456 | 293 | 0 | 32 | 21 | 119 | 465 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 | 0 | 0 | 0 | 0 | 0 | 0 | 117 | 167 | 0 | 0 | 172 | 456 |  |  | C2 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C2 | 102434 | 102434 | 102434 | 102434 | 102434 | C2 | 341.1052 | 341.1052 | 475.2938 | 1168.7719 | 2449.1969 | C2 | 99943.8295 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 431151.8764 |  | 96873.8825 | 0 | 15209.4003 | 24544.2107 | 291454.4359 | 428081.9294 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562 |  | 39909.3107 | 56964.5717 | 0 | 0 | 421261.8737 | 518135.7562
|  |  | 55 | 55 | C3 | 1 | 0 | 0 | 0 | 54 | 55 | 1 | 0 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0 | 0 | 54 | 55 |  |  | C3 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C3 | 153651 | 153651 | 153651 | 153651 | 153651 | C3 | 511.6578 | 511.6578 | 712.9406 | 1753.1579 | 3673.7954 | C3 | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 511.6578 | 0 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61 |  | 0 | 511.6578 | 0 | 0 | 198384.9521 | 198896.61
|  |  | 87 | 87 | C4 | 31 | 0 | 22 | 34 | 0 | 87 | 32 | 0 | 22 | 34 | 0 | 88 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 10 | 12 | 34 | 87 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31 | 0 | 0 | 56 | 87 |  |  | C4 | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391 | C4 | 256085 | 256085 | 256085 | 256085 | 256085 | C4 | 852.7631 | 852.7631 | 1188.2344 | 2921.9298 | 6122.9924 | C4 | 27288.4176 | 0 | 26141.1568 | 99345.6149 | 0 | 152775.1893 |  | 26435.6545 | 0 | 26141.1568 | 99345.6149 | 0 | 151922.4263 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 0 | 26435.6545 | 11882.344 | 35063.1582 | 208181.7399 | 281562.8967 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262 |  | 0 | 26435.6545 | 0 | 0 | 342887.5716 | 369323.2262
|  |  | 1025 | 1025 |  | 606 | 0 | 186 | 55 | 178 |  | 626 | 0 | 186 | 55 | 178 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 10 | 144 | 265 |  | 0 | 0 | 0 | 0 | 0 |  | 117 | 489 | 0 | 0 | 419 | [22 empty] | 199376.0011 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 906945.1046 |  | 193065.5545 | 0 | 85267.7005 | 123889.8256 | 498411.5773 | 900634.658 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 39909.3107 | 153156.2438 | 11882.344 | 143057.6855 | 836400.755 | 1184406.339 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385 |  | 39909.3107 | 153156.2438 | 0 | 0 | 1197412.384 | 1390477.9385
| EHV OHL Conductor (Tower Lines) |  | 40.481 | 40.481 | C1 | 40.019 | 0 | 0.462 | 0 | 0 | 40.481 | 40.483 | 0 | 0.467 | 0 | 0 | 40.95 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.019 | 0 | 0.462 | 0 | 40.481 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | 73028.9 | C1 | 5.8423 | 5.8423 | 8.0332 | 20.4481 | 43.0871 | C1 | 236.5143 | 0 | 3.7515 | 0 | 0 | 240.2658 |  | 233.8035 | 0 | 3.7113 | 0 | 0 | 237.5148 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505 |  | 0 | 233.8035 | 0 | 9.447 | 0 | 243.2505
|  |  | 52.696 | 52.696 | C2 | 27.481 | 0 | 25.215 | 0 | 0 | 52.696 | 27.8 | 0 | 25.508 | 0 | 0 | 53.308 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.085 | 14.73 | 10.484 | 0 | 52.696 | 0 | 0 | 0 | 0 | 0 | 0 | 11.397 | 16.084 | 3.802 | 21.413 | 0 | 52.696 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 104327 | 104327 | 104327 | 104327 | 104327 | C2 | 8.3462 | 8.3462 | 11.476 | 29.2116 | 61.5529 | C2 | 232.0232 | 0 | 292.729 | 0 | 0 | 524.7523 |  | 229.3608 | 0 | 289.3666 | 0 | 0 | 518.7274 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.248 | 169.041 | 306.254 | 0 | 704.6642 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996 |  | 95.1212 | 134.2396 | 43.6316 | 625.5071 | 0 | 898.4996
|  |  | 6.374 | 6.374 | C3 | 0.129 | 0 | 6.245 | 0 | 0 | 6.374 | 0.13 | 0 | 6.317 | 0 | 0 | 6.447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.129 | 0 | 6.245 | 0 | 6.374 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | 156490.5 | C3 | 12.5192 | 12.5192 | 17.214 | 43.8173 | 92.3294 | C3 | 1.6275 | 0 | 108.7406 | 0 | 0 | 110.3681 |  | 1.615 | 0 | 107.5011 | 0 | 0 | 109.1161 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543 |  | 0 | 1.615 | 0 | 273.6393 | 0 | 275.2543
|  |  | 8.199 | 8.199 | C4 | 5.053 | 3.146 | 0 | 0 | 0 | 8.199 | 5.112 | 3.183 | 0 | 0 | 0 | 8.295 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 8.199 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.053 | 3.146 | 0 | 0 | 8.199 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | 260817.5 | C4 | 20.8654 | 20.8654 | 28.6899 | 73.0289 | 153.8823 | C4 | 106.6639 | 66.4146 | 0 | 0 | 0 | 173.0785 |  | 105.4329 | 65.6425 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 171.0754 | 0 | 0 | 0 | 171.0754 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914 |  | 0 | 105.4329 | 90.2585 | 0 | 0 | 195.6914
|  |  | 107.75 | 107.75 |  | 72.682 | 3.146 | 31.922 | 0 | 0 |  | 73.525 | 3.183 | 32.292 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 64.432 | 14.73 | 17.191 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.397 | 61.285 | 6.948 | 28.12 | 0 | [22 empty] | 576.829 | 66.4146 | 405.2211 | 0 | 0 | 1048.4646 |  | 570.2122 | 65.6425 | 400.5791 | 0 | 0 | 1036.4338 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 540.7419 | 169.041 | 589.3403 | 0 | 1394.2444 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957 |  | 95.1212 | 475.091 | 133.8901 | 908.5934 | 0 | 1612.6957
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 |  | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 |  | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 |  | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 |  | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 |  | 1577061.3003 | 3770609.5321 | 1920577.4963 | 3724706.5147 | 19650715.4154 | 30643670.2588
| 132kV Network | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| 132kV CBs |  | 72 | 72 | C1 | 50 | 5 | 12 | 4 | 1 | 72 | 49 | 5 | 12 | 4 | 2 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 47 | 8 | 11 | 1 | 5 | 72 | 0 | 0 | 0 | 0 | 0 | 0 | 34 | 19 | 9 | 4 | 6 | 72 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | 175933.8 | C1 | 2255.4713 | 2255.4713 | 3138.659 | 7721.7345 | 16178.8722 | C1 | 110518.0945 | 11277.3566 | 37663.9079 | 30886.9379 | 32357.7445 | 222704.0414 |  | 112773.5658 | 11277.3566 | 37663.9079 | 30886.9379 | 16178.8722 | 208780.6405 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 106007.1519 | 18043.7705 | 34525.2489 | 7721.7345 | 80894.3612 | 247192.267 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821 |  | 76686.0247 | 42853.955 | 28247.9309 | 30886.9379 | 97073.2335 | 275748.0821
|  |  | 61 | 61 | C2 | 48 | 3 | 8 | 2 | 0 | 61 | 35 | 3 | 8 | 2 | 2 | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 43 | 8 | 4 | 4 | 2 | 61 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 16 | 2 | 3 | 5 | 61 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 251334 | 251334 | 251334 | 251334 | 251334 | C2 | 3222.1019 | 3222.1019 | 4483.7986 | 11031.0493 | 23112.6746 | C2 | 112773.5658 | 9666.3056 | 35870.3885 | 22062.0985 | 46225.3493 | 226597.7077 |  | 154660.8902 | 9666.3056 | 35870.3885 | 22062.0985 | 0 | 222259.6829 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 138550.3808 | 25776.815 | 17935.1942 | 44124.197 | 46225.3493 | 272611.9364 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314 |  | 112773.5658 | 51553.6301 | 8967.5971 | 33093.1478 | 115563.3732 | 321951.314
|  |  | 26 | 26 | C3 | 15 | 2 | 3 | 5 | 1 | 26 | 14 | 2 | 3 | 5 | 2 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 0 | 3 | 6 | 26 | 0 | 0 | 0 | 0 | 0 | 0 | 11 | 5 | 1 | 0 | 9 | 26 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 377001 | 377001 | 377001 | 377001 | 377001 | C3 | 4833.1528 | 4833.1528 | 6725.6978 | 16546.5739 | 34669.012 | C3 | 67664.1395 | 9666.3056 | 20177.0935 | 82732.8694 | 69338.0239 | 249578.432 |  | 72497.2923 | 9666.3056 | 20177.0935 | 82732.8694 | 34669.012 | 219742.5729 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 62830.9867 | 19332.6113 | 0 | 49639.7217 | 208014.0718 | 339817.3914 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506 |  | 53164.681 | 24165.7641 | 6725.6978 | 0 | 312021.1076 | 396077.2506
|  |  | 7 | 7 | C4 | 7 | 0 | 0 | 0 | 0 | 7 | 7 | 0 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 2 | 5 | 0 | 0 | 0 | 7 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 628335 | 628335 | 628335 | 628335 | 628335 | C4 | 8055.2547 | 8055.2547 | 11209.4964 | 27577.6231 | 57781.6866 | C4 | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 56386.7829 | 0 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 32221.0188 | 24165.7641 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829 |  | 16110.5094 | 40276.2735 | 0 | 0 | 0 | 56386.7829
|  |  | 166 | 166 |  | 120 | 10 | 23 | 11 | 2 |  | 105 | 10 | 23 | 11 | 6 |  | 0 | 0 | 0 | 0 | 0 |  | 107 | 23 | 15 | 8 | 13 |  | 0 | 0 | 0 | 0 | 0 |  | 82 | 45 | 12 | 7 | 20 | [22 empty] | 347342.5827 | 30609.9679 | 93711.3899 | 135681.9059 | 147921.1177 | 755266.964 |  | 396318.5312 | 30609.9679 | 93711.3899 | 135681.9059 | 50847.8842 | 707169.6791 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 339609.5382 | 87318.9609 | 52460.4432 | 101485.6532 | 335133.7823 | 916008.3777 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296 |  | 258734.781 | 158849.6227 | 43941.2259 | 63980.0857 | 524657.7143 | 1050163.4296
| 132kV Transformer |  | 27 | 27 | C1 | 16 | 2 | 8 | 1 | 0 | 27 | 16 | 2 | 8 | 1 | 0 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 4 | 8 | 1 | 1 | 27 | 0 | 0 | 0 | 0 | 0 | 0 | 12 | 4 | 8 | 2 | 1 | 27 |  |  | C1 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C1 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | 1662540.6 | C1 | 21313.7705 | 21313.7705 | 29659.7243 | 72968.9069 | 152887.2336 | C1 | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 341020.3279 | 42627.541 | 237277.7944 | 72968.9069 | 0 | 693894.5702 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 277079.0164 | 85255.082 | 237277.7944 | 72968.9069 | 152887.2336 | 825468.0333 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697 |  | 255765.2459 | 85255.082 | 237277.7944 | 145937.8139 | 152887.2336 | 877123.1697
|  |  | 48 | 48 | C2 | 20 | 7 | 17 | 4 | 0 | 48 | 18 | 7 | 17 | 5 | 0 | 47 | 0 | 0 | 0 | 0 | 0 | 0 | 19 | 5 | 18 | 5 | 1 | 48 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 5 | 14 | 9 | 4 | 48 |  |  | C2 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C2 | 2375058 | 2375058 | 2375058 | 2375058 | 2375058 | C2 | 30448.2436 | 30448.2436 | 42371.0347 | 104241.2956 | 218410.3337 | C2 | 548068.3841 | 213137.7049 | 720307.5902 | 521206.4781 | 0 | 2002720.1573 |  | 608964.8712 | 213137.7049 | 720307.5902 | 416965.1825 | 0 | 1959375.3488 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 578516.6276 | 152241.2178 | 762678.625 | 521206.4781 | 218410.3337 | 2233053.2822 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961 |  | 487171.897 | 152241.2178 | 593194.4861 | 938171.6606 | 873641.3347 | 3044420.5961
|  |  | 13 | 13 | C3 | 5 | 2 | 4 | 2 | 0 | 13 | 4 | 2 | 4 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 5 | 2 | 3 | 3 | 0 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 3 | 2 | 2 | 2 | 13 |  |  | C3 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C3 | 3562587 | 3562587 | 3562587 | 3562587 | 3562587 | C3 | 45672.3653 | 45672.3653 | 63556.5521 | 156361.9434 | 327615.5005 | C3 | 182689.4614 | 91344.7307 | 254226.2083 | 469085.8303 | 0 | 997346.2307 |  | 228361.8267 | 91344.7307 | 254226.2083 | 312723.8869 | 0 | 886656.6526 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 228361.8267 | 91344.7307 | 190669.6562 | 469085.8303 | 0 | 979462.0439 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494 |  | 182689.4614 | 137017.096 | 127113.1042 | 312723.8869 | 655231.001 | 1414774.5494
|  |  | 6 | 6 | C4 | 1 | 2 | 3 | 0 | 0 | 6 | 1 | 2 | 3 | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 4 | 1 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 2 | 2 | 1 | 6 |  |  | C4 | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196 | C4 | 5937645 | 5937645 | 5937645 | 5937645 | 5937645 | C4 | 76120.6089 | 76120.6089 | 105927.5868 | 260603.2391 | 546025.8342 | C4 | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 76120.6089 | 152241.2178 | 317782.7604 | 0 | 0 | 546144.5871 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 0 | 76120.6089 | 423710.3472 | 260603.2391 | 0 | 760434.1952 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948 |  | 0 | 76120.6089 | 211855.1736 | 521206.4781 | 546025.8342 | 1355208.0948
|  |  | 94 | 94 |  | 42 | 13 | 32 | 7 | 0 |  | 39 | 13 | 32 | 9 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 37 | 12 | 33 | 10 | 2 |  | 0 | 0 | 0 | 0 | 0 |  | 32 | 13 | 26 | 15 | 8 | [22 empty] | 1147898.7822 | 499351.1944 | 1529594.3534 | 1063261.2153 | 0 | 4240105.5453 |  | 1254467.6347 | 499351.1944 | 1529594.3534 | 802657.9763 | 0 | 4086071.1587 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 1083957.4707 | 404961.6393 | 1614336.4228 | 1323864.4544 | 371297.5673 | 4798417.5545 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101 |  | 925626.6042 | 450634.0047 | 1169440.5583 | 1918039.8394 | 2227785.4035 | 6691526.4101
| 132kV UG Cable (Gas) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV UG Cable (Oil) |  | 24.121 | 24.121 | C1 | 3.232 | 17.356 | 3.533 | 0 | 0 | 24.121 | 3.232 | 17.356 | 3.533 | 2.954 | 0 | 27.075 | 0 | 0 | 0 | 0 | 0 | 0 | 3.226 | 10.377 | 10.518 | 0 | 0 | 24.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 7.759 | 16.362 | 0 | 0 | 24.121 |  |  | C1 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C1 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | 115434.2 | C1 | 687.9878 | 687.9878 | 23328.0975 | 56942.5365 | 119312.7891 | C1 | 2223.5767 | 11940.7168 | 82418.1684 | 168208.2529 | 0 | 264790.7147 |  | 2223.5767 | 11940.7168 | 82418.1684 | 0 | 0 | 96582.4619 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 2219.4487 | 7139.2497 | 245364.9293 | 0 | 0 | 254723.6278 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285 |  | 0 | 5338.0976 | 381694.3309 | 0 | 0 | 387032.4285
|  |  | 11.91 | 11.91 | C2 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 1.467 | 10.443 | 0 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 10.493 | 1.305 | 0 | 0 | 11.91 | 0 | 0 | 0 | 0 | 0 | 0 | 0.112 | 3.389 | 8.409 | 0 | 0 | 11.91 |  |  | C2 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C2 | 164906 | 164906 | 164906 | 164906 | 164906 | C2 | 982.8398 | 982.8398 | 33325.8535 | 81346.4807 | 170446.8416 | C2 | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 1441.8259 | 10263.7956 | 0 | 0 | 0 | 11705.6215 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 10312.9376 | 43490.2389 | 0 | 0 | 53913.2545 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244 |  | 110.0781 | 3330.8439 | 280237.1024 | 0 | 0 | 283678.0244
|  |  | 25.639 | 25.639 | C3 | 7.842 | 17.397 | 0 | 0.4 | 0 | 25.639 | 7.842 | 17.397 | 0 | 0.646 | 0 | 25.885 | 0 | 0 | 0 | 0 | 0 | 0 | 7.842 | 0.632 | 16.765 | 0 | 0.4 | 25.639 | 0 | 0 | 0 | 0 | 0 | 0 | 5.049 | 2.857 | 17.333 | 0 | 0.4 | 25.639 |  |  | C3 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C3 | 247359 | 247359 | 247359 | 247359 | 247359 | C3 | 1474.2596 | 1474.2596 | 49988.7803 | 122019.7211 | 255670.2624 | C3 | 11561.1441 | 25647.695 | 0 | 78824.7398 | 0 | 116033.5789 |  | 11561.1441 | 25647.695 | 0 | 48807.8884 | 0 | 86016.7275 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 11561.1441 | 931.7321 | 838061.9019 | 0 | 102268.105 | 952822.883 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308 |  | 7443.5369 | 4211.9598 | 866455.5291 | 0 | 102268.105 | 980379.1308
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336 | C4 | 412265 | 412265 | 412265 | 412265 | 412265 | C4 | 2457.0994 | 2457.0994 | 83314.6338 | 203366.2019 | 426117.104 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 61.67 | 61.67 |  | 12.541 | 45.196 | 3.533 | 0.4 | 0 |  | 12.541 | 45.196 | 3.533 | 3.6 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 11.18 | 21.502 | 28.588 | 0 | 0.4 |  | 0 | 0 | 0 | 0 | 0 |  | 5.161 | 14.005 | 42.104 | 0 | 0.4 | [22 empty] | 15226.5467 | 47852.2074 | 82418.1684 | 247032.9927 | 0 | 392529.9152 |  | 15226.5467 | 47852.2074 | 82418.1684 | 48807.8884 | 0 | 194304.8109 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 13890.6709 | 18383.9194 | 1126917.07 | 0 | 102268.105 | 1261459.7653 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837 |  | 7553.615 | 12880.9013 | 1528386.9625 | 0 | 102268.105 | 1651089.5837
| 132kV UG Cable (Non Pressurised) |  | 7.356 | 7.356 | C1 | 7.356 | 0 | 0 | 0 | 0 | 7.356 | 4.121 | 0 | 0 | 0 | 0 | 4.121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | 1127624.4 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 9.671 | 9.671 | C2 | 9.671 | 0 | 0 | 0 | 0 | 9.671 | 9.383 | 0 | 0 | 0 | 0 | 9.383 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 1610892 | 1610892 | 1610892 | 1610892 | 1610892 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 2.775 | 2.775 | C3 | 2.775 | 0 | 0 | 0 | 0 | 2.775 | 2.248 | 0 | 0 | 0 | 0 | 2.248 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 2416338 | 2416338 | 2416338 | 2416338 | 2416338 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 0.253 | 0.253 | C4 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0.253 | 0 | 0 | 0 | 0 | 0.253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 4027230 | 4027230 | 4027230 | 4027230 | 4027230 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
|  |  | 20.055 | 20.055 |  | 20.055 | 0 | 0 | 0 | 0 |  | 16.005 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Support - Tower |  | 1148 | 1148 | C1 | 334 | 653 | 121 | 40 | 0 | 1148 | 334 | 653 | 121 | 40 | 0 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 676 | 128 | 45 | 1 | 1148 | 0 | 0 | 0 | 0 | 0 | 0 | 267 | 705 | 125 | 48 | 3 | 1148 |  |  | C1 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C1 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | 554331.4 | C1 | 293.7956 | 293.7956 | 293.7956 | 14878.2548 | 50976.3155 | C1 | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 98127.7444 | 191848.5542 | 35549.2727 | 595130.191 | 0 | 920655.7624 |  | 87551.1013 | 198605.854 | 37605.8422 | 669521.4649 | 50976.3155 | 1044260.5779 |  | 87551.1013 | 198605.854 | 37605.8422 | 669521.4649 | 50976.3155 | 1044260.5779 |  | 78443.4364 | 207125.9276 | 36724.4552 | 714156.2292 | 152928.9466 | 1189378.9952 |  | 78443.4364 | 207125.9276 | 36724.4552 | 714156.2292 | 152928.9466 | 1189378.9952
|  |  | 1252 | 1252 | C2 | 303 | 763 | 127 | 59 | 0 | 1252 | 300 | 763 | 127 | 59 | 3 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 298 | 755 | 125 | 70 | 4 | 1252 | 0 | 0 | 0 | 0 | 0 | 0 | 294 | 743 | 132 | 71 | 12 | 1252 |  |  | C2 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C2 | 791902 | 791902 | 791902 | 791902 | 791902 | C2 | 419.7081 | 419.7081 | 419.7081 | 21254.6497 | 72823.3079 | C2 | 125912.418 | 320237.2498 | 53302.9236 | 1254024.3311 | 218469.9238 | 1971946.8463 |  | 127171.5422 | 320237.2498 | 53302.9236 | 1254024.3311 | 0 | 1754736.0467 |  | 125073.0019 | 316879.5853 | 52463.5075 | 1487825.4776 | 291293.2317 | 2273534.804 |  | 125073.0019 | 316879.5853 | 52463.5075 | 1487825.4776 | 291293.2317 | 2273534.804 |  | 123394.1696 | 311843.0886 | 55401.4639 | 1509080.1273 | 873879.695 | 2873598.5445 |  | 123394.1696 | 311843.0886 | 55401.4639 | 1509080.1273 | 873879.695 | 2873598.5445
|  |  | 501 | 501 | C3 | 45 | 396 | 45 | 15 | 0 | 501 | 45 | 366 | 45 | 45 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 39 | 366 | 81 | 15 | 0 | 501 | 0 | 0 | 0 | 0 | 0 | 0 | 35 | 349 | 101 | 14 | 2 | 501 |  |  | C3 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C3 | 1187853 | 1187853 | 1187853 | 1187853 | 1187853 | C3 | 629.5621 | 629.5621 | 629.5621 | 31881.9745 | 109234.9619 | C3 | 28330.2941 | 230419.7249 | 28330.2941 | 1434688.8534 | 0 | 1721769.1664 |  | 28330.2941 | 249306.5876 | 28330.2941 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 24552.9215 | 230419.7249 | 50994.5293 | 478229.6178 | 0 | 784196.7935 |  | 22034.6731 | 219717.1694 | 63585.7711 | 446347.6433 | 218469.9238 | 970155.1807 |  | 22034.6731 | 219717.1694 | 63585.7711 | 446347.6433 | 218469.9238 | 970155.1807
|  |  | 187 | 187 | C4 | 68 | 114 | 5 | 0 | 0 | 187 | 68 | 114 | 5 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 63 | 104 | 20 | 0 | 0 | 187 | 0 | 0 | 0 | 0 | 0 | 0 | 60 | 94 | 33 | 0 | 0 | 187 |  |  | C4 | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196 | C4 | 1979755 | 1979755 | 1979755 | 1979755 | 1979755 | C4 | 1049.2702 | 1049.2702 | 1049.2702 | 53136.6242 | 182058.2698 | C4 | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 71350.3702 | 119616.7971 | 5246.3508 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 66104.0195 | 109124.0956 | 20985.403 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181 |  | 62956.209 | 98631.3941 | 34625.9149 | 0 | 0 | 196213.5181
|  |  | 3088 | 3088 |  | 750 | 1926 | 298 | 114 | 0 |  | 747 | 1896 | 298 | 144 | 3 |  | 0 | 0 | 0 | 0 | 0 |  | 698 | 1901 | 354 | 130 | 5 |  | 0 | 0 | 0 | 0 | 0 |  | 656 | 1891 | 391 | 133 | 17 | [22 empty] | 323720.8267 | 862122.326 | 122428.8411 | 3283843.3756 | 218469.9238 | 4810585.2931 |  | 324979.9509 | 881009.1887 | 122428.8411 | 2327384.14 | 0 | 3655802.1207 |  | 303281.0442 | 855029.2598 | 162049.282 | 2635576.5603 | 342269.5472 | 4298205.6935 |  | 303281.0442 | 855029.2598 | 162049.282 | 2635576.5603 | 342269.5472 | 4298205.6935 |  | 286828.4882 | 837317.5797 | 190337.6052 | 2669583.9998 | 1245278.5654 | 5229346.2384 |  | 286828.4882 | 837317.5797 | 190337.6052 | 2669583.9998 | 1245278.5654 | 5229346.2384
| 132kV OHL Fittings and Conductors (Tower Lines) |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| 132kV OHL Fittings |  | 1974 | 1974 | C1 | 881 | 628 | 420 | 45 | 0 | 1974 | 669 | 628 | 420 | 48 | 209 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 881 | 200 | 455 | 401 | 37 | 1974 | 0 | 0 | 0 | 0 | 0 | 0 | 873 | 153 | 489 | 0 | 459 | 1974 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C1 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | 303327.5 | C1 | 24.2662 | 24.2662 | 33.366 | 78.8651 | 166.8301 | C1 | 16234.0878 | 15239.1736 | 14013.7305 | 3785.5272 | 34867.4961 | 84140.0152 |  | 21378.5222 | 15239.1736 | 14013.7305 | 3548.9318 | 0 | 54180.3581 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 21378.5222 | 4853.24 | 15181.5414 | 31624.9251 | 6172.7146 | 79210.9433 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348 |  | 21184.3926 | 3712.7286 | 16315.9862 | 0 | 76575.0274 | 117788.1348
|  |  | 1409 | 1409 | C2 | 820 | 306 | 245 | 38 | 0 | 1409 | 771 | 306 | 245 | 41 | 46 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 820 | 104 | 261 | 224 | 0 | 1409 | 0 | 0 | 0 | 0 | 0 | 0 | 816 | 99 | 230 | 0 | 264 | 1409 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C2 | 433325 | 433325 | 433325 | 433325 | 433325 | C2 | 34.666 | 34.666 | 47.6658 | 112.6645 | 238.3288 | C2 | 26727.486 | 10607.796 | 11678.1088 | 4619.2445 | 10963.1225 | 64595.7578 |  | 28426.12 | 10607.796 | 11678.1088 | 4281.251 | 0 | 54993.2758 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 28426.12 | 3605.264 | 12440.7608 | 25236.848 | 0 | 69708.9928 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025 |  | 28287.456 | 3431.934 | 10963.1225 | 0 | 62918.79 | 105601.3025
|  |  | 945 | 945 | C3 | 507 | 262 | 167 | 9 | 0 | 945 | 472 | 262 | 167 | 9 | 35 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 33 | 255 | 149 | 1 | 945 | 0 | 0 | 0 | 0 | 0 | 0 | 507 | 32 | 231 | 0 | 175 | 945 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C3 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | 649987.5 | C3 | 51.999 | 51.999 | 71.4986 | 168.9967 | 357.4931 | C3 | 24543.528 | 13623.738 | 11940.2704 | 1520.9707 | 12512.2594 | 64140.7665 |  | 26363.493 | 13623.738 | 11940.2704 | 1520.9707 | 0 | 53448.4721 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 26363.493 | 1715.967 | 18232.1494 | 25180.5157 | 357.4931 | 71849.6182 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402 |  | 26363.493 | 1663.968 | 16516.1824 | 0 | 62561.2969 | 107104.9402
|  |  | 436 | 436 | C4 | 313 | 97 | 26 | 0 | 0 | 436 | 309 | 97 | 26 | 0 | 4 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 11 | 92 | 20 | 0 | 436 | 0 | 0 | 0 | 0 | 0 | 0 | 313 | 8 | 89 | 0 | 26 | 436 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055 | C4 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | 1083312.5 | C4 | 86.665 | 86.665 | 119.1644 | 281.6612 | 595.8219 | C4 | 26779.485 | 8406.505 | 3098.2738 | 0 | 2383.2875 | 40667.5513 |  | 27126.145 | 8406.505 | 3098.2738 | 0 | 0 | 38630.9238 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27126.145 | 953.315 | 10963.1225 | 5633.225 | 0 | 44675.8075 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631 |  | 27126.145 | 693.32 | 10605.6294 | 0 | 15491.3688 | 53916.4631
|  |  | 4764 | 4764 |  | 2521 | 1293 | 858 | 92 | 0 |  | 2221 | 1293 | 858 | 98 | 294 |  | 0 | 0 | 0 | 0 | 0 |  | 2521 | 348 | 1063 | 794 | 38 |  | 0 | 0 | 0 | 0 | 0 |  | 2509 | 292 | 1039 | 0 | 924 | [22 empty] | 94284.5868 | 47877.2126 | 40730.3834 | 9925.7424 | 60726.1655 | 253544.0907 |  | 103294.2802 | 47877.2126 | 40730.3834 | 9351.1535 | 0 | 201253.0297 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 103294.2802 | 11127.786 | 56817.574 | 87675.5139 | 6530.2078 | 265445.3618 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407 |  | 102961.4866 | 9501.9506 | 54400.9205 | 0 | 217546.483 | 384410.8407
| 132kV OHL Conductor (Tower Lines) |  | 582.743 | 582.743 | C1 | 74.232 | 147.439 | 357.706 | 3.366 | 0 | 582.743 | 74.466 | 147.903 | 358.632 | 3.366 | 0 | 584.367 | 0 | 0 | 0 | 0 | 0 | 0 | 54.539 | 82.501 | 378.804 | 58.44 | 8.459 | 582.743 | 0 | 0 | 0 | 0 | 0 | 0 | 10.436 | 114.53 | 335.821 | 55.057 | 66.899 | 582.743 |  |  | C1 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C1 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | 303582.3 | C1 | 24.2866 | 24.2866 | 33.3941 | 85.003 | 179.1136 | C1 | 1808.5248 | 3592.0586 | 11976.176 | 286.1202 | 0 | 17662.8797 |  | 1802.8417 | 3580.7897 | 11945.2531 | 286.1202 | 0 | 17615.0047 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 1324.566 | 2003.6675 | 12649.8009 | 4967.5779 | 1515.1216 | 22460.7338 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952 |  | 253.4548 | 2781.5425 | 11214.4243 | 4680.0126 | 11982.5178 | 30911.952
|  |  | 372.373 | 372.373 | C2 | 155.425 | 72.674 | 144.274 | 0 | 0 | 372.373 | 155.914 | 72.903 | 144.64 | 0 | 0 | 373.457 | 0 | 0 | 0 | 0 | 0 | 0 | 154.935 | 21.698 | 167.759 | 27.981 | 0 | 372.373 | 0 | 0 | 0 | 0 | 0 | 0 | 14.814 | 152.391 | 160.951 | 16.236 | 27.981 | 372.373 |  |  | C2 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C2 | 433689 | 433689 | 433689 | 433689 | 433689 | C2 | 34.6951 | 34.6951 | 47.7058 | 121.4329 | 255.8765 | C2 | 5409.4549 | 2529.3783 | 6900.1655 | 0 | 0 | 14838.9987 |  | 5392.489 | 2521.4332 | 6882.7051 | 0 | 0 | 14796.6273 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 5375.4884 | 752.8147 | 8003.0756 | 3397.8145 | 0 | 17529.1933 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577 |  | 513.9735 | 5287.224 | 7678.2946 | 1971.5849 | 7159.6806 | 22610.7577
|  |  | 282.328 | 282.328 | C3 | 32.76 | 107.715 | 141.853 | 0 | 0 | 282.328 | 32.863 | 108.054 | 142.288 | 0 | 0 | 283.205 | 0 | 0 | 0 | 0 | 0 | 0 | 22.451 | 91.227 | 153.632 | 15.018 | 0 | 282.328 | 0 | 0 | 0 | 0 | 0 | 0 | 0.893 | 82.052 | 175.652 | 23 | 0.731 | 282.328 |  |  | C3 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C3 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | 650533.5 | C3 | 52.0427 | 52.0427 | 71.5587 | 182.1494 | 383.8148 | C3 | 1710.2786 | 5623.4197 | 10181.9422 | 0 | 0 | 17515.6405 |  | 1704.9182 | 5605.7773 | 10150.8141 | 0 | 0 | 17461.5096 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 1168.4102 | 4747.6976 | 10993.7039 | 2735.5194 | 0 | 19645.3311 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106 |  | 46.4741 | 4270.206 | 12569.4261 | 4189.4357 | 280.5686 | 21356.1106
|  |  | 131.686 | 131.686 | C4 | 95.835 | 21.625 | 14.226 | 0 | 0 | 131.686 | 96.137 | 21.693 | 14.271 | 0 | 0 | 132.101 | 0 | 0 | 0 | 0 | 0 | 0 | 86.825 | 23.588 | 21.273 | 0 | 0 | 131.686 | 0 | 0 | 0 | 0 | 0 | 0 | 42.431 | 60.567 | 28.688 | 0 | 0 | 131.686 |  |  | C4 | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059 | C4 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | 1084222.5 | C4 | 86.7378 | 86.7378 | 119.2645 | 303.5823 | 639.6913 | C4 | 8338.7119 | 1881.6031 | 1702.0233 | 0 | 0 | 11922.3383 |  | 8312.5171 | 1875.7049 | 1696.6564 | 0 | 0 | 11884.8784 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 7531.0095 | 2045.9712 | 2537.1132 | 0 | 0 | 12114.0939 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792 |  | 3680.3716 | 5253.4483 | 3421.4593 | 0 | 0 | 12355.2792
|  |  | 1369.13 | 1369.13 |  | 358.252 | 349.453 | 658.059 | 3.366 | 0 |  | 359.38 | 350.553 | 659.831 | 3.366 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 318.75 | 219.014 | 721.468 | 101.439 | 8.459 |  | 0 | 0 | 0 | 0 | 0 |  | 68.574 | 409.54 | 701.112 | 94.293 | 95.611 | [22 empty] | 17266.9702 | 13626.4598 | 30760.307 | 286.1202 | 0 | 61939.8572 |  | 17212.766 | 13583.705 | 30675.4288 | 286.1202 | 0 | 61758.0201 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 15399.4741 | 9550.151 | 34183.6935 | 11100.9118 | 1515.1216 | 71749.352 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994 |  | 4494.274 | 17592.4208 | 34883.6043 | 10841.0332 | 19422.7671 | 87234.0994
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 |  | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 |  | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 |  | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 |  | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 |  | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018
| Other | [66 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
| Submarine Cables |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] |  | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C1 | 0 | 0 | 0 | 0 | 0 | C1 | 0 | 0 | 0 | 0 | 0 | C1 | [5 empty] | C1 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C2 | 0 | 0 | 0 | 0 | 0 | C2 | 0 | 0 | 0 | 0 | 0 | C2 | [5 empty] | C2 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C3 | 0 | 0 | 0 | 0 | 0 | C3 | 0 | 0 | 0 | 0 | 0 | C3 | [5 empty] | C3 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  |  | C4 | 0 | 0 | 0 | 0 | 0 | C4 | 0 | 0 | 0 | 0 | 0 | C4 | [5 empty] | C4 | [5 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0 | [6 empty] | 0
|  |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [22 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
[63 empty] | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0
| TOTAL |  | 519588.883 | 519588.883 |  | 96564.04 | 320797.18 | 32683.208 | 51195.545 | 18348.91 |  | 79643.489 | 320933.054 | 33723.601 | 53438.35 | 31343.641 |  | 0 | 0 | 0 | 0 | 0 |  | 65903.872 | 318927.121 | 33587.545 | 57631.431 | 35753.859 |  | 0 | 0 | 0 | 0 | 0 |  | 39380.523 | 318896.705 | 34598.74 | 62110.048 | 56817.812 |  |  |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | [7 empty] | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 |  | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 |  | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 |  | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 |  | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 |  | 8379358.875 | 29293203.6074 | 11180183.8339 | 25356336.1149 | 59909425.7855 | 134118508.2167
Health Index Definitions
|  |  | HI1 | New or as new | [57 empty] | LV Network | 1857984.115 | 9017481.095 | 1793943.5538 | 6051378.2712 | 6253992.7972 | 24974779.8322 | LV Network | 2361289.0798 | 9014901.5192 | 1740681.0314 | 5830617.5932 | 3523779.3175 | 22471268.5411 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 1586789.0035 | 9026340.1657 | 1873662.9589 | 6476194.236 | 6958723.7201 | 25921710.0843 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342 | LV Network | 814308.0405 | 9015922.6586 | 1828054.3459 | 7260488.7997 | 11166061.0896 | 30084834.9342
|  |  | HI2 | Good or seviceable condition | [57 empty] | HV Network | 6439227.0098 | 14926153.5381 | 4702282.3798 | 7635840.7305 | 12899368.7986 | 46602872.4568 | HV Network | 7434071.5816 | 14895298.7336 | 4602701.1344 | 7307289.9692 | 7939380.3605 | 42178741.7793 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 5917146.406 | 14971976.6077 | 4562999.7497 | 8815012.636 | 15314937.0516 | 49582072.4509 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219 | HV Network | 4401790.2852 | 15019894.9369 | 4410161.1151 | 9708695.8424 | 24755690.2422 | 58296232.4219
|  |  | HI3 | Deterioration requires assessment and monitoring | [57 empty] | EHV Network | 2420264.0667 | 3347170.377 | 3006188.926 | 5748878.4089 | 5427482.4941 | 19949984.2727 | EHV Network | 2607403.8665 | 3347507.5005 | 2988186.2741 | 5624518.73 | 4511493.561 | 19079109.9322 | EHV Network | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 | EHV Network | 2066135.4127 | 3634481.9883 | 2220137.3879 | 4685818.8122 | 13295492.0857 | 25902065.6869 | EHV Network | 1577061.3003 | 3802511.539 | 1920577.4963 | 3839176.844 | 19650715.4154 | 30790042.5951 | EHV Network | 1577061.3003 | 3770609.5321 | 1920577.4963 | 3724706.5147 | 19650715.4154 | 30643670.2588
|  |  | HI4 | Material deterioration, intervention requires consideration | [57 empty] | 132kV Network | 1945740.2952 | 1501439.3681 | 1899643.4431 | 4740031.3522 | 427117.207 | 10513971.6656 | 132kV Network | 2111499.7097 | 1520283.476 | 1899558.565 | 3324169.1843 | 50847.8842 | 8906358.8192 | 132kV Network | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 | 132kV Network | 1859432.4783 | 1386371.7165 | 3046764.4855 | 4159703.0936 | 1159014.331 | 11611286.105 | 132kV Network | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018 | 132kV Network | 1586199.249 | 1486776.4798 | 3021390.8766 | 4662444.9581 | 4336959.0383 | 15093770.6018
|  |  | HI5 | End of serviceable life, intervention required | [57 empty] | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0 | Other | 0 | 0 | 0 | 0 | 0 | 0
[62 empty] | Total | 12663215.4868 | 28792244.3781 | 11402058.3028 | 24176128.7628 | 25007961.2968 | 102041608.2273 | Total | 14514264.2376 | 28777991.2293 | 11231127.0049 | 22086595.4768 | 16025501.1232 | 92635479.0718 | Total | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 | Total | 11429503.3005 | 29019170.4782 | 11703564.5821 | 24136728.7778 | 36728167.1884 | 113017134.327 | Total | 8379358.875 | 29325105.6143 | 11180183.8339 | 25470806.4443 | 59909425.7855 | 134264880.5529 | Total | 8379358.875 | 29293203.6074 | 11180183.8339 | 25356336.1149 | 59909425.7855 | 134118508.2167
Criticality Index Definitions
|  |  | C1 | Low criticality
|  |  | C2 | Average criticality
|  |  | C3 | High criticality
|  |  | C4 | Very high criticality

## SWEST - Ave. Cons. of Failure
Secondary deliverables RIIO-ED1 - Average Consequence of Asset Failure
SWEST
Price base (2012/13)
| ASSET CATEGORIES | RIIO-ED1 period |  |  |  |  | ASSET CATEGORIES | RIIO-ED1 period
|  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure |  | Network Performance | Safety | Environmental | Financial consequence of repair/ replacement | Average Consequence of Asset Failure
| LV Network | [5 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other |  |  |  |  | 0
| LV UGB | 0 | 0 | 0 | 0 | 0 | LV UGB |  |  |  |  | 0
| LV OHL Support | 502 | 1405 | 278 | 2688 | 4873 | LV OHL Support | 502 | 1405 | 278 | 2688 | 4873
| LV Switchgear (at s/s) | 763 | 641 | 488 | 3771 | 5663 | LV Switchgear (at s/s) | 763 | 641 | 488 | 3771 | 5663
| LV UGB and LV Pillar OD (not at s/s) | 933 | 781 | 487 | 2469 | 4670 | LV UGB and LV Pillar OD (not at s/s) | 933 | 781 | 487 | 2469 | 4670
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| HV Network | [5 empty] | HV Network
| HV Switchgear (GM) - Primary | 48320 | 1213 | 1901 | 11522 | 62956 | HV Switchgear (GM) - Primary | 48320 | 1213 | 1901 | 11522 | 62956
| HV Switchgear (GM) - Distribution | 6914 | 1622 | 2365 | 4254 | 15155 | HV Switchgear (GM) - Distribution | 6914 | 1622 | 2365 | 4254 | 15155
| HV Transformer (GM) | 6675 | 1241 | 3654 | 4722 | 16292 | HV Transformer (GM) | 6675 | 1241 | 3654 | 4722 | 16292
| HV UG Cable | 21246 | 142 | 1102 | 10500 | 32990 | HV UG Cable | 21246 | 142 | 1102 | 10500 | 32990
| HV OHL Support - Poles | 1985 | 1463 | 478 | 2920 | 6846 | HV OHL Support - Poles | 1985 | 1463 | 478 | 2920 | 6846
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| EHV Network | [5 empty] | EHV Network
| EHV Switchgear (GM) | 82205 | 737 | 3545 | 15027 | 101514 | EHV Switchgear (GM) | 82205 | 737 | 3545 | 15027 | 101514
| EHV Transformer | 252538 | 961 | 18652 | 104435 | 376586 | EHV Transformer | 252538 | 961 | 18652 | 104435 | 376586
| EHV UG Cable (Gas) | 1976 | 7 | 423 | 6018 | 8424 | EHV UG Cable (Gas) | 1976 | 7 | 423 | 6018 | 8424
| EHV UG Cable (Oil) | 47104 | 710 | 11901 | 12557 | 72272 | EHV UG Cable (Oil) | 47104 | 710 | 11901 | 12557 | 72272
| EHV UG Cable (Non Pressurised) | 36616 | 142 | 1600 | 12307 | 50665 | EHV UG Cable (Non Pressurised) | 36616 | 142 | 1600 | 12307 | 50665
| EHV OHL Support - Towers | 127939 | 25436 | 2956 | 63510 | 219841 | EHV OHL Support - Towers | 127939 | 25436 | 2956 | 63510 | 219841
| EHV OHL Support - Poles | 5955 | 1468 | 478 | 4580 | 12481 | EHV OHL Support - Poles | 5955 | 1468 | 478 | 4580 | 12481
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| EHV OHL Fittings | 84836 | 12718 | 880 | 4000 | 102434 | EHV OHL Fittings | 84836 | 12718 | 880 | 4000 | 102434
| EHV OHL Conductor (Tower Lines) | 86729 | 12718 | 880 | 4000 | 104327 | EHV OHL Conductor (Tower Lines) | 86729 | 12718 | 880 | 4000 | 104327
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| 132kV Network | [5 empty] | 132kV Network
| 132kV CBs | 217321 | 944 | 6684 | 26385 | 251334 | 132kV CBs | 217321 | 944 | 6684 | 26385 | 251334
| 132kV Transformer | 2030169 | 1261 | 55430 | 288198 | 2375058 | 132kV Transformer | 2030169 | 1261 | 55430 | 288198 | 2375058
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas) |  |  |  |  | 0
| 132kV UG Cable (Oil) | 127182 | 710 | 11901 | 25113 | 164906 | 132kV UG Cable (Oil) | 127182 | 710 | 11901 | 25113 | 164906
| 132kV UG Cable (Non Pressurised) | 1382681 | 710 | 2501 | 225000 | 1610892 | 132kV UG Cable (Non Pressurised) | 1382681 | 710 | 2501 | 225000 | 1610892
| 132kV OHL Support - Tower | 625094 | 25436 | 4249 | 137123 | 791902 | 132kV OHL Support - Tower | 625094 | 25436 | 4249 | 137123 | 791902
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines) |  |  |  |  | 0
| 132kV OHL Fittings | 415727 | 12718 | 880 | 4000 | 433325 | 132kV OHL Fittings | 415727 | 12718 | 880 | 4000 | 433325
| 132kV OHL Conductor (Tower Lines) | 416091 | 12718 | 880 | 4000 | 433689 | 132kV OHL Conductor (Tower Lines) | 416091 | 12718 | 880 | 4000 | 433689
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| Other | [5 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | Submarine Cables |  |  |  |  | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | [Please insert new asset category as required]

## SWEST - Probs. of Failure
Probabilities of Asset Failure
SWEST
Price base (2012/13)
Average Probabilities of Asset Failure
| ASSET CATEGORIES | HI Rating | [9 empty] | ASSET CATEGORIES | HI1 | HI2 | HI3 | HI4 | HI5
|  | HI 1 |  | HI 2 |  | HI 3 |  | HI 4 |  | HI 5
|  | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary | Low boundary | High boundary
| LV Network | [10 empty] | LV Network
| LV Switchgear and Other | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV Switchgear and Other
| LV UGB | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | LV UGB
| LV OHL Support | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | LV OHL Support | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| LV Switchgear (at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV Switchgear (at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| LV UGB and LV Pillar OD (not at s/s) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | LV UGB and LV Pillar OD (not at s/s) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| HV Network | [10 empty] | HV Network
| HV Switchgear (GM) - Primary | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Primary | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Switchgear (GM) - Distribution | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV Switchgear (GM) - Distribution | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| HV Transformer (GM) | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.019216 | 0.053094 | 0.053094 | 0.079656 | 0.079656 | 0.20984 | HV Transformer (GM) | 0.01922 | 0.01922 | 0.02673 | 0.06577 | 0.13781
| HV UG Cable | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | HV UG Cable
| HV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | HV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| EHV Network | [10 empty] | EHV Network
| EHV Switchgear (GM) | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Switchgear (GM) | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV UG Cable (Gas) | 0.093876 | 0.093876 | 0.093876 | 0.093876 | 0.093876 | 6.2683 | 6.2683 | 9.4042 | 9.4042 | 24.7742 | EHV UG Cable (Gas) | 0.09388 | 0.09388 | 3.1811 | 7.7649 | 16.27
| EHV UG Cable (Oil) | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.39821 | 0.39821 | 0.59743 | 0.59743 | 1.5738 | EHV UG Cable (Oil) | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336
| EHV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV UG Cable (Non Pressurised)
| EHV OHL Support - Towers | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Towers | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| EHV OHL Support - Poles | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | EHV OHL Support - Poles | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| EHV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | EHV OHL Fittings and Conductors (Tower Lines)
| [Please insert new asset category as required] | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0033335 | 0.0092105 | 0.0092105 | 0.013818 | 0.013818 | 0.036402 | EHV OHL Fittings | 0.00333 | 0.00333 | 0.00464 | 0.01141 | 0.02391
| [Please insert new asset category as required] | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 0.00022574 | 0.00022574 | 0.00033866 | 0.00033866 | 0.00089217 | EHV OHL Conductor (Tower Lines) | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| 132kV Network | [10 empty] | 132kV Network
| 132kV CBs | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV CBs | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV Transformer | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.012823 | 0.035429 | 0.035429 | 0.053153 | 0.053153 | 0.14003 | 132kV Transformer | 0.01282 | 0.01282 | 0.01784 | 0.04389 | 0.09196
| 132kV UG Cable (Gas) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Gas)
| 132kV UG Cable (Oil) | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.0059637 | 0.39821 | 0.39821 | 0.59743 | 0.59743 | 1.5738 | 132kV UG Cable (Oil) | 0.00596 | 0.00596 | 0.20209 | 0.49329 | 1.0336
| 132kV UG Cable (Non Pressurised) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV UG Cable (Non Pressurised)
| 132kV OHL Support - Tower | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.00053059 | 0.053153 | 0.053153 | 0.14003 | 132kV OHL Support - Tower | 0.00053 | 0.00053 | 0.00053 | 0.02684 | 0.09196
| 132kV OHL Fittings and Conductors (Tower Lines) | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 132kV OHL Fittings and Conductors (Tower Lines)
| [Please insert new asset category as required] | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 7.6928e-05 | 0.00021255 | 0.00021255 | 0.00031888 | 0.00031888 | 0.00084005 | 132kV OHL Fittings | 8e-05 | 8e-05 | 0.00011 | 0.00026 | 0.00055
| [Please insert new asset category as required] | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 8.17e-05 | 0.00022574 | 0.00022574 | 0.00033866 | 0.00033866 | 0.00089217 | 132kV OHL Conductor (Tower Lines) | 8e-05 | 8e-05 | 0.00011 | 0.00028 | 0.00059
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Other | [10 empty] | Other
| Submarine Cables | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | Submarine Cables
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| [Please insert new asset category as required] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## RIIO-ED1 Monetised Risk Profile
| Start ED1 | Mid ED1 |  | End ED1
| Position at Beginning of RIIO-ED1 | Mid Period (Without Investment) | Mid Period (With Investment) | End of RIIO-ED1 (Without Investment) | End of RIIO-ED1 (With Investment)
LV Network | 22471268.5411 | 25921710.0843 | 21596512.8358 | 30084834.9342 | 21176011.765
HV Network | 42178741.7793 | 49582072.4509 | 39412991.219 | 58296232.4219 | 37316982.6123
EHV Network | 19079109.9322 | 25902065.6869 | 18838437.9279 | 30790042.5951 | 16097908.8056
132kV Network | 8906358.8192 | 11611286.105 | 9347878.5998 | 15093770.6018 | 8400543.5729
Other | 0 | 0 | 0 | 0 | 0
Total | 92635479.0718 | 113017134.327 | 89195820.5825 | 134264880.5529 | 82991446.7559
|  | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to mid-point without investment | Increase in risk since start of RIIO-ED1 | Reduction in risk compared to end-point without investment (Secondary deliverables target)
LV Network |  | 3450441.5432 | -4325197.2484 | 7613566.3931 | -8908823.1692
HV Network |  | 7403330.6716 | -10169081.2319 | 16117490.6426 | -20979249.8095
EHV Network |  | 6822955.7546 | -7063627.7589 | 11710932.6628 | -14692133.7894
132kV Network |  | 2704927.2858 | -2263407.5052 | 6187411.7827 | -6693227.0289
Other |  | 0 | 0 | 0 | 0
|  | 0 | 0 | 0 | 0
Total |  | 20381655.2552 | -23821313.7445 | 41629401.4812 | -51273433.797