## High-voltage Direct Current
Reference | Section | HVDC TEXT | Obligation on |  |  |  | Multiple TSO Clause
|  |  | TO | SO | IC | OFTO
[Recitals hidden below]
Having regard to the Treaty on the Functioning of the European Union,
| Recitals | Having regard to Regulation (EC) No 714/2009 of the European Parliament and of the Council of 13 July 2009 on conditions for access to the network for cross-border exchanges in electricity and repealing Regulation (EC) No 1228/2003 , and in particular Article 6(11) thereof, Whereas:
1 | Recitals | The swift completion of a fully functioning and interconnected internal energy market is crucial to maintaining security of energy supply, increasing competitiveness and ensuring that all consumers can purchase energy at affordable prices.
2 | Recitals | Regulation (EC) No 714/2009 sets out non-discriminatory rules governing access to the network for cross-border exchanges in electricity with a view to ensuring the proper functioning of the internal market in electricity. In addition Article 5 of Directive 2009/72/EC of the European Parliament and of the Council requires that Member States or, where Member States have so provided, regulatory authorities ensure, inter alia, that objective and non-discriminatory technical rules are developed which establish minimum technical design and operational requirements for the connection to the system. Where requirements constitute terms and conditions for connection to national networks, Article 37(6) of the same Directive requires regulatory authorities to be responsible for fixing or approving at least the methodologies used to calculate or establish them. In order to provide system security within the interconnected transmission system, it is essential to establish a common understanding of the requirements for High-Voltage Direct Current (HVDC) systems and direct current-connected power park modules (DC-connected power park modules). Those requirements that contribute to maintaining, preserving and restoring system security in order to facilitate proper functioning of the internal electricity market within and between synchronous areas, and to achieve cost efficiencies, should be regarded as cross-border network issues and market integration issues.
3 | Recitals | Harmonised rules for grid connection for HVDC systems and DC-connected power park modules should be set out in order to provide a clear legal framework for grid connections, facilitate Union-wide trade in electricity, ensure system security, facilitate the integration of renewable electricity sources, increase competition, and allow more efficient use of the network and resources, for the benefit of consumers.
4 | Recitals | System security depends partly on the technical capabilities of HVDC systems and DC-connected power park modules. Therefore regular coordination at the level of the transmission and distribution networks and adequate performance of the equipment connected to the transmission and distribution networks with sufficient robustness to cope with disturbances and to help to prevent any major disruption or to facilitate restoration of the system after a collapse are fundamental prerequisites.
5 | Recitals | Secure system operation is only possible if there is close cooperation between owners of HVDC systems and DC-connected power park modules and system operators. In particular, the functioning of the system under abnormal operating conditions depends on the response of the HVDC systems and DC-connected power park modules to deviations from the reference 1 per unit (pu) values of voltage and nominal frequency. In the context of system security, the networks and the HVDC systems and DC-connected power park modules should be considered as one entity from a system engineering point of view, given that those parts are interdependent. Therefore, as a prerequisite for grid connection, relevant technical requirements should be set for HVDC systems and DC-connected power park modules.
6 | Recitals | Regulatory authorities should consider the reasonable costs effectively incurred by system operators in the implementation of this Regulation when fixing or approving transmission or distribution tariffs or their methodologies or when approving the terms and conditions for connection and access to national networks in accordance with Article 37(1) and (6) of Directive 2009/72/EC and with Article 14 of Regulation (EC) No 714/2009.
7 | Recitals | Different synchronous electricity systems in the Union have different characteristics which need to be taken into account when setting the requirements for HVDC systems and DC-connected power park modules. It is therefore appropriate to consider regional specificities when establishing network connection rules as required by Article 8(6) of Regulation (EC) No 714/2009.
8 | Recitals | In view of the need to provide regulatory certainty, the requirements of this Regulation should apply to new HVDC systems and new DC-connected power park modules but should not apply to HVDC systems and DC-connected power park modules already existing or at an advanced stage of planning but not yet completed unless the relevant regulatory authority or Member State decides otherwise based on evolution of system requirements and a full cost-benefit analysis, or where there has been substantial modernisation of those facilities.
9 | Recitals | Due to its cross-border impact, this Regulation should aim at the same frequency-related requirements for all voltage levels, at least within a synchronous area. That is necessary because, within a synchronous area, a change in frequency in one Member State would immediately impact frequency and could damage equipment in all other Member States.
10 | Recitals | To ensure system security, it should be possible for HVDC systems and DC-connected power park modules in each synchronous area of the interconnected system to remain connected to the system for specified frequemcy and voltage ranges.
11 | Recitals | Voltage ranges should be coordinated between interconnected systems because they are crucial to secure planning and operation of a power system within a synchronous area. Disconnections because of voltage disturbances have an impact on neighbouring systems. Failure to specify voltage ranges could lead to widespread uncertainty in planning and operation of the system with respect to operation beyond normal operating conditions.
12 | Recitals | Appropriate and proportionate compliance testing should be introduced so that system operators can ensure operational security. In accordance with Article 37(1)(b) of Directive 2009/72/EC, regulatory authorities are responsible for ensuring that system operators are compliant with this Regulation.
13 | Recitals | The regulatory authorities, Member States and system operators should ensure that, in the process of developing and approving the requirements for network connection, they are harmonised to the extent possible, in order to ensure full market integration. Established technical standards should be taken into particular consideration in the development of connection requirements.
14 | Recitals | A process for derogating from the rules should be set out in this Regulation to take into account local circumstances where exceptionally, for example, compliance with those rules could jeopardise the stability of the local network or where the safe operation of an HVDC system or DC-connected power park module might require operating conditions that are not in line with this Regulation.
15 | Recitals | In the case of DC-connected power park modules, new modules could, in the future form part of a meshed off-shore grid connecting to more than one synchronous area. In this case, certain technical requirements should be set in order to maintain system security and ensure that future meshed networks can be developed cost-effectively. However, for certain requirements, DC-connected power park modules should only be required to fit the equipment needed for system security at the time it becomes necessary.
16 | Recitals | Therefore, the owners of DC-connected power park modules which are, or will be, connected to one synchronous area with a radial connection should have the possibility to apply, via an expedited process, for derogations to requirements that will only be needed where the power park modules become connected to a meshed grid and which take account of case-by-case circumstances. They should also be informed as early as possible whether they qualify for a derogation for the purposes of their investment decision-making.
17 | Recitals | Subject to approval by the relevant regulatory authority, or other authority where applicable in a Member State, system operators should be allowed to propose derogations for certain classes of HVDC systems and DC-connected power park modules.
18 | Recitals | This Regulation has been adopted on the basis of Regulation (EC) No 714/2009 which it supplements and of which it forms an integral part. References to Regulation (EC) No 714/2009 in other legal acts should be understood as also referring to this Regulation.
19 | Recitals | The measures provided for in this Regulation are in accordance with the opinion of the Committee referred to in Article 23(1) of Regulation (EC) No 714/2009,
| General Provisions | Title 1 - GENERAL PROVISIONS
General Provisions
| General Provisions | Article 1 - Subject matter
General Provisions
| General Provisions | This Regulation establishes a network code which lays down the requirements for grid connections of high-voltage direct current (HVDC) systems and DC-connected power park modules. It, therefore, helps to ensure fair conditions of competition in the internal electricity market, to ensure system security and the integration of renewable electricity sources, and to facilitate Union-wide trade in electricity. This regulation also lays down the obligations for ensuring that system operators make appropriate use of HVDC systems and DC-connected power park modules capabilities in a transparent and non-discriminatory manner to provide a level playing field throughout the Union.
| General Provisions | Article 2 - DEFINITIONS
| General Provisions | For the purposes of this Regulation, the definitions in Article 2 of Regulation (EC) No 714/2009, Article 2 of Commission Regulation No 2015/1222 , Article 2 of Commission Regulation (EU) No 543/2013 , Article 2 of Commission Regulation (EC) N° [RfG], Article 2 of Commission Regulation (EC) N° [DCC] and Article 2 of Directive 2009/72/EC shall apply. In addition, the following definitions shall apply:
General Provisions
1 | General Provisions | 'HVDC system' means an electrical power system which transfers energy in the form of high-voltage direct current between two or more alternating current (AC) buses and comprises at least two HVDC converter stations with DC transmission lines or cables between the HVDC converter stations;
2 | General Provisions | DC-connected power park module' means a power park module that is connected via one or more interface points to one or more HVDC systems;
3 | General Provisions | embedded HVDC system' means an HVDC system connected within a control area that is not installed for the purpose of connecting a DC-connected power park module at the time of installation, nor installed for the purpose of connecting a demand facility;
4 | General Provisions | HVDC converter station' means part of an HVDC system which consists of one or more HVDC converter units installed in a single location together with buildings, reactors, filters, reactive power devices, control, monitoring, protective, measuring and auxiliary equipment;
5 | General Provisions | 'HVDC interface point' means an AC point in a network connecting equipment owned by two or more parties, at which technical specifications affecting the performance of the equipment of one or more parties can be prescribed;
6 | General Provisions | DC-connected power park module owner' means a natural or legal entity owning a DC-connected power park module;
7 | General Provisions | maximum HVDC active power transmission capacity' (Pmax) means the maximum continuous active power which an HVDC system can exchange with the network at each connection point as defined in the connection agreement or as agreed between the relevant system operator and the HVDC system owner;
8 | General Provisions | minimum HVDC active power transmission capacity' (Pmin) means the minimum continuous active power which an HVDC system can exchange with the network at each connection point as defined in the connection agreement or as agreed between the relevant system operator and the HVDC system owner;
9 | General Provisions | HVDC system maximum current' means the highest phase current, associated with an operating point inside the U-Q/Pmax-profile of the HVDC converter station at maximum HVDC active power transmission capacity;
10 | General Provisions | HVDC converter unit' means a unit comprising one or more converter bridges, together with one or more converter transformers, reactors, converter unit control equipment, essential protective and switching devices and auxiliaries, if any, used for the conversion
General Provisions
| General Provisions | Article 3 - Scope of application
General Provisions
1 | General Provisions | The requirements of this Regulation shall apply to:
a) | General Provisions | HVDC systems connecting synchronous areas or control areas, including back-to-back schemes;
b) | General Provisions | HVDC systems connecting power park modules to a transmission network or a distribution network, pursuant to paragraph 2;
c) | General Provisions | embedded HVDC systems within one control area and connected to the transmission network; and
d) | General Provisions | embedded HVDC systems within one control area and connected to the distribution network when a cross-border impact is demonstrated by the relevant transmission system operator (TSO). The relevant TSO shall consider the long-term development of the network in this assessment
2 | General Provisions | Relevant system operators, in coordination with relevant TSOs, shall propose to competent regulatory authorities the application of this Regulation for DC-connected power park modules with a single connection point to a transmission network or distribution network which is not part of a synchronous area for approval in accordance with Article 5. All other power park modules which are AC-collected but are DC-connected to a synchronous area are considered DC-connected power park modules and fall within the scope of this Regulation. |  | ü |  |  | ü
3 | General Provisions | Articles 55 to 59, 67 to 72 and 82 shall not apply to HVDC systems within one control area referred to in points (c) and (d) of paragraph 1 where:
a) | General Provisions | the HVDC system has at least one HVDC converter station owned by the relevant TSO;
b) | General Provisions | the HVDC system is owned by an entity which exercises control over the relevant TSO;
c) | General Provisions | the HVDC system is owned by an entity directly or indirectly controlled by an entity which also exercises control over the relevant TSO.
4 | General Provisions | The connection requirements for HVDC systems provided for in Title II shall apply at the AC connection points of such systems, except the requirements provided for in Articles 29(4), 29(5) and 31(5), which can apply at other connection points, and Article 19(1) which may apply at the terminals of the HVDC converter station.
5 | General Provisions | The connection requirements for DC-connected power park modules and remote-end HVDC converter stations, provided for in Title III shall apply at the HVDC interface point of such systems, except the requirements provided for in Article 39(1)(a) and Article 47(2), which apply at the connection point in the synchronous area to which frequency response is being provided.
6 | General Provisions | The relevant system operator shall refuse to allow the connection of a new HVDC system or DC-connected power park module which does not comply with the requirements set out in this Regulation and which is not covered by a derogation granted by the National regulatory authority, or other authority where applicable in a Member State pursuant to Title VII. The relevant system operator shall communicate such refusal, by means of a reasoned statement in writing, to the demand facility owner or distribution network owner and, unless specified otherwise by the regulatory authority, to the regulatory authority. |  | ü |  |  | ü
7 | General Provisions | This Regulation shall not apply to:
a) | General Provisions | HVDC systems whose connection point is below 110kV unless a cross-border impact is demonstrated by the relevant TSO. The relevant TSO shall consider the long-term development of the network in this assessment; |  | ü |  |  | ü
b) | General Provisions | HVDC systems or DC-connected power park modules connected to the transmission system and distribution systems or to parts of the transmission system, or distribution systems, of islands of Member States of which the systems are not operated synchronously with either the Continental Europe, Great Britain, Nordic, Ireland and Northern Ireland or Baltic synchronous area.
General Provisions
| General Provisions | Article 4 - Application to existing HVDC systems and DC-connected power park modules
General Provisions
1 | General Provisions | Except for Articles 26, 31, 33 and 50, existing HVDC systems and existing DC-connected power park modules are not subject to the requirements of this Regulation, unless:
a) | General Provisions | the HVDC system or DC-connected power park module has been modified to such an extent that its connection agreement must be substantially revised in accordance with the following procedure:
| General Provisions | (i) the HVDC system or DC-connected power park module owners who intend to undertake the modernisation of a plant or replacement of equipment impacting the technical capabilities of the HVDC system or DC-connected power park module shall notify their plans to the relevant system operator in advance;
| General Provisions | (ii) if the relevant system operator considers that the extent of the modernisation or replacement of equipment is such that a new connection agreement is required, the system operator shall notify the relevant regulatory authority or, where applicable, the Member State; and |  | ü |  |  | ü
| General Provisions | (iii) the relevant regulatory authority or, where applicable, the Member State shall decide if the existing connection agreement needs to be revised or a new connection agreement is required and which elements of this Regulation shall apply, in accordance with paragraph [X] of Article [X]; or
b) | General Provisions | a regulatory authority or, where applicable, a Member State decides to make an existing HVDC system or existing DC-connected power park module subject to all or some of the requirements of this Regulation, following a proposal from the relevant TSO in accordance with paragraphs 3, 4 and 5.
2 | General Provisions | For the purposes of this Regulation, an HVDC system or DC-connected power park module shall be considered existing if:
a) | General Provisions | it is already connected to the network on the date of entry into force of this Regulation; or
b) | General Provisions | the HVDC system owner or DC-connected power park module owner has concluded a final and binding contract for the purchase of the main generating plant of HVDC equipment by two years after the entry into force of the Regulation. The HVDC system owner or DC-connected power park module owner must notify the relevant system operator and relevant TSO of conclusion of the contract within 30 months after the entry into force of the Regulation. The notification submitted by the HVDC system owner or DC-connected power park module owner to the relevant system operator and to the relevant TSO shall at least indicate the contract title, its date of signature and date of entry into force and the specifications of the main generating plant or HVDC equipment to be constructed, assembled or purchased. A Member State may provide that in specified circumstances the regulatory authority may determine whether the HVDC system or DC-connected power park module is to be considered an existing or new HVDC system or DC-connected power park module.
3 | General Provisions | Following a public consultation in accordance to Article 8 and in order to address significant factual changes in circumstances, such as the evolution of system requirements including penetration of renewable energy sources, smart grids, distributed generation or demand response, the relevant TSO may propose to the regulatory authority concerned, or where applicable, to the Member State to extend the application of this Regulation to existing HVDC systems and/or DC-connected power park modules. For that purpose a sound and transparent quantitative cost-benefit analysis shall be carried out, in accordance with Articles 65 and 66. The analysis shall indicate: |  | ü |  |  | ü
a) | General Provisions | the costs, in regard to existing power generating modules, of requiring compliance with this Regulation;
b) | General Provisions | the socio-economic benefit resulting from applying the requirements set out in this Regulation; and
c | General Provisions | the potential of alternative measures to achieve the required performance.
4 | General Provisions | Before carrying out the quantitative cost-benefit analysis referred to in paragraph 3, the relevant TSO shall: |  | ü |  |  | ü
a) | General Provisions | carry out a preliminary qualitative comparison of costs and benefits;
b) | General Provisions | obtain approval from the relevant regulatory authority or, where applicable, the Member State.
5 | General Provisions | The relevant regulatory authority or, where applicable, the Member State shall decide on the extension of the applicability of this Regulation to existing HVDC systems or DC-connected power park modules within six months of receipt of the report and the recommendation of the relevant TSO in accordance with paragraph 4 of Article 65. The decision of the regulatory authority or, where applicable, the Member State shall be published. |  | ü |  |  | ü
6 | General Provisions | The relevant TSO shall take account of the legitimate expectations of HVDC system owners and DC-connected power park modules owners as part of the assessment of the application of this Regulation to existing HVDC systems or DC-connected power park modules. |  | ü |  |  | ü
7 | General Provisions | The relevant TSO may assess the application of some or all of the provisions of this Regulation to existing power generating modules every three years with in accordance with the criteria and process set out in paragraphs 3 to 5. |  | ü |  |  | ü
General Provisions
| General Provisions | Article 5 - Regulatory aspects
General Provisions
1 | General Provisions | Requirements of general application to be established by relevant system operators or TSOs under this Regulation shall be subject to approval by the entity designated by the Member State and be published. The designated entity shall be the regulatory authority unless otherwise provided by the Member State.
2 | General Provisions | For site specific requirements to be established by relevant system operators or TSOs under this Regulation, Member States may require approval by a designated entity.
3 | General Provisions | When applying this Regulation, Member States, competent entities and system operators shall:
a) | General Provisions | apply the principles of proportionality and non-discrimination;
b) | General Provisions | ensure transparency;
c | General Provisions | apply the principle of optimisation between the highest overall efficiency and lowest total costs for all parties involved;
d | General Provisions | respect the responsibility assigned to the relevant TSO in order to ensure system security, including as required by national legislation;
e | General Provisions | consult with relevant DSOs and take account of potential impacts on their system;
f | General Provisions | take into consideration agreed European standards and technical specifications.
4 | General Provisions | The relevant system operator or TSO shall submit a proposal for requirements of general application, or the methodology used to calculate or establish them, for approval by the competent entity within two years of entry into force of this Regulation. |  | ü |  |  | ü
5 | General Provisions | Where this Regulation requires the relevant system operator, relevant TSO, HVDC system owner, DC-connected power park module owner and/or the distribution system operator to seek agreement, they shall endeavour to do so within six months after a first proposal has been submitted by one party to the other parties. If no agreement has been found within this timeframe, each party may request the relevant regulatory authority to issue a decision within six months.
6 | General Provisions | Competent entities shall take decisions on proposals for requirements or methodologies within six months following the receipt of such proposals.
7 | General Provisions | If the relevant system operator or TSO deems an amendment to requirements or methodologies as provided for and approved under paragraph 1 and 2 to be necessary, the requirements provided for in paragraphs 3 to 9 shall apply to the proposed amendment. System operators and TSOs proposing an amendment shall take into account the legitimate expectations, if any, of HVDC system owners, DC-connected power park module owners, equipment manufacturers and other stakeholders based on the initially specified or agreed requirements or methodologies.
8 | General Provisions | Any party having a complaint against a relevant system operator or TSO in relation to that relevant system operator's or TSO's obligations under this Regulation may refer the complaint to the regulatory authority which, acting as dispute settlement authority, shall issue a decision within two months after receipt of the complaint. That period may be extended by two months where additional information is sought by the regulatory authority. That extended period may be further extended with the agreement of the complainant. The regulatory authority's decision shall have binding effect unless and until overruled on appeal.
9 | General Provisions | Where the requirements under this Regulation are to be established by a relevant system operator that is not a TSO, Member States may provide that instead the TSO be responsible for establishing the relevant requirements.
General Provisions
| General Provisions | Article 6 - Multiple TSOs
General Provisions
1 | General Provisions | Where more than one TSO exists in a Member State, this Regulation shall apply to all those TSOs.
2 | General Provisions | Member States may, under the national regulatory regime, provide that the responsibility of a TSO to comply with one or some or all obligations under this Regulation is assigned to one or more specific TSOs.
General Provisions
| General Provisions | Article 7 - Recovery of costs
General Provisions
1 | General Provisions | The costs borne by regulated system operators subject to network tariff regulation and stemming from the obligations laid down in this Regulation shall be assessed by the relevant regulatory authorities. Costs assessed as reasonable, efficient and proportionate shall be recovered through network tariffs or other appropriate mechanisms.
2 | General Provisions | If requested by the relevant regulatory authorities, regulated system operators shall, within three months of the request, provide the information necessary to facilitate assessment of the costs incurred.
General Provisions
| General Provisions | Article 8 - Public Consultation
General Provisions
1 | General Provisions | Relevant system operators and relevant TSOs shall carry out consultation with stakeholders, including the competent authorities of each Member State, on proposals to extend the applicability of this Regulation to existing HVDC systems and DC-connected power park modules, in accordance with Article 4(3), on the report prepared in accordance with Article 65(3), and the cost-benefit analysis undertaken in accordance with Article 78(2). The consultation shall last at least for a period of one month. |  | ü |  |  | ü
2 | General Provisions | The relevant system operators or relevant TSOs shall duly take into account the views of the stakeholders resulting from the consultations prior to the submission of the draft proposal or the report or cost benefit analysis for approval by the regulatory authority or, if applicable, the Member State. In all cases, a sound justification for including or not the views of the stakeholders shall be provided and published in a timely manner before, or simultaneously with, the publication of the proposal. |  | ü |  |  | ü
General Provisions
| General Provisions | Article 9 - Stakeholder involvement
General Provisions
| General Provisions | The Agency, in close cooperation with the ENTSO for Electricity, shall organise stakeholder involvement regarding the requirements for grid connection of HVDC systems and DC-connected power park modules, and other aspects of the implementation of this Regulation. This shall include regular meetings with stakeholders to identify problems and propose improvements notably related to the requirements for grid connection of HVDC systems and DC-connected power park modules.
General Provisions
| General Provisions | Article 10 - Confidentiality obligations
General Provisions
1 | General Provisions | Any confidential information received, exchanged or transmitted pursuant to this Regulation shall be subject to the conditions of professional secrecy laid down in paragraphs 2, 3 and 4.
2 | General Provisions | The obligation of professional secrecy shall apply to any persons, regulatory authorities or entities subject to the provisions of this Regulation.
3 | General Provisions | Confidential information received by the persons, regulatory authorities or entities referred to in paragraph 2 in the course of their duties may not be divulged to any other person or authority, without prejudice to cases covered by national law, the other provisions of this Regulation or other relevant Union law.
4 | General Provisions | Without prejudice to cases covered by national or Union law, regulatory authorities, entities or persons who receive confidential information pursuant to this Regulation may use it only for the purpose of carrying out their duties under this Regulation.
Requirements
| Requirements | Title 2 - GENERAL REQUIREMENTS FOR HVDC CONNECTIONS
Requirements
| Requirements | Chapter 1 - REQUIREMENTS FOR ACTIVE POWER CONTROL AND FREQUENCY SUPPORT
Requirements
| Requirements | Article 11 - Frequency ranges
Requirements
1 | Requirements | An HVDC system shall be capable of staying connected to the network and remaining operable within the frequency ranges and time periods specified in Table 1, Annex I for the short circuit power range as specified in Article 32(2).
2 | Requirements | The relevant TSO and HVDC system owner may agree on wider frequency ranges or longer minimum times for operation if needed to preserve or to restore system security. If wider frequency ranges or longer minimum times for operation are economically and technically feasible, the HVDC system owner shall not unreasonably withhold consent. |  | ü |  |  | ü
3 | Requirements | Without prejudice to paragraph 1, an HVDC system shall be capable of automatic disconnection at frequencies specified by the relevant TSO. |  | ü |  |  | ü
4 | Requirements | The relevant TSO may specify a maximum admissible active power output reduction from its operating point if the system frequency falls below 49 Hz. |  | ü |  |  | ü
Requirements
| Requirements | Article 12 - Rate-of-change-of-frequency withstand capability
Requirements
| Requirements | An HVDC system shall be capable of staying connected to the network and operable if the network frequency changes at a rate between -2.5 and +2.5 Hz/s (measured at any point in time as an average of the rate of change of frequency for the previous 1s).
Requirements
| Requirements | Article 13 - Active power controllability, control range and ramping rate
Requirements
1 | Requirements | With regard to the capability of controlling the transmitted Active Power:
a | Requirements | an HVDC ystem shall be capable of adjusting the transmitted active power up to its maximum HVDC active power transmission capacity in each direction following an instruction from the relevant TSO. The relevant TSO: |  | ü |  |  | ü
| Requirements | (i) may specify a maximum and minimum power step size for adjusting the transmitted active power;
| Requirements | (ii) may specify a minimum HVDC active power transmission capacity for each direction, below which active power transmission capability is not requested; and
| Requirements | (iii) shall specify the maximum delay within which the HVDC system shall be capable of adjusting the transmitted active power upon receipt of request from the relevant TSO. |  | ü |  |  | ü
b | Requirements | the relevant TSO shall specify how an HVDC system shall be capable of modifying the transmitted active power infeed in case of disturbances into one or more of the AC networks to which it is connected. If the initial delay prior to the start of the change is greater than 10 milliseconds from receiving the triggering signal sent by the relevant TSO, it shall be reasonably justified by the HVDC system owner to the relevant TSO. |  | ü |  |  | ü
c | Requirements | the relevant TSO may specify that an HVDC system be capable of fast active power reversal. The power reversal shall be possible from the maximum active power transmission capacity in one direction to the maximum active power transmission capacity in the other direction as fast as technically feasible and reasonably justified by the HVDC system owner to the relevant TSOs if greater than 2 seconds. |  | ü |  |  | ü
d | Requirements | for HVDC systems linking various control areas or synchronous areas, the HVDC system shall be equipped with control functions enabling the relevant TSOs to modify the transmitted active power for the purpose of cross-border balancing. |  | ü |  |  | ü
2 | Requirements | An HVDC system shall be capable of adjusting the ramping rate of active power variations within its technical capabilities in accordance with instructions sent by relevant TSOs. In case of modification of active power according to Article 13(5) and (6), there shall be no adjustment of ramping rate. |  | ü |  |  | ü
3 | Requirements | If specified by a relevant TSO, in coordination with adjacent TSOs, the control functions of an HVDC system shall be capable of taking automatic remedial actions including, but not limited to, stopping the ramping and blocking FSM, LFSM-O, LFSM-U and frequency control. The triggering and blocking criteria shall be specified by relevant TSO and subject to notification to the regulatory authority. The modalities of that notification shall be determined in accordance with the applicable national regulatory framework. |  | ü |  |  | ü
Requirements
| Requirements | Article 14 - Synthetic inertia
Requirements
1 | Requirements | If specified by a relevant TSO, an HVDC system shall be capable of providing synthetic inertia in response to frequency changes, activated in low and/or high frequency regimes by rapidly adjusting the active power injected to or withdrawn from the AC network in order to limit the rate of change of frequency. The requirement shall at least take account of the results of the studies undertaken by TSOs to identify if there is a need to set out minimum inertia. |  | ü |  |  | ü
2 | Requirements | The principle of this control system and the associated performance parameters shall be agreed between the relevant TSO and the HVDC system owner. |  | ü |  |  | ü
Requirements
| Requirements | Article 15 - Requirements relating to frequency sensitive mode overfrequency and limited frequency sensitive mode underfrequency
Requirements
| Requirements | Requirements applying to frequency sensitive mode, limited frequency sensitive mode overfrequency and limited frequency sensitive mode underfrequency shall be as set out in Annex II.
Requirements
| Requirements | Article 16 - Frequency Control
Requirements
1 | Requirements | If specified by the relevant TSO, an HVDC system shall be equipped with an independent control mode to modulate the active power output of the HVDC converter station depending on the frequencies at all connection points of the HVDC system in order to maintain stable system frequencies |  | ü |  |  | ü
2 | Requirements | The relevant TSO shall specify the operating principle, the associated performance parameters and the activation criteria of the frequency control referred to in paragraph 1. |  | ü |  |  | ü
Requirements
| Requirements | Article 17 - Maximum loss of active power
Requirements
1 | Requirements | An HVDC system shall be configured in such a way that its loss of active power injection in a synchronous area shall be limited to a value specified by the relevant TSOs for their respective load frequency control area, based on the HVDC system's impact on the power system. |  | ü |  |  | ü
2 | Requirements | Where an HVDC system connects two or more control areas, the relevant TSOs shall consult each other in order to set a coordinated value of the maximum loss of active power injection as referred to in paragraph 1, taking into account common mode failures. |  | ü |  |  | ü
Requirements
| Requirements | Chapter 2 - REQUIREMENTS FOR REACVTIVE POWER CONTROL AND VOLTAGE SUPPORT
Requirements
| Requirements | Article 18 - Voltage Ranges
Requirements
1 | Requirements | Without prejudice to Article 25, an HVDC converter station shall be capable of staying connected to the network and capable of operating at HVDC system maximum current, within the ranges of the network voltage at the connection point, expressed by the voltage at the connection point related to reference 1 pu voltage, and the time periods specified in Tables 4 and 5, Annex III. The establishment of the reference 1 pu voltage shall be subject to coordination between the adjacent relevant system operators. | ü | ü | ü | ü | ü
2 | Requirements | The HVDC system owner and the relevant system operator, in coordination with the relevant TSO, may agree on wider voltage ranges or longer minimum times for operation than those specified in paragraph 1 in order to ensure the best use of the technical capabilities of an HVDC sytem if needed to preserve or to restore system security. If wider voltage ranges or longer minimum times for operation are economically and technically feasible, the HVDC system owner shall not unreasonably withhold consent. |  | ü |  |  | ü
3 | Requirements | An HVDC converter station shall be capable of automatic disconnection at connection point voltages specified by the relevant system operator, in coordination with the relevant TSO. The terms and settings for automatic disconnection shall be agreed between the relevant system operator in coordination with the relevant TSO and the HVDC system owner. |  | ü |  |  | ü
4 | Requirements | For connection points at reference 1 pu AC voltages not included in the scope of Table 4 and Table 5set out in Annex III, the relevant system operator, in coordination with relevant TSOs, shall definespecify applicable requirements at the connection points. |  | ü |  |  | ü
5 | Requirements | Notwithstanding the provisions of paragraph 1, the relevant TSOs in the Baltic synchronous area may, following consultation with relevant neighboring TSOs, require HVDC converter stations to remain connected to the 400 kV network in the voltage ranges and for time periods that apply in the Continental Europe synchronous area.
Requirements
| Requirements | Article 19 - Short circuit contribution during faults
Requirements
1 | Requirements | If specified by the relevant system operator, in coordination with the relevant TSO, an HVDC system shall have the capability to provide fast fault current at a connection point in case of symmetrical (3-phase) faults. |  | ü |  |  | ü
2 | Requirements | Where an HVDC system is required to have the capability referred to in paragraph 1, the relevant system operator, in coordination with the relevant TSO, shall specify the following: |  | ü |  |  | ü
a | Requirements | how and when a voltage deviation is to be determined as well as the end of the voltage deviation;
b | Requirements | the characteristics of the fast fault current;
c | Requirements | the timing and accuracy of the fast fault current, which may include several stages.
3 | Requirements | The relevant system operator, in coordination the relevant TSO, may specify a requirement for asymmetrical current injection in the case of asymmetrical (1-phase or 2-phase) faults. |  | ü |  |  | ü
Requirements
| Requirements | Article 20 - Reactive power capability
Requirements
1 | Requirements | The relevant system operator, in coordination with the relevant TSO, shall specify the reactive power capability requirements at the connection points, in the context of varying voltage. The proposal for those requirements shall include a U-Q/Pmax-profile, within the boundary of which the HVDC converter station shall be capable of providing reactive power at its maximum HVDC active power transmission capacity. |  | ü |  |  | ü
2 | Requirements | The U-Q/Pmax-profile referred to in paragraph 1 shall comply with the following principles:
a | Requirements | the U-Q/Pmax-profile shall not exceed the U-Q/Pmax-profile envelope represented by the inner envelope in the figure set out in Annex IV, and does not need to be rectangular;
b | Requirements | the dimensions of the U-Q/Pmax-profile envelope shall respect the values established for each synchronous area in the table set out in Annex IV; and
c | Requirements | the position of the U-Q/Pmax-profile envelope shall lie within the limits of the fixed outer envelope in the figure set out in Annex IV.
3 | Requirements | An HVDC system shall be capable of moving to any operating point within its U-Q/Pmax profile in timescales specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
4 | Requirements | When operating at an active power output below the maximum HVDC active power transmission capacity (P<Pmax), the HVDC converter station shall be capable of operating in every possible operating point, as specified by the relevant system operator in coordination with the relevant TSO and in accordance with the reactive power capability set out by the U-Q/Pmax profile specified in paragraphs 1 to 3. |  | ü |  |  | ü
Requirements
| Requirements | Article 21 - Reactive power exchanged with the network
Requirements
1 | Requirements | The HVDC system owner shall ensure that the reactive power of its HVDC converter station exchanged with the network at the connection point is limited to values specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
2 | Requirements | The reactive power variation caused by the reactive power control mode operation of the HVDC converter Station, referred to in Article 22(1), shall not result in a voltage step exceeding the allowed value at the connection point. The relevant system operator, in coordination with the relevant TSO, shall specify this maximum tolerable voltage step value. |  | ü |  |  | ü
Requirements
| Requirements | Article 22 - Reactive power control mode
Requirements
1 | Requirements | An HVDC converter station shall be capable of operating in one or more of the three following control modes, as specified by the relevant system operator in coordination with the relevant TSO: |  | ü |  |  | ü
a | Requirements | voltage control mode;
b | Requirements | reactive power control mode;
c | Requirements | power factor control mode.
2 | Requirements | An HVDC converter station shall be capable of operating in additional control modes specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
3 | Requirements | For the purposes of voltage control mode, each HVDC converter station shall be capable of contributing to voltage control at the connection point utilising its capabilities, while respecting Articles 20 and 21, in accordance with the following control characteristics:
a | Requirements | a setpoint voltage at the connection point shall be specified to cover a specific operation range, either continuously or in steps, by the relevant system operator, in coordination with the relevant TSO; |  | ü |  |  | ü
b | Requirements | the voltage control may be operated with or without a deadband around the setpoint selectable in a range from zero to +/-5 % of reference 1 pu network voltage. The deadband shall be adjustable in steps as specified by the relevant system operator in coordination with the relevant TSO; |  | ü |  |  | ü
c | Requirements | following a step change in voltage, the HVDC converter station shall be capable of:
| Requirements | (ii) achieving 90 % of the change in reactive power output within a time t1specied by the relevant system operator in coordination with the relevant TSO. The time t1 shall be in the range of 0.1 - 10 seconds; and |  | ü |  |  | ü
| Requirements | (i) settling at the value defined by the operating slope within a time t2 specified by the relevant system operator in coordination with the relevant TSO. The time t2 shall be in the range of 1 - 60 seconds, with a specified steady-state tolerance given in % of the maximum reactive power. |  | ü |  |  | ü
d | Requirements | voltage control mode shall include the capability to change reactive power output based on a combination of a modified setpoint voltage and an additional instructed reactive power component. The slope shall be specified by a range and step specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
4 | Requirements | With regard to reactive power control mode, the relevant system operator shall specify, a reactive power range in MVAr or in % of maximum reactive power, as well as its associated accuracy at the connection point, using the capabilities of the HVDC system, while respecting Articles 20 and 21. | ü | ü | ü | ü | ü
5 | Requirements | For the purposes of power factor control mode, the HVDC converter station shall be capable of controlling the power factor to a target at the connection point, while respecting the provisions of Articles 20 and 21. The available setpoints shall be available in steps no greater than a maximum allowed step specified by the relevant system operator. | ü | ü | ü | ü | ü
6 | Requirements | The relevant system operator in coordination with the relevant TSO shall specify any equipment needed to enable the remote selection of control modes and relevant setpoints. |  | ü |  |  | ü
Requirements
| Requirements | Article 23 - Priority to active or reactive power contribution
Requirements
| Requirements | Taking into account the capabilities of the HVDC system specified in accordance with this Regulation, the relevant TSO shall determine whether active power contribution or reactive power contribution shall have priority during low or high voltage operation and during faults for which fault-ride-through capability is required. If priority is given to active power contribution, its provision shall be established within a time from the fault inception as specified by relevant TSO. |  | ü |  |  | ü
Requirements
| Requirements | Article 24 - Power quality
Requirements
| Requirements | An HVDC system owner shall ensure that its HVDC system connection to the network does not result in a level of distortion or fluctuation of the supply voltage on the network, at the connection point, exceeding the level specified by the relevant system operator in coordination with the relevant TSO. The process for necessary studies to be conducted and relevant data to be provided by all grid users involved, as well as mitigating actions identified and implemented shall be in accordance with the process in Article 29. |  | ü |  |  | ü
Requirements
| Requirements | Chapter 3 - REQUIREMENTS FOR FAULT RIDE THROUGH CAPABILITY
Requirements
| Requirements | Article 25 - Fault ride through capability
Requirements
1 | Requirements | The relevant TSO shall specify, while respecting Article 18, a voltage-against time profile as set out in Annex V and having regard to the voltage-against-time-profile specified for power park modules according to [NC RfG]. This profile shall apply at connection points for fault conditions, under which the HVDC converter station shall be capable of staying connected to the network and continuing stable operation after the power system has recovered following fault clearance. The voltage-against-time-profile shall express a lower limit of the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, as a function of time before, during and after the fault. Any ride through period beyond trec2 shall be specified by the relevant TSO consistent with Article 18. |  | ü |  |  | ü
2 | Requirements | On request by the HVDC system owner, the relevant system operator shall provide the pre-fault and post-fault conditions as provided for in Article 32 regarding: | ü | ü | ü | ü | ü
a | Requirements | pre-fault minimum short circuit capacity at each connection point expressed in MVA;
b | Requirements | pre-fault operating point of the HVDC converter station expressed as active power output and reactive power output at the connection point and voltage at the connection point; and
c | Requirements | post-fault minimum short circuit capacity at each connection point expressed in MVA.
| Requirements | Alternatively, generic values for the above conditions derived from typical cases may be provided by the relevant system operator. | ü | ü | ü | ü | ü
3 | Requirements | The HVDC converter station shall be capable of staying connected to the network and continue stable operation when the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, given the pre-fault and post-fault conditions provided for in Article 32, remain above the lower limit set out in the 6th Figure in Annex V, unless the protection scheme for internal faults requires the disconnection of the HVDC converter station from the network. The protection schemes and settings for internal faults shall be designed not to jeopardize fault-ride-through performance.
4 | Requirements | The relevant TSO may specify voltages (Ublock) at the connection points under specific network conditions whereby the HVDC system is allowed to block. Blocking means remaining connected to the network with no active and reactive power contribution for a time frame that shall be as short as technically feasible and which shall be agreed between the relevant TSOs and the HVDC system owner. |  | ü |  |  | ü
5 | Requirements | In accordance Article 34, undervoltage protection shall be set by the HVDC system owner to the widest possible technical capability of the HVDC converter station. The relevant system operator, in coordination with the relevant TSO, may specify narrower settings pursuant to Article 34. |  | ü |  |  | ü
6 | Requirements | The relevant TSO shall specify fault-ride-through capabilities in case of asymmetrical faults. |  | ü |  |  | ü
Requirements
| Requirements | Article 26 - Post fault active power recovery
Requirements
| Requirements | The relevant TSO shall specify the magnitude and time profile of active power recovery that the HVDC system shall be capable of providing, in accordance with the Article 25. |  | ü |  |  | ü
Requirements
| Requirements | Article 27 - Fast recovery from DC faults
Requirements
| Requirements | HVDC systems, including DC overhead lines, shall be capable of fast recovery from transient faults within the HVDC system. Details of this capability shall be subject to coordination and agreements on protection schemes and settings pursuant to Article 34.
| Requirements | Chapter 4 - REQUIREMENTS FOR CONTROL
Requirements
| Requirements | Article 28 - Energisation and synchronisation of HVDC converter stations
Requirements
| Requirements | Unless otherwise instructed by the relevant system operator, during the energisation or synchronisation of an HVDC converter station to the AC network or during the connection of an energised HVDC converter station to an HVDC system, the HVDC converter station shall have the capability to limit any voltage changes to a steady-state level specified by the relevant system operator in coordination with the relevant TSO. The level specified shall not exceed 5 per cent of the pre-synchronisation voltage. The relevant system operator, in coordination with the relevant TSO, shall specify the maximum magnitude, duration and measurement window of the voltage transients. |  | ü |  |  | ü
Requirements
| Requirements | Article 29 - Interaction between HVDC systems or other plants and equipment
Requirements
1 | Requirements | When several HVDC converter stations or other plants and equipment are within close electrical proximity, the relevant TSO may specify that a study is required, and the scope and extent of that study, to demonstrate that no adverse interaction will occur. If adverse interaction is identified, the studies shall identify possible mitigating actions to be implemented to ensure compliance with the requirements of this Regulation |  | ü |  |  | ü
2 | Requirements | The studies shall be carried out by the connecting HVDC system owner with the participation of all other parties identified by the TSOs as relevant to each connection point. Member States may provide that the responsibility for undertaking the studies in accordance with this Article lies with the TSO. All parties shall be informed of the results of the studies. |  | ü |  |  | ü
3 | Requirements | All parties identified by the relevant TSO as relevant to each connection point, including the relevant TSO, shall contribute to the studies and shall provide all relevant data and models as reasonably required to meet the purposes of the studies. The relevant TSO shall collect this input and, where applicable, pass it on to the party responsible for the studies in accordance with Article 10. |  | ü |  |  | ü
4 | Requirements | The relevant TSO shall assess the result of the studies based on their scope and extent as specified in accordance with paragraph 1. If necessary for the assessment, the relevant TSO may request the HVDC system owner to perform further studies in line with the scope and extent specified in accordance with paragraph 1. |  | ü |  |  | ü
5 | Requirements | The relevant TSO may review or replicate some or all of the studies. The HVDC system owner shall provide the relevant TSO all relevant data and models that allow such study to be performed. |  | ü |  |  | ü
6 | Requirements | Any necessary mitigating actions identified by the studies carried out in accordance with paragraphs 2 to 5 and reviewed by the relevant TSO shall be undertaken by the HVDC system owner as part of the connection of the new HVDC converter station. |  | ü |  |  | ü
7 | Requirements | The relevant TSO may specify transient levels of performance associated with events for the individual HVDC system or collectively across commonly impacted HVDC systems. This specification may be provided to protect the integrity of both TSO equipment and that of grid users in a manner consistent with its national code. |  | ü |  |  | ü
Requirements
| Requirements | Article 30 - Power oscillation damping capability
Requirements
| Requirements | The HVDC system shall be capable of contributing to the damping of power oscillations in connected AC networks. The control system of the HVDC system shall not reduce the damping of power oscillations. The relevant TSO shall specify a frequency range of oscillations that the control scheme shall positively damp and the network conditions when this occurs, at least accounting for any dynamic stability assessment studies undertaken by TSOs to identify the stability limits and potential stability problems in their transmission systems. The selection of the control parameter settings shall be agreed between the relevant TSO and the HVDC system owner. |  | ü |  |  | ü
Requirements
| Requirements | Article 31 - Subsynchronous torsional interaction damping capability
Requirements
1 | Requirements | With regard to subsynchronous torsional interaction (SSTI) damping control, the HVDC system shall be capable of contributing to electrical damping of torsional frequencies.
2 | Requirements | The relevant TSO shall specify the necessary extent of SSTI studies and provide input parameters, to the extent available, related to the equipment and relevant system conditions in its network. The SSTI studies shall be provided by the HVDC system owner. The studies shall identify the conditions, if any, where SSTI exists and propose any necessary mitigation procedure. Member States may provide that the responsibility for undertaking the studies in accordance with this Article lies with the TSO. All parties shall be informed of the results of the studies. |  | ü |  |  | ü
3 | Requirements | All parties identified by the relevant TSO as relevant to each connection point, including the relevant TSO, shall contribute to the studies and shall provide all relevant data and models as reasonably required to meet the purposes of the studies. The relevant TSO shall collect this input and, where applicable, pass it on to the party responsible for the studies in accordance with Article 10. |  | ü |  |  | ü
4 | Requirements | The relevant TSO shall assess the result of the SSTI studies. If necessary for the assessment, the relevant TSO may request that the HVDC system owner perform further SSTI studies in line with this same scope and extent. |  | ü |  |  | ü
5 | Requirements | The relevant TSO may review or replicate the study. The HVDC system owner shall provide the relevant TSO all relevant data and models that allow such study to be performed. |  | ü |  |  | ü
6 | Requirements | Any necessary mitigating actions identified by the studies carried out in accordance with paragraphs 2 or 4, and reviewed by the relevant TSOs, shall be undertaken by the HVDC system owner as part of the connection of the new HVDC converter station. |  | ü |  |  | ü
Requirements
| Requirements | Article 32 - Network characteristics
Requirements
1 | Requirements | The relevant system operator shall specify and make publicly available the method and the pre-fault and post-fault conditions for the calculation of at least the minimum and maximum short circuit power at the connection points. | ü | ü | ü | ü | ü
2 | Requirements | The HVDC system shall be capable of operating within the range of short circuit power and network characteristics specified by the relevant system operator. | ü | ü | ü | ü | ü
3 | Requirements | Each relevant system operator shall provide the HVDC system owner with network equivalents describing the behaviour of the network at the connection point, enabling the HVDC system owners to design their system with regard to at least, but not limited to, harmonics and dynamic stability over the lifetime of the HVDC system. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 33 - HVDC system robustness
Requirements
1 | Requirements | The HVDC system shall be capable of finding stable operation points with a minimum change in active power flow and voltage level, during and after any planned or unplanned change in the HVDC system or AC network to which it is connected. The relevant TSO shall specify the changes in the system conditions for which the HVDC systems shall remain in stable operation. |  | ü |  |  | ü
2 | Requirements | The HVDC system owner shall ensure that the tripping or disconnection of an HVDC converter station, as part of any multi-terminal or embedded HVDC system, does not result in transients at the connection point beyond the limit specified by the relevant TSO. |  | ü |  |  | ü
3 | Requirements | The HVDC system shall withstand transient faults on HVAC lines in the network adjacent or close to the HVDC system, and shall not cause any of the equipment in the HVDC system to disconnect from the network due to auto-reclosure of lines in the network.
4 | Requirements | The HVDC system owner shall provide information to the relevant system operator on the resilience of the HVDC system to AC system disturbances. | ü | ü | ü | ü | ü
Requirements
| Requirements | Chapter 5 - REQUIREMENTS FOR PROTECTION DEVICES AND SETTINGS
Requirements
| Requirements | Article 34 - Electrical protection schemes and settings
Requirements
1 | Requirements | The relevant system operator shall specify, in coordination with the relevant TSO, the schemes and settings necessary to protect the network taking into account the characteristics of the HVDC system. Protection schemes relevant for the HVDC system and the network, and settings relevant for the HVDC system, shall be coordinated and agreed between the relevant system operator, the relevant TSO and the HVDC system owner. The protection schemes and settings for internal electrical faults shall be designed so as not to jeopardize the performance of the HVDC system in accordance with this Regulation. | ü | ü | ü | ü | ü
2 | Requirements | Electrical protection of the HVDC system shall take precedence over operational controls taking into account system security, health and safety of staff and the public and mitigation of the damage to the HVDC system.
3 | Requirements | Any change to the protection schemes or their settings relevant to the HVDC system and the network shall be agreed between the relevant system operator, the relevant TSO and the HVDC system owner before being implemented by the HVDC system owner. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 35 - Priority ranking of protection and control
Requirements
1 | Requirements | A control scheme, specified by the HVDC system owner consisting of different control modes, including the settings of the specific parameters, shall be coordinated and agreed between the relevant TSO, the relevant system operator and the HVDC system owner. | ü | ü | ü | ü | ü
2 | Requirements | With regard to priority ranking of protection and control, the HVDC system owner shall organise its protections and control devices in compliance with the following priority ranking, listed in decreasing order of importance, unless otherwise specified by the relevant TSOs, in coordination with the relevant system operator: | ü | ü | ü | ü | ü
a) | Requirements | network system and HVDC system protection;
b) | Requirements | active power control for emergency assistance;
c) | Requirements | synthetic inertia, if applicable;
d | Requirements | automatic remedial actions as specified in Article 13(3);
e | Requirements | LFSM;
f | Requirements | FSM and frequency control; and
g | Requirements | power gradient constraint.
Requirements
| Requirements | Article 36 - Changes to protection and control schemes and settings
Requirements
1 | Requirements | The parameters of the different control modes and the protection settings of the HVDC system shall be able to be changed in the HVDC converter station, if required by the relevant system operator or the relevant TSO, and in accordance with Article 38(3). | ü | ü | ü | ü | ü
2 | Requirements | Any change to the schemes or settings of parameters of the different control modes and protection of the HVDC system, including the procedure, shall be coordinated and agreed between the relevant system operator, the relevant TSO and the HVDC system owner. | ü | ü | ü | ü | ü
3 | Requirements | The control modes and associated setpoints of the HVDC system shall be capable of being changed remotely, as specified by the relevant system operator, in coordination with the relevant TSO. | ü | ü | ü | ü | ü
Requirements
| Requirements | Chapter 6 - REQUIREMENTS FOR POWER SYSTEM RESTORATION
Requirements
| Requirements | Article 37 - Black Start
Requirements
1 | Requirements | The relevant TSO may obtain a quote for black start capability from an HVDC system owner. |  | ü |  |  | ü
2 | Requirements | An HVDC system with black start capability shall be able, in case one converter station is energised, to energise the busbar of the AC-substation to which another converter station is connected, within a timeframe after shut down determined by the relevant TSOs. The HVDC system shall be able to synchronise within the frequency limits set out in Article 11 and within the voltage limits specified by the relevant TSO or as provided for in Article 18, where applicable. Wider frequency and voltage ranges can be specified by the relevant TSO where needed in order to restore system security. |  | ü |  |  | ü
3 | Requirements | The relevant TSO and the HVDC system owner shall agree on the capacity and availability of the black start capability and the operational procedure. |  | ü |  |  | ü
Requirements
| Requirements | Title 3 - REQUIREMENTS FOR DC-CONNECTED POWER PARK MODULES AND REMOTE-END HVDC CONVERTER STATIONS
Requirements
| Requirements | Chapter 1 - REQUIREMENTS FOR DC-CONNECTED POWER PARK MODULES
Requirements
| Requirements | Article 38 - Scope
Requirements
| Requirements | The requirements applicable to offshore power park modules under Articles 13 to 22 of [NC RfG] shall apply to DC-connected power park modules subject to specific requirements provided for in Articles 41 to Article 45 of this Regulation. These requirements shall apply at the HVDC interface points of the DC-connected power park module and the HVDC systems. The categorization in Article 5 of [NC RfG] shall apply to DC-connected power park modules.
Requirements
| Requirements | Article 39 - Frequency stability requirements
Requirements
1 | Requirements | With regards to frequency response:
a) | Requirements | A DC-connected power park module shall be capable of receiving a fast signal from a connection point in the synchronous area to which frequency response is being provided, within 0.1 second from sending to completion of processing the signal for activation of the response. Frequency shall be measured at the connection point in the synchronous area to which frequency response is being provided
b) | Requirements | DC-connected power park modules connected via HVDC systems which connect with more than one control area shall be capable of delivering coordinated frequency control as specified by the relevant TSO. |  | ü |  |  | ü
2 | Requirements | With regard to frequency ranges and response:
a) | Requirements | a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operating within the frequency ranges and time periods specified in Annex VI for the 50 Hz nominal system. Where a nominal frequency other than 50 Hz, or a frequency variable by design is used, subject to agreement with the relevant TSO, the applicable frequency ranges and time periods shall be specified by the relevant TSO taking into account specificities of the system and the requirements set out in Annex VI; |  | ü |  |  | ü
b) | Requirements | wider frequency ranges or longer minimum times for operation can be agreed between the relevant TSO and the DC-connected power park module owner to ensure the best use of the technical capabilities of a DC-connected power park module if needed to preserve or to restore system security. If wider frequency ranges or longer minimum times for operation are economically and technically feasible, the DC-connected power park module owner shall not unreasonably withhold consent; |  | ü |  |  | ü
c) | Requirements | while respecting the provisions of Article 41(2)(a), a DC-connected power park module shall be capable of automatic disconnection at specified frequencies, if specified by the relevant TSO. Terms and settings for automatic disconnection shall be agreed between the relevant TSO and the DC-connected power park module owner. |  | ü |  |  | ü
3 | Requirements | With regards to rate-of-change-of-frequency withstand capability, a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operable if the system frequency changes at a rate up to +/-2 Hz/s (measured at any point in time as an average of the rate of change of frequency for the previous 1s) at the HVDC interface point of the DC-connected power park module at the remote end HVDC converter station for the 50 Hz nominal system.
4 | Requirements | DC-connected power park modules shall have limited frequency sensitive mode - overfrequency (LFSM-O) capability in accordance with Article 8(1)(c) of [the NC RfG], subject to fast signal response as specified in Article 41(1) of this Regulation for the 50 Hz nominal system.
5 | Requirements | A capability for DC-connected power park modules to maintain constant power shall be determined in accordance with Article 8(1)(d) of [the NC RfG] for the 50 Hz nominal system.
6 | Requirements | A capability for active power controllability of DC-connected power park modules shall be determined in accordance with Article 10(2)(a) of [the NC RfG] for the 50Hz nominal system. Manual control shall be possible in the case that remote automatic control devices are out of service.
7 | Requirements | A capability for limited frequency sensitive mode - underfrequency (LFSM-U) for a DC-connected power park module shall be determined in accordance with Article 10(2)(b) of [the NC RfG], subject to fast signal response as specified in paragraph 1 of Article 41 of this Regulation for the 50 Hz nominal system.
8 | Requirements | A capability for frequency sensitive mode for a DC-connected power park module shall be determined in accordance with [Article 10(2)(c) of [the NC RfG], subject to a fast signal response as specified in paragraph 1 of Article 41 of this Regulation for the 50 Hz nominal system.
9 | Requirements | A capability for frequency restoration for a DC-connected power park module shall be determined in accordance with Article 10(2)(d) of [the NC RfG] for the 50 Hz nominal system.
10 | Requirements | Where a constant nominal frequency other than 50 Hz, a frequency variable by design or a DC system voltage is used, subject to the agreement of the relevant TSO, the capabilities listed in Article 41(3) to (9) and the parameters associated with such capabilities shall be specified by the relevant TSO. |  | ü |  |  | ü
Requirements
| Requirements | Article 40 - Reactive power and voltage requirements
Requirements
1 | Requirements | With respect to voltage ranges:
a) | Requirements | a DC-connected power park module shall be capable of staying connected to the remote-end HVDC converter station network and operating within the voltage ranges (per unit), for the time periods specified in Tables 9 and 10, Annex VII. The applicable voltage range and time periods specified are selected based on the reference 1 pu voltage;
b) | Requirements | wider voltage ranges or longer minimum times for operation can be agreed between the relevant system operator, the relevant TSO and the DC-connected power park module owner to ensure the best use of the technical capabilities of a DC-connected power park module if needed to preserve or to restore system security. If wider voltage ranges or longer minimum times for operation are economically and technically feasible, the DC-connected power park module owner shall not unreasonably withhold consent; |  | ü |  |  | ü
c) | Requirements | for DC connected power park modules which have an HVDC interface point to the remote-end HVDC converter station network, the relevant system operator, in coordination with the relevant TSO may specify voltages at the HVDC interface point at which a DC-connected power park module shall be capable of automatic disconnection. The terms and settings for automatic disconnection shall be agreed between the relevant system operator, the relevant TSO and the DC-connected power park module owner; |  | ü |  |  | ü
d) | Requirements | for HVDC interface points at AC voltages that are not included in the scope of Annex VII, the relevant system operator, in coordination with the relevant TSO shall specify applicable requirements at the connection point; |  | ü |  |  | ü
e | Requirements | where frequencies other than nominal 50 Hz are used, subject to relevant TSO agreement, the voltage ranges and time periods specified by the relevant system operator, in coordination with the relevant TSO, shall be proportional to those in Tables 9 and 10, Annex VII. |  | ü |  |  | ü
2 | Requirements | With respect to reactive power capability for DC-connected power park modules:
a) | Requirements | If the DC-connected power park module owner can obtain a bilateral agreement with the owners of the HVDC systems connecting the DC-connected power park module to a single connection point on a AC network, it shall fulfil all of the following requirements :
| Requirements | (i) it shall have the ability with additional plant or equipment and/or software, to meet the reactive power capabilities prescribed by the relevant system operator, in coordination with the relevant TSO, according to point (b) and it shall either: |  | ü |  |  | ü
| Requirements | - have the reactive power capabilities, in coordination with the relevant TSO for some or all of its equipment in accordance with Article 42(2)b) already installed as part of the connection of the DC-connected power park module to the AC network at the time of initial connection and commissioning; or |  | ü |  |  | ü
| Requirements | - demonstrate to, and then reach agreement with, the relevant system operator and the relevant TSO on how the reactive power capability will be provided when the DC-connected power park module is connected to more than a single connection point in the AC network, or the AC network at the remote-end HVDC converter station network has either another DC-connected power park module or HVDC system with a different owner connected to it. This agreement shall include a contract by the DC-connected power park module owner (or any subsequent owner), that it will finance and install reactive power capabilities required by this Article for its power park modules at a point in time specified by the relevant system operator, in coordination with the relevant TSO. The relevant system operator, in coordination with the relevant TSO shall inform the DC-connected power park module owner of the proposed completion date of any committed development which will require the DC-connected power park module owner to install the full reactive power capability. |  | ü |  |  | ü
| Requirements | (ii) the relevant system operator, in coordination with the relevant TSO shall account for the development time schedule of retrofitting the reactive power capability to the DC-connected power park module in specifying the point in time by which this reactive power capability retrofitting is to take place. The development time schedule shall be provided by the DC-connected power park module owner at the time of connection to the AC network. |  | ü |  |  | ü
b) | Requirements | DC-connected power park modules shall fulfil the following requirements relating to voltage stability either at the time of connection or subsequently, according to the agreement as referred to in point (a):
| Requirements | (i) with regard to reactive power capability at maximum HVDC active power transmission capacity, DC-connected power park modules shall meet the reactive power provision capability requirements specified by the relevant system operator, in coordination with the relevant TSO, in the context of varying voltage. The relevant system operator shall specify a U-Q/Pmax-profile that may take any shape with ranges in accordance with Table 11, Annex VII, within the DC-connected power park module shall be capable of providing reactive power at its maximum HVDC active power transmission capacity. The relevant system operator, in coordination with the relevant TSO, shall consider the long term development of the network when determining these ranges, as well as the potential costs for power park modules of delivering the capability of providing reactive power production at high voltages and reactive power consumption at low voltages. |  | ü |  |  | ü
| Requirements | If the Ten-Year Network Development Plan developed in accordance with Article 8 of Regulation (EC) No 714/2009 specifies that a DC-connected power park module will become AC-connected to the synchronous area, the relevant TSO may specify that either: |  | ü |  |  | ü
| Requirements | - the DC-connected power park module shall have the capabilities prescribed in Article 20(3) of [the NC RfG] for that synchronous area installed at the time of initial connection and commissioning of the DC-connected power park module to the AC-network; or
| Requirements | - the DC-connected power park module owner shall demonstrate to, and then reach agreement with, the relevant system operator and the relevant TSO on how the reactive power capability prescribed in Article 20(3) of [the NC RfG] for that synchronous area will be provided in the event that the DC-connected power park module becomes AC-connected to the synchronous area. |  | ü |  |  | ü
| Requirements | With regard to reactive power capability, the relevant system operator may specify supplementary reactive power to be provided if the connection point of a DC-connected power park module is neither located at the high-voltage terminals of the step-up transformer to the voltage level of the connection point nor at the alternator terminals, if no step-up transformer exists. This supplementary reactive power shall compensate the reactive power demand of the high-voltage line or cable between the high-voltage terminals of the step-up transformer of the synchronous power generating module or its alternator terminals, if no step-up transformer exists, and the connection point and shall be provided by the responsible owner of that line or cable. |  | ü |  |  | ü
3 | Requirements | With regard to priority to active or reactive power contribution for DC-connected power park modules, the relevant system operator, in coordination with the relevant TSO shall specify whether active power contribution or reactive power contribution has priority during faults for which fault-ride-through capability is required. If priority is given to active power contribution, its provision shall be established within a time from the fault inception as specified by the relevant system operator, in coordination with the relevant TSO. |  | ü |  |  | ü
Requirements
| Requirements | Article 41 - Control requirements
Requirements
1 | Requirements | During the synchronisation of a DC-connected power park module to the AC collection network, the DC-connected power park module shall have the capability to limit any voltage changes to a steady-state level specified by the relevant system operator, in coordination with the relevant TSO. The level specified shall not exceed 5 per cent of the pre-synchronisation voltage. The relevant system operator, in coordination with the relevant TSO, shall specify the maximum magnitude, duration and measurement window of the voltage transients. |  | ü |  |  | ü
2 | Requirements | The DC-connected power park module owner shall provide output signals as specified by the relevant system operator, in coordination with the relevant TSO. |  | ü |  |  | ü
Requirements
| Requirements | Article 42 - Network characteristics
Requirements
1 | Requirements | With regard to the network characteristics, the following shall apply for the DC-connected power park modules:
a) | Requirements | each relevant system operator shall specify and make publicly available the method and the pre-fault and post-fault conditions for the calculation of minimum and maximum short circuit power at the HVDC interface point . | ü | ü | ü | ü | ü
b) | Requirements | the DC-connected power park module shall be capable of stable operation within the minimum to maximum range of short circuit power and network characteristics of the HVDC interface point specified by the relevant system operator, in coordination with the relevant TSO. |  | ü |  |  | ü
c) | Requirements | each relevant system operator and HVDC system owner shall provide the DC-connected power park module owner with network equivalents representing the system, enabling the DC-connected power park module owners to design their system with regard to harmonics. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 43 - Protection requirements
Requirements
1 | Requirements | Electrical protection schemes and settings of DC-connected power park modules shall be determined in accordance with Article 14(5)(b) of [the NC RfG], where the network refers to the synchronous area network. The protection schemes have to be designed taking into account the system performance, grid specificities as well as technical specificities of the power park module technology and agreed with the relevant system operator, in coordination with the relevant TSO. | ü | ü | ü | ü | ü
2 | Requirements | Priority ranking of protection and control of DC-connected power park modules shall be determined in accordance with Article 14(5)(c) of [the NC RfG], where the network refers to the synchronous area network, and agreed with the relevant system operator, in coordination with the relevant TSO. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 44 - Power quality
Requirements
| Requirements | DC-connected power park modules owners shall ensure that their connection to the network does not result in a level of distortion or fluctuation of the supply voltage on the network, at the connection point, exceeding the level specified by the relevant system operator, in coordination with the relevant TSO. The necessary contribution from grid users to associated studies, including, but not limited to, existing DC-connected power park modules and existing HVDC systems, shall not be unreasonably withheld. The process for necessary studies to be conducted and relevant data to be provided by all grid users involved, as well as mitigating actions identified and implemented, shall be in accordance with the process in Article 29. | ü | ü | ü | ü | ü
| Requirements | Article 45 - General system management requirements applicable to DC connected power park modules
Requirements
| Requirements | With regard to general system management requirements, Articles 14(5), 15(6) and 16(4) of [the NC RfG] shall apply to any DC-connected power park module.
Requirements
| Requirements | Chapter 2 - REQUIREMENTS FOR REMOTE-END HVDC CONVERTER STATIONS
Requirements
| Requirements | Article 46 - Scope
Requirements
| Requirements | The requirements of Articles 11 to 39 apply to remote-end HVDC converter stations, subject to specific requirements provided for in Articles 47 to 50.
Requirements
| Requirements | Article 47 - Frequency stability requirements
Requirements
1 | Requirements | Where a nominal frequency other than 50 Hz, or a frequency variable by design is used in the network connecting the DC-connected power park modules, subject to relevant TSO agreement, Article 11 shall apply to the remote-end HVDC converter station with the applicable frequency ranges and time periods specified by the relevant TSO, taking into account specificities of the system and the requirements laid down in Annex I. |  | ü |  |  | ü
2 | Requirements | With regards to frequency response, the remote-end HVDC converter station owner and the DC-connected power park module owner shall agree on the technical modalities of the fast signal communication in accordance with Article 39(1). Where the relevant TSO requires, the HVDC system shall be capable of providing the network frequency at the connection point as a signal. For an HVDC system connecting a power park module the adjustment of active power frequency response shall be limited by the capability of the DC-connected power park modules. |  | ü |  |  | ü
Requirements
| Requirements | Article 48 - Reactive power and voltage requirements
Requirements
1 | Requirements | With respect to voltage ranges:
a) | Requirements | a remote-end HVDC converter station shall be capable of staying connected to the remote-end HVDC converter station network and operating within the voltage ranges (per unit) and time periods specified in Tables 12 and 13, Annex VIII. The applicable voltage range and time periods specified are selected based on the reference 1 pu voltage;
b) | Requirements | wider voltage ranges or longer minimum times for operation may be agreed between the relevant system operator, in coordination with the relevant TSO, and the DC-connected power park module owner in accordance with Article 40; |  | ü |  |  | ü
c) | Requirements | for HVDC interface points at AC voltages that are not included in the scope of Table 12 and Table 13, Annex VIII, the relevant system operator, in coordination with the relevant TSO shall specify applicable requirements at the connection points; |  | ü |  |  | ü
d | Requirements | where frequencies other than nominal 50 Hz are used, subject to agreement by the relevant TSO, the voltage ranges and time periods specified by the relevant system operator, in coordination with the relevant TSO, shall be proportional to those in Annex VIII. |  | ü |  |  | ü
2 | Requirements | A remote-end HVDC converter station shall fulfil the following requirements referring to voltage stability, at the connection points with regard to reactive power capability:
a) | Requirements | The relevant system operator, in coordination with the relevant TSO shall specify the reactive power provision capability requirements for various voltage levels. In doing so, the relevant system operator, in coordination with the relevant TSO shall specify a U-Q/Pmax-profile of any shape and within the boundaries of which the remote-end HVDC converter station shall be capable of providing reactive power at its maximum HVDC active power transmission capacity. |  | ü |  |  | ü
b) | Requirements | the U-Q/Pmax-profile shall be specified by each relevant system operator, in coordination with the relevant TSO. The U-Q/Pmax-profile shall be within the range of Q/Pmax and steady state voltage specified in Table 14, Annex VIII, and the position of the U-Q/Pmax-profile envelope shall lie within the limits of the fixed outer envelope specified in Annex IV. The relevant system operator, in coordination with the relevant TSO shall consider the long term development of the network when determining these ranges. |  | ü |  |  | ü
Requirements
| Requirements | Article 49 - Network characteristics
Requirements
| Requirements | With regard to the network characteristics, the remote-end HVDC converter station owner shall provide relevant data to any DC-connected power park module owner in accordance with Article 42.
Requirements
| Requirements | Article 50 - Power quality
Requirements
| Requirements | Remote-end HVDC converter station owners shall ensure that their connection to the network does not result in a level of distortion or fluctuation of the supply voltage on the network, at the connection point, exceeding the level allocated to them by the relevant system operator, in coordination with the relevant TSO. The necessary contribution from grid users to the associated studies shall not be unreasonably withheld, including from, but not limited to, existing DC-connected power park modules and existing HVDC systems. The process for necessary studies to be conducted and relevant data to be provided by all grid users involved, as well as mitigating actions identified and implemented shall be in accordance with the process provided for in Article 29. | ü | ü | ü | ü | ü
Title 4 - INFORMATION EXCHANGE AND COORDINATION
Requirements
| Requirements | Article 51 - OPERATION of HVDC systems
Requirements
1 | Requirements | With regard to instrumentation for the operation, each HVDC converter unit of an HVDC system shall be equipped with an automatic controller capable of receiving instructions from the relevant system operator and from the relevant TSO. This automatic controller shall be capable of operating the HVDC converter units of the HVDC system in a coordinated way. The relevant system operator shall specify the automatic controller hierarchy per HVDC converter unit. |  | ü |  |  | ü
2 | Requirements | The automatic controller of the HVDC system referred to in paragraph 1 shall be capable of sending the following signal types to the relevant system operator: | ü | ü | ü | ü | ü
a) | Requirements | operational signals, providing at least the following:
| Requirements | (i) start-up signals;
| Requirements | (ii) AC and DC voltage measurements;
| Requirements | (iii) AC and DC current measurements;
| Requirements | (iv) active and reactive power measurements on the AC side;
| Requirements | (v) DC power measurements;
| Requirements | (vi) HVDC converter unit level operation in a multi-pole type HVDC converter;
| Requirements | (vii) elements and topology status; and
| Requirements | (viii) FSM, LFSM-O and LFSM-U active power ranges.
b) | Requirements | alarm signals, providing at least the following:
| Requirements | (i) emergency blocking;
| Requirements | (ii) ramp blocking;
| Requirements | (iii) fast active power reversal.
3 | Requirements | The automatic controller referred to in paragraph 1 shall be capable of receiving the following signal types from the relevant system operator: | ü | ü | ü | ü | ü
a) | Requirements | operational signals, receiving at least the following:
| Requirements | (i) start-up command;
| Requirements | (ii) active power setpoints;
| Requirements | (iii) frequency sensitive mode settings;
| Requirements | (iv) reactive power, voltage or similar setpoints;
| Requirements | (v) reactive power control modes;
| Requirements | (vi) power oscillation damping control; and
| Requirements | (vii) synthetic inertia.
b) | Requirements | alarm signals, receiving at least the following:
| Requirements | (i) emergency blocking command;emergency blocking command;
| Requirements | (ii) ramp blocking command;
| Requirements | (iii) active power flow direction; and
| Requirements | (iv) fast active power reversal command.
4 | Requirements | With regards to each signal, the relevant system operator may specify the quality of the supplied signal. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 52 - Parameters and settings
Requirements
1 | Requirements | The parameters and settings of the main control functions of an HVDC system shall be agreed between the HVDC system owner and the relevant system operator, in coordination with the relevant TSO. The parameters and settings shall be implemented within such a control hierarchy that makes their modification possible if necessary. Those main control functions are at least: | ü | ü | ü | ü | ü
a) | Requirements | synthetic inertia, if applicable as referred to in Articles 14 and 41;
b) | Requirements | frequency sensitive modes (FSM, LFSM-O, LFSM-U) referred to in Articles 15, 16 and 17;
c) | Requirements | frequency control, if applicable, referred to in Article 16;
d | Requirements | reactive power control mode, if applicable as referred to in Article 22;
e | Requirements | power oscillation damping capability, referred to Article 30;
f | Requirements | subsynchronous torsional interaction damping capability, referred to Article 31.
Requirements
| Requirements | Article 53 - Fault recording and monitoring
Requirements
1 | Requirements | An HVDC system shall be equipped with a facility to provide fault recording and dynamic system behaviour monitoring of the following parameters for each of its HVDC converter stations:
a) | Requirements | AC and DC voltage;
b) | Requirements | AC and DC current;
c) | Requirements | active power;
d | Requirements | reactive power; and
e | Requirements | frequency.
2 | Requirements | The relevant system operator may specify quality of supply parameters to be complied with by the HVDC system, provided a reasonable prior notice is given. | ü | ü | ü | ü | ü
3 | Requirements | The particulars of the fault recording equipment referred to in paragraph 1, including analogue and digital channels, the settings, including triggering criteria and the sampling rates shall be agreed between the HVDC system owner, the relevant system operator and the relevant TSO. | ü | ü | ü | ü | ü
4 | Requirements | All dynamic system behaviour monitoring equipment shall include an oscillation trigger, specified by the relevant system operator, in coordination with the relevant TSO, with the purpose of detecting poorly damped power oscillations. | ü | ü | ü | ü | ü
5 | Requirements | The facilities for quality of supply and dynamic system behaviour monitoring shall include arrangements for the HVDC system owner and the relevant system operator to access the information electronically. The communications protocols for recorded data shall be agreed between the HVDC system owner, the relevant system operator and the relevant TSO. | ü | ü | ü | ü | ü
Requirements
| Requirements | Article 54 - SIMULATION MODELS
Requirements
1 | Requirements | The relevant system operator in coordination with the relevant TSO may specify that an HVDC system owner deliver simulation models which properly reflect the behaviour of the HVDC system in both steady-state, dynamic simulations (fundamental frequency component) and in electromagnetic transient simulations. |  | ü |  |  | ü
| Requirements | The format in which models shall be provided and the provision of documentation of models structure and block diagrams shall be specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
2 | Requirements | For the purpose of dynamic simulations, the models provided shall contain at least, but not limited to the following sub-models, depending on the existence of the mentioned components:
a) | Requirements | HVDC converter unit models;
b) | Requirements | AC component models;
c) | Requirements | DC grid models;
d | Requirements | Voltage and power control;
e | Requirements | Special control features if applicable e.g. power oscillation damping (POD) function, subsynchronous torsional interaction (SSTI) control;
f | Requirements | Multi terminal control, if applicable;
g | Requirements | HVDC system protection models as agreed between the relevant TSO and the HVDC system owner. |  | ü |  |  | ü
3 | Requirements | The HVDC system owner shall verify the models against the results of compliance tests carried out according to Title VI and a report of this verification shall be submitted to the relevant TSO. The models shall then be used for the purpose of verifying compliance with the requirements of this Regulation including, but not limited to, compliance simulations as provided for in Title VI and used in studies for continuous evaluation in system planning and operation. |  | ü |  |  | ü
4 | Requirements | An HVDC system owner shall submit HVDC system recordings to the relevant system operator or relevant TSO if requested in order to compare the response of the models with these recordings. |  | ü |  |  | ü
5 | Requirements | An HVDC system owner shall deliver an equivalent model of the control system when adverse control interactions may result with HVDC converter stations and other connections in close electrical proximity if requested by the relevant system operator or relevant TSO. The equivalent model shall contain all necessary data for the realistic simulation of the adverse control interactions. |  | ü |  |  | ü
Requirements
| Requirements | TITLE 5 - OPERATIONAL NOTIFICATION PROCEDURE FOR CONNECTION
Requirements
| Requirements | Chapter 1 - CONNECTION OF NEW HVDC SYSTEMS
Requirements
| Requirements | Article 55 - General provisions
Requirements
1 | Requirements | The HVDC system owner shall demonstrate to the relevant system operator that it has complied with the requirements set out in Title II to Title IV at the respective connection point by successfully completing the operational notification procedure for connection of the HVDC system as described in Articles 56 to 59. |  | ü |  |  | ü
2 | Requirements | The relevant system operator shall specify any detailed provisions of the operational notification procedure and make the details publicly available. |  | ü |  |  | ü
3 | Requirements | The operational notification procedure for connection for each new HVDC system shall comprise:
a) | Requirements | energisation operational notification (EON);
b) | Requirements | interim operational notification (ION); and
c) | Requirements | final operational notification (FON).
Requirements
| Requirements | Article 56 - EON for HVDC systems
Requirements
| Requirements | An EON shall entitle the HVDC system owner to energise its internal network and auxiliaries and connect it to the network at its specified connection points.
| Requirements | An EON shall be issued by the relevant system operator, subject to completion of preparation and the fulfilment of the requirements specified by the relevant system operator in the relevant operational procedures. This preparation will include agreement on the protection and control settings relevant to the connection points between the relevant system operator and the HVDC system owner. |  | ü |  |  | ü
Requirements
| Requirements | Article 57 - ION for HVDC systems
Requirements
1 | Requirements | ION shall entitle a HVDC system owner or HVDC converter unit owner to operate the HVDC system or HVDC converter unit by using the network connections specified for the connection points for a limited period of time.
2 | Requirements | An ION shall be issued by the relevant system operator subject to the completion of the data and study review process. |  | ü |  |  | ü
3 | Requirements | For the purpose of the completion of data and study review, the HVDC system owner or HVDC converter unit owner shall provide the following upon request from the relevant system operator: |  | ü |  |  | ü
a) | Requirements | itemized statement of compliance;
b) | Requirements | detailed technical data of the HVDC system with relevance to the network connection, that is specified with respect to the connection points, as specified by the relevant system operator, in coordination with the relevant TSOs; |  | ü |  |  | ü
c) | Requirements | equipment certificates of HVDC systems or HVDC converter units where these are relied upon as part of the evidence of compliance;
d | Requirements | simulation models or a replica of the exact control system as specified by Article 54 and by the relevant system operator in coordination with the relevant TSOs; |  | ü |  |  | ü
e | Requirements | studies demonstrating expected steady-state and dynamic performance as required by Titles II, III and IV;
f | Requirements | details of intended compliance tests according to Article 70;
g | Requirements | details of intended practical method of completing compliance tests pursuant to Title VI.
4 | Requirements | Except where paragraph 5 applies, the maximum period for the HVDC system owner or HVDC converter unit owner to remain in the ION status shall not exceed twenty four months. The Relevant system operator may specify a shorter ION validity period. The ION validity period shall be notified to the regulatory authority in accordance with the applicable national regulatory framework. ION extension shall be granted only if the HVDC system owner demonstrates substantial progress towards full compliance. At the time of ION extension, the outstanding issues shall be explicitly identified. |  | ü |  |  | ü
5 | Requirements | The maximum period for an HVDC system owner or HVDC converter unit owner to remain in the ION status may be extended beyond 24 months upon request for derogation made to the relevant system operator in accordance with the procedure in Title VII. The request shall be made before the expiry of the twenty four month period. |  | ü |  |  | ü
Requirements
| Requirements | Article 58 - FON for HVDC systems
Requirements
1 | Requirements | FON shall entitle an HVDC system owner to operate the HVDC system or HVDC converter units by using the grid connection points.
2 | Requirements | A FON shall be issued by the relevant system operator upon prior removal of all incompatibilities identified for the purpose of the ION status and subject to the completion of the data and study review process. |  | ü |  |  | ü
3 | Requirements | For the purpose of the completion of data and study review, the HVDC system owner shall provide the following upon request from the relevant system operator in coordination with the relevant TSO: |  | ü |  |  | ü
a) | Requirements | itemized statement of compliance; and
b) | Requirements | update of applicable technical data, simulation models, a replica of the exact control system and studies as referred to in Article 57, including use of actual measured values during testing.
4 | Requirements | In case of incompatibility identified for the purpose of the granting of the FON, a derogation may be granted upon a request to the relevant system operator, in accordance with Articles 77 and 78. A FON shall be issued by the relevant system operator, if the HVDC system is compliant with the provisions of the derogation. Where a request for a derogation is rejected, the relevant system operator shall have the right to refuse the operation of the HVDC system or HVDC converter units, whose owner’s request for a derogation was rejected, until the HVDC system owner and the relevant system operator have resolved the incompatibility and the relevant system operator considers that the HVDC system complies with the provisions of this Regulation. If the relevant system operator and the HVDC system owner do not resolve the incompatibility within a reasonable timeframe, but in any case not later than six months after the notification of the rejection of the request for a derogation, each party may refer the issue for decision to the regulatory authority. |  | ü |  |  | ü
Requirements
| Requirements | Article 59 - Limited operational notification for HVDC systems/derogations
Requirements
1 | Requirements | HVDC system owners to whom a FON has been granted shall inform the relevant system operator immediately in the following circumstances: |  | ü |  |  | ü
a) | Requirements | the HVDC system is temporarily subject to either a significant modification or loss of capability, due to implementation of one or more modifications of significance to its performance; or
b) | Requirements | in case of equipment failures leading to non-compliance with some relevant requirements.
2 | Requirements | The HVDC system owner shall apply to the relevant system operator for a limited operational notification (LON) if the HVDC system owner reasonably expects the circumstances detailed in paragraph 1 to persist for more than three months. |  | ü |  |  | ü
3 | Requirements | A LON shall be issued by the relevant system operator with a clear identification of: |  | ü |  |  | ü
a) | Requirements | the unresolved issues justifying the granting of the LON;
b) | Requirements | the responsibilities and timescales for expected solution; and
c) | Requirements | a maximum period of validity which shall not exceed 12 months. The initial period granted may be shorter with the possibility for extension if evidence to the satisfaction of the relevant system operator demonstrating that substantial progress has been made towards achieving full compliance. |  | ü |  |  | ü
4 | Requirements | The FON shall be suspended during the period of validity of the LON with regard to the subjects for which the LON has been issued.
5 | Requirements | A further prolongation of the period of validity of the LON may be granted upon request for a derogation made to the relevant system operator, before the expiry of that period, in accordance with Articles 77 and 78. |  | ü |  |  | ü
6 | Requirements | The relevant system operator may refuse the operation of the HVDC system if the LON terminates and the circumstance which caused it to be issued remains. In such a case the FON shall automatically be invalid. |  | ü |  |  | ü
7 | Requirements | If the relevant system operator does not grant an extension of the period of validity of the LON in accordance with paragraph 5 or if it refuses to allow the operation of the HVDC system once the LON is no longer valid in accordance with paragraph 6, the HVDC system owner may refer the issue for decision to the regulatory authority within six months after the notification of the decision of the relevant system operator. |  | ü |  |  | ü
Requirements
| Requirements | Chapter 2 - CONNECTION OF NEW DC-CONNECTED POWER PARK MODULES
Requirements
| Requirements | Article 60 - General provisions
Requirements
1 | Requirements | The provisions of this Chapter shall apply to new DC-connected power park modules only.
2 | Requirements | The DC-connected power park module owner shall demonstrate to the relevant system operator its compliance with the requirements referred to in Title III at the respective connection points by successfully completing the operational notification procedure for connection of the DC-connected power park module in accordance with Articles 61 through to 66. |  | ü |  |  | ü
3 | Requirements | The relevant system operator shall specify further details of the operational notification procedure and make those details publically available. |  | ü |  |  | ü
4 | Requirements | The operational notification procedure for connection for each new DC-connected power park module shall comprise:
a) | Requirements | energisation operational notification (EON);
b) | Requirements | interim operational notification (ION); and
c) | Requirements | final operational notification (FON).
Requirements
| Requirements | Article 61 - EON for DC-connected power park modules
Requirements
1 | Requirements | An EON shall entitle the owner of a DC-connected power park module to energise its internal network and auxiliaries by using the grid connection that is specified by the connection points.
2 | Requirements | An EON shall be issued by the relevant system operator, subject to completion of preparation including agreement on the protection and control settings relevant to the connection points between the relevant system operator and the DC-connected power park module. |  | ü |  |  | ü
Requirements
| Requirements | Article 62 - ION for DC-connected power park modules
Requirements
1 | Requirements | An ION shall entitle the DC-connected power park module owner to operate the DC-connected power park module and generate power by using the grid connection for a limited period of time.
2 | Requirements | An ION shall be issued by the relevant system operator, subject to the completion of the data and study review process. |  | ü |  |  | ü
3 | Requirements | With respect to data and study review, the DC-connected power park module owner shall provide the following upon request from the relevant system operator: |  | ü |  |  | ü
a) | Requirements | itemized statement of compliance;
b) | Requirements | detailed technical data of the DC-connected power park module with relevance to the grid connection, that is specified by the connection points, as specified by the relevant system operator in coordination with the relevant TSO; |  | ü |  |  | ü
c) | Requirements | equipment certificates of DC-connected power park module, where these are relied upon as part of the evidence of compliance;
d | Requirements | simulation models as specified in Article 54 and as required by the relevant system operator in coordination with the relevant TSO; |  | ü |  |  | ü
e | Requirements | studies demonstrating expected steady-state and dynamic performance as required by Title III; and
f | Requirements | details of intended compliance tests in accordance with Article 71.
4 | Requirements | Except where paragraph 5 applies, the maximum period for the DC-connected power park module owner to remain in the ION status shall not exceed twenty-four months. The relevant system operator may specify shorter ION validity. The ION validity period shall be notified to the regulatory authority in accordance with the applicable national regulatory framework. ION extensions shall be granted only if the DC-connected power park module owner demonstrates substantial progress towards full compliance. At the time of ION extension, any outstanding issues shall be explicitly identified. |  | ü |  |  | ü
5 | Requirements | The maximum period for a DC-connected power park module owner to remain in the ION status may be extended beyond 24 months upon request for a derogation made to the relevant system operator in accordance with the procedure in Title VII. |  | ü |  |  | ü
Requirements
| Requirements | Article 63 - FON for DC-connected power park modules
Requirements
1 | Requirements | A FON shall entitle the DC-connected power park module owner to operate the DC-connected power park module by using the grid connection that is specified by the connection point.
2 | Requirements | A FON shall be issued by the relevant system operator, upon prior removal of all incompatibilities identified for the purpose of the ION status and subject to the completion of the data and study review process as required by this Regulation. |  | ü |  |  | ü
3 | Requirements | For the purpose of the completion of data and study review, the DC-connected power park module owner shall provide the following upon request from the relevant system operator: |  | ü |  |  | ü
a) | Requirements | itemized Statement of compliance; and
b) | Requirements | update of applicable technical data, simulation models and studies as referred to in Article 62(3), including use of actual measured values during testing.
4 | Requirements | In case of incompatibility identified for the purpose of the granting of the FON, a derogation may be granted upon request made to the relevant system operator, in accordance with the derogation procedure according to Title VII. A FON shall be issued by the relevant system operator, if the DC-connected power park module is compliant with the provisions of the derogation. The relevant system operator shall have the right to refuse the operation of the DC-connected power park module, whose owner’s request for a derogation was rejected, until the DC-connected power park module owner and the relevant system operator have resolved the incompatibility and the DC-connected power park module is considered to be compliant by the relevant system operator. |  | ü |  |  | ü
Requirements
| Requirements | Article 64 - Limited operational notification for DC-connected power park modules
Requirements
1 | Requirements | DC-connected power park module owners to whom a FON has been granted shall inform the relevant system operator immediately in the following circumstances: |  | ü |  |  | ü
a) | Requirements | the DC-connected power park module is temporarily subject to either a significant modification or loss of capability, due to implementation of one or more modifications of significance to its performance; or
b) | Requirements | in case of equipment failures leading to non-compliance with some relevant requirements.
2 | Requirements | The DC-connected power park module owner shall apply to the relevant system operator for a limited operational notification (LON), if the DC-connected power park module owner reasonably expects the circumstances detailed in paragraph 1 to persist for more than three months. |  | ü |  |  | ü
3 | Requirements | A LON shall be issued by the relevant TSO with a clear identification of: |  | ü |  |  | ü
a) | Requirements | the unresolved issues justifying the granting of the LON;
b) | Requirements | the responsibilities and timescales for expected solution; and
c) | Requirements | a maximum period of validity which shall not exceed 12 months. The initial period granted may be shorter with the possibility for extension if evidence to the satisfaction of the relevant system operator demonstrating that substantial progress has been made towards achieving full compliance. |  | ü |  |  | ü
4 | Requirements | The FON shall be suspended during the period of validity of the LON with regard to the subjects for which the LON has been issued.
5 | Requirements | A further prolongation of the period of validity of the LON may be granted upon request for a derogation made to the relevant system operator, before the expiry of that period, in accordance with the derogation procedure described in Title VII. |  | ü |  |  | ü
6 | Requirements | The relevant system operator may refuse the operation of the DC-connected power park module if the LON terminates and the circumstance which caused it to be issued remains. In such a case the FON shall automatically be invalid. |  | ü |  |  | ü
Requirements
| Requirements | Chapter 3 - Cost Benefit Analysis
Requirements
| Requirements | Article 65 - Identification of costs and benefits of application of requirements to existing HVDC systems or DC-connected power park modules
Requirements
1 | Requirements | Prior to the application of any requirement set out in this Regulation to existing HVDC systems or DC-connected power park modules in accordance with paragraph 3 of Article 4, the relevant TSO shall undertake a qualitative comparison of costs and benefits related to the requirement under consideration. This comparison shall take into account available network-based or market-based alternatives. The relevant TSO may only proceed to undertake a quantitative cost-benefit analysis in accordance with paragraphs 2 to 5, if the qualitative comparison indicates that the likely benefits exceed the likely costs. If, however, the cost is deemed high or the benefit is deemed low, then the relevant TSO shall not proceed further. |  | ü |  |  | ü
2 | Requirements | Following a preparatory stage undertaken in accordance with paragraph 1, the relevant TSO shall carry out a quantitative cost-benefit analysis of any requirement under consideration for application to existing HVDC systems or DC-connected power park modules that have demonstrated potential benefits as a result of the preparatory stage according to paragraph 1. |  | ü |  |  | ü
3 | Requirements | Within three months of concluding the cost-benefit analysis, the relevant TSO shall summarise the findings in a report which shall: |  | ü |  |  | ü
a) | Requirements | include the cost-benefit analysis and a recommendation on how to proceed;
b) | Requirements | include a proposal for a transitional period for applying the requirement to existing HVDC systems or DC-connected power park modules. That transitional period shall not be more than two years from the date of the decision of the regulatory authority or where applicable the Member State on the requirement’s applicability;
c) | Requirements | be subject to public consultation in accordance with Article 8.
4 | Requirements | No later than six months after the end of the public consultation, the relevant TSO shall prepare a report explaining the outcome of the consultation and making a proposal on the applicability of the requirement under consideration to existing HVDC systems or DC-connected power park modules. The report and proposal shall be notified to the regulatory authority or, where applicable, the Member State, and the HVDC system owner, DC-connected power park module owner or, where applicable, third party shall be informed on its content. |  | ü |  |  | ü
5 | Requirements | The proposal made by the relevant TSO to the regulatory authority or, where applicable, the Member State pursuant to paragraph 4 shall include the following: |  | ü |  |  | ü
a) | Requirements | an operational notification procedure for demonstrating the implementation of the requirements by the existing HVDC system owner or DC-connected power park module owner;
b) | Requirements | a transitional period for implementing the requirements which shall take into account the category of HVDC system or DC-connected power park module and any underlying obstacles to the efficient implementation of the equipment modification/refitting.
Requirements
| Requirements | Article 66 - Principles of cost-benefit analysis
Requirements
1 | Requirements | HVDC system owners, DC-connected power park module owners and DSOs, including CDSOs, shall assist and contribute to the cost-benefit analysis undertaken according to Article 65 and 78 and provide the necessary data as requested by the relevant system operator or relevant TSO within three months of receiving a request, unless agreed otherwise by the relevant TSO. For the preparation of a cost-benefit-analysis by a HVDC system owner or DC-connected power park module owner, or their prospective owner, assessing a potential derogation pursuant to Article 77, the relevant TSO and DSO, including CDSO, shall assist and contribute to the cost-benefit analysis and provide the necessary data as requested by the HVDC system owner or DC-connected power park module owner, or their prospective owner, within three months of receiving a request, unless agreed otherwise by the HVDC system owner or DC-connected power park module owner, or their prospective owner. |  | ü |  |  | ü
2 | Requirements | A cost-benefit analysis shall be in line with the following principles:
a) | Requirements | the relevant TSO, or HVDC system owner or DC-connected power park module owner, or their prospective owner, shall base its cost-benefit analysis on one or more of the following calculating principles: |  | ü |  |  | ü
| Requirements | (i) the net present value;
| Requirements | (ii) the return on investment;
| Requirements | (iii) the rate of return;
| Requirements | (iv) the time needed to break even.
b) | Requirements | the relevant TSO, or HVDC system owner or DC-connected power park module owner, or their prospective owner, shall also quantify socio-economic benefits in terms of improvement in security of supply and shall include at least: |  | ü |  |  | ü
| Requirements | (i) the associated reduction in probability of loss of supply over the lifetime of the modification;
| Requirements | (ii) the probable extent and duration of such loss of supply;
| Requirements | (iii) the societal cost per hour of such loss of supply.
c) | Requirements | the relevant TSO, or HVDC system owner or DC-connected power park module owner, or their prospective owner, shall quantify the benefits to the internal market in electricity, cross-border trade and integration of renewable energies, including at least: |  | ü |  |  | ü
| Requirements | (i) the active power frequency response;
| Requirements | (ii) the balancing reserves;
| Requirements | (iii) the reactive power provision;
| Requirements | (iv) congestion management;
| Requirements | (v) defence measures.
d) | Requirements | the relevant TSO shall quantify the costs of applying the necessary rules to existing HVDC systems or DC-connected power park modules, including at least: |  | ü |  |  | ü
| Requirements | (i) the direct costs incurred in implementing a requirement;
| Requirements | (ii) the costs associated with attributable loss of opportunity;
| Requirements | (iii) the costs associated with resulting changes in maintenance and operation.
| Compliance | TITLE 6 - Compliance
Compliance
| Compliance | Chapter 1 - COMPLIANCE MONITORING
Compliance
| Compliance | Article 66a - Common provisions for compliance testing
Compliance
1 | Compliance | Testing of the performance of HVDC systems and DC-connected power park modules power generating modules shall aim at demonstrating that the requirements of this Regulation have been complied with.
2 | Compliance | Notwithstanding the minimum requirements for compliance testing set out in this Regulation, the relevant system operator is entitled to: |  | ü |  |  | ü
a) | Compliance | allow the HVDC system owner or DC-connected power park module owner to carry out an alternative set of tests, provided that those tests are efficient and suffice to demonstrate that a HVDC system or DC-connected power park module complies with the requirements of this Regulation;
b) | Compliance | require the HVDC system owner or DC-connected power park module owner to carry out additional or alternative sets of tests in those cases where the information supplied to the relevant system operator in relation to compliance testing under the provisions of [Chapter 2, 3 or 4 of Title IV], is not sufficient to demonstrate compliance with the requirements of this Regulation; and |  | ü |  |  | ü
3 | Compliance | The HVDC system owner or DC-connected power park module owner is responsible for carrying out the tests in accordance with the conditions laid down in [Chapters 2, 3 and 4 of Title IV]. The relevant system operator shall cooperate and not unduly delay the performance of the tests. |  | ü |  |  | ü
4 | Compliance | The relevant system operator may participate in the compliance testing either on site or remotely from the system operator’s control centre. For that purpose, the HVDC system owner or DC-connected power park module owner shall provide the monitoring equipment necessary to record all relevant test signals and measurements as well as ensure that the necessary representatives of the HVDC system owner or DC-connected power park module owner available on site for the entire testing period. Signals specified by the relevant system operator shall be provided if, for selected tests, the system operator wishes to use its own equipment to record performance. The relevant system operator has sole discretion to decide about its participation. |  | ü |  |  | ü
Compliance
| Compliance | Article 66(b) - Common provisions on compliance simulation
Compliance
1 | Compliance | Simulation of the performance of HVDC systems and DC-connected power park modules shall aim at demonstrating that the requirements of this Regulation have been fulfilled.
2 | Compliance | Notwithstanding the minimum requirements set out in this Regulation for compliance simulation, the relevant system operator may: |  | ü |  |  | ü
a) | Compliance | allow the HVDC system owner or DC-connected power park module owner to carry out an alternative set of simulations, provided that those simulations are efficient and suffice to demonstrate that a HVDC system or DC-connected power park module complies with the requirements of this Regulation or with national legislation; and
b) | Compliance | require the HVDC system owner or DC-connected power park module owner to carry out additional or alternative sets of simulations in those cases where the information supplied to the relevant system operator in relation to compliance simulation under the provisions of [Chapter 5, 6 or 7 of Title IV], is not sufficient to demonstrate compliance with the requirements of this Regulation. |  | ü |  |  | ü
3 | Compliance | To demonstrate compliance with the requirements of this Regulation, the HVDC system owner and DC-connected power park module owner shall provide a report with the simulation results. The HVDC system owner and DC-connected power park module owner shall produce and provide a validated simulation model for a given HVDC system or DC-connected power park module. The scope of the simulation models is set out in point [(c) of Article 15(6)].
4 | Compliance | The relevant system operator shall have the right to check that a HVDC system and DC-connected power park module complies with the requirements of this Regulation by carrying out its own compliance simulations based on the provided simulation reports, simulation models and compliance test measurements. |  | ü |  |  | ü
5 | Compliance | The relevant system operator shall provide the HVDC system owner or DC-connected power park module owner with technical data and a simulation model of the network, to the extent necessary to carry out the requested simulations in accordance with [Chapter 5, 6 or 7 of Title IV]. |  | ü |  |  | ü
Compliance
| Compliance | Article 67 - Responsibility of the HVDC system owner and DC-connected power park module owner
Compliance
1 | Compliance | The HVDC system owner shall ensure that the HVDC system and HVDC converter stations are compliant with the requirements provided for by this Regulation. This compliance shall be maintained throughout the lifetime of the facility.
2 | Compliance | The DC-connected power park module owner shall ensure that the DC-connected power park module is compliant with the requirements under this Regulation. This compliance shall be maintained throughout the lifetime of the facility.
3 | Compliance | Planned modifications of the technical capabilities of the HVDC system, HVDC converter station or DC-connected power park module with possible impact on its compliance to the requirements under this Regulation shall be notified to the relevant system operator by the HVDC system owner or DC-connected power park module owner before initiating such modification. |  | ü |  |  | ü
4 | Compliance | Any operational incidents or failures of an HVDC system, HVDC converter station or DC-connected power park module that have impact on its compliance to the requirements of this Regulation shall be notified to the relevant system operator by the HVDC system owner or DC-connected power park module owner as soon as possible without any delay after the occurrence of such an incident. |  | ü |  |  | ü
5 | Compliance | Any foreseen test schedules and procedures to verify compliance of an HVDC system, HVDC converter station or DC-connected power park module with the requirements of this Regulation shall be notified to the relevant system operator by the HVDC system owner or DC-connected power park module owner in due time and prior to their launch and shall be approved by the relevant system operator. |  | ü |  |  | ü
6 | Compliance | The relevant system operator shall be facilitated to participate in such tests and may record the performance of the HVDC systems, HVDC converter stations or DC-connected power park modules. |  | ü |  |  | ü
Compliance
| Compliance | Article 68 - Tasks of the relevant system operator
Compliance
1 | Compliance | The relevant system operator shall assess the compliance of an HVDC system, HVDC converter station and DC-connected power park module with the requirements under this Regulation throughout the lifetime of the HVDC system, HVDC converter station or DC-connected power park module. The HVDC system owner or DC-connected power park module owner shall be informed of the outcome of this assessment. |  | ü |  |  | ü
2 | Compliance | Where requested by the relevant system operator , the HVDC system owner or DC-connected power park module owner shall carry out compliance tests and simulations, not only during the operational notification procedures according to Title V, but repeatedly throughout the lifetime of the HVDC system, HVDC converter station or DC-connected power park module according to a plan or general scheme for repeated tests and specified simulations or after any failure, modification or replacement of any equipment that may have impact on the compliance with the requirements under this Regulation. The HVDC system owner or DC-connected power park module owner shall be informed of the outcome of these compliance tests and simulations. |  | ü |  |  | ü
3 | Compliance | The relevant system operator shall make publicly available the list of information and documents to be provided as well as the requirements to be fulfilled by the HVDC system owner or DC-connected power park module owner in the frame of the compliance process. Such list shall cover at least the following information, documents and requirements: |  | ü |  |  | ü
a | Compliance | all documentation and certificates to be provided by the HVDC system owner or DC-connected power park module owner;
b | Compliance | details of the technical data of the HVDC system, HVDC converter station or DC-connected power park module with relevance to the grid connection;
c | Compliance | requirements for models for steady-state and dynamic system studies;
d | Compliance | timeline for the provision of system data required to perform the studies;
e | Compliance | studies by the HVDC system owner or DC-connected power park module owner to demonstrate the expected steady-state and dynamic performance in accordance with the requirements set out in Titles II, III and IV
f | Compliance | conditions and procedures including the scope for registering equipment certificates; and
g | Compliance | conditions and procedures for use of relevant equipment certificates, issued by an authorised certifier, by the DC-connected power park module owner.
4 | Compliance | The relevant system operator shall make publicly available the allocation of responsibilities to the HVDC system owner or DC-connected power park module owner and to the system operator for compliance testing, simulation and monitoring. |  | ü |  |  | ü
5 | Compliance | The relevant system operator may partially or totally assign the performance of its compliance monitoring to third parties. In this case, the relevant system operator shall ensure compliance with Article 10 by appropriate confidentiality commitments with the assignee. |  | ü |  |  | ü
6 | Compliance | The relevant system operator shall not unreasonably withhold any operational notification in accordance with Title V, if compliance tests or simulations cannot be performed as agreed between the relevant system operator and the HVDC system owner or DC-connected power park module owner due to reasons which are in the sole control of the relevant system operator. |  | ü |  |  | ü
7 | Compliance | The relevant system operator shall provide the relevant TSO when requested the compliance test and simulation results referred to in this Chapter. |  | ü |  |  | ü
Chapter 2 - COMPLIANCE TESTING
Compliance
| Compliance | ARTICLE 69 - Compliance testing for HVDC systems
Compliance
1 | Compliance | Equipment Certificate may be used instead of part of the tests below, on the condition that they are provided to the relevant system operator. |  | ü |  |  | ü
2 | Compliance | With regard to the reactive power capability test:
a | Compliance | the HVDC converter unit or the HVDC converter station shall demonstrate its technical capability to provide leading and lagging reactive power capability according to Article 20.
b | Compliance | the reactive power capability test shall be carried out at maximum reactive power, both leading and lagging, and concerning the verification of the following parameters:
| Compliance | (i) Operation at minimum HVDC active power transmission capacity;
| Compliance | (ii) Operation at maximum HVDC active power transmission capacity;
| Compliance | (iii) Operation at active power setpoint between those minimum and maximum HVDC active power transmission capacity.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC converter unit or the HVDC converter station has been operating no shorter than 1 hour at maximum reactive power, both leading and lagging, for each parameter as referred to in point b);
| Compliance | (ii) the HVDC converter unit or the HVDC converter station demonstrates its capability to change to any reactive power setpoint within the applicable reactive power range within the specified performance targets of the relevant reactive power control scheme; and
| Compliance | (iii) no action of any protection within the operation limits specified by reactive power capacity diagram occurs.
3 | Compliance | With regard to the voltage control mode test:
a | Compliance | the HVDC converter unit or the HVDC converter station shall demonstrate its capability to operate in voltage control mode in the conditions set forth in Article 22(3);
b | Compliance | the voltage control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the implemented slope and deadband of the static characteristic;
| Compliance | (ii) the accuracy of the regulation;
| Compliance | (iii) the insensitivity of the regulation;
| Compliance | (iv) the time of reactive power activation.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the range of regulation and adjustable droop and deadband is compliant with agreed or decided characteristic parameters, according to Article 22(3);
| Compliance | (ii) tthe insensitivity of voltage control is not higher than 0.01 pu, according to Article 22(3);
| Compliance | (iii) following a step change in voltage, 90 % of the change in reactive power output has been achieved within the times and tolerances according to Article 22(3).
4 | Compliance | With regard to the reactive power control mode test:
a | Compliance | the HVDC converter unit or the HVDC converter station shall demonstrate its capability to operate in reactive power control mode, according to the conditions referred to in Article 22(4);
b | Compliance | the reactive power control mode test shall be complementary to the reactive power capability test;
c | Compliance | the reactive power control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the reactive power setpoint range and step;
| Compliance | (ii) the accuracy of the regulation; and
| Compliance | (iii) the time of reactive power activation.
d | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the reactive power setpoint range and step is ensured according to Article 22(4);
| Compliance | (ii) the accuracy of the regulation is compliant with the conditions as referred to in Article 22(3).
5 | Compliance | With regard to the power factor control mode test:
a | Compliance | the HVDC converter unit or the HVDC converter station shall demonstrate its capability to operate in power factor control mode according to the conditions referred to in Article 22(5);
b | Compliance | the power factor control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the power factor setpoint range;
| Compliance | (ii) the accuracy of the regulation;
| Compliance | (iii) the response of reactive power due to step change of active power.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the power factor setpoint range and step is ensured according to Article 22(5);
| Compliance | (ii) the time of reactive power activation as result of step active power change does not exceed the requirements specified in accordance with Article 22(5);
| Compliance | (iii) the accuracy of the regulation is compliant with the value, as referred to in Article 22(5).
6 | Compliance | 6. With regard to the FSM response test:
a | Compliance | the HVDC system shall demonstrate its technical capability to continuously modulate active power over the full operating range between maximum HVDC active power transmission capacity and minimum HVDC active power transmission capacity to contribute to frequency control and shall verify the steady-state parameters of regulations, such as droop and deadband and dynamic parameters, including robustness during frequency step change response and large, fast frequency changes;
b | Compliance | the test shall be carried out by simulating frequency steps and ramps big enough to activate at least 10% of the full active power frequency response range in each direction, taking into account the droop settings and the deadband. Simulated frequency deviation signals shall be injected into the controller of the HVDC converter unit or the HVDC converter station;
c | Compliance | the test shall be deemed to be passed, provided that the following conditions are all fulfilled:
| Compliance | (i) activation time of full active power frequency response range as result of a step frequency change has been no longer than required by Annex II;
| Compliance | (ii) undamped oscillations do not occur after the step change response;
| Compliance | (iii) the initial delay time has been according to Annex II;
| Compliance | (iv) the droop settings are available within the range provided for in Annex II and deadband (thresholds) is not more than the value in Annex II;
| Compliance | (v) insensitivity of active power frequency response at any relevant operating point does not exceed the requirements set forth in Annex II.
7 | Compliance | With regard to the LFSM-O response test:
a | Compliance | the HVDC system shall demonstrate its technical capability to continuously modulate active power to contribute to frequency control in case of large increase of frequency in the system and shall verify the steady-state parameters of regulations, such as droop and deadband, and dynamic parameters, including frequency step change response;
b | Compliance | the test shall be carried out by simulating frequency steps and ramps big enough to activate at least 10 % of the full operating range for active power, taking into account the droop settings and the deadband. simulated frequency deviation signals shall be injected into the controller of the HVDC converter unit or the HVDC converter station;
c | Compliance | the test shall be deemed passed, provided that the following conditions are both fulfilled:
| Compliance | (i) the test results, for both dynamic and static parameters, are in line with the requirements as referred to in Annex II;
| Compliance | (ii) undamped oscillations do not occur after the step change response.
8 | Compliance | With regard to the LFSM-U response test:
a | Compliance | the HVDC system shall demonstrate its technical capability to continuously modulate active power at operating points below maximum HVDC active power transmission capacity to contribute to frequency control in case of large drop of frequency in the system;
b | Compliance | the test shall be carried out by simulating at appropriate active power load points with low frequency steps and ramps big enough to activate at least 10 % of the full operating range for active power, taking into account the droop settings and the deadband. Simulated frequency deviation signals shall be injected into the controller of the HVDC converter unit or the HVDC converter station;
c | Compliance | the test shall be deemed passed, provided that the following conditions are both fulfilled:
| Compliance | (i) the test results, for both dynamic and static parameters, are in line with the requirements as referred to in Annex II;
| Compliance | (ii) undamped oscillations do not occur after the step change response.
9 | Compliance | With regard to the active power controllability test:
a | Compliance | the HVDC system shall demonstrate its technical capability to continuously modulate active power over the full operating range according to Article 13 (1)a) and d);
b | Compliance | the test shall be carried out by sending manual and automatic instructions by the relevant TSO; |  | ü |  |  | ü
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC system has demonstrated stable operation;
| Compliance | (ii) the time of adjustment of the active power is shorter than the delay specified pursuant to Article 13(1)(a);
| Compliance | (iii) the dynamic response of the HVDC system when receiving instructions for the purposes of exchange or sharing of reserves, or for participating in imbalance netting processes, if capable of fulfilling the requirements for these products, as specified by the relevant TSO. |  | ü |  |  | ü
10 | Compliance | With regard to the ramping rate modification test:
a | Compliance | the HVDC system shall demonstrate its technical capability to adjust the ramping rate according to Article 13(2);
b | Compliance | the test shall be carried out by the relevant TSO sending instructions of ramping modifications; |  | ü |  |  | ü
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) ramping rate is adjustable;
| Compliance | (ii) the HVDC system has demonstrated stable operation during ramping periods.
11 | Compliance | With regard to the black start test, if applicable:
a | Compliance | the HVDC system shall demonstrate its technical capability to energise the busbar of the remote AC substation to which it is connected, within a time frame specified by the relevant TSO, according to Article 37(2). |  | ü |  |  | ü
b | Compliance | the test shall be carried out while the HVDC system starts from shut down.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC system has demonstrated being able to energise the busbar of the remote AC-substation to which it is connected
| Compliance | (ii) the HVDC system operates from a stable operating point at agreed capacity, according to the procedure of Article 37(3).
Compliance
| Compliance | Article 70 - Compliance testing for DC-connected power park modules and remote-end HVDC converter units
Compliance
1 | Compliance | Equipment certificate may be used instead of part of the tests below, on the condition that they are provided to the relevant system operator |  | ü |  |  | ü
2 | Compliance | With regard to the reactive power capability test of DC-connected power park modules:
a | Compliance | the DC-connected power park module shall demonstrate its technical capability to provide leading and lagging reactive power capability according to Article 40(2);
b | Compliance | the reactive power capability test shall be carried out at maximum reactive power, both leading and lagging, and concerning the verification of the following parameters:
| Compliance | (i) operation in excess of 60 % of maximum capacity for 30 minutes;
| Compliance | (ii) operation within the range of 30 – 50 % of maximum capacity for 30 minutes; and
| Compliance | (iii) operation within the range of 10 – 20 % of maximum capacity for 60 minutes.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the DC-connected power park module has been operating no shorter than requested duration at maximum reactive power, both leading and lagging, in each parameter as referred to in point (b);
| Compliance | (ii) the DC-connected power park module has demonstrated its capability to change to any reactive power setpoint within the agreed or decided reactive power range within the specified performance targets of the relevant reactive power control scheme; and
| Compliance | (iii) no action of any protection within the operation limits specified by reactive power capacity diagram occurs.
3 | Compliance | With regard to the reactive power capability test of remote-end HVDC converter units:
a | Compliance | the HVDC converter unit or the HVDC converter station shall demonstrate its technical capability to provide leading and lagging reactive power capability according to Article 48(2);
b | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC converter unit or the HVDC converter station has been operating no shorter than 1 hour at maximum reactive power, both leading and lagging, at:
| Compliance | - minimum HVDC active power transmission capacity;
| Compliance | - maximum HVDC active power transmission capacity; and
| Compliance | - an active power operating point between those maximum and minimum ranges.
| Compliance | (ii) the HVDC converter unit or the HVDC converter station demonstrates its capability to change to any reactive power setpoint within the agreed or decided reactive power range within the specified performance targets of the relevant reactive power control scheme; and
| Compliance | (iii) no action of any protection within the operation limits specified by reactive power capacity diagram occurs.
4 | Compliance | With regard to the voltage control mode test:
a | Compliance | the DC-connected power park module shall demonstrate its capability to operate in voltage control mode in the conditions set forth in Article 16(3) (d) point 2) of [the NC RfG];
b | Compliance | the voltage control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the implemented slope and deadband of the static characteristic;
| Compliance | (ii) the accuracy of the regulation;
| Compliance | (iii) the insensitivity of the regulation;
| Compliance | (iv) the time of reactive power activation.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the range of regulation and adjustable the droop and deadband is compliant with agreed or decided characteristic parameters, according to Article 21(3)(d) of [the NC RfG];
| Compliance | (ii) the insensitivity of voltage control is not higher than 0.01 pu, according to Article 21(3) (d) of [the NC RfG];
| Compliance | (iii) following a step change in voltage, 90 % of the change in reactive power output has been achieved within the times and tolerances according to Article 21(3)(d) of [the NC RfG].
5 | Compliance | With regard to the reactive power control mode test:
a | Compliance | the DC-connected power park module shall demonstrate its capability to operate in reactive power control mode, according to the conditions referred to in Article 21(3)(d)(iii) of [the NC RfG];
b | Compliance | the reactive power control mode test shall be complementary to the reactive power capability test;
c | Compliance | the reactive power control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the reactive power setpoint range and step;
| Compliance | (ii) the accuracy of the regulation;
| Compliance | (iii) the time of reactive power activation.
d | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the reactive power setpoint range and step is ensured according to Article 21(3)(d) of [the NC RfG];
| Compliance | (ii) the accuracy of the regulation is compliant with the conditions as referred to in Article 21(3)(d) of [the NC RfG].
6 | Compliance | With regard to the power factor control mode test:
a | Compliance | (a) the DC-connected power park module shall demonstrate its capability to operate in power factor control mode according to the conditions referred to in Article 21(3)(d)(iv) of [the NC RfG];
b | Compliance | the power factor control mode test shall apply concerning the verification of the following parameters:
| Compliance | (i) the power factor setpoint range;
| Compliance | (ii) the accuracy of the regulation;
| Compliance | (iii) the response of reactive power due to step change of active power.
c | Compliance | the test shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the power factor setpoint range and step is ensured according to Article 21(3)(d) of the [NC RfG];
| Compliance | (ii) the time of reactive power activation as result of step active power change does not exceed the requirement according to Article 21(3)(d) of [the NC RfG];
| Compliance | (iii) the accuracy of the regulation is compliant with the value, as referred to in Article 21(3)(d) of [the NC RfG].
7 | Compliance | With regard to the tests identified in paragraphs 4, 5 and 6 the relevant TSO may select only two of the three control options for testing. |  | ü |  |  | ü
8 | Compliance | With regard to LFSM-O response of DC-connected power park module, the tests shall be carried out in accordance with Article 41 (2) of [NC RfG].
9 | Compliance | With regard to LFSM-U response of DC-connected power park module, the tests shall be carried out in accordance with Article 42(3) of [NC RfG].
10 | Compliance | With regard to active power controllability of DC-connected power park module, the tests shall be carried out in accordance with 42(2) of [NC RfG].
11 | Compliance | With regard to FSM response of DC-connected power park module, the tests shall be carried out in accordance with Article 42(4) of [NC RfG].
12 | Compliance | With regard to frequency restoration control of DC-connected power park module, the tests shall be carried out in accordance with Article 42(5) of [NC RfG].
13 | Compliance | With regard to fast signal response of DC-connected power park module, the test shall be deemed passed if the DC-connected power park module can demonstrate its response within the time specified in Article 39(1)a).
14 | Compliance | With regard to tests for DC-connected power park modules where the AC collector system is not at nominal 50 Hz frequency, the relevant system operator, in coordination with the relevant TSO, shall agree with the DC-connected power park module owner the compliance tests required. |  | ü |  |  | ü
Compliance
| Compliance | Chapter 2 - COMPLIANCE SIMULATIONS
Compliance
| Compliance | Article 71 - Compliance simulations for HVDC systems
Compliance
1 | Compliance | Equipment certificates may be used instead of part of the simulations below, on the condition that they are provided to the relevant system operator. |  | ü |  |  | ü
2 | Compliance | With regard to the fast fault current injection simulation:
a | Compliance | the HVDC converter unit owner or the HVDC converter station owner shall simulate fast fault current injection in the conditions set forth in Article 19;
b | Compliance | the simulation is deemed passed, provided that compliance with Article 19 is demonstrated.
3 | Compliance | With regard to the fault-ride-through capability simulation:
a | Compliance | the HVDC system owner shall simulate the capability for fault-ride-through in the conditions set forth in Article 25; and
b | Compliance | the simulation is deemed passed, provided that compliance with the requirement according to Article 25 is demonstrated.
4 | Compliance | With regard to the post fault active power recovery simulation:
a | Compliance | the HVDC system owner shall simulate the capability for post fault active power recovery in the conditions set forth in Article 26;
b | Compliance | the simulation is deemed passed, provided that compliance with the requirements specified in accordance with Article 26 is demonstrated.
5 | Compliance | With regard to the reactive power capability simulation:
a | Compliance | the HVDC converter unit owner or the HVDC converter station owner shall simulate the capability for leading and lagging reactive power capability in the conditions referred to in Article 20(2) to(4);
b | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the simulation model of the HVDC converter unit or the HVDC converter station is validated against the compliance tests for reactive power capability as referred to in Article 69; and
| Compliance | (ii) compliance with the requirements as referred to in Article 20(2) to (4) is demonstrated.
6 | Compliance | With regard to the power oscillations damping control simulation:
a | Compliance | the HVDC system owner shall demonstrate the performance of its control system (POD function) to damp power oscillations in the conditions set forth in Article 30;
b | Compliance | the tuning shall result in improved damping of corresponding active power response of the HVDC system in combination with the POD function compared to the active power response of the HVDC system without POD; and
c | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the POD function damps the existing power oscillations of the HVDC system within a frequency range specified by the relevant TSO. This frequency range shall include the local mode frequency of the HVDC system and the expected network oscillations; and |  | ü |  |  | ü
| Compliance | (ii) a change of active power transfer of the HVDC system as specified by the relevant TSO does not lead to undamped oscillations in active or reactive power of the HVDC system. |  | ü |  |  | ü
7 | Compliance | With regard to the simulation of active power modification in case of disturbance:
a | Compliance | the HVDC system owner shall simulate the capability to quickly modify active power according to Article 9(15)(b); and
b | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC system has demonstrated stable operation when following the pre-specified sequence of active power variation;
| Compliance | (ii) the initial delay of the adjustment of the active power is shorter than the value specified in Article 9(15)(b) or reasonably justified if greater.
8 | Compliance | With regard to the fast active power reversal simulation, as applicable:
a | Compliance | the HVDC system owner shall simulate the capability to quickly reverse active power according to Article 13(16)(c);
b | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the HVDC system has demonstrated stable operation;
| Compliance | (ii) the time of adjustment of the active power is shorter than the value specified in Article 13(16)(c) or reasonably justified if greater
Compliance
Compliance
| Compliance | Article 72 - Compliance simulations for DC-connected power park modules and remote-end HVDC converter units
Compliance
1 | Compliance | DC-connected power park modules are subject to the compliance simulations detailed in this Article. Equipment certificates may be used instead of part of the simulations described below, on the condition that they are provided to the relevant system operator. |  | ü |  |  | ü
2 | Compliance | With regard to the fast fault current injection simulation:
a | Compliance | the DC-connected power park module owner shall simulate the capability for fast fault current injection in the conditions set forth in Article 20(2)(b) of [the NC RfG]; and
b | Compliance | the simulation shall be deemed passed, provided that compliance with the requirement according to Article 20(2) (b) of [the NC RfG] is demonstrated.
3 | Compliance | With regard to the post fault active power recovery simulation:
a | Compliance | the DC-connected power park module owner shall simulate the capability for post fault active power recovery in the conditions set forth in Article 20(3) (a) of the [NC RfG]; and
b | Compliance | the simulation shall be deemed passed, provided that compliance with the requirement according to Article 20(3) (a) of the [NC RfG] is demonstrated.
4 | Compliance | With regard to the reactive power capability simulation of DC-connected power park modules:
a | Compliance | the DC-connected power park module owner shall simulate the capability for leading and lagging reactive power capability in the conditions referred to in Article 40(2); and
b | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the simulation model of the DC-connected power park module is validated against the compliance tests for reactive power capability as referred to in Article 70(2);
| Compliance | (ii) compliance with the requirements as referred to in Article 40(2) is demonstrated.
5 | Compliance | With regard to the reactive power capability simulation of remote-end HVDC converter units:
a | Compliance | the remote-end HVDC converter unit owner or the remote-end HVDC converter station owner shall simulate the capability for leading and lagging reactive power capability in the conditions referred to in Article 48(2); and
b | Compliance | the simulation shall be deemed passed, provided that the following conditions are cumulatively fulfilled:
| Compliance | (i) the simulation model of the remote-end HVDC converter unit or the remote-end HVDC converter station is validated against the compliance tests for reactive power capability at the as referred to in Article 70(3);
| Compliance | (ii) compliance with the requirements as referred to in Article 48(2) is demonstrated.
6 | Compliance | With regard to the power oscillations damping control simulation:
a | Compliance | the DC-connected power park module owner shall simulate the capability for power oscillations damping under the conditions as referred to in Article 21(3)(f) of [the NC RfG]; and
b | Compliance | the simulation shall be deemed passed, provided that the model demonstrates compliance with the conditions of Article 21(3)(f) of [the NC RfG].
7 | Compliance | With regard to fault-ride-through capability simulation:
a | Compliance | the DC-connected power park module owner shall simulate the capability for fault-ride-through under the conditions as referred to in Article 16(3) (a) of the [NC RfG];
b | Compliance | the simulation shall be deemed passed, provided that the model demonstrates compliance with the conditions of Article 16(3) (a) of [the NC RfG].
Chapter 4 - NON-BINDING GUIDANCE AND MONITORING OF IMPLEMENTATION;
Compliance
| Compliance | Article 73 - Non-binding guidance on implementation
Compliance
1 | Compliance | No later than six months after the entry into force of this Regulation, the ENTSO for Electricity shall prepare and thereafter every two years provide non-binding written guidance to its members and other system operators concerning the elements of this Regulation requiring national decisions. The ENTSO for Electricity shall publish this guidance on its website.
2 | Compliance | ENTSO for Electricity shall consult stakeholders when providing non-binding guidance.
3 | Compliance | The non-binding guidance shall explain the technical issues, conditions and interdependencies which need to be considered when complying with the requirements of this Regulation at national level.
Compliance
| Compliance | Article 74 - Monitoring
Compliance
1 | Compliance | ENTSO for Electricity shall monitor the implementation of this Regulation in accordance with Article 8(8) of Regulation (EC) No 714/2009. Monitoring shall cover in particular the following matters:
a | Compliance | identification of any divergences in the national implementation of this Regulation;
b | Compliance | assessment of whether the choice of values and ranges in the requirements applicable to power generating modules under this Regulation continues to be valid.
2 | Compliance | The Agency, in cooperation with ENTSO for Electricity, shall produce by 12 months after the entry into force of this Regulation a list of the relevant information to be communicated by ENTSO for Electricity to the Agency in accordance with Article 8(9) and Article 9(1) of Regulation (EC) No 714/2009. The list of relevant information may be subject to updates. ENTSO for Electricity shall maintain a comprehensive, standardised format, digital data archive of the information required by the Agency.
3 | Compliance | Relevant TSOs shall submit to ENTSO for Electricity the information required to perform the tasks referred to in paragraphs 1 and 2. Based on a request of the regulatory authority, DSOs shall provide TSOs with information under paragraph 2 unless the information is already obtained by regulatory authorities, the Agency or ENTSO-E in relation to their respective implementation monitoring tasks, with the objective of avoiding duplication of information. |  | ü |  |  | ü
4 | Compliance | Where ENTSO for Electricity or the Agency establish areas subject to this Regulation where, based on market developments or experience gathered in the application of this Regulation, further harmonisation of the requirements under this Regulation is advisable to promote market integration, they shall propose draft amendments to this Regulation pursuant to Article 7(1) of Regulation (EC) No 714/2009.
TITLE 7 - DEROGATIONS
Derogations
| Derogations | Article 75
Derogations
1 | Derogations | Regulatory authorities may, at the request of a HVDC system owner or DC-connected power park module owner, or their prospective owner, relevant system operator or relevant TSO, grant HVDC system owners or DC-connected power park module owners, or their prospective owner, relevant system operators or relevant TSOs derogations from one or more provisions of this Regulation for new and existing HVDC system and/or DC-connected power park modules in accordance with Articles 76 to 80.
2 | Derogations | Where applicable in a Member State, derogations may be granted and revoked in accordance with Articles 76 to 79 by other authorities than the regulatory authority.
Derogations
| Derogations | Article 76 - General Provisions
Derogations
1 | Derogations | Each regulatory authority shall specify, after consulting relevant system operators, HVDC system owners and DC-connected power park module owners and other stakeholders whom it deems affected by this Regulation, the criteria for granting derogations pursuant to Articles 77 to 79. It shall publish those criteria on its website and notify them to the Commission within nine months of the entry into force of this Regulation. The Commission may require a regulatory authority to amend the criteria if it considers that they are not in line with this Regulation. This possibility to review and amend the criteria for granting derogations shall not affect the derogations already granted which shall continue to apply until the scheduled expiry date as detailed in the decision granting the exemption. | ü | ü | ü | ü | ü
2 | Derogations | If the regulatory authority deems that it is necessary due to a change in circumstances relating to the evolution of system requirements, it may review and amend at most once every year the criteria for granting derogations in accordance with paragraph 1. Any changes to the criteria shall not apply to derogations for which a request has already been made.
3 | Derogations | The regulatory authority may decide that HVDC systems or DC-connected power park modules for which a request for a derogation has been filed pursuant to Articles 77 to 79 do not need to comply with the requirements of this Regulation from which a derogation has been sought from the day of filing the request until the regulatory authority’s decision is issued.
Derogations
| Derogations | Article 77 - Request for derogations by an HVDC system owner, DC-connected power park module owner
Derogations
1 | Derogations | HVDC system owners and DC-connected power park module owners, or their prospective owner, may request a derogation to one or several requirements of this Regulation.
2 | Derogations | A request for a derogation shall be filed with the relevant system operator and include: |  | ü |  |  | ü
a | Derogations | an identification of the HVDC system owner or DC-connected power park module owner, or their prospective owner, and a contact person for any communications;
b | Derogations | a description of the HVDC system or DC-connected power park module for which a derogation is requested;
c | Derogations | a reference to the provisions of this Regulation from which a derogation is requested and a detailed description of the requested derogation;
d | Derogations | detailed reasoning, with relevant supporting documents, and cost-benefit analysis pursuant to the requirements of Article 66;
e | Derogations | demonstration that the requested derogation would have no adverse effect on cross-border trade;
f | Derogations | in the case of a DC-connected power park module connected to one or more remote-end HVDC converter stations, evidence that the converter station will not be affected by the derogation or, alternatively, agreement from the converter station owner to the proposed derogation.
3 | Derogations | Within two weeks of receipt of a request for a derogation, the relevant system operator shall confirm to the HVDC system owner or DC-connected power park module owner, or their prospective owner, whether the request is complete. If the relevant system operator considers that the request is incomplete, the HVDC system owner or DC-connected power park module owner, or their prospective owner, shall submit the additional required information within one month from the receipt of the request for additional information. If the HVDC system owner or DC-connected power park module owner, or their prospective owner, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn. |  | ü |  |  | ü
4 | Derogations | The relevant system operator shall, in coordination with the relevant TSO and any affected adjacent DSO or DSOs, assess the request for a derogation and the provided cost-benefit analysis, taking into account the criteria determined by the regulatory authority pursuant to Article 76. |  | ü |  |  | ü
5 | Derogations | If a request for a derogation concerns a HVDC system or DC-connected power park module connected to a distribution system, including a closed distribution system, the relevant system operator’s assessment must be accompanied by an assessment of the request for a derogation by the relevant TSO. The relevant TSO shall provide its assessment within two months of being requested to do so by the relevant system operator. |  | ü |  |  | ü
6 | Derogations | Within six months of receipt of a request for a derogation, the relevant system operator shall forward the request to the regulatory authority and submit the assessment(s) prepared in accordance with paragraphs 4 and 5. That period may be extended by one month where the relevant system operator seeks further information from the HVDC system owner or DC-connected power park module owner, or their prospective owner, and by two months where the relevant system operator requests the relevant TSO to submit an assessment of the request for a derogation. |  | ü |  |  | ü
7 | Derogations | The regulatory authority shall adopt a decision concerning any request for a derogation within six months from the day after it receives the request. That time limit may be extended by three months before its expiry where the regulatory authority requires further information from the HVDC system owner or DC-connected power park module owner, or their prospective owner, or from any other interested parties. The additional period shall begin when the complete information has been received.
8 | Derogations | The HVDC system owner or DC-connected power park module owner, or their prospective owner, shall submit any additional information requested by the regulatory authority within two months of such request. If the HVDC system owner or DC-connected power park module owner, or the prospective owner, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn unless, before its expiry:
a | Derogations | the regulatory authority decides to provide an extension; or
b | Derogations | the HVDC system owner or DC-connected power park module owner, or their prospective owner, informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete.
9 | Derogations | The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants a derogation, it shall specify its duration.
10 |  | The regulatory authority shall notify its decision to the HVDC system owner or DC-connected power park module owner, or their prospective owner, the relevant system operator and the relevant TSO.
11 | Derogations | A regulatory authority may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply or upon a reasoned recommendation of the Commission or reasoned recommendation by the Agency pursuant to Article 81(2).
Derogations
| Derogations | Article 78 - Request for a derogation by a relevant system operator or relevant TSO
Derogations
1 | Derogations | Relevant system operators or relevant TSOs may request a derogation for classes of HVDC systems or DC-connected power park modules connected or to be connected to their network. | ü | ü | ü | ü | ü
2 | Derogations | Relevant system operators or relevant TSOs shall submit their requests for a derogation to the regulatory authority. Each request for a derogation shall include: | ü | ü | ü | ü | ü
a | Derogations | identification of the relevant system operator or relevant TSO, and a contact person for any communications | ü | ü | ü | ü | ü
b | Derogations | a description of the HVDC systems or DC-connected power park modules for which a derogation is requested and the total installed capacity and number of HVDC systems or DC-connected power park modules;
c | Derogations | the requirement or requirements of this Regulation for which a derogation is requested, with a detailed description of the requested derogation;
d | Derogations | detailed reasoning, with all relevant supporting documents;
e | Derogations | demonstration that the requested derogation would have no adverse effect on cross-border trade;
f | Derogations | a cost-benefit analysis pursuant to the requirements of Article 66. If applicable, the cost-benefit analysis shall be carried out in coordination with the relevant TSO and any adjacent DSOs. |  | ü |  |  | ü
3 | Derogations | Where the request for a derogation is submitted by a relevant DSO or CDSO, the regulatory authority shall, within two weeks from the day after receipt of that request, ask the relevant TSO to assess the request for a derogation in the light of the criteria determined by the regulatory authority pursuant to Article 76. |  | ü |  |  | ü
4 | Derogations | Within two weeks from the day after the receipt of such request for assessment, the relevant TSO shall confirm to the relevant DSO or CDSO whether the request for a derogation is complete. If the relevant TSO considers that it is incomplete, the relevant DSO or CDSO shall submit the required additional information within one month from the receipt of the request for additional information. |  | ü |  |  | ü
5 | Derogations | Within six months of receipt of a request for a derogation, the relevant TSO shall submit to the regulatory authority its assessment, including any relevant documentation. The six-month time limit may be extended by one month where the relevant TSO seeks further information from the relevant DSO or from the relevant CDSO. |  | ü |  |  | ü
6 | Derogations | The regulatory authority shall adopt a decision concerning a request for a derogation within six months from the day after it receives the request. Where the request for a derogation is submitted by the relevant DSO or CDSO, the six-month time limit runs from the day following receipt of the relevant TSO’s assessment pursuant to paragraph 5. |  | ü |  |  | ü
7 | Derogations | The six-month time limit referred to in paragraph 6 may, before its expiry, be extended by an additional three months where the regulatory authority requests further information from the relevant system operator requesting the derogation or from any other interested parties. That additional period shall run from the day following the date of receipt of the complete information. The relevant system operator shall provide any additional information requested by the regulatory authority within two months from the date of the request. If the relevant system operator does not provide the requested additional information within that time limit, the request for a derogation shall be deemed withdrawn unless, before expiry of the time limit: | ü | ü | ü | ü | ü
a | Derogations | the regulatory authority decides to provide an extension; or
b | Derogations | the relevant system operator informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete. | ü | ü | ü | ü | ü
8 | Derogations | The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants a derogation, it shall specify its duration.
9 | Derogations | The regulatory authority shall notify its decision to the relevant system operator requesting the derogation, the relevant TSO and the Agency.
10 | Derogations | Regulatory authorities may lay down further requirements concerning the preparation of requests for derogations by relevant system operators. In doing so, regulatory authorities shall take into account the delineation between the transmission system and the distribution system at the national level and shall consult with system operators, HVDC system owners, DC-connected power park module owners and stakeholders, including manufacturers.
11 | Derogations | A regulatory authority or, where applicable, the Member State may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply.
Derogations
| Derogations | Article 79 - Request for derogations from the provisions of Title III by a DC-connected power park module owner
Derogations
1 | Derogations | A request for a derogation to the provisions of Articles 40(1)(b) and (c), 40(2)(a) and (b), and 41 to 45 shall not be subject to Article 77(2)(d) to (e) where it relates to a DC-connected power park module that has, or will have, a single connection to a single synchronous area.
2 | Derogations | The regulatory authority may attach any conditions to a decision concerning request for a derogation referred to in paragraph 1. This may include a condition that the development of the connection into a multi-terminal network, or that connection of a further power park module at the same point, will cause the derogation to be evaluated by the regulatory authority or to expire. The regulatory authority shall take into account the need to optimise the configuration between the DC-connected power park module and the remote-end HVDC converter station, as well as the legitimate expectations of the DC-connected power park module owner when adopting a decision concerning a request for a derogation.
Derogations
| Derogations | Article 80 - Register of derogations from the requirements of this regulation
Derogations
1 | Derogations | Regulatory authorities shall maintain a register of all derogations they have granted or refused and shall provide the Agency with an updated and consolidated register at least once every six months, a copy of which shall be given to ENTSO for Electricity.
2 | Derogations | The register shall contain in particular:
a | Derogations | the requirement or requirements for which the derogation is granted or refused;
b | Derogations | the content of the derogation;
c | Derogations | the reasons for granting or refusing the derogation;
d | Derogations | the consequences resulting from granting the derogation.
Derogations
| Derogations | Article 81 -Monitoring of derogations
Derogations
1 | Derogations | The Agency shall monitor the procedure of granting derogations with the cooperation of the regulatory authorities or relevant authorities of the Member State. Those authorities or relevant authorities of the Member State shall provide the Agency with all the information necessary for that purpose.
2 | Derogations | The Agency may issue a reasoned recommendation to a regulatory authority to revoke a derogation due to a lack of justification. The Commission may issue a reasoned recommendation to a regulatory authority or relevant authority of the Member State to revoke a derogation due to a lack of justification.
3 | Derogations | The Commission may request the Agency to report on the application of paragraphs 1 and 2 and to provide reasons for requesting or not requesting derogations to be revoked.
| Final Provisions | TITLE 8 - FINAL PROVISIONS
Final Provisions
| Final Provisions | Article 82 - Amendment of contracts and general terms and conditions
Final Provisions
1 | Final Provisions | Regulatory authorities shall ensure that all relevant clauses in contracts and general terms and conditions relating to the grid connection of new HVDC systems or new DC-connected power park modules are brought into compliance with the requirements of this Regulation.
2 | Final Provisions | All relevant clauses in contracts and relevant clauses of general terms and conditions relating to the grid connection of existing HVDC systems or existing DC-connected power park modules subject to all or some of the requirements of this Regulation in accordance with paragraph 1 of Article 4 shall be amended in order to comply with the requirements of this Regulation. The relevant clauses shall be amended within three years following the decision of the regulatory authority or Member State as referred to in Article 4(1).
3 | Final Provisions | Regulatory authorities shall ensure that national agreements between system operators and owners of new or existing HVDC systems and DC-connected power park modules subject to this Regulation and relating to grid connection requirements for HVDC systems and DC-connected power park modules, in particular in national network codes, reflect the requirements set out in this Regulation.
Final Provisions
| Final Provisions | Article 83 - HVDC System or DC-connected power park modules connecting with synchronous areas or control areas not bound by EU legislation
Final Provisions
1 | Final Provisions | Where an HVDC system to which the requirements of this Regulation apply is connecting synchronous areas or control areas, with at least one synchronous area or one control area not falling under the scope of application of Union legislation, the relevant TSO or, where applicable, the HVDC system owner shall endeavour to implement an agreement to ensure that the owners of HVDC systems with no legal obligation to comply with this Regulation also cooperate to fulfil the requirements. |  | ü |  |  | ü
2 | Final Provisions | If an agreement as referred to in paragraph 1 cannot be implemented, the relevant TSO or, as the case may be, the HVDC system owner concerned shall use all available means to comply with the requirements of this Regulation. |  | ü |  |  | ü
Final Provisions
| Final Provisions | Article 84 -Entry into force
Final Provisions
| Final Provisions | This Regulation shall enter into force on the twentieth day following that of its publication in the Official Journal of the European Union.
| Final Provisions | Without prejudice to Articles 4(2)(b), 5, 73, 74, and 76 the requirements of this Regulation shall apply from three years after publication. This Regulation shall be binding in its entirety and directly applicable in all Member States.

## HVDC - Annex's
|  |  | Opbligation on |  |  |  | Multiple TSO Clause
|  |  | TO | SO | IC | OFTO
ANNEX I - Frequency ranges referred to in Article 11
Frequency range | Time period for operation
47.0 Hz – 47.5 Hz | 60 seconds
47.5 Hz – 48.5 Hz | To be specified by each relevant TSO , but longer than established times for generation and demand according to [NC RfG] and [DCC] respectively, and longer than for DC-connected PPMs according to Article 39 |  |  | ü |  |  | ü
48.5 Hz – 49.0 Hz | To be specified by each relevant TSO, but longer than established times for generation and demand according to [NC RfG] and [DCC] respectively, and longer than for DC-connected PPMs according to Article 39 |  |  | ü |  |  | ü
49.0 Hz – 51.0 Hz | Unlimited
51.0 Hz – 51.5 Hz | To be specified by each relevant TSO, but longer than established times for generation and demand according to [NC RfG] and [DCC] respectively, and longer than for DC-connected PPMs according to Article 39 |  |  | ü |  |  | ü
51.5 Hz – 52.0 Hz | To be specified by each relevant TSO , but longer than for DC-connected PPMs according to Article 39 |  |  | ü |  |  | ü
Table 1: Minimum time periods an HVDC system shall be able to operate for different frequencies deviating from a nominal value without disconnecting from the network.
ANNEX II
Requirements applying to frequency sensitive mode, limited frequency sensitive mode overfrequency and limited frequency sensitive mode underfrequency
A. Frequency sensitive mode
1. When operating in frequency sensitive mode (FSM):
(a) the HVDC system shall be capable of responding to frequency deviations in each connected AC network by adjusting the active power transmission as indicated in Figure 1 and in accordance with the parameters specified by each TSO within the ranges shown in Table 2. This specification shall be subject to notification to the regulatory authority. The modalities of that notification shall be determined in accordance with the applicable national regulatory framework; |  |  |  | ü |  |  | ü
(b) the adjustment of active power frequency response shall be limited by the minimum HVDC active power transmission capacity and maximum HVDC active power transmission capacity of the HVDC system (in each direction);
Figure 1
Figure 1: Active power frequency response capability of an HVDC system in FSM illustrating the case of zero deadband and insensitivity with a positive active power setpoint (import mode). DP is the change in active power output from the HVDC system. fn is the target frequency in the AC network where the FSM service is provided and Df is the frequency deviation in the AC network where the FSM service is provided.
Table 2: Parameters for active power frequency response in FSM
Parameters | Ranges
Frequency response deadband | 0 – ±500mHz
Droop s1 (upward regulation) | Minimum 0.1%
Droop s2 (downward regulation) | Minimum 0.1%
Frequency response insensitivity | Maximum 30 mHz
(c) the HVDC system shall be capable, following an instruction from the relevant TSO, of adjusting the droops for upward and downward regulation, the frequency response deadband and the operational range of variation within the active power range available for FSM, set out in Figure 1 and more generally within the limits set by points (a) and (b). These values shall be subject to notification to the regulatory authority. The modalities of that notification shall be determined in accordance with the applicable national regulatory framework; |  |  |  | ü |  |  | ü
(d) as a result of a frequency step change, the HVDC system shall be capable of adjusting active power to the active power frequency response defined in Figure 1, in such a way that the response is:
(i) as fast as inherently technically feasible; and
(ii) at or above the solid line according to Figure 2 in accordance with the parameters specified by each relevant TSO within the ranges according to Table 3: |  |  |  | ü |  |  | ü
-the HVDC system shall be able to adjust active power output DP up to the limit of the active power range requested by the relevant TSO in accordance with the times t1 and t2 according to the ranges in Table 3, where t1 is the initial delay and t2 is the time for full activation. The values of t1and t2 shall be specified by the relevant TSO, subject to notification to the regulatory authority. The modalities of that notification shall be determined in accordance with the applicable national regulatory framework. |  |  |  | ü |  |  | ü
- if the initial delay of activation is greater than 0.5 second, the HVDC system owner shall reasonably justify it to the relevant TSO. |  |  |  | ü |  |  | ü
Figure 2
Figure 2: Active power frequency response capability of an HVDC system. DP is the change in active power triggered by the step change in frequency.
Table 3: Parameters for full activation of active power frequency response resulting from frequency step change.
Parameters | Time
Maximum admissible initial delay | 0.5 seconds
Maximum admissible time for full activation | 30 seconds
, unless longer activation times are specified by the relevant TSO |  |  |  | ü |  |  | ü
(i) for HVDC systems linking various control areas or synchronous areas, in frequency sensitive mode operation the HVDC system shall be capable of adjusting full active power frequency response at any time and for a continuous time period.
(ii) as long as a frequency deviation continues active power control shall not have any adverse impact on the active power frequency response.
B. Limited frequency sensitive mode overfrequency
2. In addition to the requirements of Article 11 the following shall apply with regard to limited frequency sensitive mode – overfrequency (LFSM-O):
(a) the HVDC system shall be capable of adjusting active power frequency response to the AC network or networks, during both import and export, according to Figure 3 at a frequency threshold f1 between and including 50.2 Hz and 50.5 Hz with a droop S3 adjustable from 0.1 % upwards;
(b) the HVDC system shall be capable of adjusting active power down to its minimum HVDC active power transmission capacity;
(c) the HVDC system shall be capable of adjusting active power frequency response as fast as inherently technically feasible, with an initial delay and time for full activation determined by the relevant TSO and notified to the regulatory authority in accordance with the applicable national regulatory framework; |  |  |  | ü |  |  | ü
(d) the HVDC system shall be capable of stable operation during LFSM-O operation. When LFSM-O is active, hierarchy of control functions shall be organised in accordance with Article 35.
3. The frequency threshold and droop settings referred to in point (a) of paragraph 1 shall be determined by the relevant TSO and be notified to the regulatory authority in accordance with the applicable national regulatory framework. |  |  |  | ü |  |  | ü
Figure 3
Figure 3: Active power frequency response capability of HVDC systems in LFSM-O. DP is the change in active power output from the HVDC system and, depending on the operational conditions, either a decrease of import power or an increase of export power. fn is the nominal frequency of the AC network or networks the HVDC system is connected to and Df is the frequency change in the AC network or networks the HVDC is connected to. At overfrequencies where f is above f1 the HVDC system shall reduce active power according to the droop setting.
C. Limited frequency sensitive mode underfrequency
4. In addition to the requirements of Article 11, the following shall apply with regard to limited frequency sensitive mode – underfrequency (LFSM-U):
(a) the HVDC system shall be capable of adjusting active power frequency response to the AC network or networks, during both import and export, according to Figure 4 at a frequency threshold f2 between and including 49.8 Hz and 49.5 Hz with a droop S4 adjustable from 0.1 % upwards.
(b) in the LFSM-U mode the HVDC system shall be capable of adjusting active power up to its maximum HVDC active power transmission capacity;
(c) the active power frequency response shall be activated as fast as inherently technically feasible, with an initial delay and time for full activation determined by the relevant TSO and notified to regulatory authority in accordance with the applicable national regulatory framework; |  |  |  | ü |  |  | ü
(d) the HVDC system shall be capable of stable operation during LFSM-U operation. When LFSM-U is active, hierarchy of control functions shall be organised in accordance with Article 35.
5. The frequency threshold and droop settings referred to in point (a) of paragraph 1 shall be determined by the relevant TSO and be notified to the regulatory authority in accordance with the applicable national regulatory framework. |  |  |  | ü |  |  | ü
Figure 4
Figure 4: Active power frequency response capability of HVDC systems in LFSM-U. DP is the change in active power output from the HVDC system, depending on the operation condition a decrease of import power or an increase of export power. fn is the nominal frequency in the AC network or networks the HVDC system is connected and Df is the frequency change in the AC network or networks the HVDC is connected. At underfrequencies where f is below f2, the HVDC system has to increase active power output according to the droop s4.
ANNEX III
Voltage ranges referred to in Article 18
Table 4: Minimum time periods an HVDC system shall be capable of operating for voltages deviating from the reference 1 pu value at the connection points without disconnecting from the network. This table applies in case of pu voltage base values at or above 110 kV and up to 300 kV.
Synchronous Area | Voltage Range | Time period for operation
Continental Europe | 0.85 pu – 1.118 pu | Unlimited
| 1.118 pu – 1.15 pu | To be established by each relevant system operator, in coordination with the relevant TSO but not less than 20 minutes
Nordic | 0.90 pu – 1.05 pu | Unlimited
| 1.05 pu – 1.10 pu | 60 minutes
Great Britain | 0.90 pu – 1.10 pu | Unlimited
Ireland and Northern Ireland | 0.90 pu – 1.118 pu | Unlimited
Baltic | 0.85 pu – 1.118 pu | Unlimited
| 1.118 pu – 1.15 pu | 20 minutes
Table 5: Minimum time periods an HVDC system shall be capable of operating for voltages deviating from the reference 1 pu value at the connection points without disconnecting from the network. This table applies in case of pu voltage base values from 300 kV to 400 kV (included).
Synchronous Area | Voltage Range | Time period for operation
Continental Europe | 0.85 pu – 1.05 pu | Unlimited
| 1.05 pu – 1.0875 pu | To be specified by each TSO, but not less than 60 minutes
| 1.0875 pu – 1.10 pu | 60 minutes
Nordic | 0.90 pu – 1.05 pu | Unlimited
| 1.05 pu – 1.10 pu | To be specified by each TSO, but not less than 60 minutes
Great Britain | 0.90 pu – 1.05 pu | Unlimited
| 1.05 pu – 1.10 pu | 15 minutes
Ireland and Northern Island | 0.90 pu – 1.05 pu | Unlimited
Baltic | 0.88 pu – 1.097 pu | Unlimited
| 1.097 pu – 1.15 pu | 20 minutes
ANNEX IV
Requirements for U-Q/Pmax-profile (referred to in Article 20)
Figure 5
Figure 5: The diagram represents boundaries of a U-Q/Pmax-profile with U being the voltage at the connection points expressed by the ratio of its actual value to its reference 1 pu value in per unit, and Q/Pmax the ratio of the reactive power to the maximum HVDC active power transmission capacity. The position, size and shape of the inner envelope are indicative and shapes other than rectangular may be used within the inner envelope. For profile shapes other than rectangular, the voltage range represents the highest and lowest voltage points in this shape. Such a profile would not give rise to the full reactive power range being available across the range of steady-state voltages.
Table 6: Parameters for the Inner Envelope in the Figure.
Synchronous Area | Maximum range of Q/Pmax | Maximum range of steady-state Voltage level in PU
Continental Europe | 0.95 | 0.225
Nordic | 0.95 | 0.15
Great Britain | 0.95 | 0.225
Ireland and Northern Ireland | 1.08 | 0.218
Baltic States | 1 | 0.22
ANNEX V
Voltage-against-time-profile referred to in Article 25
Figure 6: Fault-ride-through profile of an HVDC converter station. The diagram represents the lower limit of a voltage-against-time profile at the connection point, expressed by the ratio of its actual value and its reference 1 pu value in per unit before, during and after a fault. URET is the retained voltage at the connection point during a fault, TCLEAR is the instant when the fault has been cleared, UREC1 and tREC1 specify a point of lower limits of voltage recovery following fault clearance. Ublock is the blocking voltage at the connection point. The time values referred to are measured from TFAULT.
Table 7: Parameters for Figure 6 for the fault-ride-through capability of an HVDC converter station.
Voltage parameters [pu] | Time parameters [seconds] | Time parameters [seconds]
URET - 0.00 – 0.30 | tCLEAR - 0.14-0.25 | tCLEAR
UREC1 - 0.25-0.85 | tREC1 - 1.5 – 2.5 | tREC1
UREC2 - 0.85-0.90 | tREC2 - tREC1 – 10.0 | tREC2
ANNEX VI
Frequency ranges and time periods referred to in Article 39(2)(a)
Frequency range | Time period for operation
47.0 Hz – 47.5 Hz | 20 seconds
47.5Hz – 49.0 Hz | 90 minutes
49.0 Hz – 51.0 Hz | Unlimited
51.0 Hz – 51.5 Hz | 90 minutes
51.5 Hz – 52.0 Hz | 15 minutes
Table 8: Minimum time periods for the 50Hz nominal system for which a PPM shall be capable of operating for different frequencies deviating from a nominal value without disconnecting from the network.
ANNEX VII
Voltage Range | Time period for operation
0.85 pu – 0.90 pu | 60 minutes
0.90 pu – 1.10 pu | Unlimited
1.10 pu – 1.118 pu | Unlimited, unless specified otherwise by the relevant system operator, in coordination with the relevant TSO. |  |  | ü |  |  | ü
1.118 pu – 1.15 pu | To be specified by the relevant system operator, in coordination with the relevant TSO. |  |  | ü |  |  | ü
Table 9: Minimum time periods for which a DC-connected power park module shall be capable of operating for different voltages deviating from a reference 1 pu value without disconnecting from the network where the voltage base for pu values is from 110 kV to 300 kV.
Voltage Range | Time period for operation
0.85 pu – 0.90 pu | 60 minutes
0.90 pu – 1.05 pu | Unlimited
1.05 pu – 1.15 pu | To be specified by the relevant system operator, in coordination with the relevant TSO. Various sub-ranges of voltage withstand capability can be specified. |  |  | ü |  |  | ü
Table 10: Minimum time periods for which a DC-connected power park module shall be capable of operating for different voltages deviating from a reference 1 pu value without disconnecting from the network where the voltage base for pu values is from 300 kV to 400 kV (included).
Figure 7: U-Q/Pmax-profile of a DC-connected power park module at the connection point. The diagram represents boundaries of a U-Q/Pmax-profile of the voltage at the connection point[s], expressed by the ratio of its actual value to its reference 1 pu value in per unit, against the ratio of the reactive power (Q) to the maximum capacity (Pmax).The position, size and shape of the inner envelope are indicative and other than rectangular may be used within the inner envelope. For profile shapes other than rectangular, the voltage range represents the highest and lowest voltage points. Such a profile would not give rise to the full reactive power range being available across the range of steady-state voltages.
Range of width of Q/Pmax profile | Range of steady-state Voltage level in pu
0 - 0.95 | 0.1 - 0.225
Table 11: Maximum and minimum range of both Q/Pmax and steady-state voltage for a DC-connected PPM
ANNEX VIII
Reactive power and voltage requirements referred to in Article 48
Voltage range | Time period for operation
0.85 pu – 0.90 pu | 60 minutes
0.90 pu – 1.10 pu | Unlimited
1.10 pu – 1.12 pu | Unlimited, unless specified otherwise by the relevant system operator, in coordination with the relevant TSO. |  |  | ü |  |  | ü
1.12 pu – 1.15 pu | To be specified by the relevant system operator, in coordination with the relevant TSO. |  |  | ü |  |  | ü
Table 12: Minimum time periods for which a remote-end HVDC converter station shall be capable of operating for different voltages deviating from a reference 1 pu value without disconnecting from the network where the voltage base for pu values is from 110 kV to 300 kV.
Voltage range | Time period for operation
0.85 pu – 0.90 pu | 60 minutes
0.90 pu – 1.05 pu | Unlimited
1.05 pu – 1.15 pu | To be specified by the relevant system operator, in coordination with the relevant TSO. Various sub-ranges of voltage withstand capability may be specified. |  |  | ü |  |  | ü
Table 13: Minimum time periods for which a remote-end HVDC converter station shall be capable of operating for different voltages deviating from a reference 1 pu value without disconnecting from the network where the voltage base for pu values is from 300 kV to 400 kV (included).
Maximum range of Q/Pmax | Maximum range of steady-state voltage level in PU
0.95 | 0.225
Table 14: Maximum range of both Q/Pmax and steady-state voltage for a remote-end HVDC converter station.

## Requirements for Generators
RfG TEXT | Obligation on |  |  |  | Multiple TSO Clause
| TO | SO | IC | OFTO
[Recitals hidden below]
Having regard to the Treaty on the Functioning of the European Union,
Whereas:
(1) The swift completion of a fully functioning and interconnected internal energy market is crucial to maintaining security of energy supply, increasing competitiveness and ensuring that all consumers can purchase energy at affordable prices.
(2) Regulation (EC) No 714/2009 sets out non-discriminatory rules governing access to the network for cross-border exchanges in electricity with a view to ensuring the proper functioning of the internal market in electricity. In addition Article 5 of Directive 2009/72/EC of the European Parliament and of the Council[2] requires that Member States or, where Member States have so provided, regulatory authorities ensure, inter alia, that objective and non-discriminatory technical rules are developed which establish minimum technical design and operational requirements for the connection to the system. Where requirements constitute terms and conditions for connection to national networks, Article 37(6) of the same Directive requires regulatory authorities to be responsible for fixing or approving at least the methodologies used to calculate or establish them. In order to provide system security within the interconnected transmission system, it is essential to establish a common understanding of the requirements applicable to power generating modules. Those requirements that contribute to maintaining, preserving and restoring system security in order to facilitate proper functioning of the internal electricity market within and between synchronous areas, and to achieve cost efficiencies, should be regarded as cross-border network issues and market integration issues.
(3) Harmonised rules for grid connection for power generating modules should be set out in order to provide a clear legal framework for grid connections, facilitate Union-wide trade in electricity, ensure system security, facilitate the integration of renewable electricity sources, increase competition and allow more efficient use of the network and resources, for the benefit of consumers.
(4) System security depends partly on the technical capabilities of power generating modules. Therefore regular coordination at the level of the transmission and distribution networks and adequate performance of the equipment connected to the transmission and distribution networks with sufficient robustness to cope with disturbances and to help to prevent any major disruption or to facilitate restoration of the system after a collapse are fundamental prerequisites.
(5) Secure system operation is only possible if there is close cooperation between power generating facility owners and system operators. In particular, the functioning of the system under abnormal operating conditions depends on the response of power generating modules to deviations from the reference 1 per unit (pu)values of voltage and nominal frequency. In the context of system security, the networks and the power generating modules should be considered as one entity from a system engineering point of view, given that those parts are interdependent. Therefore, as a prerequisite for grid connection, relevant technical requirements should be set for power generating modules.
(6) Regulatory authorities should consider the reasonable costs effectively incurred by system operators in the implementation of this Regulation when fixing or approving transmission or distribution tariffs or their methodologies or when approving the terms and conditions for connection and access to national networks in accordance with Article 37(1) and (6) of Directive 2009/72/EC and with Article 14 of Regulation (EC) No 714/2009.
(7) Different synchronous electricity systems in the Union have different characteristics which need to be taken into account when setting the requirements for generators. It is therefore appropriate to consider regional specificities when establishing network connection rules as required by Article 8(6) of Regulation (EC) No 714/2009.
(8) In view of the need to provide regulatory certainty, the requirements of this Regulation should apply to new generating facilities but should not apply to existing generating modules and generating modules already at an advanced stage of planning but not yet completed unless the relevant regulatory authority or Member State decides otherwise based on evolution of system requirements and a full cost-benefit analysis, or where there has been substantial modernisation of those generating facilities.
(9) The significance of power generating modules should be based on their size and their effect on the overall system. Synchronous machines should be classed on the machine size and include all the components of a generating facility that normally run indivisibly, such as separate alternators driven by the separate gas and steam turbines of a single combined cycle gas turbine installation. For a facility including several such combined cycle gas turbine installations, each should be assessed on its size, and not on the whole capacity of the facility. Non-synchronously connected power generating units, where they are collected together to form an economic unit and where they have a single connection point should be assessed on their aggregated capacity.
(10) In view of the different voltage level at which generators are connected and their maximum generating capacity, this Regulation should make a distinction between different types of generators by establishing different levels of requirements. This Regulation does not set the rules to determine the voltage level of the connection point to which the power generating module shall be connected.
(11) The requirements applicable to type A power generating modules should be set at the basic level necessary to ensure capabilities of generation with limited automated response and minimal system operator control. They should ensure that there is no large-scale loss of generation over system operational ranges, thereby minimising critical events, and include requirements necessary for widespread intervention during system-critical events.
(12) The requirements applicable to type B power generating modules should provide for a wider range of automated dynamic response with greater resilience to operational events, in order to ensure the use of this dynamic response, and a higher level of system operator control and information to utilise those capabilities. They ensure an automated response to mitigate the impact of, and maximise dynamic generation response to, system events.
(13) The requirements applicable to type C power generating modules should provide for a refined, stable and highly controllable real-time dynamic response aiming to provide principle ancillary services to ensure security of supply. Those requirements should cover all system states with consequential detailed specification of interactions of requirements, functions, control and information to utilise those capabilities and ensure the real time system response necessary to avoid, manage and respond to system events. Those requirements should also provide for sufficient capability of generating modules to respond to both intact and system disturbed situations, and should provide the information and control necessary to utilise generation in different situations.
(14) The requirements applicable to type D power generating modules should be specific to higher voltage connected generation with an impact on control and operation of the entire system. They should ensure stable operation of the interconnected system, allowing the use of ancillary services from generation Europe-wide.
(15) The requirements should be based on the principles of non-discrimination and transparency as well as on the principle of optimisation between the highest overall efficiency and lowest total cost for all involved parties. Therefore those requirements should reflect the differences in the treatment of generation technologies with different inherent characteristics, and avoid unnecessary investments in some geographical areas in order to take into account their respective regional specificities. Transmission system operators ('TSOs') and distribution system operators ('DSOs') including closed distribution system operators ('CDSOs') can take those differences into account when defining the requirements in accordance with the provisions of this Regulation, whilst recognising that the thresholds which determine whether a system is a transmission system or a distribution system are established at the national level.
(16) Due to its cross-border impact, this Regulation should aim at the same frequency-related requirements for all voltage levels, at least within a synchronous area. That is necessary because, within a synchronous area, a change in frequency in one Member State would immediately impact frequency and could damage equipment in all other Member States.
(17) To ensure system security, it should be possible for power generating modules in each synchronous area of the interconnected system to remain connected to the system for specified frequency and voltage ranges.
(18) This Regulation should provide for ranges of parameters for national choices for fault-ride-through capability to maintain a proportionate approach reflecting varying system needs such as the level of renewable energy sources ('RES') and existing network protection schemes, both transmission and distribution. In view of the configuration of some networks, the upper limit for fault-ride-through requirements should be 250 milliseconds. However, given that the most common fault clearing time in Europe is currently 150 milliseconds it leaves scope for the entity, as designated by the Member State to approve the requirements of this Regulation, to verify that a longer requirement is necessary before approving it.
(19) When defining the pre-fault and post-fault conditions for the fault-ride-through capability, taking into account system characteristics such as network topology and generation mix, the relevant TSO should decide whether priority is given to pre-fault operating conditions of power generating modules or to longer fault clearance times.
(20) Ensuring appropriate reconnection after an incidental disconnection due to a network disturbance is important to the functioning of the interconnected system. Proper network protection is essential for maintaining system stability and security, particularly in case of disturbances to the system. Protection schemes can prevent aggravation of disturbances and limit their consequences.
(21) Adequate information exchange between system operators and power generating facility owners is a prerequisite for enabling system operators to maintain system stability and security. System operators need to have a continuous overview of the state of the system, which includes information on the operating conditions of power generating modules, as well as the possibility to communicate with them in order to direct operational instructions.
(22) In emergency situations which could endanger system stability and security, system operators should have the possibility to instruct that the output of power generating modules be adjusted in a way which allows system operators to meet their responsibilities for system security.
(23) Voltage ranges should be coordinated between interconnected systems because they are crucial to secure planning and operation of a power system within a synchronous area. Disconnections because of voltage disturbances have an impact on neighbouring systems. Failure to specify voltage ranges could lead to widespread uncertainty in planning and operation of the system with respect to operation beyond normal operating conditions.
(24) The reactive power capability needs depend on several factors including the degree of network meshing and the ratio of in-feed and consumption, which should be taken into account when establishing reactive power requirements. When regional system characteristics vary within a systems operator's area of responsibility, more than one profile could be appropriate. Reactive power production, known as lagging, at high voltages and reactive power consumption, known as leading, at low voltages might not be necessary. Reactive power requirements could put constraints on the design and operation of power generating facilities. Therefore it is important that the capabilities actually required for efficient system operation be thoroughly assessed.
(25) Synchronous power generating modules have an inherent capability to resist or slow down frequency deviations, a characteristic which many RES technologies do not have. Therefore countermeasures should be adopted, to avoid a larger rate of change of frequency during high RES production. Synthetic inertia could facilitate further expansion of RES, which do not naturally contribute to inertia.
(26) Appropriate and proportionate compliance testing should be introduced so that system operators can ensure operational security.
(27) The regulatory authorities, Member States and system operators should ensure that, in the process of developing and approving the requirements for network connection, they are harmonised to the extent possible, in order to ensure full market integration. Established technical standards should be taken into particular consideration in the development of connection requirements.
(28) A process for derogating from the rules should be set out in this Regulation to take into account local circumstances where exceptionally, for example, compliance with those rules could jeopardise the stability of the local network or where the safe operation of a power generating module might require operating conditions that are not in line with the Regulation. In the case of particular combined heat and power plants, which bring wider efficiency benefits, applying the rules set out in this Regulation could result in disproportionate costs and lead to the loss of those efficiency benefits.
(29) Subject to approval by the relevant regulatory authority, or other authority where applicable in a Member State, system operators should be allowed to propose derogations for certain classes of power generating modules.
(30) This Regulation has been adopted on the basis of Regulation (EC) No 714/2009 which it supplements and of which it forms an integral part. References to Regulation (EC) No 714/2009 in other legal acts should be understood as also referring to this Regulation.
(31) The measures provided for in this Regulation are in accordance with the opinion of the Committee referred to in Article 23(1) of Regulation (EC) No 714/2009
HAS ADOPTED THIS REGULATION:
TITLE I
GENERAL PROVISIONS
Article 1: Subject matter
This Regulation establishes a network code which lays down the requirements for grid connection of power generating facilities, namely synchronous power generating modules, power park modules and offshore power park modules, to the interconnected system. It, therefore, helps to ensure fair conditions of competition in the internal electricity market, to ensure system security and the integration of renewable electricity sources, and to facilitate Union-wide trade in electricity.
This regulation also lays down the obligations for ensuring that system operators make appropriate use of the power generating facilities’ capabilities in a transparent and non-discriminatory manner to provide a level playing field throughout the Union.
Article 2: Definitions
For the purposes of this Regulation, the definitions in Article 2 of Directive 2012/27/EU,[1] Article 2 of Regulation (EC) No 714/2009, Article 2 of Commission Regulation No [000/2014 – CACM], Article 2 of Commission Regulation (EU) No 543/2013[2] and Article 2 of Directive 2009/72/EC shall apply.
In addition, the following definitions shall apply:
1. ‘entity’ means a regulatory authority, other national authority, system operator or other public or private body appointed under national law.
2. ‘synchronous area’ means an area covered by synchronously interconnected TSOs, such as the synchronous areas of Continental Europe, Great Britain, Ireland-Northern Ireland and Nordic and the power systems of Lithuania, Latvia and Estonia, together referred to as ‘Baltic’ which are part of a wider synchronous area;
3. ‘voltage’ means the difference in electrical potential between two points measured as the root-mean-square value of the positive sequence phase-to-phase voltages at fundamental frequency;
4. ‘apparent power’ means the product of voltage and current at fundamental frequency, and the square root of three in the case of three-phase systems, usually expressed in kilovolt-amperes ('kVA') or megavolt-amperes ('MVA');
5. ‘power generating module’ means either a synchronous power generating module or a power park module;
6. ‘power generating facility’ means a facility that converts primary energy into electrical energy and which consists of one or more power generating modules connected to a network at one or more connection points;
7. ‘power generating facility owner’ means a natural or legal entity owning a power generating facility;
8. ‘main generating plant’ means one or more of the principal items of equipment required to convert the primary source of energy into electricity;
9. ‘synchronous power generating module’ means an indivisible set of installations which can generate electrical energy such that the frequency of the generated voltage, the generator speed and the frequency of network voltage are in a constant ratio and thus in synchronism;
10. ‘power generating module document’ or ‘PGMD’ means a document provided by the power generating facility owner to the relevant system operator for a type B or C power generating module which confirms that the power generating module’s compliance with the technical criteria set out in this Regulation has been demonstrated and provides the necessary data and statements, including a statement of compliance;
11. ‘relevant TSO’ means the TSO in whose control area a power generating module, a demand facility, a distribution system or a HVDC system is or will be connected to the network at any voltage level;
12. ‘network’ means a plant and apparatus connected together in order to transmit or distribute electricity;
13. 'relevant system operator’ means the transmission system operator or distribution system operator to whose system a power generating module, demand facility, distribution system or HVDC system is or will be connected;
14. ‘connection agreement’ means a contract between the relevant system operator and either the power generating facility owner, demand facility owner, distribution system operator or HVDC system owner, which includes the relevant site and specific technical requirements for the power generating facility, demand facility, distribution system, distribution system connection or HVDC system;
15. ‘connection point’ means the interface at which the power generating module, demand facility, distribution system or HVDC system is connected to a transmission system, offshore network, distribution system, including closed distribution systems, or HVDC system, as identified in the connection agreement;
16. ‘maximum capacity’ or ‘Pmax’ means the maximum continuous active power which a power generating module can produce, less any demand associated solely with facilitating the operation of that power generating module and not fed into the network as specified in the connection agreement or as agreed between the relevant system operator and the power generating facility owner;
17. ‘power park module’ or ‘PPM’ means a unit or ensemble of units generating electricity, which is either non-synchronously connected to the network or connected through power electronics, and that also has a single connection point to a transmission system, distribution system including closed distribution system or HVDC system;
18. ‘offshore power park module’ means a power park module located offshore with an offshore connection point;
19. ‘synchronous compensation operation’ means the operation of an alternator without prime mover to regulate voltage dynamically by production or absorption of reactive power;
20. ‘active power’ means the real component of the apparent power at fundamental frequency, expressed in watts or multiples thereof such as kilowatts ('kW') or megawatts ('MW');
21. ‘pump-storage’ means a hydro unit in which water can be raised by means of pumps and stored to be used for the generation of electrical energy;
22. ‘frequency’ means the electric frequency of the system expressed in hertz that can be measured in all parts of the synchronous area under the assumption of a consistent value for the system in the time frame of seconds, with only minor differences between different measurement locations. Its nominal value is 50Hz;
23. 'droop’ means the ratio of a steady-state change of frequency to the resulting steady-state change in active power output, expressed in percentage terms. The change in frequency is expressed as a ratio to nominal frequency and the change in active power expressed as a ratio to maximum capacity or actual active power at the moment the relevant threshold is reached;
24. ‘minimum regulating level’ means the minimum active power, as specified in the connection agreement or as agreed between the relevant system operator and the power generating facility owner, down to which the power generating module can control active power;
25. ‘setpoint’ means the target value for any parameter typically used in control schemes;
26. ‘instruction’ means any command, within its authority, given by a system operator to a power generating facility owner, demand facility owner, distribution system operator or HVDC system owner in order to perform an action;
27. ‘secured fault’ means a fault which is successfully cleared according to the system operator’s planning criteria;
28. ‘reactive power’ means the imaginary component of the apparent power at fundamental frequency, usually expressed in kilovar ('kVAr') or megavar ('MVAr');
29. 'fault-ride-through' means the capability of electrical devices to be able to remain connected to the network and operate through periods of low voltage at the connection point caused by secured faults;
30. ‘alternator’ means a device that converts mechanical energy into electrical energy by means of a rotating magnetic field;
31. ‘current’ means the rate at which electric charge flows which is measured by the root-mean-square value of the positive sequence of the phase current at fundamental frequency;
32. 'stator' means the portion of a rotating machine which includes the stationary magnetic parts with their associated windings;
33. ‘inertia’ means the property of a rotating rigid body, such as the rotor of an alternator, such that it maintains its state of uniform rotational motion and angular momentum unless an external torque is applied;
34. ‘synthetic inertia’ means the facility provided by a power park module or HVDC system to replace the effect of inertia of a synchronous power generating module to a prescribed level of performance;
35. ‘frequency control’ means the capability of a power generating module or HVDC system to adjust its active power output in response to a measured deviation of system frequency from a setpoint, in order to maintain stable system frequency;
36. ‘frequency sensitive mode’ or ‘FSM’ means the operating mode of a power generating module or HVDC system in which the active power output changes in response to a change in system frequency, in such a way that it assists with the recovery to target frequency;
37. ‘limited frequency sensitive mode – overfrequency’ or ‘LFSM-O’ means a power generating module or HVDC system operating mode which will result in active power output reduction in response to a change in system frequency above a certain value;
38. ‘limited frequency sensitive mode – underfrequency’ ‘LFSM-U’ means a power generating module or HVDC system operating mode which will result in active power output increase in response to a change in system frequency below a certain value;
39. ‘frequency response deadband’ means an interval used intentionally to make the frequency control unresponsive;
40. ‘frequency response insensitivity’ means the inherent feature of the control system specified as the minimum magnitude of change in the frequency or input signal that results in a change of output power or output signal;
41. ‘P-Q-capability diagram’ means a diagram describing the reactive power capability of a power generating module in the context of varying active power at the connection point;
42. ‘steady-state stability’ means the ability of a network or a synchronous power generating module to revert and maintain stable operation following a minor disturbance;
43. ‘island operation’ means the independent operation of a whole network or part of a network that is isolated after being disconnected from the interconnected system, having at least one power generating module or HVDC system supplying power to this network and controlling the frequency and voltage;
44. ‘houseload operation’ means the operation which ensures that power generating facilities are able to continue to supply their in-house loads in the event of network failures resulting in power generating modules being disconnected from the network and tripped onto their auxiliary supplies;
45. ‘black start capability’ means the capability of recovery of a power generating module from a total shutdown through a dedicated auxiliary power source without any electrical energy supply external to the power generating facility;
46. ‘authorised certifier’ means an entity that issues equipment certificates and power generating module documents and whose accreditation is given by the national affiliate of the European cooperation for Accreditation ('EA'), established in accordance with Regulation (EC) No 765/2008;
47. ‘equipment certificate’ means a document issued by an authorised certifier for equipment used by a power generating module, demand unit, distribution system, demand facility or HVDC system. The equipment certificate defines the scope of its validity at a national or other level at which a specific value is selected from the range allowed at a European level. For the purpose of replacing specific parts of the compliance process, the equipment certificate may include models that have been verified against actual test results;
48. ‘excitation control system’ means a feedback control system that includes the synchronous machine and its excitation system;
49. ‘U-Q/Pmax-profile’ means a profile representing the reactive power capability of a power generating module or HVDC converter station in the context of varying voltage at the connection point;
50. ‘minimum stable operating level’ means the minimum active power, as specified in the connection agreement or as agreed between the relevant system operator and the power generating facility owner, at which the power generating module can be operated stably for an unlimited time;
51. ‘overexcitation limiter’ means a control device within the AVR which prevents the rotor of an alternator from overloading by limiting the excitation current;
52. ‘underexcitation limiter’ means a control device within the AVR, the purpose of which is to prevent the alternator from losing synchronism due to lack of excitation;
53. ‘automatic voltage regulator’ or ‘AVR’ means the continuously acting automatic equipment controlling the terminal voltage of a synchronous power generating module by comparing the actual terminal voltage with a reference value and controlling the output of an excitation control system;
54. ‘power system stabiliser’ or ‘PSS’ means an additional functionality of the AVR of a synchronous power generating module whose purpose is to damp power oscillations;
55. ‘fast fault current’ means a current injected by a power park module or HVDC system during and after a voltage deviation caused by an electrical fault with the aim of identifying a fault by network protection systems at the initial stage of the fault, supporting system voltage retention at a later stage of the fault and system voltage restoration after fault clearance;
56. ‘power factor’ means the ratio of the absolute value of active power to apparent power;
57. ‘slope’ means the ratio of the change in voltage, based on reference 1 pu voltage, to a change in reactive power in-feed from zero to maximum reactive power, based on maximum reactive power;
58. ‘offshore grid connection system’ means the complete interconnection between an offshore connection point and the onshore system at the onshore grid interconnection point;
59. ‘onshore grid interconnection point’ means the point at which the offshore grid connection system is connected to the onshore network of the relevant system operator;
60. ‘installation document’ means a simple structured document containing information about a type A power generating module or a demand unit, with demand-side response connected below 1000V, and confirming its compliance with the relevant requirements;
61. ‘statement of compliance’ means a document provided by the power generating facility owner, demand facility owner, distribution system operator or HVDC system owner to the system operator stating the current status of compliance with the relevant specifications and requirements;
62. ‘final operational notification’ or ‘FON’ means a notification issued by the relevant system operator to a power generating facility owner, demand facility owner, distribution system operator or HVDC system owner who complies with the relevant specifications and requirements, allowing them to operate respectively a power generating module, demand facility, distribution system or HVDC system by using the grid connection;
63. ‘energisation operational notification’ or ‘EON’ means a notification issued by the relevant system operator to a power generating facility owner, demand facility owner, distribution system operator or HVDC system owner prior to energisation of its internal network;
64. ‘interim operational notification’ or ‘ION’ means a notification issued by the relevant system operator to a power generating facility owner, demand facility owner, distribution system operator or HVDC system owner which allows them to operate respectively a power generating module, demand facility, distribution system or HVDC system by using the grid connection for a limited period of time and to initiate compliance tests to ensure compliance with the relevant specifications and requirements;
65. ‘limited operational notification’ or ‘LON’ means a notification issued by the relevant system operator to a power generating facility owner, demand facility owner, distribution system operator or HVDC system owner who had previously attained FON status but is temporarily subject to either a significant modification or loss of capability resulting in non-compliance with the relevant specifications and requirements.
Article 3: Scope of application
1. The connection requirements set out in this Regulation shall apply to new power generating modules which are considered significant in accordance with Article 5, unless otherwise provided.
The relevant system operator shall refuse to allow the connection of a power generating module which does not comply with the requirements set out in this Regulation and which is not covered by a derogation granted by the regulatory authority, or other authority where applicable in a Member State pursuant to Article 60. The relevant system operator shall communicate such refusal, by means of a reasoned statement in writing, to the power generating facility owner and, unless specified otherwise by the regulatory authority, to the regulatory authority.
2. This Regulation shall not apply to:
(a) power generating modules connected to the transmission system and distribution systems, or to parts of the transmission system or distribution systems, of islands of Member States of which the systems are not operated synchronously with either the Continental Europe, Great Britain, Nordic, Ireland and Northern Ireland or Baltic synchronous area;
(b) power generating modules that were installed to provide back-up power and operate in parallel with the system for less than five minutes per calendar month while the system is in normal system state. Parallel operation during maintenance or commissioning tests of that power generating module shall not count towards the five minute limit;
(c) power generating modules that do not have a permanent connection point and are used by the system operators to temporarily provide power when normal system capacity is partly or completely unavailable;
(d) storage devices except for pump-storage power generating modules in accordance with paragraph 2 of Article 6.
Article 4: Application to existing power generating modules
1. Existing power generating modules are not subject to the requirements of this Regulation, except where:
(a) a type C or type D power generating module has been modified to such an extent that its connection agreement must be substantially revised in accordance with the following procedure:
(i) power generating facility owners who intend to undertake the modernisation of a plant or replacement of equipment impacting the technical capabilities of the power generating module shall notify their plans to the relevant system operator in advance; |  | ü |  |  | ü
(ii) if the relevant system operator considers that the extent of the modernisation or replacement of equipment is such that a new connection agreement is required, the system operator shall notify the relevant regulatory authority or, where applicable, the Member State; and |  | ü |  |  | ü
(iii) the relevant regulatory authority or, where applicable, the Member State shall decide if the existing connection agreement needs to be revised or a new connection agreement is required and which requirements of this Regulation shall apply; or
(b) a regulatory authority or, where applicable, a Member State decides to make an existing power generating module subject to all or some of the requirements of this Regulation, following a proposal from the relevant TSO in accordance with paragraphs 3, 4 and 5. |  | ü |  |  | ü
2. For the purposes of this Regulation, a power generating module shall be considered existing if:
(a) it is already connected to the network on the date of entry into force of this Regulation; or
(b) the power generating facility owner has concluded a final and binding contract for the purchase of the main generating plant by two years after the entry into force of the Regulation. The power generating facility owner must notify the relevant system operator and relevant TSO of conclusion of the contract within 30 months after the entry into force of the Regulation. |  | ü |  |  | ü
The notification submitted by the power generating facility owner to the relevant system operator and to the relevant TSO shall at least indicate the contract title, its date of signature and date of entry into force and the specifications of the main generating plant to be constructed, assembled or purchased. |  | ü |  |  | ü
A Member State may provide that in specified circumstances the regulatory authority may determine whether the power generating module is to be considered an existing power generating module or a new power generating module.
3. Following a public consultation in accordance to Article 10 and in order to address significant factual changes in circumstances, such as the evolution of system requirements including penetration of renewable energy sources, smart grids, distributed generation or demand response, the relevant TSO may propose to the regulatory authority concerned, or where applicable, to the Member State to extend the application of this Regulation to existing power generating modules. |  | ü |  |  | ü
For that purpose a sound and transparent quantitative cost-benefit analysis shall be carried out, in accordance with Articles 38 and 39. The analysis shall indicate:
(a) the costs, in regard to existing power generating modules, of requiring compliance with this Regulation;
(b) the socio-economic benefit resulting from applying the requirements set out in this Regulation; and
(c) the potential of alternative measures to achieve the required performance.
4. Before carrying out the quantitative cost-benefit analysis referred to in paragraph 3, the relevant TSO shall: |  | ü |  |  | ü
(a) carry out a preliminary qualitative comparison of costs and benefits;
(b) obtain approval from the relevant regulatory authority or, where applicable, the Member State.
5. The relevant regulatory authority or, where applicable, the Member State shall decide on the extension of the applicability of this Regulation to existing power generating modules within six months of receipt of the report and the recommendation of the relevant TSO in accordance with paragraph 4 of Article 38. The decision of the regulatory authority or, where applicable, the Member State shall be published. |  | ü |  |  | ü
6. The relevant TSO shall take account of the legitimate expectations of power generating facility owners as part of the assessment of the application of this Regulation to existing power generating modules. |  | ü |  |  | ü
7. The relevant TSO may assess the application of some or all of the provisions of this Regulation to existing power generating modules every three years in accordance with the criteria and process set out in paragraphs 3 to 5. |  | ü |  |  | ü
Article 5: Determination of significance
1. The power generating modules shall comply with the requirements on the basis of the voltage level of their connection point and their maximum capacity according to the categories set out in paragraph 2.
2. Power generating modules within the following categories shall be considered as significant:
(a) connection point below 110 kV and maximum capacity of 0.8 kW or more (type A);
(b) connection point below 110 kV and maximum capacity at or above a threshold proposed by each relevant TSO in accordance with the procedure laid out in paragraph 3 (type B). This threshold shall not be above the limits for type B power generating modules contained in Table 1; |  | ü |  |  | ü
(c) connection point below 110 kV and maximum capacity at or above a threshold specified by each relevant TSO in accordance with paragraph 3 (type C). This threshold shall not be above the limits for type C power generating modules contained in Table 1; or |  | ü |  |  | ü
(d) connection point at 110 kV or above (type D). A power generating module is also of type D if its connection point is below 110 kV and its maximum capacity is at or above a threshold specified in accordance with paragraph 3. This threshold shall not be above the limit for type D power generating modules contained in Table 1.
Table 1: Limits for thresholds for type B, C and D power generating modules
3. Proposals for maximum capacity thresholds for types B, C and D power generating modules shall be subject to approval by the relevant regulatory authority or, where applicable, the Member State. In forming proposals the relevant TSO shall coordinate with adjacent TSOs and DSOs and shall conduct a public consultation in accordance with Article 10. A proposal by the relevant TSO to change the thresholds shall not be made sooner than three years after the previous proposal. |  | ü |  |  | ü
4. Power generation facility owners shall assist this process and provide data as requested by the relevant TSO. |  | ü |  |  | ü
5. If, as a result of modification of the thresholds, a power generating module qualifies under a different type, the procedure laid down in paragraph 3 of Article 4 concerning existing power generating modules shall apply before compliance with the requirements for the new type is required.
Article 6: Application to power generating modules, pump-storage power generating modules, combined heat and power facilities, and industrial sites
1. Offshore power generating modules connected to the interconnected system shall meet the requirements for onshore power generating modules, unless the requirements are modified for this purpose by the relevant system operator or unless the connection of power park modules is via a high voltage direct current connection or via a network whose frequency is not synchronously coupled to that of the main interconnected system (such as via a back to back convertor scheme). |  | ü |  |  | ü
2. Pump-storage power generating modules shall fulfil all the relevant requirements in both generating and pumping operation mode. Synchronous compensation operation of pump-storage power generating modules shall not be limited in time by the technical design of power generating modules. Pump-storage variable speed power generating modules shall fulfil the requirements applicable to synchronous power generating modules as well as those set out in point (b) of Article 20(2), if they qualify as type B, C or D.
3. With respect to power generating modules embedded in the networks of industrial sites, power generating facility owners, system operators of industrial sites and relevant system operators whose network is connected to the network of an industrial site shall have the right to agree on conditions for disconnection of such power generating modules together with critical loads, which secure production processes, from the relevant system operator’s network. The exercise of this right shall be coordinated with the relevant TSO. | ü | ü |  |  | ü
4. Except for requirements under paragraphs 2 and 4 of Article 13 or where otherwise stated in the national framework, requirements of this Regulation relating to the capability to maintain constant active power output or to modulate active power output shall not apply to power generating modules of facilities for combined heat and power production embedded in the networks of industrial sites, where all of the following criteria are met:
(a) the primary purpose of those facilities is to produce heat for production processes of the industrial site concerned;
(b) heat and power generating is inextricably interlinked, that is to say any change of heat generation results inadvertently in a change of active power generating and vice versa;
(c) the power generating modules are of type A, B, C or, in the case of the Nordic synchronous area, type D in accordance with points (a) to (c) of Article 5(2).
5. Combined heat and power generating facilities shall be assessed on the basis of their electrical maximum capacity.
Article 7: Regulatory aspects
1. Requirements of general application to be established by relevant system operators or TSOs under this Regulation shall be subject to approval by the entity designated by the Member State and be published. The designated entity shall be the regulatory authority unless otherwise provided by the Member State.
2. For site specific requirements to be established by relevant system operators or TSOs under this Regulation, Member States may require approval by a designated entity.
3. When applying this Regulation, Member States, competent entities and system operators shall:
(a) apply the principles of proportionality and non-discrimination;
(b) ensure transparency;
(c) apply the principle of optimisation between the highest overall efficiency and lowest total costs for all parties involved;
(d) respect the responsibility assigned to the relevant TSO in order to ensure system security, including as required by national legislation; |  | ü |  |  | ü
(e) consult with relevant DSOs and take account of potential impacts on their system;
(f) take into consideration agreed European standards and technical specifications.
4. The relevant system operator or TSO shall submit a proposal for requirements of general application, or the methodology used to calculate or establish them, for approval by the competent entity within two years of entry into force of this Regulation. |  | ü |  |  | ü
5. Where this Regulation requires the relevant system operator, relevant TSO, power generating facility owner and/or the distribution system operator to seek agreement, they shall endeavour to do so within six months after a first proposal has been submitted by one party to the other parties. If no agreement has been found within this timeframe, each party may request the relevant regulatory authority to issue a decision within six months.
6. Competent entities shall take decisions on proposals for requirements or methodologies within six months following the receipt of such proposals.
7. If the relevant system operator or TSO deems an amendment to requirements or methodologies as provided for and approved under paragraph 1 and 2 to be necessary, the requirements provided for in paragraphs 3 to 8 shall apply to the proposed amendment. System operators and TSOs proposing an amendment shall take into account the legitimate expectations, if any, of power generating facility owners, equipment manufacturers and other stakeholders based on the initially specified or agreed requirements or methodologies.
8. Any party having a complaint against a relevant system operator or TSO in relation to that relevant system operator's or TSO's obligations under this Regulation may refer the complaint to the regulatory authority which, acting as dispute settlement authority, shall issue a decision within two months after receipt of the complaint. That period may be extended by two months where additional information is sought by the regulatory authority. That extended period may be further extended with the agreement of the complainant. The regulatory authority's decision shall have binding effect unless and until overruled on appeal.
9. Where the requirements under this Regulation are to be established by a relevant system operator that is not a TSO, Member States may provide that instead the TSO be responsible for establishing the relevant requirements.
Article 8: Multiple TSOs
1. Where more than one TSO exists in a Member State, this Regulation shall apply to all those TSOs.
2. Member States may, under the national regulatory regime, provide that the responsibility of a TSO to comply with one or some or all obligations under this Regulation is assigned to one or more specific TSOs.
Article 9: Recovery of costs
1. The costs borne by system operators subject to network tariff regulation and stemming from the obligations laid down in this Regulation shall be assessed by the relevant regulatory authorities. Costs assessed as reasonable, efficient and proportionate shall be recovered through network tariffs or other appropriate mechanisms.
2. If requested by the relevant regulatory authorities, system operators referred to in paragraph 1 shall, within three months of the request, provide the information necessary to facilitate assessment of the costs incurred.
Article 10: Public consultation
1. Relevant system operators and relevant TSOs shall carry out consultation with stakeholders, including the competent authorities of each Member State, on proposals to extend the applicability of this Regulation to existing power generating modules in accordance with paragraph 3 of Article 4, for the proposal for thresholds in accordance with paragraph 3 of Article 5, and on the report prepared in accordance with Article 38(3) and the cost-benefit analysis undertaken in accordance with Article 63(2). The consultation shall last at least for a period of one month. |  | ü |  |  | ü
2. The relevant system operators or relevant TSOs shall duly take into account the views of the stakeholders resulting from the consultations prior to the submission of the draft proposal for thresholds, the report or cost benefit analysis for approval by the regulatory authority or, if applicable, the Member State. In all cases, a sound justification for including or not the views of the stakeholders shall be provided and published in a timely manner before, or simultaneously with, the publication of the proposal. |  | ü |  |  | ü
Article 11: Stakeholder involvement
The Agency, in close cooperation with the ENTSO for Electricity, shall organise stakeholder involvement regarding the requirements for grid connection of power generating facilities, and other aspects of the implementation of this Regulation. This shall include regular meetings with stakeholders to identify problems and propose improvements notably related to the requirements for grid connection of power generating facilities.
Article 12: Confidentiality obligations
1. Any confidential information received, exchanged or transmitted pursuant to this Regulation shall be subject to the conditions of professional secrecy laid down in paragraphs 2, 3 and 4.
2. The obligation of professional secrecy shall apply to any persons, regulatory authorities or entities subject to the provisions of this Regulation.
3. Confidential information received by the persons referred to in paragraph 2 in the course of their duties may not be divulged to any other person or authority, without prejudice to cases covered by national law, the other provisions of this Regulation or other relevant Union law.
4. Without prejudice to cases covered by national or Union law, regulatory authorities, entities or persons who receive confidential information pursuant to this Regulation may use it only for the purpose of carrying out their duties under this Regulation.
REQUIREMENTS
CHAPTER I
GENERAL REQUIREMENTS
Article 13: General requirements for type A power generating modules
1. Type A power generating modules shall fulfil the following requirements relating to frequency stability:
(a) With regard to frequency ranges:
(i) a power generating module shall be capable of remaining connected to the network and operate within the frequency ranges and time periods specified in Table 2;
(ii) the relevant system operator, in coordination with the relevant TSO, and the power generating facility owner may agree on wider frequency ranges, longer minimum times for operation or specific requirements for combined frequency and voltage deviations to ensure the best use of the technical capabilities of a power generating module, if it is required to preserve or to restore system security;
(iii) the power generating facility owner shall not unreasonably withhold consent to apply wider frequency ranges or longer minimum times for operation, taking account of their economic and technical feasibility.
(b) With regard to the rate of change of frequency withstand capability, a power generating module shall be capable of staying connected to the network and operate at rates of change of frequency up to a value defined by the relevant TSO, unless disconnection was triggered by rate-of-change-of-frequency-type loss of mains protection. The relevant system operator, in coordination with the relevant TSO, shall define this rate-of-change-of-frequency-type loss of mains protection. |  | ü |  |  | ü
Table 2: Minimum time periods for which a power generating module has to be capable of operating on different frequencies, deviating from a nominal value, without disconnecting from the network.
2. With regard to the limited frequency sensitive mode — overfrequency (LFSM-O), the following shall apply as determined by the relevant TSO for its control area in coordination with the TSOs of the same synchronous area to ensure minimal impacts on neighbouring areas: |  | ü |  |  | ü
(a) the power generating module shall be capable of activating the provision of active power frequency response according to figure 1 at a frequency threshold and droop settings specified by the relevant TSO; |  | ü |  |  | ü
(b) instead of the capability referred to in paragraph (a), the relevant TSO may choose to allow within its control area automatic disconnection and reconnection of power generating modules of Type A at randomised frequencies, ideally uniformly distributed, above a frequency threshold, as determined by the relevant TSO where it is able to demonstrate to the relevant regulatory authority, and with the cooperation of power generating module owners, that this has a limited cross-border impact and maintains the same level of operational security in all system states; |  | ü |  |  | ü
(c) the frequency threshold shall be between 50.2 Hz and 50.5 Hz inclusive;
(d) the droop settings shall be between 2 % and 12 %;
(e) the power generating module shall be capable of activating a power frequency response with an initial delay that is as short as possible. If that delay is greater than two seconds, the power generating facility owner shall justify the delay, providing technical evidence to the relevant TSO; |  | ü |  |  | ü
(f) the relevant TSO may require that upon reaching minimum regulating level, the power generating module be capable of either: |  | ü |  |  | ü
(i) continuing operation at this level; or
(ii) further decreasing active power output;
(g) the power generating module shall be capable of operating stably during LFSM-O operation. When LFSM-O is active, the LFSM-O setpoint will prevail over any other active power setpoints.
Figure 1: active power frequency response capability of power generating modules in LFSM-O. Pref is the reference active power to which DP is related and may be defined differently for synchronous power generating modules and power park modules. DP is the change in active power output from the power generating module. fn is the nominal frequency (50 Hz) in the network and Df is the frequency change in the network. At overfrequencies where Df is above Df1, the power generating module has to provide a negative active power output change according to the droop S2.
3. The power generating module shall be capable of maintaining constant output at its target active power value regardless of changes in frequency, except where output follows the changes specified in the context of paragraphs 2 and 4 of this Article or points (c) and (d) of Article 15(2) as applicable.
4. The relevant TSO shall specify admissible active power reduction from maximum output with falling frequency in its control area as a rate of reduction falling within the boundaries, illustrated by the full lines in Figure 2: |  | ü |  |  | ü
(a) below 49 Hz falling by a reduction rate of 2 % of the maximum capacity at 50 Hz per 1 Hz frequency drop;
(b) below 49.5 Hz falling by a reduction rate of 10 % of the maximum capacity at 50 Hz per 1 Hz frequency drop.
5. The admissible active power reduction from maximum output shall:
(a) clearly define the ambient conditions applicable;
(b) take account of the technical capabilities of power generating modules.
Figure 2: Maximum power capability reduction with falling frequency. The diagram represents the boundaries in which the capability can be specified by the relevant TSO. |  | ü |  |  | ü
6. The power generating module shall be equipped with a logic interface (input port) in order to cease active power output within five seconds following an instruction being received at the input port. The relevant system operator shall have the right to define requirements for equipment to make this facility operable remotely. |  | ü |  |  | ü
7. The relevant TSO shall define the conditions under which a power generating module is capable of connecting automatically to the network. Those conditions shall include: |  | ü |  |  | ü
(a) frequency ranges within which an automatic connection is admissible, and a corresponding delay time; and
(b) maximum admissible gradient of increase in active power output.
Automatic connection is allowed unless determined otherwise by the relevant system operator in coordination with the relevant TSO.
Article 14: General requirements for type B power generating modules
1. Type B power generating modules shall fulfil the requirements set out in Article 13 except for Article 13(2)(b).
2. Type B power generating modules shall fulfil the following requirements in relation to frequency stability:
(a) to control active power output, the power generating module shall be equipped with an interface (input port) in order to be able to reduce active power output following an instruction at the input port; and
(b) the relevant system operator shall have the right to specify the requirements for further equipment to allow active power output to be remotely operated. |  | ü |  |  | ü
3. Type B power generating modules shall fulfil the following requirements in relation to robustness:
(a) with regard to fault-ride-through capability of power generating modules:
(i) each TSO shall specify a voltage-against-time-profile in line with Figure 3 at the connection point for fault conditions, which describes the conditions in which the power generating module is capable of staying connected to the network and continuing to operate stably after the power system has been disturbed by secured faults on the transmission system; |  | ü |  |  | ü
(ii) the voltage-against-time-profile shall express a lower limit of the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, as a function of time before, during and after the fault;
(iii) the lower limit referred to in point (ii) shall be specified by the relevant TSO using the parameters set out in Figure 3, and within the ranges set out in Tables 3.1 and 3.2; |  | ü |  |  | ü
(iv) each TSO shall specify and make publicly available the pre-fault and post-fault conditions for the fault-ride-through capability in terms of: |  | ü |  |  | ü
– the calculation of the pre-fault minimum short circuit capacity at the connection point;
– pre-fault active and reactive power operating point of the power generating module at the connection point and voltage at the connection point; and
– calculation of the post-fault minimum short circuit capacity at the connection point.
(v) at the request of a power generating facility owner, the relevant system operator shall provide the pre-fault and post-fault conditions to be considered for fault-ride-through capability as an outcome of the calculations at the connection point as specified in point (iv) regarding: |  | ü |  |  | ü
– pre-fault minimum short circuit capacity at each connection point expressed in MVA;
– pre-fault operating point of the power generating module expressed in active power output and reactive power output at the connection point and voltage at the connection point; and
– post-fault minimum short circuit capacity at each connection point expressed in MVA.
Alternatively, the relevant system operator may provide generic values derived from typical cases; |  | ü |  |  | ü
Figure 3: Fault-ride-through profile of a power generating module. The diagram represents the lower limit of a voltage-against-time profile of the voltage at the connection point, expressed as the ratio of its actual value and its reference 1 pu value before, during and after a fault. Uret is the retained voltage at the connection point during a fault, tclear is the instant when the fault has been cleared. Urec1, Urec2, trec1, trec2 and trec3 specify certain points of lower limits of voltage recovery after fault clearance.
Table 3.1: Parameters for Figure 3 for fault-ride-through capability of synchronous power generating modules.
Table 3.2: Parameters for Figure 3 for fault-ride-through capability of power park modules.
(vi) the power generating module shall be capable of remaining connected to the network and continuing to operate stably when the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, given the pre-fault and post-fault conditions in points (iv) and (v) of paragraph (3)(a), remain above the lower limit specified in point (ii) of paragraph (3)(a), unless the protection scheme for internal electrical faults requires the disconnection of the power generating module from the network. The protection schemes and settings for internal electrical faults must not jeopardise fault-ride-through performance;
(vii) without prejudice to point (vi) of paragraph (3)(a), undervoltage protection (either fault-ride-through capability or minimum voltage specified at the connection point voltage) shall be set by the power generating facility owner according to the widest possible technical capability of the power generating module, unless the relevant system operator requires narrower settings in accordance with point (b) of paragraph (5). The settings shall be justified by the power generating facility owner in accordance with this principle; |  | ü |  |  | ü
(b) Fault-ride-through capabilities in case of asymmetrical faults shall be specified by each TSO. |  | ü |  |  | ü
4. Type B power generating modules shall fulfil the following requirements relating to system restoration:
(a) the relevant TSO shall specify the conditions under which a power generating module is capable of reconnecting to the network after an incidental disconnection caused by a network disturbance; and |  | ü |  |  | ü
(b) installation of automatic reconnection systems shall be subject both to prior authorisation by the relevant system operator and to the reconnection conditions specified by the relevant TSO. |  | ü |  |  | ü
5. Type B power generating modules shall fulfil the following general system management requirements:
(a) with regard to control schemes and settings:
(i) the schemes and settings of the different control devices of the power generating module that are necessary for transmission system stability and for taking emergency action shall be coordinated and agreed between the relevant TSO, the relevant system operator and the power generating facility owner; |  | ü |  |  | ü
(ii) any changes to the schemes and settings, mentioned in point (i), of the different control devices of the power generating module shall be coordinated and agreed between the relevant TSO, the relevant system operator and the power generating facility owner, in particular if they apply in the circumstances referred to in point (i) of paragraph (5) (a); |  | ü |  |  | ü
(b) with regard to electrical protection schemes and settings:
(i) the relevant system operator shall specify the schemes and settings necessary to protect the network, taking into account the characteristics of the power generating module. The protection schemes needed for the power generating module and the network as well as the settings relevant to the power generating module shall be coordinated and agreed between the relevant system operator and the power generating facility owner. The protection schemes and settings for internal electrical faults must not jeopardise the performance of a power generating module, in line with the requirements set out in this Regulation; | ü | ü | ü | ü | ü
(ii) electrical protection of the power generating module shall take precedence over operational controls, taking into account the security of the system and the health and safety of staff and of the public, as well as mitigating any damage to the power generating module;
(iii) protection schemes may cover the following aspects:
– external and internal short circuit;
– asymmetric load (negative phase sequence);
– stator and rotor overload;
– over-/underexcitation;
– over-/undervoltage at the connection point;
– over-/undervoltage at the alternator terminals;
– inter-area oscillations;
– inrush current;
– asynchronous operation (pole slip);
– protection against inadmissible shaft torsions (for example, subsynchronous resonance);
– power generating module line protection;
– unit transformer protection;
– backup against protection and switchgear malfunction;
– overfluxing (U/f);
– inverse power;
– rate of change of frequency; and
– neutral voltage displacement.
(iv) changes to the protection schemes needed for the power generating module and the network and to the settings relevant to the power generating module shall be agreed between the system operator and the power generating facility owner, and agreement shall be reached before any changes are made; | ü | ü | ü | ü | ü
(c) the power generating facility owner shall organise its protection and control devices in accordance with the following priority ranking (from highest to lowest):
(i) network and power generating module protection;
(ii) synthetic inertia, if applicable;
(iii) frequency control (active power adjustment);
(iv) power restriction; and
(v) power gradient constraint.
(d) with regard to information exchange:
(i) power generating facilities shall be capable of exchanging information with the relevant system operator or the relevant TSO in real time or periodically with time stamping, as specified by the relevant system operator or the relevant TSO; |  | ü |  |  | ü
(ii) the relevant system operator, in coordination with the relevant TSO, shall specify the content of information exchanges including a precise list of data to be provided by the power generating facility. |  | ü |  |  | ü
Article 15: General requirements for type C power generating modules
1. Type C power generating modules shall fulfil the requirements laid down in Articles 13 and 14, except for Article 13(2)(b) and(6) and Article14(2).
2. Type C power generating modules shall fulfil the following requirements relating to frequency stability:
(a) with regard to active power controllability and control range, the power generating module control system shall be capable of adjusting an active power setpoint in line with instructions given to the power generating facility owner by the relevant system operator or the relevant TSO. |  | ü |  |  | ü
The relevant system operator or the relevant TSO shall establish the period within which the adjusted active power setpoint must be reached. The relevant TSO shall specify a tolerance (subject to the availability of the prime mover resource) applying to the new setpoint and the time within which it must be reached; |  | ü |  |  | ü
(b) manual, local measures shall be allowed in cases where the automatic remote control devices are out of service.
The relevant system operator or the relevant TSO shall notify the regulatory authority of the time required to reach the setpoint together with the tolerance for the active power; |  | ü |  |  | ü
(c) In addition to paragraph 2 of Article 13, the following requirements shall apply to type C power generating modules with regard to limited frequency sensitive mode – underfrequency (LFSM-U):
(i) the power generating module shall be capable of activating the provision of active power frequency response at a frequency threshold and with a droop specified by the relevant TSO in coordination with the TSOs of the same synchronous area as follows: |  | ü |  |  | ü
– the frequency threshold specified by the TSO shall be between 49.8 Hz and 49.5 Hz inclusive; |  | ü |  |  | ü
– the droop settings specified by the TSO shall be in the range 2 – 12 %. |  | ü |  |  | ü
This is represented graphically in Figure 4;
(ii) the actual delivery of active power frequency response in LFSM-U mode shall take into account:
– ambient conditions when the response is to be triggered;
– the operating conditions of the power generating module, in particular limitations on operation near maximum capacity at low frequencies and the respective impact of ambient conditions according to paragraphs 4 and 5 of Article 13; and
– the availability of the primary energy sources.
(iii) the activation of active power frequency response by the power generating module shall not be unduly delayed. In the event of any delay greater than two seconds, the power generating facility owner shall justify it to the relevant TSO; |  | ü |  |  | ü
(iv) in LFSM-U mode the power generating module shall be capable of providing a power increase up to its maximum capacity;
(v) stable operation of the power generating module during LFSM-U operation shall be ensured;
Figure 4: active power frequency response capability of power generating modules in LFSM-U. Pref is the reference active power to which DP is related and may be specified differently for synchronous power generating modules and power park modules. DP is the change in active power output from the power generating module. fn is the nominal frequency (50 Hz) in the network and Df is the frequency deviation in the network. At underfrequencies where Df is below Df1 the power generating module has to provide a positive active power output change according to the droop S2.
(d) in addition to point (c) of paragraph (2), the following shall apply cumulatively when frequency sensitive mode ('FSM') is operating:
(i) the power generating module shall be capable of providing active power frequency response in accordance with the parameters specified by each relevant TSO within the ranges shown in Table 4. In specifying those parameters, the relevant TSO shall take account of the following facts: |  | ü |  |  | ü
– in case of overfrequency, the active power frequency response is limited by the minimum regulating level;
– in case of underfrequency, the active power frequency response is limited by maximum capacity;
– the actual delivery of active power frequency response depends on the operating and ambient conditions of the power generating module when this response is triggered, in particular limitations on operation near maximum capacity at low frequencies according to paragraphs 4 and 5 of Article 13 and available primary energy sources;
Table 4: Parameters for active power frequency response in FSM (explanation for Figure 5)
Figure 5: Active power frequency response capability of power generating modules in FSM illustrating the case of zero deadband and insensitivity. Pref is the reference active power to which DP is related. DP is the change in active power output from the power generating module. fn is the nominal frequency (50 Hz) in the network and Df is the frequency deviation in the network.
(ii) the frequency response deadband of frequency deviation and droop must be able to be reselected repeatedly;
(iii) in the event of a frequency step change, the power generating module shall be capable of activating full active power frequency response, at or above the full line shown in Figure 6 in accordance with the parameters specified by each TSO (which shall aim at avoiding active power oscillations for the power generating module) within the ranges given in Table 5. The combination of choice of the parameters specified by the TSO shall take possible technology-dependent limitations into account; |  | ü |  |  | ü
(iv) The initial activation of active power frequency response required shall not be unduly delayed.
If the delay in initial activation of active power frequency response is greater than two seconds, the power generating facility owner shall provide technical evidence demonstrating why a longer time is needed.
For power generating modules without inertia, the relevant TSO may specify a shorter time than two seconds. If the power generating facility owner cannot meet this requirement they shall provide technical evidence demonstrating why a longer time is needed for the initial activation of active power frequency response; |  | ü |  |  | ü
Figure 6: Active power frequency response capability. Pmax is the maximum capacity to which DP relates. DP is the change in active power output from the power generating module. The power generating module has to provide active power output DP up to the point DP1 in accordance with the times t1 and t2 with the values of DP1, t1and t2 being specified by the relevant TSO according to Table 5. t1 is the initial delay. t2 is the time for full activation. |  | ü |  |  | ü
(v) the power generating module shall be capable of providing full active power frequency response for a period of between 15 and 30 minutes as specified by the relevant TSO. In specifying the period, the TSO shall have regard to active power headroom and primary energy source of the power generating module; |  | ü |  |  | ü
(vi) within the time limits laid down in point (v) of paragraph (2) (d), active power control must not have any adverse impact on the active power frequency response of power generating modules;
(vii) the parameters specified by the relevant TSO in accordance with paragraphs 1, 2, 3 and 5 shall be notified to the relevant regulatory authority. The modalities of that notification shall be specified in accordance with the applicable national regulatory framework; |  | ü |  |  | ü
Table 5: Parameters for full activation of active power frequency response resulting from frequency step change (explanation for Figure 6).
(e) with regard to frequency restoration control, the power generating module shall provide functionalities complying with specifications specified by the relevant TSO, aiming at restoring frequency to its nominal value or maintaining power exchange flows between control areas at their scheduled values; |  | ü |  |  | ü
(f) with regard to disconnection due to underfrequency, power generating facilities capable of acting as a load, including hydro pump-storage power generating facilities, shall be capable of disconnecting their load in case of underfrequency. The requirement referred to in this point does not extend to auxiliary supply;
(g) with regard to real-time monitoring of FSM:
(i) to monitor the operation of active power frequency response, the communication interface shall be equipped to transfer in real time and in a secured manner from the power generating facility to the network control centre of the relevant system operator or the relevant TSO, at the request of the relevant system operator or the relevant TSO, at least the following signals: |  | ü |  |  | ü
– status signal of FSM (on/off);
– scheduled active power output;
– actual value of the active power output;
– actual parameter settings for active power frequency response;
– droop and deadband;
(ii) the relevant system operator and the relevant TSO shall specify additional signals to be provided by the power generating facility for monitoring and recording devices in order to verify the performance of the active power frequency response provision of participating power generating modules. |  | ü |  |  | ü
3. With regard to voltage stability, type C power generating modules shall be capable of automatic disconnection when voltage at the connection point reaches levels specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
The terms and settings for actual automatic disconnection of power generating modules shall be specified by the relevant system operator in coordination with the relevant TSO. |  | ü |  |  | ü
4. Type C power generating modules shall fulfil the following requirements relating to robustness:
(a) in the event of power oscillations, power generating modules shall retain steady-state stability when operating at any operating point of the P-Q-capability diagram;
(b) without prejudice to paragraph 4 and 5 of Article 13, power generating modules shall be capable of remaining connected to the network and operating without power reduction, as long as voltage and frequency remain within the specified limits pursuant to this Regulation;
(c) power generating modules shall be capable of remaining connected to the network during single-phase or three-phase auto-reclosures on meshed network lines, if applicable to the network to which they are connected. The details of that capability shall be subject to coordination and agreements on protection schemes and settings as referred to in point (b) of Article 14(5).
5. Type C power generating modules shall fulfil the following requirements relating to system restoration:
(a) with regard to black start capability:
(i) black start capability is not mandatory without prejudice to the Member State’s rights to introduce obligatory rules in order to ensure system security;
(ii) power generating facility owners shall, at the request of the relevant TSO, provide a quotation for providing black start capability. The relevant TSO may make such a request if it considers system security to be at risk due to a lack of black start capability in its control area; |  | ü |  |  | ü
(iii) a power generating module with black start capability shall be capable of starting from shutdown without any external electrical energy supply within a timeframe specified by the relevant system operator in coordination with the relevant TSO; |  | ü |  |  | ü
(iv) a power generating module with black start capability shall be able to synchronise within the frequency limits laid down in point (a) of Article 13(1) and, where applicable, voltage limits specified by the relevant system operator or in paragraph 2 of Article 16; |  | ü |  |  | ü
(v) a power generating module with black start capability shall be capable of automatically regulating dips in voltage caused by connection of demand;
(vi) a power generating module with black start capability shall:
– be capable of regulating load connections in block load;
– be capable of operating in LFSM-O and LFSM-U, as specified in point (c) of paragraph 2 and Article 13(2);
– control frequency in case of overfrequency and underfrequency within the whole active power output range between minimum regulating level and maximum capacity as well as at houseload level;
– be capable of parallel operation of a few power generating modules within one island; and
– control voltage automatically during the system restoration phase;
(b) with regard to the capability to take part in island operation:
(i) power generating modules shall be capable of taking part in island operation if required by the relevant system operator in coordination with the relevant TSO and: |  | ü |  |  | ü
– the frequency limits for island operation shall be those established in accordance with point (a) of Article 13(1);
– the voltage limits for island operation shall be those established in accordance with paragraph 3 of Article 15 or paragraph 2 of Article 13, where applicable;
(ii) power generating modules shall be able to operate in FSM during island operation, as specified in point (d) of paragraph 2.
In the event of a power surplus, power generating modules shall be capable of reducing the active power output from a previous operating point to any new operating point within the P-Q-capability diagram. In that regard, the power generating module shall be capable of reducing active power output as much as inherently technically feasible, but to at least 55 % of its maximum capacity;
(iii) the method for detecting a change from interconnected system operation to island operation shall be agreed between the power generating facility owner and the relevant system operator in coordination with the relevant TSO. The agreed method of detection must not rely solely on the system operator’s switchgear position signals; |  | ü |  |  | ü
(iv) power generating modules shall be able to operate in LFSM-O and LFSM-U during island operation, as specified in point (c) of paragraph 2 and Article 13(2).
(c) with regard to quick re-synchronisation capability:
(i) in case of disconnection of the power generating module from the network, the power generating module shall be capable of quick re-synchronisation in line with the protection strategy agreed between the relevant system operator in coordination with the relevant TSO and the power generating facility; |  | ü |  |  | ü
(ii) a power generating module with a minimum re-synchronisation time greater than 15 minutes after its disconnection from any external power supply must be designed to trip to houseload from any operating point in its P-Q-capability diagram. In this case, the identification of houseload operation must not be based solely on the system operator’s switchgear position signals;
(iii) power generating modules shall be capable of continuing operation following tripping to houseload, irrespective of any auxiliary connection to the external network. The minimum operation time shall be specified by the relevant system operator in coordination with the relevant TSO, taking into consideration the specific characteristics of prime mover technology. |  | ü |  |  | ü
6. Type C power generating modules shall fulfil the following general system management requirements:
(a) with regard to loss of angular stability or loss of control, a power generating module shall be capable of disconnecting automatically from the network in order to help preserve system security or to prevent damage to the power generating module. The power generating facility owner and the relevant system operator in coordination with the relevant TSO shall agree on the criteria for detecting loss of angular stability or loss of control; |  | ü |  |  | ü
(b) with regard to instrumentation:
(i) Power generating facilities shall be equipped with a facility to provide fault recording and monitoring of dynamic system behaviour. This facility shall record the following parameters:
– voltage;
– active power;
– reactive power; and
– frequency.
The relevant system operator shall have the right to specify quality of supply parameters to be complied with on condition that reasonable prior notice is given; |  | ü |  |  | ü
(ii) the settings of the fault recording equipment, including triggering criteria and the sampling rates shall be agreed between the power generating facility owner and the relevant system operator in coordination with the relevant TSO; |  | ü |  |  | ü
(iii) the dynamic system behaviour monitoring shall include an oscillation trigger specified by the relevant system operator in coordination with the relevant TSO, with the purpose of detecting poorly damped power oscillations; |  | ü |  |  | ü
(iv) the facilities for quality of supply and dynamic system behaviour monitoring shall include arrangements for the power generating facility owner, and the relevant system operator and the relevant TSO to access the information. The communications protocols for recorded data shall be agreed between the power generating facility owner, the relevant system operator and the relevant TSO; |  | ü |  |  | ü
(c) with regard to the simulation models:
(i) at the request of the relevant system operator or the relevant TSO, the power generating facility owner shall provide simulation models which properly reflect the behaviour of the power generating module in both steady-state and dynamic simulations (50 Hz component) or in electromagnetic transient simulations. |  | ü |  |  | ü
The power generating facility owner shall ensure that the models provided have been verified against the results of compliance tests referred to in Chapters 2, 3 and 4 of Title IV, and shall notify the results of the verification to the relevant system operator or relevant TSO. Member States may require that such verification be carried out by an authorised certifier; |  | ü |  |  | ü
(ii) the models provided by the power generating facility owner shall contain the following sub-models, depending on the existence of the individual components:
– alternator and prime mover;
– speed and power control;
– voltage control, including, if applicable, power system stabiliser ('PSS') function and excitation control system;
– power generating module protection models, as agreed between the relevant system operator and the power generating facility owner; and |  | ü |  |  | ü
– converter models for power park modules;
(iii) the request by the relevant system operator referred to in point (i) shall be coordinated with the relevant TSO. It shall include: |  | ü |  |  | ü
– the format in which models are to be provided;
– the provision of documentation on a model’s structure and block diagrams;
– an estimate of the minimum and maximum short circuit capacity at the connection point, expressed in MVA, as an equivalent of the network;
(iv) the power generating facility owner shall provide recordings of the power generating module's performance to the relevant system operator or relevant TSO if requested. The relevant system operator or relevant TSO may make such a request, in order to compare the response of the models with those recordings; |  | ü |  |  | ü
(d) with regard to the installation of devices for system operation and devices for system security, if the relevant system operator or the relevant TSO considers that it is necessary to install additional devices in a power generating facility in order to preserve or restore system operation or security, the relevant system operator or relevant TSO and the power generating facility owner shall investigate that matter and agree on an appropriate solution; | ü | ü | ü | ü | ü
(e) the relevant system operator shall specify, in coordination with the relevant TSO, minimum and maximum limits on rates of change of active power output (ramping limits) in both an up and down direction of change of active power output for a power generating module, taking into consideration the specific characteristics of prime mover technology; | ü | ü | ü | ü | ü
(f) earthing arrangement of the neutral-point at the network side of step-up transformers shall comply with the specifications of the relevant system operator. | ü |  | ü | ü | ü
Article 16: General requirements for type D power generating modules
1. In addition to fulfilling the requirements listed in Article 13, except for Article 13 (2)(b), (6) and (7),, Article 14, except for Article 14 (2), and Article 15, except for Article 15 (3), type D power generating modules shall fulfil the requirements set out in this Article.
2. Type D power generating modules shall fulfil the following requirements relating to voltage stability:
(a) with regard to voltage ranges:
(i) without prejudice to point (a) of Article 14(3) and point (a) of Article 13(3), a power generating module shall be capable of staying connected to the network and operating within the ranges of the network voltage at the connection point, expressed by the voltage at the connection point related to the reference 1 pu voltage, and for the time periods specified in Tables 6.1 and 6.2;
(ii) the relevant TSO may specify shorter periods of time during which power generating modules shall be capable of remaining connected to the network in the event of simultaneous overvoltage and underfrequency or simultaneous undervoltage and overfrequency; |  | ü |  |  | ü
(iii) notwithstanding the provisions of point (i), the relevant TSO in Spain may require power generating modules be capable of remaining connected to the network in the voltage range between 1.05 pu and 1.0875 pu for an unlimited period;
(iv) for the 400 kV grid voltage level (or alternatively commonly referred to as 380 kV level) the reference 1 pu value is 400 kV, for other grid voltage levels the reference 1 pu voltage may differ for each system operator in the same synchronous area;
(v) notwithstanding the provisions of point (i), the relevant TSOs in the Baltic synchronous area may require power generating modules to remain connected at 400kV nominal voltage network in the voltage range limits and for the time periods that apply in the Continental Europe synchronous area.
Table 6.1: The table shows the minimum time periods during which a power generating module must be capable of operating for voltages deviating from the reference 1pu value at the connection point without disconnecting from the network, where the voltage base for pu values is from 110 kV to 300 kV.
Table 6.2: The table shows the minimum time periods during which a power generating module must be capable of operating for voltages deviating from the reference 1 pu value at the connection point without disconnecting from the network where the voltage base for pu values is from 300 kV to 400 kV.
(b) wider voltage ranges or longer minimum time periods for operation may be agreed between the relevant system operator and the power generating facility owner in coordination with the relevant TSO. If wider voltage ranges or longer minimum times for operation are economically and technically feasible, the power generating facility owner shall not unreasonably withhold an agreement; |  | ü |  |  | ü
(c) Without prejudice to point (a), the relevant system operator in coordination with the relevant TSO shall have the right to specify voltages at the connection point at which a power generating module is capable of automatic disconnection. The terms and settings for automatic disconnection shall be agreed between the relevant system operator and the power generating facility owner. |  | ü |  |  | ü
3. Type D power generating modules shall fulfil the following requirements in relation to robustness:
(a) with regard to fault-ride-through capability:
(i) power generating modules shall be capable of staying connected to the network and continuing to operate stably after the power system has been disturbed by secured faults. That capability shall be in accordance with a voltage-against-time profile at the connection point for fault conditions specified by the relevant TSO. |  | ü |  |  | ü
The voltage-against-time-profile shall express a lower limit of the actual course of the phase-to-phase voltages on the network voltage level at the connection point during a symmetrical fault, as a function of time before, during and after the fault.
That lower limit shall be specified by the relevant TSO, using the parameters set out in Figure 3 and within the ranges set out in Tables 7.1 and 7.2 for type D power generating modules connected at or above the 110 kV level. |  | ü |  |  | ü
That lower limit shall also be specified by the relevant TSO, using parameters set out in Figure 3 and within the ranges set out in Tables 3.1 and 3.2 for type D power generating modules connected below the 110 kV level.; |  | ü |  |  | ü
(ii) each TSO shall specify the pre-fault and post-fault conditions for the fault-ride-through capability referred to in point (iv) of Article 14(3)(a). The specified pre-fault and post-fault conditions for the fault-ride-through capability shall be made publicly available; |  | ü |  |  | ü
Table 7.1: Parameters for Figure 3 for fault-ride-through capability of synchronous power generating modules.
Table 7.2: Parameters for Figure 3 for fault-ride-through capability of power park modules.
(b) at the request of a power generating facility owner, the relevant system operator shall provide the pre-fault and post-fault conditions to be considered for fault-ride-through capability as an outcome of the calculations at the connection point as specified in point (iv) of Article 14(3) (a) regarding: |  | ü |  |  | ü
(i) pre-fault minimum short circuit capacity at each connection point expressed in MVA;
(ii) pre-fault operating point of the power generating module expressed as active power output and reactive power output at the connection point and voltage at the connection point; and
(iii) post-fault minimum short circuit capacity at each connection point expressed in MVA;
(c) fault-ride-through capabilities in case of asymmetrical faults shall be specified by each TSO. |  | ü |  |  | ü
4. Type D power generating modules shall fulfil the following general system management requirements:
(a) with regard to synchronisation, when starting a power generating module, synchronisation shall be performed by the power generating facility owner only after authorisation by the relevant system operator; | ü | ü | ü | ü | ü
(b) the power generating module shall be equipped with the necessary synchronisation facilities;
(c) synchronisation of power generating modules shall be possible at frequencies within the ranges set out in Table 2;
(d) the relevant system operator and the power generating facility owner shall agree on the settings of synchronisation devices to be concluded prior to operation of the power generating module. This agreement shall cover: | ü | ü | ü | ü | ü
(i) voltage;
(ii) frequency;
(iii) phase angle range;
(iv) phase sequence;
(v) deviation of voltage and frequency.
CHAPTER 2
REQUIREMENTS FOR SYNCHRONOUS POWER GENERATING MODULES
Article 17: Requirements for type B synchronous power generating modules
1. Type B synchronous power generating modules shall fulfil the requirements listed in Articles 13, except for Article 13(2)(b), and 14.
2. Type B synchronous power generating modules shall fulfil the following additional requirements relating to voltage stability:
(a) with regard to reactive power capability, the relevant system operator shall have the right to specify the capability of a synchronous power generating module to provide reactive power; |  | ü |  |  | ü
(b) with regard to the voltage control system, a synchronous power generating module shall be equipped with a permanent automatic excitation control system that can provide constant alternator terminal voltage at a selectable setpoint without instability over the entire operating range of the synchronous power generating module.
3. With regard to robustness, type B synchronous power generating modules shall be capable of providing post-fault active power recovery. The relevant TSO shall specify the magnitude and time for active power recovery. |  | ü |  |  | ü
Article 18: Requirements for type C synchronous power generating modules
1. Type C synchronous power generating modules shall fulfil the requirements laid down in Articles 13, 14, 15 and 17, except for Article 13 (2)(b) and 13(6), Article 14(2) and Article 17(2)(a).
2. Type C synchronous power generating modules shall fulfil the following additional requirements in relation to voltage stability:
(a) with regard to reactive power capability, the relevant system operator may specify supplementary reactive power to be provided if the connection point of a synchronous power generating module is neither located at the high-voltage terminals of the step-up transformer to the voltage level of the connection point nor at the alternator terminals, if no step-up transformer exists. This supplementary reactive power shall compensate the reactive power demand of the high-voltage line or cable between the high-voltage terminals of the step-up transformer of the synchronous power generating module or its alternator terminals, if no step-up transformer exists, and the connection point and shall be provided by the responsible owner of that line or cable. |  | ü |  |  | ü
(b) with regard to reactive power capability at maximum capacity:
(i) the relevant system operator in coordination with the relevant TSO shall specify the reactive power provision capability requirements in the context of varying voltage. For that purpose the relevant system operator shall specify a U-Q/Pmax-profile within the boundaries of which the synchronous power generating module shall be capable of providing reactive power at its maximum capacity. The specified U-Q/Pmax profile may take any shape, having regard to the potential costs of delivering the capability to provide reactive power production at high voltages and reactive power consumption at low voltages; |  | ü |  |  | ü
(ii) the U-Q/Pmax-profile shall be specified by the relevant system operator in coordination with the relevant TSO, in conformity with the following principles: |  | ü |  |  | ü
– the U-Q/Pmax-profile shall not exceed the U-Q/Pmax-profile envelope, represented by the inner envelope in Figure 7;
– the dimensions of the U-Q/Pmax-profile envelope (Q/Pmax range and voltage range) shall be within the range specified for each synchronous area in Table 8; and
– the position of the U-Q/Pmax-profile envelope shall be within the limits of the fixed outer envelope in Figure 7;
Figure 7: U-Q/Pmax-profile of a synchronous power generating module. The diagram represents boundaries of a U-Q/Pmax-profile by the voltage at the connection point, expressed by the ratio of its actual value and its the reference 1 pu value, against the ratio of the reactive power (Q) and the maximum capacity (Pmax). The position, size and shape of the inner envelope are indicative.
Table 8: Parameters for the inner envelope in Figure 7
(iii) the reactive power provision capability requirement applies at the connection point. For profile shapes other than rectangular, the voltage range represents the highest and lowest values. The full reactive power range is therefore not expected to be available across the range of steady-state voltages;
(iv) the synchronous power generating module shall be capable of moving to any operating point within its U-Q/Pmax profile in appropriate timescales to target values requested by the relevant system operator; |  | ü |  |  | ü
(c) with regard to reactive power capability below maximum capacity, when operating at an active power output below the maximum capacity (P<Pmax), the synchronous power generating modules shall be capable of operating at every possible operating point in the P-Q-capability diagram of the alternator of that synchronous power generating module, at least down to minimum stable operating level. Even at reduced active power output, reactive power supply at the connection point shall correspond fully to the P-Q-capability diagram of the alternator of that synchronous power generating module, taking the auxiliary supply power and the active and reactive power losses of the step-up transformer, if applicable, into account.
Article 19: Requirements for type D synchronous power generating modules
1. Type D synchronous power generating modules shall fulfil the requirements laid down in Article 13, except for Article 13(2)(b) and (6), Article 14 except for Article 14(2), Article 15, except for Article 15(3), Article 16, Article 17, except for Article 17(2) and Article 18.
2. Type D synchronous power generating modules shall fulfil the following additional requirements in relation to voltage stability:
(a) the parameters and settings of the components of the voltage control system shall be agreed between the power generating facility owner and the relevant system operator, in coordination with the relevant TSO; |  | ü |  |  | ü
(b) the agreement referred to in subparagraph (a) shall cover the specifications and performance of an automatic voltage regulator ('AVR') with regard to steady-state voltage and transient voltage control and the specifications and performance of the excitation control system. The latter shall include:
(i) bandwidth limitation of the output signal to ensure that the highest frequency of response cannot excite torsional oscillations on other power generating modules connected to the network;
(ii) an underexcitation limiter to prevent the AVR from reducing the alternator excitation to a level which would endanger synchronous stability;
(iii) an overexcitation limiter to ensure that the alternator excitation is not limited to less than the maximum value that can be achieved whilst ensuring that the synchronous power generating module is operating within its design limits;
(iv) a stator current limiter; and
(v) a PSS function to attenuate power oscillations, if the synchronous power generating module size is above a value of maximum capacity specified by the relevant TSO. |  | ü |  |  | ü
3. The relevant TSO and the power generating facility owner shall enter into an agreement regarding technical capabilities of the power generating module to aid angular stability under fault conditions. |  | ü |  |  | ü
CHAPTER 3
REQUIREMENTS FOR POWER PARK MODULES
Article 20: Requirements for type B power park modules
1. Type B power park modules shall fulfil the requirements laid down in Articles 13, except for Article 13(2)(b), and Article 14.
2. Type B power park modules shall fulfil the following additional requirements in relation to voltage stability:
(a) with regard to reactive power capability, the relevant system operator shall have the right to specify the capability of a power park module to provide reactive power; |  | ü |  |  | ü
(b) the relevant system operator in coordination with the relevant TSO shall have the right to specify that a power park module be capable of providing fast fault current at the connection point in case of symmetrical (3-phase) faults, under the following conditions: |  | ü |  |  | ü
(i) the power park module shall be capable of activating the supply of fast fault current either by:
– ensuring the supply of the fast fault current at the connection point; or
– measuring voltage deviations at the terminals of the individual units of the power park module and providing a fast fault current at the terminals of these units;
(ii) the relevant system operator in coordination with the relevant TSO shall specify: |  | ü |  |  | ü
– how and when a voltage deviation is to be determined as well as the end of the voltage deviation;
– the characteristics of the fast fault current, including the time domain for measuring the voltage deviation and fast fault current, for which current and voltage may be measured differently from the method specified in Article 2;
– the timing and accuracy of the fast fault current, which may include several stages during a fault and after its clearance;
(c) with regard to the supply of fast fault current in case of asymmetrical (1-phase or 2-phase) faults, the relevant system operator in coordination with the relevant TSO shall have the right to specify a requirement for asymmetrical current injection. |  | ü |  |  | ü
3. Type B power park modules shall fulfil the following additional requirements in relation to robustness:
(a) the relevant TSO shall specify the post-fault active power recovery that the power park module is capable of providing and shall specify: |  | ü |  |  | ü
(i) when the post-fault active power recovery begins, based on a voltage criterion;
(ii) a maximum allowed time for active power recovery; and
(iii) a maximum allowed time for active power recovery; and
(b) the specifications shall be in accordance with the following principles:
(i) interdependency between fast fault current requirements according to points (b) and (c) of paragraph (2) and active power recovery;
(ii) dependence between active power recovery times and duration of voltage deviations;
(iii) a specified limit of the maximum allowed time for active power recovery;
(iv) adequacy between the level of voltage recovery and the minimum magnitude for active power recovery; and
(v) adequate damping of active power oscillations.
Article 21: Requirements for type C power park modules
1. Type C power park modules shall fulfil the requirements listed in Articles 13, except for Article 13(2)(b) and (6), Article 14, except for Article 14(2), Article 15 and Article 20, except for Article 20(2)(a), unless referred to otherwise in point (v) of paragraph (3)(d).
2. Type C power park modules shall fulfil the following additional requirements in relation to frequency stability:
(a) the relevant TSO shall have the right to specify that power park modules be capable of providing synthetic inertia during very fast frequency deviations; |  | ü |  |  | ü
(b) the operating principle of control systems installed to provide synthetic inertia and the associated performance parameters shall be specified by the relevant TSO. |  | ü |  |  | ü
3. Type C power park modules shall fulfil the following additional requirements in relation to voltage stability:
(a) with regard to reactive power capability, the relevant system operator may specify supplementary reactive power to be provided if the connection point of a power park module is neither located at the high-voltage terminals of the step-up transformer to the voltage level of the connection point nor at the convertor terminals, if no step-up transformer exists. This supplementary reactive power shall compensate the reactive power demand of the high-voltage line or cable between the high-voltage terminals of the step-up transformer of the power park module or its convertor terminals, if no step-up transformer exists, and the connection point and shall be provided by the responsible owner of that line or cable. |  | ü |  |  | ü
(b) with regard to reactive power capability at maximum capacity:
(i) the relevant system operator in coordination with the relevant TSO shall specify the reactive power provision capability requirements in the context of varying voltage. To that end, it shall specify a U-Q/Pmax-profile that may take any shape within the boundaries of which the power park module shall be capable of providing reactive power at its maximum capacity; |  | ü |  |  | ü
(ii) the U-Q/Pmax-profile shall be specified by each relevant system operator in coordination with the relevant TSO in conformity with the following principles: |  | ü |  |  | ü
– the U-Q/Pmax-profile shall not exceed the U-Q/Pmax-profile envelope, represented by the inner envelope in Figure 8;
– the dimensions of the U-Q/Pmax-profile envelope (Q/Pmax range and voltage range) shall be within the values specified for each synchronous area in Table 9;
– the position of the U-Q/Pmax-profile envelope shall be within the limits of the fixed outer envelope set out in Figure 8; and
– the specified U-Q/Pmax profile may take any shape, having regard to the potential costs of delivering the capability to provide reactive power production at high voltages and reactive power consumption at low voltages;
Figure 8: U-Q/Pmax-profile of a power park module. The diagram represents boundaries of a U-Q/Pmax-profile by the voltage at the connection point, expressed by the ratio of its actual value and its reference 1 pu value, against the ratio of the reactive power (Q) and the maximum capacity (Pmax). The position, size and shape of the inner envelope are indicative.
Table 9: Parameters for the inner envelope in Figure 8
(iii) the reactive power provision capability requirement applies at the connection point. For profile shapes other than rectangular, the voltage range represents the highest and lowest values. The full reactive power range is therefore not expected to be available across the range of steady-state voltages;
(c) With regard to reactive power capability below maximum capacity:
(i) the relevant system operator in coordination with the relevant TSO shall specify the reactive power provision capability requirements and shall specify a P-Q/Pmax-profile that may take any shape within the boundaries of which the power park module shall be capable of providing reactive power below maximum capacity; |  | ü |  |  | ü
(ii) the P-Q/Pmax-profile shall be specified by each relevant system operator in coordination with the relevant TSO, in conformity with the following principles: |  | ü |  |  | ü
– the P-Q/Pmax-profile shall not exceed the P-Q/Pmax-profile envelope, represented by the inner envelope in Figure 9;
– the Q/Pmax range of the P-Q/Pmax-profile envelope is specified for each synchronous area in Table 9;
– the active power range of the P-Q/Pmax-profile envelope at zero reactive power shall be 1 pu;
– the P-Q/Pmax-profile can be of any shape and shall include conditions for reactive power capability at zero active power; and
– the position of the P-Q/Pmax-profile envelope shall be within the limits of the fixed outer envelope set out in Figure 9;
(iii) when operating at an active power output below maximum capacity (P<Pmax), the power park module shall be capable of providing reactive power at any operating point inside its P-Q/Pmax-profile, if all units of that power park module which generate power are technically available that is to say they are not out of service due to maintenance or failure, otherwise there may be less reactive power capability, taking into consideration the technical availabilities;
Figure 9: P-Q/Pmax-profile of a power park module. The diagram represents boundaries of a P-Q/Pmax-profile at the connection point by the active power, expressed by the ratio of its actual value and the maximum capacity pu, against the ratio of the reactive power (Q) and the maximum capacity (Pmax). The position, size and shape of the inner envelope are indicative.
(iv) the power park module shall be capable of moving to any operating point within its P-Q/Pmax profile in appropriate timescales to target values requested by the relevant system operator; |  | ü |  |  | ü
(d) with regard to reactive power control modes:
(i) the power park module shall be capable of providing reactive power automatically by either voltage control mode, reactive power control mode or power factor control mode;
(ii) for the purposes of voltage control mode, the power park module shall be capable of contributing to voltage control at the connection point by provision of reactive power exchange with the network with a setpoint voltage covering 0.95 to 1.05 pu in steps no greater than 0.01 pu, with a slope having a range of at least 2 to 7 % in steps no greater than 0.5 %. The reactive power output shall be zero when the grid voltage value at the connection point equals the voltage setpoint;
(iii) the setpoint may be operated with or without a deadband selectable in a range from zero to +-5 % of reference 1 pu network voltage in steps no greater than 0.5 %;
(iv) following a step change in voltage, the power park module shall be capable of achieving 90 % of the change in reactive power output within a time t1 to be specified by the relevant system operator in the range of 1 to 5 seconds, and must settle at the value specified by the slope within a time t2 to be specified by the relevant system operator in the range of 5 to 60 seconds, with a steady-state reactive tolerance no greater than 5 % of the maximum reactive power. The relevant system operator shall specify the time specifications; |  | ü |  |  | ü
(v) for the purpose of reactive power control mode, the power park module shall be capable of setting the reactive power setpoint anywhere in the reactive power range, specified by point (a) of Article 20(2) and by points (a) and (b) of Article 21(3), with setting steps no greater than 5 MVAr or 5 % (whichever is smaller) of full reactive power, controlling the reactive power at the connection point to an accuracy within plus or minus 5 MVAr or plus or minus 5 % (whichever is smaller) of the full reactive power;
(vi) for the purpose of power factor control mode, the power park module shall be capable of controlling the power factor at the connection point within the required reactive power range, specified by the relevant system operator according to point (a) of Article 20(2) or specified by points (a) and (b) of Article 18(3), with a target power factor in steps no greater than 0.01. The relevant system operator shall specify the target power factor value, its tolerance and the period of time to achieve the target power factor following a sudden change of active power output. The tolerance of the target power factor shall be expressed through the tolerance of its corresponding reactive power. This reactive power tolerance shall be expressed by either an absolute value or by a percentage of the maximum reactive power of the power park module; |  |  |  |  | ü
(vii) the relevant system operator, in coordination with the relevant TSO and with the power park module owner, shall specify which of the above three reactive power control mode options and associated setpoints is to apply, and what further equipment is needed to make the adjustment of the relevant setpoint operable remotely; |  | ü |  |  | ü
(e) with regard to prioritising active or reactive power contribution, the relevant TSO shall specify whether active power contribution or reactive power contribution has priority during faults for which fault-ride-through capability is required. If priority is given to active power contribution, this provision has to be established no later than 150 ms from the fault inception; |  | ü |  |  | ü
(f) with regard to power oscillations damping control, if specified by the relevant TSO a power park module shall be capable of contributing to damping power oscillations. The voltage and reactive power control characteristics of power park modules must not adversely affect the damping of power oscillations. |  | ü |  |  | ü
Article 22: Requirements for type D power park modules
Type D power park modules shall fulfil the requirements listed in Articles 13, except for Article 13(2)(b) and (6), Article 14, except for Article 14(3), Article 15, except for Article 15(3), Article 16, Article 20 except for Article 20(2)(a) and Article 21.
CHAPTER 4
REQUIREMENTS FOR OFFSHORE POWER PARK MODULES
Article 23: General provisions
1. The requirements set out in this Chapter apply to the connection to the network of AC-connected power park modules located offshore. An AC-connected power park module located offshore which does not have an offshore connection point shall be considered as an onshore power park module and thus shall comply with the requirements governing power park modules situated onshore.
2. The offshore connection point of an AC-connected offshore power park module shall be specified by the relevant system operator. |  | ü |  |  | ü
3. AC-connected offshore power park modules within the scope of this Regulation shall be categorised in accordance with the following offshore grid connection system configurations:
(a) configuration 1: AC connection to a single onshore grid interconnection point whereby one or more offshore power park modules that are interconnected offshore to form an offshore AC system are connected to the onshore system;
(b) configuration 2: Meshed AC connections whereby a number of offshore power park modules are interconnected offshore to form an offshore AC system and the offshore AC system is connected to the onshore system at two or more onshore grid interconnection points.
Article 24: Frequency stability requirements applicable to AC-connected offshore power park modules
The frequency stability requirements laid down respectively in Article 13(1) to (5), except for Article 13(2)(b), Article 15(2) and Article 21(2) shall apply to any AC-connected offshore power park module.
Article 25: Voltage stability requirements applicable to AC-connected offshore power park modules
1. Without prejudice to point (a) of Article 14(3) and point (a) of Article 16(3), an AC-connected offshore power park module shall be capable of staying connected to the network and operating within the ranges of the network voltage at the connection point, expressed by the voltage at the connection point related to reference 1 pu voltage , and for the time periods specified in Table 10.
2. Notwithstanding the provisions of paragraph 1, the relevant TSO in Spain may require AC-connected offshore power park modules to remain connected to the network in the voltage range between 1.05 pu and 1.0875 pu for an unlimited period.
3. Notwithstanding the provisions of paragraph 1, the relevant TSOs in the Baltic synchronous area may require AC-connected offshore power park modules to remain connected at 400 kV network in the voltage range and for the time periods that apply to the Continental Europe synchronous area.
* The voltage base for pu values is below 300 kV.
** The voltage base for pu values is from 300 kV to 400 kV.
Table 10: The table shows the minimum period during which an AC-connected offshore power park module must be capable of operating over different voltage ranges deviating from the reference 1 pu value without disconnecting.
4. The voltage stability requirements specified respectively in points (b) and (c) of Article 20(2) as well as in paragraph 3 of Article 21 shall apply to any AC-connected offshore power park module.
5. The reactive power capability at maximum capacity specified in point (b) of Article 21(3) shall apply to AC-connected offshore power park modules, except for Table 9. Instead, the requirements of Table 11 shall apply.
*) at the offshore connection point for configuration 1
**) at the offshore connection point for configuration 2
Table 11: Parameters for Figure 8
Article 26: Robustness requirements applicable to AC-connected offshore power park modules
1. The robustness requirements of power generating modules laid down in paragraph 4 of Article 15 and paragraph 3 of Article 20 shall apply to AC-connected offshore power park modules.
2. The fault-ride-through capability requirements laid down in point (a) of Article 14(3) and point (a) of Article 16(3) shall apply to AC-connected offshore power park modules.
Article 27: System restoration requirements applicable to AC-connected offshore power park modules
The system restoration requirements laid down respectively in paragraph 4 of Article 14 and paragraph 5 of Article 15 shall apply to AC-connected offshore power park modules.
Article 28: General system management requirements applicable to AC-connected offshore power park modules
The general system management requirements laid down in paragraph 5 of Article 14, paragraph 6 of Article 15 and paragraph 4 of Article 16 shall apply to AC-connected offshore power park modules.
TITLE III
OPERATIONAL NOTIFICATION PROCEDURE FOR CONNECTION
CHAPTER 1
CONNECTION OF NEW POWER GENERATING MODULES
Article 29: General provisions
1. The power generating facility owner shall demonstrate to the relevant system operator that it has complied with the requirements set out in Title II of this Regulation by completing successfully the operational notification procedure for connection of each power generating module described in Articles 30 to 37. |  | ü |  |  | ü
2. The relevant system operator shall clarify and make publicly available the details of the operational notification procedure. |  | ü |  |  | ü
Article 30: Operational notification of type A power generating modules
1. The operational notification procedure for connection of each new type A power generating module shall consist of submitting an installation document. The power generating facility owner shall ensure that the required information is filled in on an installation document obtained from the relevant system operator and is submitted to the system operator. Separate installation documents shall be provided for each power generating module within the power generating facility. |  |  |  |  | ü
The relevant system operator shall ensure that the required information can be submitted by third parties on behalf of the power generating facility owner. |  |  |  |  | ü
2. The relevant system operator shall specify the content of the installation document, which shall have at least the following information: |  |  |  |  | ü
(a) the location at which the connection is made;
(b) the date of the connection;
(c) the maximum capacity of the installation in kW;
(d) the type of primary energy source;
(e) the classification of the power generating module as an emerging technology according to Title VI of this Regulation;
(f) reference to equipment certificates issued by an authorised certifier used for equipment that is in the site installation;
(g) as regards equipment used, for which an equipment certificate has not been received, information shall be provided as directed by the relevant system operator; and |  |  |  |  | ü
(h) the contact details of the power generating facility owner and the installer and their signatures.
3. The power generating facility owner shall ensure that the relevant system operator or the competent authority of the Member State is notified about the permanent decommissioning of a power generating module in accordance with national legislation. |  |  |  |  | ü
The relevant system operator shall ensure that such notification can be made by third parties, including aggregators. |  |  |  |  | ü
Article 31: Operational notification of type B, C and D power generating modules
The operational notification procedure for connection of each new type B, C and D power generating module shall allow the use of equipment certificates issued by an authorised certifier.
Article 32: Procedure for type B and C power generating modules
1. For the purpose of operational notification for connection of each new type B and C power generating module, a power generating module document ('PGMD') shall be provided by the power generating facility owner to the relevant system operator and shall include a statement of compliance. |  |  |  |  | ü
For each power generating module within the power generating facility, separate independent PGMDs shall be provided.
2. The format of the PGMD and the information to be given therein shall be specified by the relevant system operator. The relevant system operator shall have the right to request that the power generating facility owner include the following in the PGMD: |  |  |  |  | ü
(a) evidence of an agreement on the protection and control settings relevant to the connection point between the relevant system operator and the power generating facility owner; |  |  |  |  | ü
(b) itemised statement of compliance;
(c) detailed technical data of the power generating module with relevance to the grid connection as specified by the relevant system operator; |  |  |  |  | ü
(d) equipment certificates issued by an authorised certifier in respect of power generating modules, where these are relied upon as part of the evidence of compliance;
(e) for Type C power generating modules, simulation models pursuant to point (c) of Article 15(6);
(f) compliance test reports demonstrating steady-state and dynamic performance as required by Chapters 2, 3 and 4 of Title IV, including use of actual measured values during testing, to the level of detail required by the relevant system operator; and |  |  |  |  | ü
(g) studies demonstrating steady-state and dynamic performance as required by Chapters 5, 6 or 7 of Title IV, to the level of detail required by the relevant system operator. |  |  |  |  | ü
3. The relevant system operator, on acceptance of a complete and adequate PGMD, shall issue a final operational notification to the power generating facility owner. |  |  |  |  | ü
4. The power generating facility owner shall notify the relevant system operator or the competent authority of the Member State about the permanent decommissioning of a power generating module in accordance with national legislation. |  |  |  |  | ü
5. Where applicable, the relevant system operator shall ensure that the commissioning and decommissioning of Type B and Type C power generating modules can be notified electronically. |  |  |  |  | ü
6. Member States may provide that the PGMD shall be issued by an authorised certifier.
Article 33: Procedure for type D power generating modules
The operational notification procedure for connection of each new type D power generating module shall comprise:
(a) energisation operational notification ('EON');
(b) interim operational notification ('ION'); and
(c) final operational notification ('FON').
Article 34: Energisation operational notification for type D power generating modules
1. An EON shall entitle the power generating facility owner to energise its internal network and auxiliaries for the power generating modules by using the grid connection that is specified for the connection point.
2. An EON shall be issued by the relevant system operator, subject to completion of preparations including agreement on the protection and control settings relevant to the connection point between the relevant system operator and the power generating facility owner. |  | ü |  |  | ü
Article 35: Interim operational notification for type D power generating modules
1. An ION shall entitle the power generating facility owner to operate the power generating module and generate power by using the grid connection for a limited period of time.
2. An ION shall be issued by the relevant system operator, subject to completion of the data and study review process as required by this Article. |  | ü |  |  | ü
3. With regard to the data and study review, the relevant system operator shall have the right to request that the power generating facility owner provide the following: |  | ü |  |  | ü
(a) itemised statement of compliance;
(b) detailed technical data on the power generating module of relevance to the grid connection as specified by the relevant system operator; |  | ü |  |  | ü
(c) equipment certificates issued by an authorised certifier in respect of power generating modules, where they are relied upon as part of the evidence of compliance;
(d) simulation models, as specified by point (c) of Article 15(6) and required by the relevant system operator; |  | ü |  |  | ü
(e) studies demonstrating the expected steady-state and dynamic performance as required by Chapter 5, 6 or 7 of Title IV; and
(f) details of intended compliance tests in accordance with Chapters 2, 3 and 4 of Title IV.
4. The maximum period during which the power generating facility owner may maintain ION status shall be 24 months. The relevant system operator is entitled to specify a shorter ION validity period. An extension of the ION shall be granted only if the power generating facility owner has made substantial progress towards full compliance. Outstanding issues shall be clearly identified at the time of requesting extension. |  | ü |  |  | ü
5. An extension of the period during which the power generating facility owner may maintain ION status, beyond the period established in paragraph 4, may be granted if a request for a derogation is made to the relevant system operator before the expiry of that period in accordance with the derogation procedure laid down in Article 60. |  | ü |  |  | ü
Article 36: Final operational notification for type D power generating modules
1. A FON shall entitle the power generating facility owner to operate a power generating module by using the grid connection.
2. A FON shall be issued by the relevant system operator, upon prior removal of all incompatibilities identified for the purpose of ION status and subject to completion of the data and study review process as required by this Article. |  | ü |  |  | ü
3. For the purposes of the data and study review, the power generating facility owner must submit the following to the relevant system operator: |  | ü |  |  | ü
(a) an itemised statement of compliance; and
(b) an update of applicable technical data, simulation models and studies as referred to in points (b), (d) and (e) of Article 35(3), including the use of actual measured values during testing.
4. If incompatibility is identified in connection with the issuing of the FON, a derogation may be granted upon a request made to the relevant system operator, in accordance with the derogation procedure described in Title V. A FON shall be issued by the relevant system operator if the power generating module complies with the provisions of the derogation. |  | ü |  |  | ü
Where a request for a derogation is rejected, the relevant system operator shall have the right to refuse to allow the operation of the power generating module until the power generating facility owner and the relevant system operator resolve the incompatibility and the relevant system operator considers that the power generating module complies with the provisions of this Regulation. |  | ü |  |  | ü
If the relevant system operator and the power generating facility owner do not resolve the incompatibility within a reasonable timeframe, but in any case not later than six months after the notification of the rejection of the request for a derogation, each party may refer the issue for decision to the regulatory authority. |  | ü |  |  | ü
Article 37: Limited operational notification for type D power generating modules
1. Power generating facility owners to whom a FON has been granted shall inform the relevant system operator immediately in the following circumstances: |  | ü |  |  | ü
(a) the facility is temporarily subject to either significant modification or loss of capability affecting its performance; or
(b) equipment failure leading to non-compliance with some relevant requirements.
2. The power generating facility owner shall apply to the relevant system operator for a LON, if the power generating facility owner reasonably expects the circumstances described in paragraph 1 to persist for more than three months. |  | ü |  |  | ü
3. A LON shall be issued by the relevant system operator and shall contain the following information which shall be clearly identifiable: |  | ü |  |  | ü
(a) the unresolved issues justifying the granting of the LON;
(b) the responsibilities and timescales for the expected solution; and
(c) a maximum period of validity which shall not exceed 12 months. The initial period granted may be shorter with the possibility of an extension if evidence is submitted to the satisfaction of the relevant system operator demonstrating that substantial progress has been made towards achieving full compliance. |  | ü |  |  | ü
4. The FON shall be suspended during the period of validity of the LON with regard to the items for which the LON has been issued.
5. A further extension of the period of validity of the LON may be granted upon a request for a derogation made to the relevant system operator before the expiry of that period, in accordance with the derogation procedure described in Title V. |  | ü |  |  | ü
6. The relevant system operator shall have the right to refuse to allow the operation of the power generating module, once the LON is no longer valid. In such cases, the FON shall automatically become invalid. |  | ü |  |  | ü
7. If the relevant system operator does not grant an extension of the period of validity of the LON in accordance with paragraph 5 or if it refuses to allow the operation of the power generating module once the LON is no longer valid in accordance with paragraph 6, the power generating facility owner may refer the issue for decision to the regulatory authority within six months after the notification of the decision of the relevant system operator. |  | ü |  |  | ü
CHAPTER 2
COST BENEFIT ANALYSIS
Article 38: Identification of costs and benefits of application of requirements to existing power generating modules
1. Prior to the application of any requirement set out in this Regulation to existing power generating modules in accordance with paragraph 3 of Article 4, the relevant TSO shall undertake a qualitative comparison of costs and benefits related to the requirement under consideration. This comparison shall take into account available network-based or market-based alternatives. The relevant TSO may only proceed to undertake a quantitative cost-benefit analysis in accordance with paragraphs 2 to 5, if the qualitative comparison indicates that the likely benefits exceed the likely costs. If, however, the cost is deemed high or the benefit is deemed low, then the relevant TSO shall not proceed further. |  | ü |  |  | ü
2. Following a preparatory stage undertaken in accordance with paragraph 1, the relevant TSO shall carry out a quantitative cost-benefit analysis of any requirement under consideration for application to existing power generating modules that have demonstrated potential benefits as a result of the preparatory stage according to paragraph 1. |  | ü |  |  | ü
3. Within three months of concluding the cost-benefit analysis, the relevant TSO shall summarise the findings in a report which shall: |  | ü |  |  | ü
(a) include the cost-benefit analysis and a recommendation on how to proceed;
(b) include a proposal for a transitional period for applying the requirement to existing power generating modules. That transitional period shall not be more than two years from the date of the decision of the regulatory authority or where applicable the Member State on the requirement’s applicability;
(c) be subject to public consultation in accordance with Article 10.
4. No later than six months after the end of the public consultation, the relevant TSO shall prepare a report explaining the outcome of the consultation and making a proposal on the applicability of the requirement under consideration to existing power generating modules. The report and proposal shall be notified to the regulatory authority or, where applicable, the Member State, and the power generating facility owner or, where applicable, third party shall be informed on its content. |  | ü |  |  | ü
5. The proposal made by the relevant TSO to the regulatory authority or, where applicable, the Member State pursuant to paragraph 4 shall include the following: |  | ü |  |  | ü
(a) an operational notification procedure for demonstrating the implementation of the requirements by the existing power generating facility owner;
(b) a transitional period for implementing the requirements which shall take into account the category of the power generating module as specified in paragraph 2 of Article 5 and paragraph 1 of Article 6 and any underlying obstacles to the efficient implementation of the equipment modification/refitting.
Article 39: Principles of cost-benefit analysis
1. Power generating facility owners and DSOs including CDSOs shall assist and contribute to the cost-benefit analysis undertaken according to Articles 38 and 63 and provide the necessary data as requested by the relevant system operator or relevant TSO within three months of receiving a request, unless agreed otherwise by the relevant TSO. For the preparation of a cost-benefit-analysis by a power generating facility owner, or prospective owner, assessing a potential derogation pursuant to Article 62, the relevant TSO and DSO, including CDSO, shall assist and contribute to the cost-benefit analysis and provide the necessary data as requested by the power generating facility owner, or the prospective owner, within three months of receiving a request, unless agreed otherwise by the power generating facility owner or the prospective owner. |  | ü |  |  | ü
2. A cost-benefit analysis shall be in line with the following principles:
(a) the relevant TSO, power generating facility owner or prospective owner shall base its cost-benefit analysis on one or more of the following calculating principles: |  | ü |  |  | ü
(i) the net present value;
(ii) the return on investment;
(iii) the rate of return;
(iv) the time needed to break even;
(b) the relevant TSO, power generating facility owner or prospective owner shall also quantify socio-economic benefits in terms of improvement in security of supply and shall include at least: |  | ü |  |  | ü
(i) the associated reduction in probability of loss of supply over the lifetime of the modification;
(ii) the probable extent and duration of such loss of supply;
(iii) the societal cost per hour of such loss of supply;
(c) the relevant TSO, power generating facility owner or prospective owner shall quantify the benefits to the internal market in electricity, cross-border trade and integration of renewable energies, including at least: |  | ü |  |  | ü
(i) the active power frequency response;
(ii) the balancing reserves;
(iii) the reactive power provision;
(iv) congestion management;
(v) defence measures;
(d) the relevant TSO, shall quantify the costs of applying the necessary rules to existing power generating modules, including at least: |  | ü |  |  | ü
(i) the direct costs incurred in implementing a requirement;
(ii) the costs associated with attributable loss of opportunity;
(iii) the costs associated with resulting changes in maintenance and operation.
TITLE IV
COMPLIANCE
CHAPTER 1
COMPLIANCE MONITORING
Article 40: Responsibility of the power generating facility owner
1. The power generating facility owner shall ensure that each power generating module complies with the requirements applicable under this Regulation throughout the lifetime of the facility. For type A power generating modules, the power generating facility owner may rely upon equipment certificates, issued as per Regulation (EC) No 765/2008.
2. The power generating facility owner shall notify to the relevant system operator any planned modification of the technical capabilities of a power generating module which may affect its compliance with the requirements applicable under this Regulation, before initiating that modification. |  | ü |  |  | ü
3. The power generating facility owner shall notify the relevant system operator of any operational incidents or failures of a power generating module that affect its compliance with the requirements of this Regulation, without undue delay, after the occurrence of those incidents. |  | ü |  |  | ü
4. The power generating facility owner shall notify the relevant system operator of the planned test schedules and procedures to be followed for verifying the compliance of a power generating module with the requirements of this Regulation, in due time and prior to their launch. The relevant system operator shall approve in advance the planned test schedules and procedures. Such approval by the relevant system operator shall be provided in a timely manner and shall not be unreasonably withheld. |  | ü |  |  | ü
5. The relevant system operator may participate in such tests and record the performance of the power generating modules. |  | ü |  |  | ü
Article 41: Tasks of the relevant system operator
1. The relevant system operator shall assess the compliance of a power generating module with the requirements applicable under this Regulation, throughout the lifetime of the power generating facility. The power generating facility owner shall be informed of the outcome of this assessment. For type A power generating modules, the relevant system operator may rely upon equipment certificates issued by an authorised certifier for this assessment. |  | ü |  |  | ü
2. The relevant system operator shall have the right to request that the power generating facility owner carry out compliance tests and simulations according to a repeat plan or general scheme or after any failure, modification or replacement of any equipment that may have an impact on the power generating module’s compliance with the requirements of this Regulation. The power generating facility owner shall be informed of the outcome of those compliance tests and simulations. |  | ü |  |  | ü
3. The relevant system operator shall make publicly available a list of information and documents to be provided as well as the requirements to be fulfilled by the power generating facility owner within the framework of the compliance process. The list shall cover at least the following: |  | ü |  |  | ü
(a) all the documentation and certificates to be provided by the power generating facility owner;
(b) details of the technical data on the power generating module of relevance to the grid connection;
(c) requirements for models for steady-state and dynamic system studies;
(d) timeline for the provision of system data required to perform the studies;
(e) studies by the power generating facility owner to demonstrate the expected steady-state and dynamic performance in accordance with the requirements set out in Chapters 4 and 5 of Title IV;
(f) conditions and procedures, including the scope, for registering equipment certificates; and
(g) conditions and procedures for the use of relevant equipment certificates issued by an authorised certifier by the power generating facility owner.
4. The relevant system operator shall make public the allocation of responsibilities between the power generating facility owner and the system operator for compliance testing, simulation and monitoring. |  | ü |  |  | ü
5. The relevant system operator may totally or partially delegate the performance of its compliance monitoring to third parties. In such cases, the relevant system operator shall continue ensuring compliance with Article 12, including entering into confidentiality commitments with the assignee. |  | ü |  |  | ü
6. If compliance tests or simulations cannot be carried out as agreed between the relevant system operator and the power generating facility owner due to reasons attributable to the relevant system operator, then the relevant system operator shall not unreasonably withhold the operational notification referred to in Title III. |  | ü |  |  | ü
Article 42: Common provisions for compliance testing
1. Testing of the performance of individual power generating modules within a power generating facility shall aim at demonstrating that the requirements of this Regulation have been complied with.
2. Notwithstanding the minimum requirements for compliance testing set out in this Regulation, the relevant system operator is entitled to: |  | ü |  |  | ü
(a) allow the power generating facility owner to carry out an alternative set of tests, provided that those tests are efficient and suffice to demonstrate that a power generating module complies with the requirements of this Regulation;
(b) require the power generating facility owner to carry out additional or alternative sets of tests in those cases where the information supplied to the relevant system operator in relation to compliance testing under the provisions of Chapter 2, 3 or 4 of Title IV, is not sufficient to demonstrate compliance with the requirements of this Regulation; and |  | ü |  |  | ü
(c) require the power generating facility owner to carry out appropriate tests in order to demonstrate a power generating module’s performance when operating on alternative fuels or fuel mixes. The relevant system operator and the power generating facility owner shall agree on which types of fuel are to be tested. |  | ü |  |  | ü
3. The power generating facility owner is responsible for carrying out the tests in accordance with the conditions laid down in Chapters 2, 3 and 4 of Title IV. The relevant system operator shall cooperate and not unduly delay the performance of the tests. |  | ü |  |  | ü
4. The relevant system operator may participate in the compliance testing either on site or remotely from the system operator’s control centre. For that purpose, the power generating facility owner shall provide the monitoring equipment necessary to record all relevant test signals and measurements as well as ensure that the necessary representatives of the power generating facility owner are available on site for the entire testing period. Signals specified by the relevant system operator shall be provided if, for selected tests, the system operator wishes to use its own equipment to record performance. The relevant system operator has sole discretion to decide about its participation. |  | ü |  |  | ü
Article 43: Common provisions on compliance simulation
1. Simulation of the performance of individual power generating modules within a power generating facility shall aim at demonstrating that the requirements of this Regulation have been fulfilled.
2. Notwithstanding the minimum requirements set out in this Regulation for compliance simulation, the relevant system operator may: |  | ü |  |  | ü
(a) allow the power generating facility owner to carry out an alternative set of simulations, provided that those simulations are efficient and suffice to demonstrate that a power generating module complies with the requirements of this Regulation or with national legislation; and
(b) require the power generating facility owner to carry out additional or alternative sets of simulations in those cases where the information supplied to the relevant system operator in relation to compliance simulation under the provisions of Chapter 5, 6 or 7 of Title IV, is not sufficient to demonstrate compliance with the requirements of this Regulation. |  | ü |  |  | ü
3. To demonstrate compliance with the requirements of this Regulation, the power generating facility owner shall provide a report with the simulation results for each individual power generating module within the power generating facility. The power generating facility owner shall produce and provide a validated simulation model for a given power generating module. The scope of the simulation models is set out in point (c) of Article 15(6).
4. The relevant system operator shall have the right to check that a power generating module complies with the requirements of this Regulation by carrying out its own compliance simulations based on the provided simulation reports, simulation models and compliance test measurements. |  | ü |  |  | ü
5. The relevant system operator shall provide the power generating facility owner with technical data and a simulation model of the network, to the extent necessary to carry out the requested simulations in accordance with Chapter 5, 6 or 7 of Title IV. |  | ü |  |  | ü
CHAPTER 2
COMPLIANCE TESTING FOR SYNCHRONOUS POWER GENERATING MODULES
Article 44: Compliance tests for type B synchronous power generating modules
1. Power generating facility owners shall undertake LFSM-O response compliance tests in relation to type B synchronous power generating modules.
Instead of carrying out the relevant test, power generating facility owners may rely upon equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In such a case, the equipment certificate shall be provided to the relevant system operator. |  | ü |  |  | ü
2. The following requirements with regard to the LFSM-O response test shall apply:
(a) the power generating module’s technical capability to continuously modulate active power to contribute to frequency control in case of any large increase of frequency in the system shall be demonstrated. The steady-state parameters of regulations, such as droop and deadband, and dynamic parameters, including frequency step change response shall be verified;
(b) the test shall be carried out by simulating frequency steps and ramps big enough to trigger at least 10 % of maximum capacity change in active power, taking into account the droop settings and the deadband. If required, simulated frequency deviation signals shall be injected simultaneously at both the speed governor and load controller of the control systems, taking into account the scheme of those control systems;
(c) The test shall be deemed successful if the following conditions are fulfilled:
(i) the test results, for both dynamic and static parameters, meet the requirements set out in paragraph 2 of Article 13; and
(ii) undamped oscillations do not occur after the step change response.
Article 45: Compliance tests for type C synchronous power generating modules
1. In addition to the compliance tests for type B synchronous power generating modules described in Article 44, power generating facility owners shall undertake the compliance tests set out in paragraphs 2, 3, 4 and 6 of this Article in relation to type C synchronous power generating modules. Where a power generating module provides black start capability, power generating facility owners shall also undertake the tests referred to in paragraph 5. Instead of the relevant test, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In that case, the equipment certificate shall be provided to the relevant system operator. |  | ü |  |  | ü
2. The following requirements with regard to the LFSM-U response test shall apply:
(a) it shall demonstrate that the power generating module is technically capable of continuously modulating active power at operating points below maximum capacity to contribute to frequency control in case of a large frequency drop in the system;
(b) the test shall be carried out by simulating appropriate active power load points, with low frequency steps and ramps big enough to trigger active power change of at least 10 % of maximum capacity, taking into account the droop settings and the deadband. If required, simulated frequency deviation signals shall be injected simultaneously into both the speed governor and the load controller references;
(c) the test shall be deemed successful if the following conditions are fulfilled:
(i) the test results, for both dynamic and static parameters, comply with point (c) of Article 15(2); and
(ii) undamped oscillations do not occur after the step change response.
3. The following requirements with regard to the FSM response test shall apply:
(a) it shall demonstrate that the power generating module is technically capable of continuously modulating active power over the full operating range between maximum capacity and minimum regulating level to contribute to frequency control. The steady-state parameters of regulations, such as droop and deadband and dynamic parameters, including robustness through frequency step change response and large, fast frequency deviations shall be verified;
(b) the test shall be carried out by simulating frequency steps and ramps big enough to trigger the whole active power frequency response range, taking into account the settings of droop and deadband, as well as the capability to actually increase or decrease active power output from the respective operating point. If required, simulated frequency deviation signals shall be injected simultaneously into the references of both the speed governor and the load controller of the unit or plant control system.
(c) The test shall be deemed successful if the following conditions are fulfilled:
(i) the activation time of full active power frequency response range as a result of a frequency step change is no longer than required by point (d) of Article 15(2);
(ii) undamped oscillations do not occur after the step change response;
(iii) the initial delay time complies with point (d) of Article 15(2);
(iv) the droop settings are available within the range specified in point (d) of Article 15(2) and the deadband (threshold) is not higher than the value specified in that Article; and
(v) the insensitivity of active power frequency response at any relevant operating point does not exceed the requirements set out in point (d) of Article 15(2).
4. With regard to the frequency restoration control test the following requirements shall apply:
(a) the power generating module’s technical capability to participate in frequency restoration control shall be demonstrated and the cooperation of FSM and frequency restoration control shall be checked;
(b) the test shall be deemed successful if the results, for both dynamic and static parameters, comply with the requirements of point (e) of Article 15(2).
5. With regard to the black start capability test the following requirements shall apply:
(a) for power generating modules with black start capability, this technical capability to start from shut down without any external electrical energy supply shall be demonstrated;
(b) the test shall be deemed successful if the start-up time is kept within the timeframe set out in point (iii) of Article 15(5)(a).
6. With regard to the tripping to houseload test the following requirements shall apply:
(a) the power generating modules’ technical capability to trip to and stably operate on house load shall be demonstrated;
(b) the test shall be carried out at the maximum capacity and nominal reactive power of the power generating module before load shedding;
(c) the relevant system operator shall have the right to set additional conditions , taking into account point (c) of Article 15(5); |  | ü |  |  | ü
(d) the test shall be deemed successful if tripping to house load is successful, stable houseload operation has been demonstrated in the time period set out in point (c) of Article 15(5) and re-synchronisation to the network has been performed successfully.
7. With regard to the reactive power capability test the following requirements shall apply:
(a) the power generating module’s technical capability to provide leading and lagging reactive power capability in accordance with points (b) and (c) of Article 18(2) shall be demonstrated;
(b) the test shall be deemed successful if the following conditions are fulfilled:
(i) the power generating module operates at maximum reactive power for at least one hour, both leading and lagging, at:
– minimum stable operating level;
– maximum capacity; and
– an active power operating point between those maximum and minimum levels;
(ii) the power generating module’s capability to change to any reactive power target value within the agreed or decided reactive power range shall be demonstrated.
Article 46: Compliance tests for type D synchronous power generating modules
1. Type D synchronous power generating modules are subject to the compliance tests for type B and C synchronous power generating modules described in Articles 44 and 45.
2. Instead of the relevant test, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In such a case, the equipment certificates shall be provided to the relevant system operator. |  | ü |  |  | ü
CHAPTER 3
COMPLIANCE TESTING FOR POWER PARK MODULES
Article 47: Compliance tests for type B power park modules
1. Power generating facility owners shall undertake LFSM-O response compliance tests in relation to type B power park modules.
Instead of the relevant test, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In that case, the equipment certificate shall be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to type B power park modules, the LFSM-O response tests shall reflect the choice of control scheme selected by the relevant system operator. |  | ü |  |  | ü
3. With regard to the LFSM-O response tests the following requirements shall apply:
(a) the power park module’s technical capability to continuously modulate active power to contribute to frequency control in case of increase of frequency in the system shall be demonstrated. The steady-state parameters of regulations, such as droop and deadband, and dynamic parameters shall be verified;
(b) the test shall be carried out by simulating frequency steps and ramps big enough to trigger at least 10 % of maximum capacity change in active power, taking into account the droop settings and the deadband. To perform this test simulated frequency deviation signals shall be injected simultaneously into the references of both the speed governor and the load controller of the unit or plant control system.
(c) The test shall be deemed successful in the event that the test results, for both dynamic and static parameters, comply with the requirements set out in paragraph 2 of Article 13.
Article 48: Compliance tests for type C power park modules
1. In addition to the compliance tests for type B power park modules described in Article 47, power generating facility owners shall undertake the compliance tests set out in paragraphs 2 to 9 in relation to type C power park modules. Instead of the relevant test, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In such a case, the equipment certificate shall be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the active power controllability and control range test the following requirements shall apply:
(a) the power park module’s technical capability to operate at a load level below the setpoint set by the relevant system operator or the relevant TSO shall be demonstrated. |  | ü |  |  | ü
(b) the test shall be deemed successful if the following conditions are fulfilled:
(i) the load level of the power park module is kept below the setpoint;
(ii) the setpoint is implemented according to the requirements laid down in Article 15(2) (a); and
(iii) the accuracy of the regulation complies with the value specified in point (a) of Article 15(2).
3. With regard to the LFSM-U response test the following requirements shall apply:
(a) the power park module’s technical capability to continuously modulate active power to contribute to frequency control in case of a large frequency drop in the system shall be demonstrated;
(b) the test shall be carried out by simulating the frequency steps and ramps big enough to trigger at least 10 % of maximum capacity active power change with a starting point of no more than 80 % of maximum capacity, taking into account the droop settings and the deadband.
(c) the test shall be deemed successful if the following conditions are fulfilled:
(i) the test results, for both dynamic and static parameters, comply with the requirements laid down in Article 15(2) (c); and
(ii) undamped oscillations do not occur after the step change response.
4. With regard to the FSM response test the following requirements shall apply:
(a) the power park module’s technical capability to continuously modulate active power over the full operating range between maximum capacity and minimum regulating level to contribute to frequency control shall be demonstrated. The steady-state parameters of regulations, such as insensitivity, droop, deadband and range of regulation, as well as dynamic parameters, including frequency step change response shall be verified;
(b) the test shall be carried out by simulating frequency steps and ramps big enough to trigger the whole active power frequency response range, taking into account the droop settings and the deadband. Simulated frequency deviation signals shall be injected to perform the test.
(c) The test shall be deemed successful if the following conditions are fulfilled:
(i) the activation time of the full active power frequency response range as a result of a frequency step change is no longer than that required by point (d) of Article 15(2);
(ii) undamped oscillations do not occur after the step change response;
(iii) the initial delay is in line with point (d) of Article 15(2);
(iv) the droop settings are available within the ranges specified in point (d) of Article 15(2) and the deadband (threshold) is not higher than the value chosen by the relevant TSO; and |  | ü |  |  | ü
(v) the insensitivity of active power frequency response does not exceed the requirement set out in point (d) of Article 15(2).
5. With regard to the frequency restoration control test the following requirements shall apply:
(a) the power park module’s technical capability to participate in frequency restoration control shall be demonstrated. The cooperation of both FSM and frequency restoration control shall be checked;
(b) the test shall be deemed successful if the results for both dynamic and static parameters comply with the requirements of point (e) of Article 15(2).
6. With regard to the reactive power capability test the following requirements shall apply:
(a) the power park module’s technical capability to provide leading and lagging reactive power capability in accordance with points (b) and (c) of Article 21(3) shall be demonstrated;
(b) it shall be carried out at maximum reactive power, both leading and lagging, and shall verify the following parameters:
(i) operation in excess of 60 % of maximum capacity for 30 min;
(ii) operation within the range of 30 – 50 % of maximum capacity for 30 min; and
(iii) operation within the range of 10 – 20 % of maximum capacity for 60 min;
(c) the test shall be deemed successful if the following criteria are fulfilled:
(i) the power park module operates for a duration no shorter than the requested duration at maximum reactive power, both leading and lagging, in each parameter specified in paragraph (6) (b);
(ii) the power park module’s capability to change to any reactive power target value within the agreed or decided reactive power range; and
(iii) no protection action takes place within the operation limits specified by the reactive power capacity diagram.
7. With regard to the voltage control mode test the following requirements shall apply:
(a) the power park module’s capability to operate in voltage control mode referred to in the conditions set out in points (ii) to (iv) of Article 21(3) (d) shall be demonstrated;
(b) The voltage control mode test shall verify the following parameters:
(i) the implemented slope and deadband according to Article 21(3)(d)(iii);
(ii) the accuracy of the regulation;
(iii) the insensitivity of the regulation; and
(iv) the time of reactive power activation;
(c) The test shall be deemed successful if the following conditions are fulfilled:
(i) the range of regulation and adjustable droop and deadband complies with the agreed or decided characteristic parameters set out in point (d) of Article 21(3);
(ii) the insensitivity of voltage control is not higher than 0.01 pu, in accordance with point (d) of Article 21(3); and
(iii) following a step change in voltage, 90 % of the change in reactive power output has been achieved within the times and tolerances specified in point (d) of Article 21(3).
8. With regard to the reactive power control mode test the following requirements shall apply:
(a) the power park module’s capability to operate in reactive power control mode, in accordance with point (v) of Article 21(3) (d), shall be demonstrated;
(b) the reactive power control mode test shall be complementary to the reactive power capability test;
(c) the reactive power control mode test shall verify the following parameters:
(i) the reactive power setpoint range and increment;
(ii) the accuracy of the regulation; and
(iii) the time of reactive power activation.
(d) the test shall be deemed successful if the following conditions are fulfilled:
(i) the reactive power setpoint range and increment are ensured in accordance with point (d) of Article 21(3); and
(ii) the accuracy of the regulation complies with the conditions set out in point (d) of Article 21(3).
9. With regard to the power factor control mode test the following requirements shall apply:
(a) the power park module’s capability to operate in power factor control mode in accordance with point (vi) of Article 21(3) (d) shall be demonstrated;
(b) the power factor control mode test shall verify the following parameters:
(i) the power factor setpoint range;
(ii) the accuracy of the regulation; and
(iii) the response of reactive power due to step change of active power;
(c) the test shall be deemed successful if the following conditions are cumulatively fulfilled:
(i) the power factor setpoint range and increment are ensured in accordance with point (d) of Article 21(3);
(ii) the time of reactive power activation as a result of step active power change does not exceed the requirement laid down in point (d) of Article 21(3); and
(iii) the accuracy of the regulation complies with the value specified in point (d) of Article 21(3).
10. With regard to the tests referred to in paragraphs 7, 8 and 9, the relevant system operator may select only one of the three control options for testing. |  | ü |  |  | ü
Article 49: Compliance tests for type D power park modules
1. Type D power park modules are subject to the compliance tests for type B and C power park modules in accordance with the conditions set out in Articles 47 and 48.
2. Instead of the relevant test, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In that case, the equipment certificates shall be provided to the relevant system operator. |  | ü |  |  | ü
CHAPTER 4
COMPLIANCE TESTING FOR OFFSHORE POWER PARK MODULES
Article 50: Compliance tests for offshore power park modules
The compliance tests established in paragraph 2 of Article 44, as well as in paragraphs (2), (3), (4), (5), (7), (8) and (9) of Article 48 shall apply to offshore power park modules.
CHAPTER 5
COMPLIANCE SIMULATIONS FOR SYNCHRONOUS POWER GENERATING MODULES
Article 51: Compliance simulations for type B synchronous power generating modules
1. Power generating facility owners shall undertake LFSM-O response simulations in relation to type B synchronous power generating modules. Instead of the relevant simulations, the power generating facility owner may use equipment certificates issued by an authorised certifier to demonstrate compliance with the relevant requirement. In that case, the equipment certificates shall be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the LFSM-O response simulation the following requirements shall apply:
(a) the power generating module’s capability to modulate active power at high frequency in accordance with paragraph 2 of Article 13 shall be demonstrated by simulation;
(b) the simulation shall be carried out by means of high frequency steps and ramps reaching minimum regulating level, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power generating module is validated against the compliance test for LFSM-O response described in paragraph 2 of Article 44; and
(ii) compliance with the requirement set out in paragraph 2 of Article 13 is demonstrated.
3. With regard to the simulation of fault-ride-through capability of type B synchronous power generating modules, the following requirements shall apply:
(a) the power generating module’s capability to ride through faults in accordance with the conditions set out in subparagraph (a) of Article 14(3) shall be demonstrated by simulation;
(b) the simulation shall be deemed successful if compliance with the requirement set out in point (a) of Article 14(3) is demonstrated.
4. With regard to the post fault active power recovery simulation the following requirements shall apply:
(a) the power generating module’s capability to provide post fault active power recovery referred to in the conditions set out in paragraph 3 of Article 17 shall be demonstrated;
(b) the simulation shall be deemed successful if compliance with the requirement set out in paragraph 3 of Article 17 is demonstrated.
Article 52: Compliance simulations for type C synchronous power generating modules
1. In addition to the compliance simulations for type B synchronous power generating modules set out in Article 51, type C synchronous power generating modules shall be subject to the compliance simulations detailed in paragraphs 2 to 5. Instead of all or part of those simulations, the power generating facility owner may use equipment certificates issued by an authorised certifier, which must be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the LFSM-U response simulation the following requirements shall apply:
(a) the power generating module’s capability to modulate active power at low frequencies in accordance with point (c) of Article 15(2) shall be demonstrated;
(b) the simulation shall be carried out by means of low frequency steps and ramps reaching maximum capacity, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power generating module is validated against the compliance test for LFSM-U response described in paragraph 2 of Article 45; and
(ii) compliance with the requirement of point (c) of Article 15(2) is demonstrated.
3. With regard to the FSM response simulation the following requirements shall apply:
(a) the power generating module’s capability to modulate active power over the full frequency range in accordance with point (d) of Article 15(2) shall be demonstrated;
(b) the simulation shall be carried out by simulating frequency steps and ramps big enough to trigger the whole active power frequency response range, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power generating module is validated against the compliance test for FSM response described in paragraph 3 of Article 42; and
(ii) compliance with the requirement of point (d) of Article 15(2) is demonstrated.
4. With regard to the island operation simulation the following requirements shall apply:
(a) the power generating module’s performance during island operation referred to in the conditions set out in point (b) of Article 15(5) shall be demonstrated;
(b) the simulation shall be deemed successful if the power generating module reduces or increases the active power output from its previous operating point to any new operating point within the P-Q-capability diagram within the limits of point (b) of Article 15(5), without disconnection of the power generating module from the island due to over or under-frequency.
5. With regard to the reactive power capability simulation the following requirements shall apply:
(a) the power generating module’s capability to provide leading and lagging reactive power capability in accordance with the conditions set out in points (b) and (c) of Article 18(2) shall be demonstrated;
(b) the simulation shall be deemed successful if the following conditions are fulfilled:
(i) the simulation model of the power generating module is validated against the compliance tests for reactive power capability described in paragraph 7 of Article 45; and
(ii) compliance with the requirements of points (b) and (c) of Article 18(2) is demonstrated.
Article 53: Compliance simulations for type D synchronous power generating modules
1. In addition to the compliance simulations for type B and C synchronous power generating modules set out in Articles 51 and 52, except for the simulation of fault-ride-through capability of type B synchronous power generating modules referred to in paragraph 3 of Article 51, type D synchronous power generating modules are subject to the compliance simulations set out in paragraphs 2 and 3. Instead of all or part of those simulations, the power generating facility owner may use equipment certificates issued by an authorised certifier, which must be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the power oscillations damping control simulation the following requirements shall apply:
(a) it shall be demonstrated that the power generating module’s performance in terms of its control system ('PSS function') is capable of damping active power oscillations in accordance with the conditions set out in paragraph 2 of Article 19;
(b) the tuning must result in improved damping of corresponding active power response of the AVR in combination with the PSS function, compared to the active power response of the AVR alone;
(c) The simulation shall be deemed successful if the following conditions are cumulatively fulfilled:
(i) the PSS function damps the existing active power oscillations of the power generating module within a frequency range specified by the relevant TSO. That frequency range shall include the local mode frequencies of the power generating module and the expected network oscillations; and |  | ü |  |  | ü
(ii) a sudden load reduction of the power generating module from 1 p.u. to 0.6 p.u. of the maximum capacity does not lead to undamped oscillations in active or reactive power of the power generating module.
3. With regard to the simulation of fault-ride-through capability of type D synchronous power generating modules, the following requirements shall apply:
(a) the power generating module’s capability to provide fault-ride-through in accordance with the conditions set out in point (a) of Article 16(3) shall be demonstrated;
(b) the simulation shall be deemed successful if compliance with the requirement laid down in point (a) of Article 16(3) is demonstrated.
CHAPTER 6
COMPLIANCE SIMULATIONS FOR POWER PARK MODULES
Article 54: Compliance simulations for type B power park modules
1. Type B power park modules are subject to the compliance simulations in paragraphs 2 to 5. Instead of all or part of those simulations, the power generating facility owner may use equipment certificates issued by an authorised certifier, which must be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the LFSM-O response simulation the following requirements shall apply:
(a) the power park module’s capability to modulate active power at high frequency in accordance with paragraph 2 of Article 13 shall be demonstrated;
(b) the simulation shall be carried out by means of high frequency steps and ramps reaching minimum regulating level, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power park module is validated against the compliance test for LFSM-O response set out in paragraph 2 of Article 47; and
(ii) the simulation model of the power park module is validated against the compliance test for LFSM-O response set out in paragraph 2 of Article 47; and
3. With regard to the fast fault current injection simulation the following requirements shall apply:
(a) the power park module’s capability to provide fast fault current injection in accordance with the conditions set out in point (b) of Article 20(2) shall be demonstrated;
(b) the simulation shall be deemed successful if compliance with the requirement laid down in point (b) of Article 20(2) is demonstrated.
4. With regard to the fault-ride-through simulation capability of type B power park modules, the following requirements shall apply:
(a) the power park module’s capability to ride through faults in accordance with the conditions set out in point (a) of Article 14(3) shall be demonstrated by simulation;
(b) the simulation shall be deemed successful if compliance with the requirement laid down in point (a) of Article 14(3) is demonstrated.
5. The following requirements with regard to the post fault active power recovery simulation shall apply:
(a) the power park module’s capability to provide post fault active power recovery in accordance with the conditions set out in paragraph 3 of Article 20 shall be demonstrated;
(b) the simulation shall be deemed successful if compliance with the requirement laid down in paragraph 3 of Article 20 is demonstrated.
Article 55: Compliance simulations for type C power park modules
1. In addition to the compliance simulations for type B power park modules set out in Article 54, type C power park modules are subject to the compliance simulations set out in paragraphs 2 to 7. Instead of all or part of those simulations, the power generating facility owner may use equipment certificates issued by an authorised certifier, which must be provided to the relevant system operator. |  | ü |  |  | ü
2. With regard to the LFSM-U response simulation the following requirements shall apply:
(a) the power park module’s capability to modulate active power at low frequencies in accordance with point (c) of Article 15(2) shall be demonstrated;
(b) the simulation shall be carried out by simulating low frequency steps and ramps reaching maximum capacity, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power park module is validated against the compliance test for LFSM-U response set out in paragraph 3 of Article 48; and
(ii) compliance with the requirement laid down in point (c) of Article 15(2) is demonstrated.
3. With regard to the FSM response simulation the following requirements shall apply:
(a) the power park module’s capability to modulate active power over the full frequency range as referred to in point (d) of Article 15(2) shall be demonstrated;
(b) the simulation shall be carried out by simulating frequency steps and ramps big enough to trigger the whole active power frequency response range, taking into account the droop settings and the deadband;
(c) the simulation shall be deemed successful in the event that:
(i) the simulation model of the power park module is validated against the compliance test for FSM response set out in paragraph 4 of Article 48; and
(ii) compliance with the requirement laid down in point (d) of Article 15(2) is demonstrated.
4. With regard to the island operation simulation, the following requirements shall apply:
(a) the power park module’s performance during island operation in accordance with the conditions set out in point (b) of Article 15(5) shall be demonstrated;
(b) the simulation shall be deemed successful in the event that the power park module reduces or increases the active power output from its previous operating point to any new operating point, within the P-Q-capability diagram and within the limits set out in point (b) of Article 15(5), without disconnection of the power park module from the island due to over-/underfrequency.
5. With regard to the simulation of the capability of providing synthetic inertia, the following requirements shall apply:
(a) the model of the power park module's capability of providing synthetic inertia to a low frequency event as set out in point (a) of Article 21(2) shall be demonstrated;
(b) the simulation shall be deemed successful if the model demonstrates that it complies with the conditions set out in paragraph 2 of Article 21.
6. With regard to the reactive power capability simulation, the following requirements shall apply:
(a) the power park module shall demonstrate that it can provide leading and lagging reactive power capability as set out in points (b) and (c) of Article 21(3).
(b) the simulation shall be deemed successful if the following conditions are cumulatively fulfilled:
(i) the simulation model of the power park module is validated against the compliance tests for reactive power capability set out in paragraph (6) of Article 48; and
(ii) compliance with the requirements laid down in points (b) and (c) of Article 21(3) is demonstrated.
7. With regard to the power oscillations damping control simulation, the following requirements shall apply:
(a) the model of the power park module shall demonstrate that it can provide active power oscillations damping capability accordance with point (f) of Article 21(3);
(b) the simulation shall be deemed successful in the event that the model demonstrates compliance with the conditions described in point (f) of Article 21(3).
Article 56: Compliance simulations for type D power park modules
1. In addition to the compliance simulations for type B and C power park modules set out in Articles 54 and 55, except for the fault-ride-through capability of type B power park modules referred to in paragraph 4 of Article 54, type D power park modules are subject to the fault-ride-through capability of power park modules compliance simulation.
2. Instead of all or part of the simulations mentioned in paragraph 1, the power generating facility owner may use equipment certificates issued by an authorised certifier, which must be provided to the relevant system operator. |  | ü |  |  | ü
3. The model of the power park module shall demonstrate that it is suitable for simulating the fault-ride-through capability in accordance with point (a) of Article 16(3).
4. The simulation shall be deemed successful if the model demonstrates compliance with the conditions set out in point (a) of Article 16(3).
CHAPTER 7
COMPLIANCE SIMULATIONS FOR OFFSHORE POWER PARK MODULES
Article 57: Compliance simulations applicable to offshore power park modules
The compliance simulations specified in paragraphs 3 and 5 of Article 54 as well as in paragraphs 4, 5 and 7 of Article 55 shall apply to any offshore power park module.
CHAPTER 8
Non-binding guidance and Monitoring OF implementation
Article 58: Non-binding guidance on implementation
1. No later than six months after the entry into force of this Regulation, the ENTSO for Electricity shall prepare and thereafter every two years provide non-binding written guidance to its members and other system operators concerning the elements of this Regulation requiring national decisions. The ENTSO for Electricity shall publish this guidance on its website. |  | ü |  |  | ü
2. ENTSO for Electricity shall consult stakeholders when providing non-binding guidance.
3. The non-binding guidance shall explain the technical issues, conditions and interdependencies which need to be considered when complying with the requirements of this Regulation at national level.
Article 59: Monitoring
1. ENTSO for Electricity shall monitor the implementation of this Regulation in accordance with Article 8(8) of Regulation (EC) No 714/2009. Monitoring shall cover in particular the following matters:
(a) identification of any divergences in the national implementation of this Regulation;
(b) assessment of whether the choice of values and ranges in the requirements applicable to power generating modules under this Regulation continues to be valid.
2. The Agency, in cooperation with ENTSO for Electricity, shall produce by 12 months after the entry into force of this Regulation a list of the relevant information to be communicated by ENTSO for Electricity to the Agency in accordance with Article 8(9) and Article 9(1) of Regulation (EC) No 714/2009. The list of relevant information may be subject to updates. ENTSO for Electricity shall maintain a comprehensive, standardised format, digital data archive of the information required by the Agency.
3. Relevant TSOs shall submit to ENTSO for Electricity the information required to perform the tasks referred to in paragraphs 1 and 2. Based on a request of the regulatory authority, DSOs shall provide TSOs with information under paragraph 2 unless the information is already obtained by regulatory authorities, the Agency or ENTSO-E in relation to their respective implementation monitoring tasks, with the objective of avoiding duplication of information. |  | ü |  |  | ü
4. Where ENTSO for Electricity or the Agency establish areas subject to this Regulation where, based on market developments or experience gathered in the application of this Regulation, further harmonisation of the requirements under this Regulation is advisable to promote market integration, they shall propose draft amendments to this Regulation pursuant to Article 7 (1) of Regulation (EC) No 714/2009.
TITLE V
DEROGATIONS
Article 60: Power to grant derogations
1. Regulatory authorities may, at the request of a power generating facility owner or prospective owner, relevant system operator or relevant TSO, grant power generating facility owners or prospective owners, relevant system operators or relevant TSOs derogations from one or more provisions of this Regulation for new and existing power generating modules in accordance with Articles 61 to 63. | ü | ü | ü | ü | ü
2. Where applicable in a Member State, derogations may be granted and revoked in accordance with Articles 61 to 63 by other authorities than the regulatory authority.
Article 61: General provisions
1. Each regulatory authority shall specify, after consulting relevant system operators and power generating facility owners and other stakeholders whom it deems affected by this Regulation, the criteria for granting derogations pursuant to Articles 62 and 63. It shall publish those criteria on its website and notify them to the Commission within nine months of the entry into force of this Regulation. The Commission may require a regulatory authority to amend the criteria if it considers that they are not in line with this Regulation. This possibility to review and amend the criteria for granting derogations shall not affect the derogations already granted which shall continue to apply until the scheduled expiry date as detailed in the decision granting the exemption.
2. If the regulatory authority deems that it is necessary due to a change in circumstances relating to the evolution of system requirements, it may review and amend at most once every year the criteria for granting derogations in accordance with paragraph 1. Any changes to the criteria shall not apply to derogations for which a request has already been made.
3. The regulatory authority may decide that power generating modules for which a request for a derogation has been filed pursuant to Articles 62 or 63 do not need to comply with the requirements of this Regulation from which a derogation has been sought from the day of filing the request until the regulatory authority’s decision is issued.
Article 62: Request for a derogation by a power generating facility owner
1. Power generating facility owners, or prospective owners, may request a derogation to one or several requirements of this Regulation for power generating modules within their facilities.
2. A request for a derogation shall be filed with the relevant system operator and include: |  | ü |  |  | ü
(a) an identification of the power generating facility owner, or prospective owner, and a contact person for any communications;
(b) a description of the power generating module or modules for which a derogation is requested;
(c) a reference to the provisions of this Regulation from which a derogation is requested and a detailed description of the requested derogation;
(d) detailed reasoning, with relevant supporting documents and cost-benefit analysis pursuant to the requirements of Article 39;
(e) demonstration that the requested derogation would have no adverse effect on cross-border trade.
3. Within two weeks of receipt of a request for a derogation, the relevant system operator shall confirm to the power generating facility owner, or prospective owner, whether the request is complete. If the relevant system operator considers that the request is incomplete, the power generating facility owner, or prospective owner, shall submit the additional required information within one month from the receipt of the request for additional information. If the power generating facility owner, or prospective owner, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn. |  | ü |  |  | ü
4. The relevant system operator shall, in coordination with the relevant TSO and any affected adjacent DSO or DSOs, assess the request for a derogation and the provided cost-benefit analysis, taking into account the criteria determined by the regulatory authority pursuant to Article 61. |  | ü |  |  | ü
5. If a request for a derogation concerns a type C or D power generating module connected to a distribution system, including a closed distribution system, the relevant system operator’s assessment must be accompanied by an assessment of the request for a derogation by the relevant TSO. The relevant TSO shall provide its assessment within two months of being requested to do so by the relevant system operator. |  | ü |  |  | ü
6. Within six months of receipt of a request for a derogation, the relevant system operator shall forward the request to the regulatory authority and submit the assessment(s) prepared in accordance with paragraphs 4 and 5. That period may be extended by one month where the relevant system operator seeks further information from the power generating facility owner, or prospective owner and by two months where the relevant system operator requests the relevant TSO to submit an assessment of the request for a derogation. |  | ü |  |  | ü
7. The regulatory authority shall adopt a decision concerning any request for a derogation within six months from the day after it receives the request. That time limit may be extended by three months before its expiry where the regulatory authority requires further information from the power generating facility owner, or prospective owner, or from any other interested parties. The additional period shall begin when the complete information has been received.
8. The power generating facility owner, or prospective owner, shall submit any additional information requested by the regulatory authority within two months of such request. If the power generating facility owner, or prospective owner, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn unless, before its expiry:
(a) the regulatory authority decides to provide an extension; or
(b) the power generating facility owner, or prospective owner, informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete.
9. The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants derogation, it shall specify its duration.
10. The regulatory authority shall notify its decision to the relevant power generating facility owner, or prospective owner, the relevant system operator and the relevant TSO.
11. A regulatory authority may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply or upon a reasoned recommendation of the Commission or reasoned recommendation by the Agency pursuant to Article 65(2).
12. For Type A power generating modules, a request for a derogation under this Article may be made by a third party on behalf of the power generating module owner, or prospective owner. Such a request may be for a single power generating module or multiple, identical power generating modules. In the case of the latter, and provided the cumulative maximum capacity is specified, the third party may substitute the details required by point (a) of paragraph 2 with their details.
Article 63: Request for a derogation by a relevant system operator or relevant TSO
1. Relevant system operators or relevant TSOs may request derogations for classes of power generating modules connected or to be connected to their network. | ü | ü | ü | ü | ü
2. Relevant system operators or relevant TSOs shall submit their requests for derogation to the regulatory authority. Each request for a derogation shall include: | ü | ü | ü | ü | ü
(a) identification of the relevant system operator or relevant TSO, and a contact person for any communications; | ü | ü | ü | ü | ü
(b) a description of the power generating modules for which a derogation is requested and the total installed capacity and number of power generating modules;
(c) the requirement or requirements of this Regulation for which a derogation is requested, with a detailed description of the requested derogation;
(d) detailed reasoning, with all relevant supporting documents;
(e) demonstration that the requested derogation would have no adverse effect on cross-border trade;
(f) a cost-benefit analysis pursuant to the requirements of Article 39. If applicable, the cost-benefit analysis shall be carried out in coordination with the relevant TSO and any adjacent DSO or DSOs. |  | ü |  |  | ü
3. Where the request for a derogation is submitted by a relevant DSO or CDSO, the regulatory authority shall, within two weeks from the day after receipt of that request, ask the relevant TSO to assess the request for a derogation in the light of the criteria determined by the regulatory authority pursuant to Article 61. |  | ü |  |  | ü
4. Within two weeks from the day after the receipt of such request for assessment, the relevant TSO shall confirm to the relevant DSO or CDSO whether the request for a derogation is complete. If the relevant TSO considers that it is incomplete, the relevant DSO or CDSO shall submit the required additional information within one month from the receipt of the request for additional information. |  | ü |  |  | ü
5. Within six months of receipt of a request for a derogation, the relevant TSO shall submit to the regulatory authority its assessment, including any relevant documentation. The six-month time limit may be extended by one month where the relevant TSO seeks further information from the relevant DSO or from the relevant CDSO. |  | ü |  |  | ü
6. The regulatory authority shall adopt a decision concerning a request for a derogation within six months from the day after it receives the request. Where the request for a derogation is submitted by the relevant DSO or CDSO, the six-month time limit runs from the day following receipt of the relevant TSO’s assessment pursuant to paragraph 5. |  | ü |  |  | ü
7. The six-month time limit referred to in paragraph 6 may, before its expiry, be extended by an additional three months where the regulatory authority requests further information from the relevant system operator requesting the derogation or from any other interested parties. That additional period shall run from the day following the date of receipt of the complete information. | ü | ü | ü | ü | ü
The relevant system operator shall provide any additional information requested by the regulatory authority within two months from the date of the request. If the relevant system operator does not provide the requested additional information within that time limit, the request for a derogation shall be deemed withdrawn unless, before expiry of the time limit: | ü | ü | ü | ü | ü
(a) the regulatory authority decides to provide an extension; or
(b) the relevant system operator informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete. | ü | ü | ü | ü | ü
8. The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants derogation, it shall specify its duration.
9. The regulatory authority shall notify its decision to the relevant system operator requesting the derogation, the relevant TSO and the Agency.
10. Regulatory authorities may lay down further requirements concerning the preparation of requests for derogation by relevant system operators. In doing so, regulatory authorities shall take into account the delineation between the transmission system and the distribution system at the national level and shall consult with system operators, power generating facility owners and stakeholders, including manufacturers. | ü | ü | ü | ü | ü
11. A regulatory authority may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply or upon a reasoned recommendation of the Commission or reasoned recommendation by the Agency pursuant to paragraph 2 of Article 65.
Article 64
Register of derogations from the requirements of this Regulation
1. Regulatory authorities shall maintain a register of all derogations they have granted or refused and shall provide the Agency with an updated and consolidated register at least once every six months, a copy of which shall be given to ENTSO for Electricity.
2. The register shall contain, in particular:
(a) the requirement or requirements for which the derogation is granted or refused;
(b) the content of the derogation;
(c) the reasons for granting or refusing the derogation;
(d) the consequences resulting from granting the derogation.
Article 65: Monitoring of derogations
1. The Agency shall monitor the procedure of granting derogations with the cooperation of the regulatory authorities or relevant authorities of the Member State. Those authorities or relevant authorities of the Member State shall provide the Agency with all the information necessary for that purpose.
2. The Agency may issue a reasoned recommendation to a regulatory authority to revoke a derogation due to a lack of justification. The Commission may issue a reasoned recommendation to a regulatory authority or relevant authority of the Member State to revoke derogation due to a lack of justification.
3. The Commission may request the Agency to report on the application of paragraphs 1 and 2 and to provide reasons for requesting or not requesting derogations to be revoked.
TITLE VI
TRANSITIONAL ARRANGEMENTS FOR EMERGING TECHNOLOGIES
Article 66: Emerging technologies
1. With the exception of Article 30, the requirements of this Regulation shall not apply to power generating modules classified as an emerging technology, in accordance with the procedures set out in this Title.
2. A power generating module shall be eligible to be classified as an emerging technology pursuant to Article 69, provided that:
(a) it is of type A;
(b) it is a commercially available power generating module technology; and
(c) the accumulated sales of the power generating module technology within a synchronous area at the time of application for classification as an emerging technology do not exceed 25 % of the maximum level of cumulative maximum capacity established pursuant to paragraph 1 of Article 67.
Article 67: Establishment of thresholds for classification as emerging technologies
1. The maximum level of cumulative maximum capacity of power generating modules classified as emerging technologies in a synchronous area shall be 0.1 % of the annual maximum load in [2014] in that synchronous area.
For Member States belonging to parts of different synchronous areas, the calculation shall be carried out on a pro rata basis for each of those parts and combined to give the total allocation to that Member State.
For Member States belonging to parts of different synchronous areas, the calculation shall be carried out on a pro rata basis for each of those parts and combined to give the total allocation to that Member State.
3. The source of the data for applying this Article shall be the ENTSO for Electricity's Statistical Factsheet published in [2015].
Article 68: Application for classification as an emerging technology
1. Within six months of the entry into force of this Regulation manufacturers of Type A power generating modules may submit to the relevant regulatory authority a request for classification of their power generating module technology as an emerging technology.
2. In connection with a request pursuant to paragraph 1, the manufacturer shall inform the relevant regulatory authority of the accumulated sales of the respective power generating module technology within each synchronous area at the time of application for classification as an emerging technology.
3. Proof that a request submitted pursuant to paragraph 1 complies with the eligibility criteria laid down in Articles 66 and 67 shall be provided by the manufacturer.
4. Where applicable in a Member State, assessment of requests and approval and withdrawal of classification as an emerging technology may be undertaken by authorities other than the regulatory authority.
Article 69: Assessment and approval of requests for classification as an emerging technology
1. By 12 months of the entry into force of this Regulation, the relevant regulatory authority shall decide, in coordination with all the other regulatory authorities of a synchronous area, which power generating modules, if any, should be classified as an emerging technology. Any regulatory authority of the relevant synchronous area may request a prior opinion from the Agency, which shall be issued within three months of receipt of the request. The decision of the relevant regulatory authority shall take into account the opinion of the Agency.
2. A list of power generating modules approved as emerging technologies shall be published by each regulatory authority of a synchronous area.
Article 70: Withdrawal of classification as an emerging technology
1. From the date of the decision of the regulatory authorities pursuant to paragraph 1 of Article 69, the manufacturer of any power generating module classified as an emerging technology shall submit to the regulatory authority every two months an update of the sales of the module per Member States for the past two months. The regulatory authority shall make publicly available the cumulative maximum capacity of power generating modules classified as emerging technologies.
2. In the event that the cumulative maximum capacity of all power generating modules classified as emerging technologies connected to networks exceeds the threshold established in Article 67, the classification as an emerging technology shall be withdrawn by the relevant regulatory authority. The withdrawal decision shall be published.
3. Without prejudice to the provisions of paragraphs 1 and 2, all regulatory authorities of a synchronous area may decide in a coordinated manner to withdraw a classification as an emerging technology. The regulatory authorities of the synchronous area concerned may request a prior opinion from the Agency, which shall be issued within three months of receipt of the request. Where applicable, the coordinated decision of the regulatory authorities shall take into account the opinion of the Agency. The withdrawal decision shall be published by each regulatory authority of a synchronous area.
Power generating modules classified as emerging technologies and connected to the network prior to the date of withdrawal of that classification as an emerging technology shall be considered as existing power generating modules and shall therefore only be subject to the requirements of this Regulation pursuant to the provisions of paragraph 2 of Article 4 and Articles 38 and 39.
TITLE VII
FINAL PROVISIONS
Article 71: Amendment of contracts and general terms and conditions
1. Regulatory authorities shall ensure that all relevant clauses in contracts and general terms and conditions relating to the grid connection of new power generating modules are brought into compliance with the requirements of this Regulation.
2. All relevant clauses in contracts and relevant clauses of general terms and conditions relating to the grid connection of existing power generating modules subject to all or some of the requirements of this Regulation in accordance with paragraph 1 of Article 4 shall be amended in order to comply with the requirements of this Regulation. The relevant clauses shall be amended within three years following the decision of the regulatory authority or Member State as referred to in Article 4(1).
3. Regulatory authorities shall ensure that national agreements between system operators and owners of new or existing power generating facilities subject to this Regulation and relating to grid connection requirements for power generating facilities, in particular in national network codes, reflect the requirements set out in this Regulation.
Article 72: Entry into force
This Regulation shall enter into force on the twentieth day following that of its publication in the Official Journal of the European Union.

## Demand Connection
DCC TEXT | Obligation on |  |  |  | Multiple TSO Clause
| TO | SO | IC | OFTO
[Recitals hidden below]
Having regard to the Treaty on the Functioning of the European Union,
Having regard to Regulation (EC) No 714/2009 of the European Parliament and of the Council of 13 July 2009 on conditions for access to the network for cross-border exchanges in electricity and repealing Regulation (EC) No 1228/2003[1], and in particular Article 6(11) thereof,
Whereas:
(1) The swift completion of a fully functioning and interconnected internal energy market is crucial to maintaining security of energy supply, increasing competitiveness and ensuring that all consumers can purchase energy at affordable prices.
(2) Regulation (EC) No 714/2009 sets out non-discriminatory rules governing access to the network for cross-border exchanges in electricity with a view to ensuring the proper functioning of the internal market in electricity. In addition Article 5 of Directive 2009/72/EC of the European Parliament and of the Council[1] requires that Member States or, where Member States have so provided, regulatory authorities ensure, inter alia, that objective and non-discriminatory technical rules are developed which establish minimum technical design and operational requirements for the connection to the system. Where requirements constitute terms and conditions for connection to national networks, Article 37(6) of the same Directive requires regulatory authorities to be responsible for fixing or approving at least the methodologies used to calculate or establish them. In order to provide system security within the interconnected transmission system, it is essential to establish a common understanding of the requirements for grid connection applicable to demand facilities and distribution systems, including closed distribution systems. Those requirements that contribute to maintaining, preserving and restoring system security in order to facilitate proper functioning of the internal electricity market within and between synchronous areas, and to achieve cost efficiencies, should be regarded as cross-border network issues and market integration issues.
(3) Harmonised rules for grid connection for demand facilities and distribution systems should be set out in order to provide a clear legal framework for grid connections, facilitate Union-wide trade in electricity, ensure system security, facilitate the integration of renewable electricity sources, increase competition, and allow more efficient use of the network and resources, for the benefit of consumers.
(4) System security cannot be ensured independently from the technical capabilities of all users. Historically, generation facilities have formed the backbone of providing technical capabilities. However, in this regard, demand facilities are expected to play a more pivotal role in the future. Regular coordination at the level of the transmission and distribution networks and adequate performance of the equipment connected to the transmission and distribution networks with sufficient robustness to cope with disturbances and to help to prevent any major disruption or to facilitate restoration of the system after a collapse are fundamental prerequisites.
(5) Regulatory authorities should consider the reasonable costs effectively incurred by system operators in the implementation of this Regulation when fixing or approving transmission or distribution tariffs or their methodologies or when approving the terms and conditions for connection and access to national networks in accordance with Article 37(1) and (6) of Directive 2009/72/EC and with Article 14 of Regulation (EC) No 714/2009.
(6) Different synchronous electricity systems in the Union have different characteristics which need to be taken into account when setting the requirements for demand connection. It is therefore appropriate to consider regional specificities when establishing network connection rules as required by Article 8(6) of Regulation (EC) No 714/2009.
(7) In view of the need to provide regulatory certainty, the requirements of this Regulation should apply to new transmission-connected demand facilities, new transmission-connected distribution facilities, new distribution systems and new demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant transmission system operators ('TSOs'). The requirements of this Regulation should not apply to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units that are or can be used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs. The requirements of this Regulation also should not apply to new or existing demand facilities connected at the distribution level unless they provide demand response services to relevant system operators and relevant TSOs. However, the requirements of this Regulation should apply in case the relevant regulatory authority or Member State decides otherwise based on evolution of system requirements and a full cost-benefit analysis, or in case a substantial modernisation or replacement of equipment impacting the technical capabilities of an existing transmission-connected demand facility, an existing transmission-connected distribution facility, an existing distribution system, or an existing demand unit within a demand facility or a closed distribution system connected at a voltage level above 1000V has been performed.
(8) Demand response is an important instrument for increasing the flexibility of the internal energy market and for enabling optimal use of networks. It should be based on customers’ actions or on their agreement for a third party to take action on their behalf. A demand facility owner or a closed distribution system operator ('CDSO') may offer demand response services to the market as well as to system operators for grid security. In the latter case, the demand facility owner or the closed distribution system operator should ensure that new demand units used to provide such services fulfil the requirements set out in this Regulation, either individually or commonly as part of demand aggregation through a third party. In this regard, third parties have a key role in bringing together demand response capacities and can have the responsibility and obligation to ensure the reliability of those services, where those responsibilities are delegated by the demand facility owner and the closed distribution system operator.
(9) The requirements should be based on the principles of non-discrimination and transparency as well as on the principle of optimisation between the highest overall efficiency and lowest total cost for all involved parties. TSOs and distribution system operators ('DSOs') including CDSOs can take those elements into account when defining the requirements in accordance with the provisions of this Regulation, whilst recognising that the thresholds which determine whether a system is a transmission system or a distribution system are established at the national level.
(10) The requirements applicable to a demand facility connected to a transmission system should set out the capabilities at their interfaces and the necessary automated responses and data exchange. These requirements aim at ensuring the operability of the transmission system, and the capacity to utilise the generation and demand response embedded in these networks over system operational ranges and critical events.
(11) The requirements applicable to a distribution system connected to a transmission system or another distribution system should set out the operational range of these systems and the necessary automated responses and data exchange. These requirements should ensure the effective development and operability of the transmission system, and the capacity to utilise the generation and demand response embedded in these networks over system operational ranges and critical events.
(12) The requirements applicable to a demand unit used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs should ensure the capacity to use the demand response over system operational ranges thereby minimising critical events.
(13) The administrative burdens and costs associated with providing demand response should be kept within reasonable limits, in particular as regards domestic consumers, who will play an increasingly important role in the transition to low carbon society and their uptake should not be unnecessarily burdened with administrative tasks.
(14) Due to its cross-border impact, this Regulation should aim at the same frequency- related requirements for all voltage levels, at least within a synchronous area. That is necessary because, within a synchronous area, a change in frequency in one Member State would immediately impact frequency and could damage equipment in all other Member States.
(15) Voltage ranges should be coordinated between interconnected systems because they are crucial to secure planning and operation of a power system within a synchronous area. Disconnections because of voltage disturbances have an impact on neighbouring systems. Failure to specify voltage ranges could lead to widespread uncertainty in planning and operation of the system with respect to operation beyond normal operating conditions.
(16) Appropriate and proportionate compliance testing should be introduced so that system operators can ensure operational security. In accordance with Article 37(1)(b) of Directive 2009/72/EC, regulatory authorities are responsible for ensuring that system operators are compliant with this Regulation.
(17) The regulatory authorities, Member States and system operators should ensure that, in the process of developing and approving the requirements for network connection, they are harmonised to the extent possible, in order to ensure full market integration. Established technical standards should be taken into particular consideration in the development of connection requirements.
(18) System operators should not specify technical requirements for equipment that hinder the free movement of goods in the internal market. Where system operators make technical specifications resulting in requirements for the placing on the market of equipment, the respective Member State should follow the procedure referred to in Articles 8 and 9 of Directive 98/34/EC of the European Parliament and of the Council of 22 June 1998 laying down a procedure for the provision of information in the field of technical standards and regulations.
(19) A process for derogating from the rules should be set out in this Regulation to take into account local circumstances where exceptionally, for example, compliance with those rules could jeopardise the stability of the local network or where the safe operation of a transmission-connected demand facility, a transmission-connected distribution facility, a distribution system, or a demand unit used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs, might require operating conditions that are not in line with this Regulation.
(20) Subject to approval by the relevant regulatory authority, or other authority where applicable in a Member State, demand facility owners and relevant system operators should be allowed to propose derogations for certain classes of transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs.
(21) According to Article 28 of Directive 2009/72/EC, Member States may provide for the classification of a system which distributes electricity as a closed distribution system in certain circumstances. The provisions of this Regulation should apply to closed distribution systems only where Member States have so provided according to Article 28 of Directive 2009/72/EC.
(22) This Regulation has been adopted on the basis of Regulation (EC) No 714/2009 which it supplements and of which it forms an integral part. References to Regulation (EC) No 714/2009 in other legal acts should be understood as also referring to this Regulation.
(23) The measures provided for in this Regulation are in accordance with the opinion of the Committee referred to in Article 23(1) of Regulation (EC) No 714/2009,
TITLE I GENERAL PROVISIONS
Article 1 Subject matter
1. This Regulation establishes a network code which lays down the requirements for grid connection of: (a) transmission-connected demand facilities; (b) transmission-connected distribution facilities; (c) distribution systems, including closed distribution systems; (d) demand units, used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs. |  | ü |  |  | ü
2. This Regulation, therefore, helps to ensure fair conditions of competition in the internal electricity market, to ensure system security and the integration of renewable electricity sources, and to facilitate Union-wide trade in electricity.
3.This Regulation also lays down the obligations for ensuring that system operators make appropriate use of the demand facilities’ and distribution systems' capabilities in a transparent and non-discriminatory manner to provide a level playing field throughout the Union.
Article 2 Definitions
For the purposes of this Regulation, the definitions in Article 2 of Directive 2012/27/EU , Article 2 of Regulation (EC) No 714/2009, Article 2 of Commission Regulation (EU) 2015/1222 , Article 2 of Commission Regulation (EU) [000/2014 – RfG], Article 2 of Commission Regulation (EU) No 543/2013 and Article 2 of Directive 2009/72/EC shall apply. In addition, the following definitions shall apply:
'demand facility' means a facility which consumes electrical energy and is connected at one or more connection points to the transmission or distribution system. A distribution system and/or auxiliary supplies of a power generating module do no constitute a demand facility;
'transmission-connected demand facility' means a demand facility which has a connection point to a transmission system;
'transmission-connected distribution facility' means a distribution system connection or the electrical plant and equipment used at the connection to the transmission system;
'demand unit' means an indivisible set of installations containing equipment which can be actively controlled by a demand facility owner or by a CDSO, either individually or commonly as part of demand aggregation through a third party;
'closed distribution system' means a distribution system classified pursuant to Article 28 of Directive 2009/72/EC as a closed distribution system by national regulatory authorities or by other competent authorities, where so provided by the Member State, which distributes electricity within a geographically confined industrial, commercial or shared services site and does not supply household customers, without prejudice to incidental use by a small number of households located within the area served by the system and with employment or similar associations with the owner of the system;
'main demand equipment' means at least one of the following equipment: motors, transformers, high voltage equipment at the connection point and at the process production plant;
'transmission-connected distribution system' means a distribution system connected to a transmission system, including transmission-connected distribution facilities;
'maximum import capability' means the maximum continuous active power that a transmission-connected demand facility or a transmission-connected distribution facility can consume from the network at the connection point, as specified in the connection agreement or as agreed between the relevant system operator and the transmission-connected demand facility owner or transmission-connected distribution system operator respectively;
'maximum export capability' means the maximum continuous active power that a transmission-connected demand facility or a transmission-connected distribution facility, can feed into the network at the connection point, as specified in the connection agreement or as agreed between the relevant system operator and the transmission-connected demand facility owner or transmission-connected distribution system operator respectively;
'low frequency demand disconnection' means an action where demand is disconnected during a low frequency event in order to recover the balance between demand and generation and restore system frequency to acceptable limits;
'low voltage demand disconnection' means a restoration action where demand is disconnected during a low voltage event in order to recover voltage to acceptable limits;
'on load tap changer' means a device for changing the tap of a winding, suitable for operation while the transformer is energised or on load;
'on load tap changer blocking' means an action that blocks the on load tap changer during a low voltage event in order to stop transformers from further tapping and suppressing voltages in an area;
'control room' means a relevant system operator's operation centre;
'block loading' means the maximum step active power loading of reconnected demand during system restoration after black-out;
'demand response active power control' means demand within a demand facility or closed distribution system that is available for modulation by the relevant system operator or relevant TSO, which results in an active power modification;
'demand response reactive power control' means reactive power or reactive power compensation devices in a demand facility or closed distribution system that are available for modulation by the relevant system operator or relevant TSO;
'demand response transmission constraint management' means demand within a demand facility or closed distribution system that is available for modulation by the relevant system operator or relevant TSO to manage transmission constraints within the system;
'demand aggregation' means a set of demand facilities or closed distribution systems which can operate as a single facility or closed distribution system for the purposes of offering one or more demand response services;
'demand response system frequency control' means demand within a demand facility or closed distribution system that is available for reduction or increase in response to frequency fluctuations, made by an autonomous response from the demand facility or closed distribution system to diminish these fluctuations;
'demand response very fast active power control' means demand within a demand facility or closed distribution system that can be modulated very fast in response to a frequency deviation, which results in a very fast active power modification;
'demand response unit document' (DRUD) means a document, issued either by the demand facility owner or the CDSO to the relevant system operator for demand units with demand response and connected at a voltage level above 1000V, which confirms the compliance of the demand unit with the technical requirements set out in this Regulation and provides the necessary data and statements, including a statement of compliance.
Article 3 Scope of application
1. The connection requirements set out in this Regulation shall apply to:
(a) new transmission-connected demand facilities;
(b) new transmission-connected distribution facilities;
(c) new distribution systems, including new closed distribution systems;
(d) new demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs. |  | ü |  |  | ü
The relevant system operator shall refuse to allow the connection of a new transmission-connected demand facility, a new transmission-connected distribution facility, or a new distribution system, which does not comply with the requirements set out in this Regulation and which is not covered by a derogation granted by the regulatory authority, or other authority where applicable in a Member State pursuant to Article 50. The relevant system operator shall communicate such refusal, by means of a reasoned statement in writing, to the demand facility owner, DSO, or CDSO and, unless specified otherwise by the regulatory authority, to the regulatory authority. |  | ü |  |  | ü
Based on compliance monitoring in accordance with Title III, the relevant TSO shall refuse demand response services subject to Articles 27 to 30 from new demand units not fulfilling the requirements set out in this Regulation. |  | ü |  |  | ü
2. This Regulation shall not apply to:
(a) demand facilities and distribution systems connected to the transmission system and distribution systems, or to parts of the transmission system or distribution systems, of islands of Member States of which the systems are not operated synchronously with either the Continental Europe, Great Britain, Nordic, Ireland and Northern Ireland or Baltic synchronous area;
(b) storage devices except for pump-storage power generating modules in accordance with Article 5(2).
3. In case of demand facilities or closed distribution systems with more than one demand unit, these demand units shall together be considered as one demand unit if they cannot be operated independently from each other or can reasonably be considered in a combined manner.
Article 4 Application to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units used to provide demand response services
1. Existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units that are or can be used by a demand facility or a closed distribution system to provide demand response services to a relevant system operator or relevant TSO, are not subject to the requirements of this Regulation , except where: |  | ü |  |  | ü
(a) an existing transmission-connected demand facility, an existing transmission-connected distribution facility, an existing distribution system, or an existing demand unit within a demand facility at a voltage level above 1000V or a closed distribution system connected at a voltage level above 1000V, has been modified to such an extent that its connection agreement must be substantially revised in accordance with the following procedure:
(i) demand facility owners, DSOs, or CDSOs who intend to undertake the modernisation of a plant or replacement of equipment impacting the technical capabilities of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit shall notify their plans to the relevant system operator in advance; (ii) if the relevant system operator considers that the extent of the modernisation or replacement of equipment is such that a new connection agreement is required, the system operator shall notify the relevant regulatory authority or, where applicable, the Member State; and (iii) the relevant regulatory authority or, where applicable, the Member State shall decide if the existing connection agreement needs to be revised or a new connection agreement is required and which requirements of this Regulation shall apply; or |  | ü |  |  | ü
(b) a regulatory authority or, where applicable, a Member State decides to make an existing transmission-connected demand facility, an existing transmission-connected distribution facility, an existing distribution system, or an existing demand unit subject to all or some of the requirements of this Regulation, following a proposal from the relevant TSO in accordance with paragraphs 3, 4 and 5. |  | ü |  |  | ü
2. For the purposes of this Regulation, a transmission-connected demand facility, a transmission-connected distribution facility, a distribution system, or a demand unit that is, or can be, used by a demand facility or a closed distribution system to provide demand response services to a relevant system operator or relevant TSO, shall be considered as existing if: |  | ü |  |  | ü
(a) it is already connected to the network on the date of entry into force of this Regulation; or
(b) the demand facility owner, DSO, or CDSO has concluded a final and binding contract for the purchase of the main demand equipment or the demand unit by two years after the entry into force of the Regulation. The demand facility owner, DSO, or CDSO must notify the relevant system operator and relevant TSO of the conclusion of the contract within 30 months after the entry into force of the Regulation. |  | ü |  |  | ü
The notification submitted by the demand facility owner, DSO, or CDSO to the relevant system operator and the relevant TSO shall at least indicate the contract title, its date of signature and date of entry into force, and the specifications of the main demand equipment or the demand unit to be constructed, assembled or purchased. |  | ü |  |  | ü
A Member State may provide that in specified circumstances the regulatory authority may determine whether the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit is to be considered existing or new.
3. Following a public consultation in accordance with Article 9 and in order to address significant factual changes in circumstances, such as the evolution of system requirements including penetration of renewable energy sources, smart grids, distributed generation or demand response, the relevant TSO may propose to the regulatory authority concerned, or where applicable, to the Member State to extend the application of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units used by a demand facility or a closed distribution system to provide demand response services to a relevant system operator or relevant TSO. |  | ü |  |  | ü
4. Following a public consultation in accordance with Article 9 and in order to address significant factual changes in circumstances, such as the evolution of system requirements including penetration of renewable energy sources, smart grids, distributed generation or demand response, the relevant TSO may propose to the regulatory authority concerned, or where applicable, to the Member State to extend the application of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units used by a demand facility or a closed distribution system to provide demand response services to a relevant system operator or relevant TSO. |  | ü |  |  | ü
For that purpose a sound and transparent quantitative cost-benefit analysis shall be carried out, in accordance with Articles 48 and 49. The analysis shall indicate:
(a) the costs, in regard to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units, of requiring compliance with this Regulation;
(b) the socio-economic benefit resulting from applying the requirements set out in this Regulation; and
(c) the potential of alternative measures to achieve the required performance.
5. Before carrying out the quantitative cost-benefit analysis referred to in paragraph 3, the relevant TSO shall: |  | ü |  |  | ü
(a) carry out a preliminary qualitative comparison of costs and benefits;
(b) obtain approval from the relevant regulatory authority or, where applicable, the Member State.
6. The relevant regulatory authority or, where applicable, the Member State shall decide on the extension of the applicability of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units, within six months of receipt of the report and the recommendation of the relevant TSO in accordance with paragraph 4 of Article 48. The decision of the regulatory authority or, where applicable, the Member State shall be published. |  | ü |  |  | ü
7. The relevant TSO shall take account of the legitimate expectations of demand facility owners, DSOs and CDSOs as part of the assessment of the application of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units. |  | ü |  |  | ü
8. The relevant TSO may assess the application of some or all of the provisions of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units, every three years in accordance with the requirements and process set out in paragraphs 3 to 5. |  | ü |  |  | ü
Article 5 Application to pump-storage power generating modules and industrial sites
1. This Regulation shall not apply to pump-storage power generating modules that have both generating and pumping operation mode.
2. Any pumping module within a pump-storage station that only provides pumping mode shall be subject to the requirements of this Regulation and shall be treated as a demand facility.
3. In the case of industrial sites with an embedded power generating module, the system operator of an industrial site, the demand facility owner, the power generating facility owner and the relevant system operator to whose system the industrial site is connected, may agree, in coordination with the relevant TSO, on conditions for disconnection of critical loads from the relevant system. The objective of the agreement shall be to secure production processes of the industrial site in case of disturbed conditions in the relevant system. | ü | ü | ü | ü | ü
Article 6 Regulatory aspects
1. Requirements of general application to be established by relevant system operators or TSOs under this Regulation shall be subject to approval by the entity designated by the Member State and be published. The designated entity shall be the regulatory authority unless otherwise provided by the Member State.
2. For site specific requirements to be established by relevant system operators or TSOs under this Regulation, Member States may require approval by a designated entity.
3. When applying this Regulation, Member States, competent entities and system operators shall:
(a) apply the principles of proportionality and non-discrimination;
(b) ensure transparency;
(c) apply the principle of optimisation between the highest overall efficiency and lowest total costs for all parties involved;
(d) respect the responsibility assigned to the relevant TSO in order to ensure system security, including as required by national legislation;
(e) consult with relevant DSOs and take account of potential impacts on their system;
(f) take into consideration agreed European standards and technical specifications.
4. The relevant system operator or TSO shall submit a proposal for requirements of general application, or the methodology used to calculate or establish them, for approval by the competent entity within two years of entry into force of this Regulation. |  | ü |  |  | ü
5. Where this Regulation requires the relevant system operator, relevant TSO, demand facility owner, power generating facility owner, DSO and/or CDSO to seek agreement, they shall endeavour to do so within six months after a first proposal has been submitted by one party to the other parties. If no agreement has been found within this time frame, each party may request the relevant regulatory authority to issue a decision within six months. |  | ü |  |  | ü
6. Competent entities shall take decisions on proposals for requirements or methodologies within six months following the receipt of such proposals.
7. If the relevant system operator or TSO deems an amendment to requirements or methodologies as provided for and approved under paragraph 1 and 2 to be necessary, the requirements provided for in paragraphs 3 to 8 shall apply to the proposed amendment. System operators and TSOs proposing an amendment shall take into account the legitimate expectations, if any, of demand facility owners, DSOs, CDSOs, equipment manufacturers and other stakeholders based on the initially specified or agreed requirements or methodologies.
8. Any party having a complaint against a relevant system operator or a TSO in relation to that relevant system operator's or TSO's obligations under this Regulation may refer the complaint to the regulatory authority which, acting as dispute settlement authority, shall issue a decision within two months after receipt of the complaint. That period may be extended by two months where additional information is sought by the regulatory authority. That extended period may be further extended with the agreement of the complainant. The regulatory authority's decision shall have binding effect unless and until overruled on appeal.
9. Where the requirements under this Regulation are to be established by a relevant system operator that is not a TSO, Member States may provide that instead the TSO be responsible for establishing the relevant requirements.
Article 7 Multiple TSOs
1. Where more than one TSO exists in a Member State, this Regulation shall apply to all those TSOs.
2. Member States may, under the national regulatory regime, provide that the responsibility of a TSO to comply with one or some or all obligations under this Regulation is assigned to one or more specific TSOs.
Article 8 Recovery of costs
1. The costs borne by system operators subject to network tariff regulation and stemming from the obligations laid down in this Regulation shall be assessed by the relevant regulatory authorities. Costs assessed as reasonable, efficient and proportionate shall be recovered through network tariffs or other appropriate mechanisms.
2. If requested by the relevant regulatory authorities, system operators referred to in paragraph 1 shall, within three months of the request, provide the information necessary to facilitate assessment of the costs incurred.
Article 9 Public consultation
1. Relevant system operators and relevant TSOs shall carry out a consultation with stakeholders, including the competent authorities of each Member State on: |  | ü |  |  | ü
(a) proposals to extend the applicability of this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units in accordance with Article 4(3);
(b) the report prepared in accordance with Article 48(3);
(c) the cost-benefit analysis undertaken in accordance with Article 53(2);
(d) the requirements for demand units specified in accordance with Article 28(2)(c),(e),(f),(k) and (l) and Article 29(2)(c) to (e).
The consultation shall last at least for a period of one month.
2. The relevant system operators or relevant TSOs shall duly take into account the views of the stakeholders resulting from the consultations, prior to the submission of the draft proposal, the report, the cost-benefit analysis, or the requirements for demand units, for approval by the regulatory authority, competent entity or, if applicable, the Member State. In all cases, a sound justification for including or not the view of the stakeholders shall be provided and published in a timely manner before, or simultaneously with, the publication of the proposal, the report, the cost-benefit analysis, or the requirements for demand units specified in accordance with Article 28 and Article 29. |  | ü |  |  | ü
Article 10 Stakeholder involvement
The Agency, in close cooperation with the ENTSO for Electricity, shall organise stakeholder involvement regarding the requirements for the grid connection of transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs, and other aspects of the implementation of this Regulation. This shall include regular meetings with stakeholders to identify problems and propose improvements notably related to the requirements for grid connection of transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs.
Article 11 Confidentiality obligations
1. Any confidential information received, exchanged or transmitted pursuant to this Regulation shall be subject to the conditions of professional secrecy laid down in paragraphs 2, 3 and 4.
2. The obligation of professional secrecy shall apply to any persons, regulatory authorities, or entities subject to the provisions of this Regulation.
3. Confidential information received by the persons, regulatory authorities, or entities referred to in paragraph 2 in the course of their duties may not be divulged to any other person or authority, without prejudice to cases covered by national law, the other provisions of this Regulation or other relevant Union law.
Without prejudice to cases covered by national or Union law, regulatory authorities, entities, or persons who receive confidential information pursuant to this Regulation may use it only for the purpose of carrying out their duties under this Regulation.
TITLE II CONNECTION OF TRANSMISSION-CONNECTED DEMAND FACILITIES, TRANSMISSION-CONNECTED DISTRIBUTION FACILITIES AND DISTRIBUTION SYSTEMS
CHAPTER 1 GENERAL REQUIREMENTS
Article 12 General frequency requirements
1. Transmission-connected demand facilities, transmission-connected distribution facilities and distribution systems shall be capable of remaining connected to the network and operating at the frequency ranges and time periods specified in Annex I.
2. The transmission-connected demand facility owner or the DSO may agree with the relevant TSO on wider frequency ranges or longer minimum times for operation. If wider frequency ranges or longer minimum times for operation are technically feasible, the consent of the transmission-connected demand facility owner or DSO shall not be unreasonably withheld. |  | ü |  |  | ü
Article 13 General voltage requirements
1. Transmission-connected demand facilities, transmission-connected distribution facilities and transmission-connected distribution systems shall be capable of remaining connected to the network and operating at the voltage ranges and time periods specified in Annex II.
2. Equipment of distribution systems connected at the same voltage as the voltage of the connection point to the transmission system shall be capable of remaining connected to the network and operating at the voltage ranges and time periods specified in Annex II.
3. The voltage range at the connection point shall be expressed by the voltage at the connection point related to reference 1 per unit (pu) voltage. For the 400 kV grid voltage level (or alternatively commonly referred to as 380 kV level), the reference 1 pu value is 400 kV, for other grid voltage levels the reference 1 pu voltage may differ for each system operator in the same synchronous area.
4. Where the voltage base for pu values is from 300kV to 400kV included, the relevant TSO in Spain may require transmission-connected demand facilities, transmission-connected distribution facilities and transmission-connected distribution systems to remain connected in the voltage range between 1.05 pu –1.0875 pu for an unlimited period.
5. Where the voltage base for pu values is 400kV, the relevant TSOs in the Baltic synchronous area may require transmission-connected demand facilities, transmission-connected distribution facilities and transmission-connected distribution systems to remain connected to the 400 kV network in the voltage ranges and for time periods that apply to the Continental Europe synchronous area.
6. If required by the relevant TSO, a transmission-connected demand facility, a transmission-connected distribution facility, or a transmission-connected distribution system shall be capable of automatic disconnection at specified voltages. The terms and settings for automatic disconnection shall be agreed between the relevant TSO and the transmission-connected demand facility owner or the DSO. |  | ü |  |  | ü
7. With regard to transmission-connected distribution systems with a voltage below 110kV at the connection point, the relevant TSO shall specify the voltage range at the connection point that the distribution systems connected to that transmission system shall be designed to withstand. DSOs shall design the capability of their equipment, connected at the same voltage as the voltage of the connection point to the transmission system, to comply with this voltage range. |  | ü |  |  | ü
Article 14 Short-circuit requirements
1. Based on the rated short-circuit withstand capability of its transmission network elements, the relevant TSO shall specify the maximum short-circuit current at the connection point that the transmission-connected demand facility or the transmission-connected distribution system shall be capable of withstanding. | ü | ü | ü | ü | ü
2. The relevant TSO shall deliver to the transmission-connected demand facility owner or the transmission-connected distribution system operator an estimate of the minimum and maximum short-circuit currents to be expected at the connection point as an equivalent of the network. | ü | ü | ü | ü | ü
3. After an unplanned event, the relevant TSO shall inform the affected transmission-connected demand facility owner or the affected transmission-connected distribution system operator as soon as possible and no later than one week after the unplanned event, of the changes above a threshold for the maximum short-circuit current that the affected transmission-connected demand facility or the affected transmission-connected distribution system shall be able to withstand from the relevant TSO's network in accordance with paragraph 1. | ü | ü | ü | ü | ü
4. The threshold set in paragraph 3 shall either be specified by the transmission-connected demand facility owner for its facility, or by the transmission-connected distribution system operator for its network.
5. Before a planned event, the relevant TSO shall inform the affected transmission-connected demand facility owner or the affected transmission-connected distribution system operator, as soon as possible and no later than one week before the planned event, of the changes above a threshold for the maximum short-circuit current that the affected transmission-connected demand facility or the affected transmission-connected distribution system shall be able to withstand from the relevant TSO's network, in accordance with paragraph 1. | ü | ü | ü | ü | ü
6. The threshold set in paragraph 5 shall either be specified by the transmission-connected demand facility owner for its facility, or by the transmission-connected distribution system operator for its network.
7. The relevant TSO shall request information from a transmission-connected demand facility owner or a transmission-connected distribution system operator concerning the contribution in terms of short-circuit current from that facility or network. As a minimum, the equivalent modules of the network shall be delivered and demonstrated for zero, positive and negative sequences. | ü | ü | ü | ü | ü
8. After an unplanned event, the transmission-connected demand facility owner or the transmission-connected distribution system operator shall inform the relevant TSO, as soon as possible and no later than one week after the unplanned event, of the changes in short-circuit contribution above the threshold set by the relevant TSO. | ü | ü | ü | ü | ü
9. Before a planned event, the transmission-connected demand facility owner or the transmission-connected distribution system operator shall inform the relevant TSO, as soon as possible and no later than one week before the planned event, of the changes in short-circuit contribution above the threshold set by the relevant TSO. | ü | ü | ü | ü | ü
Article 15 Reactive power requirements
1. Transmission-connected demand facilities and transmission-connected distribution systems shall be capable of maintaining their steady-state operation at their connection point within a reactive power range specified by the relevant TSO, according to the following conditions: |  | ü |  |  | ü
(a) for transmission-connected demand facilities, the actual reactive power range specified by the relevant TSO for importing and exporting reactive power shall not be wider than 48 percent of the larger of the maximum import capacity or maximum export capacity (0.9 power factor import or export of active power), except in situations where either technical or financial system benefits are demonstrated, for transmission-connected demand facilities, by the transmission-connected demand facility owner and accepted by the relevant TSO; |  | ü |  |  | ü
(b) for transmission-connected distribution systems, the actual reactive power range specified by the relevant TSO for importing and exporting reactive power shall not be wider than: |  | ü |  |  | ü
(i) 48 percent (i.e. 0.9 power factor) of the larger of the maximum import capability or maximum export capability during reactive power import (consumption); and
(ii) 48 percent (i.e. 0.9 power factor) of the larger of the maximum import capability or maximum export capability during reactive power export (production);
except in situations where either technical or financial system benefits are proved by the relevant TSO and the transmission-connected distribution system operator through joint analysis; |  | ü |  |  | ü
(c) the relevant TSO and the transmission-connected distribution system operator shall agree on the scope of the analysis, which shall address the possible solutions, and determine the optimal solution for reactive power exchange between their systems, taking adequately into consideration the specific system characteristics, variable structure of power exchange, bidirectional flows and the reactive power capabilities in the distribution system; |  | ü |  |  | ü
(d) the relevant TSO may establish the use of metrics other than power factor in order to set out equivalent reactive power capability ranges; |  | ü |  |  | ü
(e) the reactive power range requirement values shall be met at the connection point;
(f) by way of derogation from point (e), where a connection point is shared between a power generating module and a demand facility, equivalent requirements shall be met at the point defined in relevant agreements or national law.
2. The relevant TSO may require that transmission-connected distribution systems have the capability at the connection point to not export reactive power (at reference 1 pu voltage) at an active power flow of less than 25% of the maximum import capability. Where applicable, Member States may require the relevant TSO to justify its request through a joint analysis with the transmission-connected distribution system operator. If this requirement is not justified based on the joint analysis, the relevant TSO and the transmission-connected distribution system operator shall agree on necessary requirements according to the outcomes of a joint analysis. |  | ü |  |  | ü
3. Without prejudice to point (b) of paragraph 1, the relevant TSO may require the transmission-connected distribution system to actively control the exchange of reactive power at the connection point for the benefit of the entire system. The relevant TSO and the transmission-connected distribution system operator shall agree on a method to carry out this control, to ensure the justified level of security of supply for both parties. The justification shall include a roadmap in which the steps and the timeline for fulfilling the requirement are specified. |  | ü |  |  | ü
4. In accordance with paragraph 3, the transmission-connected distribution system operator may require the relevant TSO to consider its transmission-connected distribution system for reactive power management. |  | ü |  |  | ü
Article 16 Protection requirements
1. The relevant TSO shall specify the devices and settings required to protect the transmission network in accordance with the characteristics of the transmission-connected demand facility or the transmission-connected distribution system. The relevant TSO and the transmission-connected demand facility owner or the transmission-connected distribution system operator shall agree on protection schemes and settings relevant for the transmission-connected demand facility or the transmission-connected distribution system. | ü | ü | ü | ü | ü
2.Electrical protection of the transmission-connected demand facility or the transmission-connected distribution system shall take precedence over operational controls while respecting system security, health and safety of staff and the public.
3. Protection scheme devices may cover the following elements:
(a) external and internal short circuit;
(b) over- and under-voltage at the connection point to the transmission system;
(c) over- and under-frequency;
(d) demand circuit protection;
(e) unit transformer protection;
(f) back-up against protection and switchgear malfunction.
4. The relevant TSO and the transmission-connected demand facility owner or the transmission-connected distribution system operator shall agree on any changes to the protection schemes relevant for the transmission-connected demand facility or the transmission-connected distribution system, and on the arrangements for the protection schemes of the transmission-connected demand facility or the transmission-connected distribution system. | ü | ü | ü | ü | ü
Article 17 Control requirements
1. The relevant TSO and the transmission-connected demand facility owner or the transmission-connected distribution system operator shall agree on the schemes and settings of the different control devices of the transmission-connected demand facility or the transmission-connected distribution system relevant for system security. | ü | ü | ü | ü | ü
2. The agreement shall cover at least the following elements:
(a) isolated (network) operation;
(b) damping of oscillations;
(c) disturbances to the transmission network;
(d) automatic switching to emergency supply and restoration to normal topology;
(e) automatic circuit-breaker re-closure (on 1-phase faults).
3. The relevant TSO and the transmission-connected demand facility owner or the transmission-connected distribution system operator shall agree on any changes to the schemes and settings of the different control devices of the transmission-connected demand facility or the transmission-connected distribution system relevant for system security. | ü | ü | ü | ü | ü
4. With regard to priority ranking of protection and control, the transmission-connected demand facility owner or the transmission-connected distribution system operator shall set the protection and control devices of its transmission-connected demand facility or its transmission-connected distribution system respectively, in compliance with the following priority ranking, organised in decreasing order of importance:
(a) transmission network protection;
(b) transmission-connected demand facility or transmission-connected distribution system protection;
(c) frequency control (active power adjustment);
(d) power restriction.
Article 18 Information exchange
1. Transmission-connected demand facilities shall be equipped according to the standards specified by the relevant TSO in order to exchange information between the relevant TSO and the transmission-connected demand facility with the specified time stamping. The relevant TSO shall make the specified standards publicly available. |  | ü |  |  | ü
2. Transmission-connected distribution system shall be equipped according to the standards specified by the relevant TSO in order to exchange information between the relevant TSO and the transmission-connected distribution system with the specified time stamping. The relevant TSO shall make the specified standards publicly available. |  | ü |  |  | ü
3. The relevant TSO shall specify the information exchange standards. The relevant TSO shall make publicly available the precise list of data required. |  | ü |  |  | ü
Article 19 Demand disconnection and demand reconnection
1. All transmission-connected demand facilities and transmission-connected distribution systems shall fulfil the following requirements related to low frequency demand disconnection functional capabilities:
(a) each transmission-connected distribution system operator and, where specified by the TSO, transmission-connected demand facility owner, shall provide capabilities that enable automatic 'low frequency' disconnection of a specified proportion of their demand. The relevant TSO may specify a disconnection trigger based on a combination of low frequency and rate-of-change-of-frequency; |  | ü |  |  | ü
(b) the low frequency demand disconnection functional capabilities shall allow for disconnecting demand in stages for a range of operational frequencies;
(c) the low frequency demand disconnection functional capabilities shall allow for operation from a nominal Alternating Current ("AC") input to be specified by the relevant system operator, and shall meet the following requirements: |  | ü |  |  | ü
(i) frequency range: at least between 47-50 Hz, adjustable in steps of 0.05Hz;
(ii) 48 percent (i.e. 0.9 power factor) of the larger of the maximum import capability or maximum export capability during reactive power export (production);
(iii) voltage lock-out: blocking of the functional capability shall be possible when the voltage is within a range of 30 to 90% of reference 1 pu voltage;
(iv) provide the direction of active power flow at the point of disconnection;
(d) the AC voltage supply used in providing low frequency demand disconnection functional capabilities, shall be provided from the network at the frequency signal measuring point, as used in providing functional capabilities in accordance with paragraph 1(c), so that the frequency of the low frequency demand disconnection functional capabilities supply voltage is the same as the one of the network.
2. With regard to low voltage demand disconnection functional capabilities, the following requirements shall apply:
(a) the relevant TSO may specify, in coordination with the transmission-connected distribution system operators, low voltage demand disconnection functional capabilities for the transmission-connected distribution facilities; |  | ü |  |  | ü
(b) the relevant TSO may specify, in coordination with the transmission-connected demand facility owners, low voltage demand disconnection functional capabilities for the transmission-connected demand facilities; |  | ü |  |  | ü
(c) based on the TSO's assessment concerning system security, the implementation of on load tap changer blocking and low voltage demand disconnection shall be binding for the transmission-connected distribution system operators; |  | ü |  |  | ü
(d) if the relevant TSO decides to implement a low voltage demand disconnection functional capability, the equipment for both on load tap changer blocking and low voltage demand disconnection shall be installed in coordination with the relevant TSO; |  | ü |  |  | ü
(e) the method for low voltage demand disconnection shall be implemented by relay or control room initiation;
(f) the low voltage demand disconnection functional capabilities shall have the following features:
(i) the low voltage demand disconnection functional capability shall monitor the voltage by measuring all three phases;
(ii) blocking of the relays' operation shall be based on direction of either active power or reactive power flow.
1. With regard to blocking of on load tap changers, the following requirements shall apply:
(a) if required by the relevant TSO, the transformer at the transmission-connected distribution facility shall be capable of automatic or manual on load tap changer blocking; |  | ü |  |  | ü
(b) the relevant TSO shall specify the automatic on load tap changer blocking functional capability. |  | ü |  |  | ü
2. All transmission-connected demand facilities and transmission-connected distribution systems shall fulfil the following requirements related to disconnection or reconnection of a transmission-connected demand facility or a transmission-connected distribution system:
(a) with regard to the capability of reconnection after a disconnection, the relevant TSO shall specify the conditions under which a transmission-connected demand facility or a transmission-connected distribution system is entitled to reconnect to the transmission system. Installation of automatic reconnection systems shall be subject to prior authorisation by the relevant TSO; |  | ü |  |  | ü
(b) with regard to reconnection of a transmission-connected demand facility or a transmission-connected distribution system, the transmission-connected demand facility or the transmission-connected distribution system shall be capable of synchronisation for frequencies within the ranges set out in Article 12. The relevant TSO and the transmission-connected demand facility owner or the transmission-connected distribution system operator shall agree on the settings of synchronisation devices prior to connection of the transmission-connected demand facility or the transmission-connected distribution system, including voltage, frequency, phase angle range and deviation of voltage and frequency; |  | ü |  |  | ü
(c) a transmission-connected demand facility or a transmission-connected distribution facility shall be capable of being remotely disconnected from the transmission system when required by the relevant TSO. If required, the automated disconnection equipment for reconfiguration of the system in preparation for block loading shall be specified by the relevant TSO. The relevant TSO shall specify the time required for remote disconnection. |  | ü |  |  | ü
Article 20 Power quality
Transmission-connected demand facility owners and transmission-connected distribution system operators shall ensure that their connection to the network does not result in a determined level of distortion or fluctuation of the supply voltage on the network, at the connection point. The level of distortion shall not exceed that allocated to them by the relevant TSO. TSOs shall coordinate their power quality requirements with the requirements of adjacent TSOs. | ü | ü | ü | ü | ü
Article 21 Simulation models
1. Transmission-connected demand facilities and transmission-connected distribution systems shall fulfil the requirements set out in paragraphs 3 and 4 related to the simulation models or equivalent information.
2. Each TSO may require simulation models or equivalent information showing the behaviour of the transmission-connected demand facility, or the transmission-connected distribution system, or both, in steady and dynamic states.
3. Each TSO shall specify the content and format of those simulation models or equivalent information. The content and format shall include:
(a) steady and dynamic states, including 50 Hz component;
(b) electromagnetic transient simulations at the connection point;
(c) structure and block diagrams.
4. For the purpose of dynamic simulations, the simulation model or equivalent information referred to in paragraph 3(a) shall contain the following sub-models or equivalent information:
(a) power control;
(b) voltage control;
(c) transmission-connected demand facility and transmission-connected distribution system protection models;
(d) the different types of demand, that is to say electro technical characteristics of the demand; and
(e) converter models.
5. Each relevant system operator or relevant TSO shall specify the requirements of the performance of the recordings of transmission-connected demand facilities or transmission-connected distribution facilities, or both, in order to compare the response of the model with these recordings. |  | ü |  |  | ü
CHAPTER 2 OPERATIONAL NOTIFICATION PROCEDURE
Article 22 General provisions
1. The operational notification procedure for the connection of each new transmission-connected demand facility, each new transmission-connected distribution facility and each new transmission-connected distribution system, shall comprise:
(a) an energisation operational notification (EON);
(b) an interim operational notification (ION);
(c) a final operational notification (FON).
2. Each transmission-connected demand facility owner or transmission-connected distribution system operator to which one or more of the requirements in Title II apply shall demonstrate to the relevant TSO that it has complied with the requirements set out in Title II of this Regulation by completing successfully the operational notification procedure for connection of each transmission-connected demand facility, each transmission-connected distribution facility and each transmission-connected distribution system described in Articles 23 to 26. |  | ü |  |  | ü
1. The relevant TSO shall specify and make publicly available further details concerning the operational notification procedure. |  | ü |  |  | ü
Article 23 Energisation operational notification
1. An EON shall entitle the transmission-connected demand facility owner or transmission-connected distribution system operator to energise its internal network and auxiliaries by using the grid connection that is specified for the connection point.
2. An EON shall be issued by the relevant TSO, subject to completion of preparations including agreement on the protection and control settings relevant to the connection point between the relevant TSO and the transmission-connected demand facility owner or transmission-connected distribution system operator. |  | ü |  |  | ü
Article 24 Interim operational notification
1. An ION shall entitle the transmission-connected demand facility owner or transmission-connected distribution system operator to operate the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system by using the grid connection for a limited period of time.
2. An ION shall be issued by the relevant TSO, subject to completion of the data and study review process as required by this Article. |  | ü |  |  | ü
3. With regard to the data and study review, the relevant TSO shall have the right to request that the transmission-connected demand facility owner or transmission-connected distribution system operator provide the following: |  | ü |  |  | ü
(a) an itemised statement of compliance;
(b) detailed technical data of the transmission-connected demand facility, the transmission-connected distribution facility or the transmission-connected distribution system relevant to the grid connection as specified by the relevant TSO; |  | ü |  |  | ü
(c) equipment certificates issued by an authorised certifier in respect of transmission-connected demand facilities, transmission-connected distribution facilities and transmission-connected distribution systems, where these are relied upon as part of the evidence of compliance;
(d) simulation models, as specified in Article 21 and required by the TSO; |  | ü |  |  | ü
(e) studies demonstrating expected steady-state and dynamic performance as required in Articles 43, 46 and 47;
(f) details of intended practical method of completing compliance tests according to Chapter 2 of Title IV.
4. The maximum period during which the transmission-connected demand facility owner or transmission-connected distribution system operator may maintain ION status shall be 24 months. The relevant TSO is entitled to specify a shorter ION validity period. An extension of the ION shall be granted only if the transmission-connected demand facility owner or transmission-connected distribution system operator has made substantial progress towards full compliance. Outstanding issues shall be clearly identified at the time of requesting extension. |  | ü |  |  | ü
5. An extension of the period during which the transmission-connected demand facility owner or transmission-connected distribution system operator may maintain ION status, beyond the period established in paragraph 4, may be granted if a request for a derogation is made to the relevant TSO before the expiry of that period in accordance with the derogation procedure laid down in Article 50. |  | ü |  |  | ü
Article 25 Final operational notification
1. A FON shall entitle the transmission-connected demand facility owner or transmission-connected distribution system operator to operate the transmission-connected demand facility, the transmission-connected distribution facility or the transmission-connected distribution system by using the grid connection.
2. A FON shall be issued by the relevant TSO, upon prior removal of all incompatibilities identified for the purposes of the ION status and subject to the completion of the data and study review process as required by this Article. |  | ü |  |  | ü
3. For the purposes of the data and study review, the transmission-connected demand facility owner or transmission-connected distribution system operator must submit the following to the relevant TSO: |  | ü |  |  | ü
(a) an itemised statement of compliance; and
(b) an update of the applicable technical data, simulation models and studies as referred to in points (b), (d) and (e) of Article 24(3), including the use of actual measured values during testing.
4. If incompatibility is identified in connection with the issuing of the FON, a derogation may be granted upon a request made to the relevant TSO, in accordance with the derogation procedure described in Chapter 2 of Title V. A FON shall be issued by the relevant TSO if the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system complies with the provisions of the derogation. |  | ü |  |  | ü
Where a request for a derogation is rejected, the relevant TSO shall have the right to refuse to allow the operation of the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system until the transmission-connected demand facility owner or transmission-connected distribution system operator and the relevant TSO resolve the incompatibility and the relevant TSO considers that the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system complies with the provisions of this Regulation. |  | ü |  |  | ü
If the relevant TSO and the transmission-connected demand facility owner or transmission-connected distribution system operator do not resolve the incompatibility within a reasonable time frame, but in any case not later than six months after the notification of the rejection of the request for a derogation, each party may refer the issue for decision to the regulatory authority. |  | ü |  |  | ü
Article 26 Limited operational notification
1. Transmission-connected demand facility owners or transmission-connected distribution system operators to whom a FON has been granted, shall inform the relevant TSO, no later than 24 hours after the incident has occurred, of the following circumstances: |  | ü |  |  | ü
(a) the facility is temporarily subject to either significant modification or loss of capability affecting its performance; or
(b) equipment failure leading to non-compliance with some relevant requirements.
A longer time period to inform the relevant TSO can be agreed with the transmission-connected demand facility owner or transmission-connected distribution system operator depending on the nature of the changes. |  | ü |  |  | ü
2. The transmission-connected demand facility owner or transmission-connected distribution system operator shall apply to the relevant TSO for a limited operational notification (LON), if the transmission-connected demand facility owner or transmission-connected distribution system operator expects the circumstances described in paragraph 1 to persist for more than three months. |  | ü |  |  | ü
3. A LON shall be issued by the relevant TSO and shall contain the following information which shall be clearly identifiable: |  | ü |  |  | ü
(a) the unresolved issues justifying the granting of the LON;
(b) the responsibilities and timescales for expected solution; and
(c) a maximum period of validity which shall not exceed 12 months. The initial period granted may be shorter with the possibility of an extension if evidence is submitted to the satisfaction of the relevant TSO demonstrating that substantial progress has been made towards achieving full compliance. |  | ü |  |  | ü
4. The FON shall be suspended during the period of validity of the LON with regard to the items for which the LON has been issued.
5. A further extension of the period of validity of the LON may be granted upon a request for a derogation made to the relevant TSO before the expiry of that period, in accordance with the derogation procedure described in Chapter 2 of Title V. |  | ü |  |  | ü
6. The relevant TSO shall have the right to refuse to allow the operation of the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system once the LON is no longer valid. In such cases, the FON shall automatically become invalid. |  | ü |  |  | ü
7. If the relevant TSO does not grant an extension of the period of validity of the LON in accordance with paragraph 5 or if it refuses to allow the operation of the transmission-connected demand facility, the transmission-connected distribution facility, or the transmission-connected distribution system once the LON is no longer valid in accordance with paragraph 6, the transmission-connected demand facility owner or transmission-connected distribution system operator may refer the issue for decision to the regulatory authority within six months after the notification of the decision of the relevant TSO. |  | ü |  |  | ü
TITLE III CONNECTION OF DEMAND UNITS USED BY A DEMAND FACILITY OR A CLOSED DISTRIBUTION SYSTEM TO PROVIDE DEMAND RESPONSE SERVICES TO SYSTEM OPERATORS CHAPTER 1 GENERAL REQUIREMENTS
Article 27 General provisions
1. Demand response services provided to system operators shall be distinguished based on the following categories:
(a) remotely controlled:
(i) demand response active power control;
(ii) demand response reactive power
(iii) demand response transmission constraint management
(b) autonomously controlled:
(i) demand response system frequency
(ii) demand response very fast active power
2. Demand facilities and closed distribution systems may provide demand response services to relevant system operators and relevant TSOs. Demand response services can include, jointly or separately, upward or downward modification of demand. |  | ü |  |  | ü
3. The categories referred to in paragraph 1 are not exclusive and this Regulation does not prevent other categories from being developed. This Regulation does not apply to demand response services provided to other entities than relevant system operators or relevant TSOs.
Article 28 Specific provisions for demand units with demand response active power control, reactive power control and transmission constraint management
1. Demand facilities and closed distribution systems may offer demand response active power control, demand response reactive power control, or demand response transmission constraint management to relevant system operators and relevant TSOs.
2. Demand units with demand response active power control, demand response reactive power control, or demand response transmission constraint management shall comply with the following requirements, either individually or, where it is not part of a transmission-connected demand facility, collectively as part of demand aggregation through a third party:
(a) be capable of operating across the frequency ranges specified in Article 12(1) and the extended range specified in Article 12(2);
(b) be capable of operating across the voltage ranges specified in Article 13 if connected at a voltage level at or above 110kV;
(c) be capable of operating across the normal operational voltage range of the system at the connection point, specified by the relevant system operator, if connected at a voltage level below 110kV. This range shall take into account existing standards and shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  |  |  |  | ü
(d) be capable of controlling power consumption from the network in a range equal to the range contracted, directly or indirectly through a third party, by the relevant TSO; |  | ü |  |  | ü
(e) be equipped to receive instructions, directly or indirectly through a third party, from the relevant system operator or the relevant TSO to modify their demand and to transfer the necessary information. The relevant system operator shall make publicly available the technical specifications approved to enable this transfer of information. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  | ü |  |  | ü
(f) be capable of adjusting its power consumption within a time period specified by the relevant system operator or the relevant TSO. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  | ü |  |  | ü
(g) be capable of full execution of an instruction issued by the relevant system operator or the relevant TSO to modify its power consumption to the limits of the electrical protection safeguards, unless a contractually agreed method is in place with the relevant system operator or relevant TSO for the replacement of their contribution (including aggregated demand facilities’ contribution through a third party); |  | ü |  |  | ü
(h) once a modification to power consumption has taken place and for the duration of the requested modification, only modify the demand used to provide the service if required by the relevant system operator or relevant TSO to the limits of the electrical protection safeguards, unless a contractually agreed method is in place with the relevant system operator or relevant TSO for the replacement of their contribution (including aggregated demand facilities’ contribution through a third party). Instructions to modify power consumption may have immediate or delayed effects; |  | ü |  |  | ü
(i) notify the relevant system operator or relevant TSO of the modification of demand response capacity. The relevant system operator or relevant TSO shall specify the modalities of the notification; |  | ü |  |  | ü
(j) where the relevant system operator or the relevant TSO, directly or indirectly through a third party, command the modification of the power consumption, enable the modification of a part of its demand in response to an instruction by the relevant system operator or the relevant TSO, within the limits agreed with the demand facility owner or the CDSO and according to the demand unit settings; |  | ü |  |  | ü
(k) have the withstand capability to not disconnect from the system due to the rate-of-change-of-frequency up to a value specified by the relevant TSO. With regard to this withstand capability, the value of rate-of-change-of-frequency shall be calculated over a 500 ms time frame. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  | ü |  |  | ü
(l) where modification to the power consumption is specified via frequency or voltage control, or both, and via pre-alert signal sent by the relevant system operator or the relevant TSO, be equipped to receive, directly or indirectly through a third party, the instructions from the relevant system operator or the relevant TSO, to measure the frequency or voltage value, or both, to command the demand trip and to transfer the information. The relevant system operator shall specify and publish the technical specifications approved to enable this transfer of information. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1). |  | ü |  |  | ü
3. For voltage control with disconnection or reconnection of static compensation facilities, each transmission-connected demand facility or transmission-connected closed distribution system shall be able to connect or disconnect its static compensation facilities, directly or indirectly, either individually or commonly as part of demand aggregation through a third party, in response to an instruction transmitted by the relevant TSO, or in the conditions set forth in the contract between the relevant TSO and the demand facility owner or the CDSO. |  | ü |  |  | ü
Article 29 Specific provisions for demand units with demand response system frequency control
1. Demand facilities and closed distribution systems may offer demand response system frequency control to relevant system operators and relevant TSOs. |  | ü |  |  | ü
2. Demand units with demand response system frequency control shall comply with the following requirements, either individually or, where it is not part of a transmission-connected demand facility, collectively as part of demand aggregation through a third party:
(a) be capable of operating across the frequency ranges specified in Article 12(1) and the extended range specified in Article 12(2);
(b) be capable of operating across the voltage ranges specified in Article 13 if connected at a voltage level at or above 110kV;
(c) be capable of operating across the normal operational voltage range of the system at the connection point, specified by the relevant system operator, if connected at a voltage level below 110kV. This range shall take into account existing standards, and shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  |  |  |  | ü
(d) be equipped with a control system that is insensitive within a dead band around the nominal system frequency of 50.00 Hz, of a width to be specified by the relevant TSO in consultation with the TSOs in the synchronous area. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1); |  | ü |  |  | ü
(e) be capable of, upon return to frequency within the dead band specified in paragraph 2(d), initiating a random time delay of up to 5 minutes before resuming normal operation.
The maximum frequency deviation from nominal value of 50.00 Hz to respond to shall be specified by the relevant TSO in coordination with the TSOs in the synchronous area. For demand units connected at a voltage level below 110kV, these specifications shall, prior to approval in accordance with Article 6, be subject to consultation with the relevant stakeholders in accordance with Article 9(1). |  | ü |  |  | ü
The demand shall be increased or decreased for a system frequency above or below the dead band of nominal (50.00 Hz) respectively;
(f) be equipped with a controller that measures the actual system frequency. Measurements shall be updated at least every 0.2 seconds;
(g) be able to detect a change in system frequency of 0.01 Hz, in order to give overall linear proportional system response, with regard to the demand response system frequency control’s sensitivity and accuracy of the frequency measurement and the consequent modification of the demand. The demand unit shall be capable of a rapid detection and response to changes in system frequency, to be specified by the relevant TSO in coordination with the TSOs in the synchronous area. An offset in the steady-state measurement of frequency shall be acceptable up to 0.05 Hz. |  | ü |  |  | ü
Article 30 Specific provisions for demand units with demand response very fast active power control
1. The relevant TSO in coordination with the relevant system operator may agree with a demand facility owner or a CDSO (including, but not restricted to, through a third party) on a contract for the delivery of demand response very fast active power control. |  | ü |  |  | ü
2. If the agreement referred to in paragraph 1 takes place, the contract referred to in paragraph 1 shall specify:
(a) a change of active power related to a measure such as the rate-of-change-of-frequency for that portion of its demand;
(b) the operating principle of this control system and the associated performance parameters;
(c) the response time for very fast active power control, which shall not be longer than 2 seconds.
CHAPTER 2 OPERATIONAL NOTIFICATION PROCEDURE
Article 31 General provisions
1. The operational notification procedure for demand units used by a demand facility or a closed distribution system to provide demand response to system operators shall be distinguished between:
(a) demand units within a demand facility or a closed distribution system connected at a voltage level of or below 1000V;
(b) demand units within a demand facility or a closed distribution system connected at a voltage level above 1000V.
2. Each demand facility owner or CDSO, providing demand response to a relevant system operator or a relevant TSO, shall confirm to the relevant system operator, or relevant TSO, directly or indirectly through a third party, its ability to satisfy the technical design and operational requirements as referred to in Chapter 1 of Title III of this Regulation. |  | ü |  |  | ü
3. The demand facility owner or the CDSO shall notify, directly or indirectly, through a third party, the relevant system operator or relevant TSO, in advance of any decision to cease offering demand response services and/or about the permanent removal of the demand unit with demand response. This information may be aggregated as specified by the relevant system operator or relevant TSO. |  | ü |  |  | ü
4. The relevant system operator shall specify and make publicly available further details concerning the operational notification procedure. |  | ü |  |  | ü
Article 32 Procedures for demand units within a demand facility or a closed distribution system connected at a voltage level of or below 1000V
1. The operational notification procedure for a demand unit within a demand facility or a closed distribution system connected at a voltage level of or below 1000V shall comprise an installation document.
2. The installation document template shall be provided by the relevant system operator, and the contents agreed with the relevant TSO, either directly or indirectly through a third party. |  |  |  |  | ü
3. Based on an installation document, the demand facility owner or the CDSO shall submit information, directly or indirectly through a third party, to the relevant system operator or relevant TSO. The date of this submission shall be prior to the offer in the market of the capacity of the demand response by the demand unit. The requirements set in the installation document shall differentiate between different types of connections and between the different categories of demand response services. |  |  |  |  | ü
4. For subsequent demand units with demand response, separate installation documents shall be provided.
5. The content of the installation document of individual demand units may be aggregated by the relevant system operator or relevant TSO. |  |  |  |  | ü
6. The installation document shall contain the following items:
(a) the location at which the demand unit with demand response is connected to the network;
(b) the maximum capacity of the demand response installation in kW;
(c) the type of demand response services;
(d) the demand unit certificate and the equipment certificate as relevant for the demand response service, or if not available, equivalent information;
(e) the contact details of the demand facility owner, the closed distribution system operator or the third party aggregating the demand units from the demand facility or the closed distribution system.
Article 33 Procedures for demand units within a demand facility or a closed distribution system connected at a voltage level above 1000V
1. The operational notification procedure for a demand unit within a demand facility or a closed distribution system connected at a voltage level above 1000V shall comprise a DRUD. The relevant system operator, in coordination with the relevant TSO, shall specify the content required for the DRUD. The content of the DRUD shall require a statement of compliance which contains the information in Articles 36 to 47 for demand facilities and closed distribution systems, but the compliance requirements in Articles 36 to 47 for demand facilities and closed distribution systems can be simplified to a single operational notification stage as well as be reduced. The demand facility owner or CDSO shall provide the information required and submit it to the relevant system operator. Subsequent demand units with demand response shall provide separate DRUDs. |  | ü |  |  | ü
2. Based on the DRUD, the relevant system operator shall issue a FON to the demand facility owner or CDSO. |  | ü |  |  | ü
TITLE IV COMPLIANCE CHAPTER 1 GENERAL PROVISIONS
Article 34 Responsibility of the demand facility owner, the distribution system operator and the closed distribution system operator
1. Transmission-connected demand facility owners and DSOs shall ensure that their transmission-connected demand facilities, transmission-connected distribution facilities, or distribution systems comply with the requirements provided for in this Regulation. A demand facility owner or a CDSO providing demand response services to relevant system operators and relevant TSOs shall ensure that the demand unit complies with the requirements provided for in this Regulation. |  | ü |  |  | ü
2. Where the requirements of this Regulation are applicable to demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs, the demand facility owner or the CDSO may totally or partially delegate to third parties tasks such as communicating with the relevant system operator or relevant TSO and gathering the documentation from the demand facility owner, the DSO or the CDSO evidencing compliance. |  | ü |  |  | ü
Third parties shall be treated as single users with the right to compile relevant documentation and demonstrate compliance of their aggregated demand facilities or aggregated closed distribution systems with the provisions of this Regulation. Demand facilities and closed distribution systems providing demand response services to relevant system operators and relevant TSOs may act collectively through third parties. |  | ü |  |  | ü
3. Where obligations are fulfilled through third parties, third parties shall only be required to inform the relevant system operator of changes to the total services being offered, taking account of location specific services. |  | ü |  |  | ü
4. Where the requirements are specified by the relevant TSO, or are for the purpose of the operation of the relevant TSO's system, alternative tests or requirements for test result acceptance for these requirements may be agreed with the relevant TSO. |  | ü |  |  | ü
5. Any intention to modify the technical capabilities of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit, which has impact on compliance with the requirements provided for in Chapters 2 to 4 of Title IV, shall be notified to the relevant system operator, directly or indirectly through a third party, prior to pursuing such modification, within the time frame provided by the relevant system operator. |  | ü |  |  | ü
6. Any operational incidents or failures of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system or the demand unit, which have an impact on compliance with the requirements provided for in Chapters 2 to 4 of Title IV, shall be notified to the relevant system operator, directly or indirectly through a third party, as soon as possible after the occurrence of such an incident. |  | ü |  |  | ü
7. Any planned test schedules and procedures to verify compliance of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit, with the requirements of this Regulation, shall be notified to the relevant system operator within the time frame specified by the relevant system operator and approved by the relevant system operator prior to their commencement. |  | ü |  |  | ü
8. The relevant system operator may participate in such tests and may record the performance of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, and the demand unit. |  | ü |  |  | ü
Article 35 Tasks of the relevant system operator
1. The relevant system operator shall assess the compliance of a transmission-connected demand facility, a transmission-connected distribution facility, a distribution system, or a demand unit, with the requirements of this Regulation throughout the lifetime of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit. The demand facility owner, the DSO or the CDSO shall be informed of the outcome of this assessment. |  | ü |  |  | ü
The compliance of a demand unit used by a demand facility or a closed distribution system to provide demand response services to relevant TSOs, shall be jointly assessed by the relevant TSO and the relevant system operator, and if applicable in coordination with the third party involved in demand aggregation. |  | ü |  |  | ü
2. The relevant system operator shall have the right to request that the demand facility owner, the DSO or the CDSO carries out compliance tests and simulations according to a repeat plan or general scheme or after any failure, modification or replacement of any equipment that may have an impact on the compliance of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit with the requirements of this Regulation. |  | ü |  |  | ü
The demand facility owner, the DSO or the CDSO shall be informed of the outcome of those compliance tests and simulations.
3. The relevant system operator shall make publicly available the list of information and documents to be provided as well as the requirements to be fulfilled by the demand facility owner, the DSO or the CDSO in the frame of the compliance process. The list shall cover at least the following information, documents and requirements: |  | ü |  |  | ü
(a) all documentation and certificates to be provided by the demand facility owner, the DSO or the CDSO;
(b) details of the technical data required from the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit, with relevance to the grid connection or operation;
(c) requirements for models for steady-state and dynamic system studies;
(d) timeline for the provision of system data required to perform the studies;
(e) studies by the demand facility owner, the DSO or the CDSO for demonstrating expected steady-state and dynamic performance referring to the requirements set forth in Articles 43, 44 and 45;
(f) conditions and procedures including scope for registering equipment certificates;
(g) conditions and procedures for the use of relevant equipment certificates issued by an authorised certifier by the demand facility owner, the DSO or the CDSO.
4. The relevant system operator shall make public the allocation of responsibilities to the demand facility owner, the DSO or the CDSO and to the system operator for compliance testing, simulation and monitoring. |  | ü |  |  | ü
5. The relevant system operator may totally or partially delegate the performance of its compliance monitoring to third parties. In such cases, the relevant system operator shall continue ensuring compliance with Article 11, including entering into confidentiality commitments with the assignee. |  | ü |  |  | ü
6. If compliance tests or simulations cannot be carried out as agreed between the relevant system operator and the demand facility owner, the DSO or the CDSO due to reasons attributable to the relevant system operator, then the relevant system operator shall not unreasonably withhold the operational notification referred to in Title II and Title III. |  | ü |  |  | ü
CHAPTER 2 COMPLIANCE TESTING
Article 36 Common provisions for compliance testing
1. Testing of the performance of a transmission-connected demand facility, a transmission-connected distribution facility, or a demand unit with demand response active power control, demand response reactive power control or demand response transmission constraint management, shall aim at demonstrating that the requirements of this Regulation have been complied with.
2. Notwithstanding the minimum requirements for compliance testing set out in this Regulation, the relevant system operator is entitled to: |  | ü |  |  | ü
(a) allow the demand facility owner, the DSO or the CDSO to carry out an alternative set of tests, provided that those tests are efficient and suffice to demonstrate that a demand facility or a distribution system complies with the requirements of this Regulation; and
(b) require the demand facility owner, the DSO or the CDSO to carry out additional or alternative sets of tests in those cases where the information supplied to the relevant system operator in relation to compliance testing under the provisions of Articles 37 to 41, is not sufficient to demonstrate compliance with the requirements of this Regulation. |  | ü |  |  | ü
3. The demand facility owner, the DSO or the CDSO is responsible for carrying out the tests in accordance with the conditions laid down in Chapter 2 of Title IV. The relevant system operator shall cooperate and not unduly delay the performance of the tests. |  | ü |  |  | ü
4. The relevant system operator may participate in the compliance testing either on site or remotely from the system operator’s control room. For that purpose, the demand facility owner, the DSO or the CDSO shall provide the monitoring equipment necessary to record all relevant test signals and measurements as well as ensure that the necessary representatives of the demand facility owner, the DSO or the CDSO are available on site for the entire testing period. Signals specified by the relevant system operator shall be provided if, for selected tests, the system operator wishes to use its own equipment to record performance. The relevant system operator has sole discretion to decide about its participation. |  | ü |  |  | ü
Article 37 Compliance testing for disconnection and reconnection of transmission-connected distribution facilities
1. The transmission-connected distribution facilities shall comply with the requirements for disconnection and reconnection referred in Article 19 and shall be subject to the following compliance tests.
2. With regard to testing of the capability of reconnection after an incidental disconnection due to a network disturbance, reconnection shall be achieved through a reconnection procedure, preferably by automation, authorised by the relevant TSO. |  | ü |  |  | ü
3. With regard to the synchronisation test, the technical synchronisation capabilities of the transmission-connected distribution facility shall be demonstrated. This test shall verify the settings of the synchronisation devices. This test shall cover the following matters: voltage, frequency, phase angle range, deviation of voltage and frequency.
4. With regard to the remote disconnection test, the transmission-connected distribution facility's technical capability for remote disconnection at the connection point or points from the transmission system when required by the relevant TSO and within the time specified by the relevant TSO shall be demonstrated. |  | ü |  |  | ü
5. With regard to the low frequency demand disconnection test, the transmission-connected distribution facility's technical capability of low frequency demand disconnection of a percentage of demand to be specified by the relevant TSO, in coordination with adjacent TSOs, where equipped as provided for in Article 19, shall be demonstrated. |  | ü |  |  | ü
6. With regard to the low frequency demand disconnection relays test, the transmission-connected distribution facility's technical capability to operate from a nominal AC supply input shall be demonstrated in accordance with Article 19(1) and (2). This AC supply input shall be specified by the relevant TSO. |  | ü |  |  | ü
7. With regard to the low voltage demand disconnection test, the transmission-connected distribution facility's technical capability to operate in a single action with on load tap changer blocking in Article 19(3) shall be demonstrated in accordance with Article 19(2).
8. An equipment certificate may be used instead of part of the tests provided for in paragraph 1, on the condition that it is provided to the relevant TSO. |  | ü |  |  | ü
Article 38 Compliance testing for information exchange of transmission-connected distribution facilities
1. With regard to information exchange between the relevant TSO and the transmission-connected distribution system operator in real time or periodically, the transmission-connected distribution facility's technical capability to comply with the information exchange standard established pursuant to Article 18(3) shall be demonstrated. |  | ü |  |  | ü
2. An equipment certificate may be used instead of part of the tests provided for in paragraph 1, on the condition that it is provided to the relevant TSO. |  | ü |  |  | ü
Article 39 Compliance testing for disconnection and reconnection of transmission-connected demand facilities
1. The transmission-connected demand facilities shall comply with the requirements for disconnection and reconnection referred to in Article 19 and shall be subject to the following compliance tests.
2. With regard to testing of the capability of reconnection after an incidental disconnection due to a network disturbance, reconnection shall be achieved through a reconnection procedure, preferably by automation, authorised by the relevant TSO. |  | ü |  |  | ü
3. With regard to the synchronisation test, the technical synchronisation capabilities of the transmission-connected demand facility shall be demonstrated. This test shall verify the settings of the synchronisation devices. This test shall cover the following matters: voltage, frequency, phase angle range, deviation of voltage and frequency.
4. With regard to the remote disconnection test, the transmission-connected demand facility's technical capability for remote disconnection at the connection point or points from the transmission system when required by the relevant TSO and within the time specified by the relevant TSO shall be demonstrated. |  | ü |  |  | ü
5. With regard to the low frequency demand disconnection relays test, the transmission-connected demand facility's technical capability to operate from a nominal AC input shall be demonstrated in accordance with Article 19(1) and (2). This AC supply input shall be specified by the relevant TSO. |  | ü |  |  | ü
6. With regard to the low voltage demand disconnection test, the transmission-connected demand facility's technical capability to operate in a single action with on load tap changer blocking in Article 19(3) shall be demonstrated in accordance with Article 19(2).
7. An equipment certificate may be used instead of part of the tests provided for in paragraph 1, on the condition that it is provided to the relevant TSO. |  | ü |  |  | ü
Article 40 Compliance testing for information exchange of transmission-connected demand facilities
1. With regard to information exchange between the relevant TSO and the transmission-connected demand facility owner in real time or periodically, the transmission-connected demand facility's technical capability to comply with the information exchange standard established pursuant to Article 18(3) shall be demonstrated. |  | ü |  |  | ü
2. An equipment certificate may be used instead of part of the tests provided for in paragraph 1, on the condition that it is provided to the relevant TSO. |  | ü |  |  | ü
Article 41 Compliance testing for demand units with demand response active power control, reactive power control and transmission constraint management
1. With regard to the demand modification test:
(a) the technical capability of the demand unit used by a demand facility or a closed distribution system to provide demand response active power control, demand response reactive power control or demand response transmission constraint management to modify its power consumption, after receiving an instruction from the relevant system operator or relevant TSO, within the range, duration and time frame previously agreed and established in accordance with Article 28, shall be demonstrated, either individually or collectively as part of demand aggregation through a third party; |  | ü |  |  | ü
(b) the test shall be carried out either by an instruction or alternatively by simulating the receipt of an instruction from the relevant system operator or relevant TSO and adjusting the power demand of the demand facility or the closed distribution system; |  | ü |  |  | ü
(c) the test shall be deemed passed, provided that the conditions specified by the relevant system operator or relevant TSO pursuant to Article 28(2)(d)(f)(g)(h)(k) and (l) are fulfilled; |  | ü |  |  | ü
(d) an equipment certificate may be used instead of part of the tests provided for in paragraph 1(b), on the condition that it is provided to the relevant system operator or relevant TSO. |  | ü |  |  | ü
2. With regard to the disconnection or reconnection of static compensation facilities test:
(a) the technical capability of the demand unit used by a demand facility owner or closed distribution system operator to provide demand response active power control, demand response reactive power control or demand response transmission constraint management to disconnect or reconnect, or both, its static compensation facility when receiving an instruction from the relevant system operator or relevant TSO, in the time frame expected in accordance with Article 28, shall be demonstrated, either individually or collectively as part of demand aggregation through a third party; |  | ü |  |  | ü
(b) the test shall be carried out by simulating the receipt of an instruction from the relevant system operator or relevant TSO and subsequently disconnecting the static compensation facility, and by simulating the receipt of an instruction from the relevant system operator or relevant TSO and subsequently reconnecting the facility; |  | ü |  |  | ü
(c) the test shall be deemed passed, provided that the conditions specified by the relevant system operator or relevant TSO pursuant to Article 28(2)(d)(f)(g)(h)(k) and (l) are fulfilled. |  | ü |  |  | ü
CHAPTER 3 COMPLIANCE SIMULATION
Article 42 Common provisions on compliance simulations
1. Simulation of the performance of a transmission-connected demand facility, a transmission-connected distribution facility, or a demand unit with demand response very fast active power control within a demand facility or a closed distribution system shall result in demonstrating whether the requirements of this Regulation have been fulfilled or not.
2. Simulations shall be run in the following circumstances:
(a) a new connection to the transmission system is required;
(b) a new demand unit used by a demand facility or a closed distribution system to provide demand response very fast active power control to a relevant TSO has been contracted in accordance with Article 30; |  | ü |  |  | ü
(c) a further development, replacement or modernisation of equipment takes place;
(d) alleged incompliance by the relevant system operator with the requirements of this Regulation. |  | ü |  |  | ü
3. Notwithstanding the minimum requirements for compliance simulation set out in this Regulation, the relevant system operator is entitled to: |  | ü |  |  | ü
(a) allow the demand facility owner, the DSO or the CDSO to carry out an alternative set of simulations, provided that those simulations are efficient and suffice to demonstrate that a demand facility or a distribution system complies with the requirements of this Regulation or with national legislation; and
(b) require the demand facility owner, the DSO or the CDSO to carry out additional or alternative sets of simulations in those cases where the information supplied to the relevant system operator in relation to compliance simulation under the provisions of Articles 43, 44 and 45, is not sufficient to demonstrate compliance with the requirements of this Regulation. |  | ü |  |  | ü
4. The transmission-connected demand facility owner or the transmission-connected distribution system operator shall provide a report with the simulation results for each individual transmission-connected demand facility or transmission-connected distribution facility. The transmission-connected demand facility owner or the transmission-connected distribution system operator shall produce and provide a validated simulation model for a given transmission-connected demand facility or transmission-connected distribution facility. The scope of the simulation models is set out in Article 21(1) and (2).
5. The relevant system operator shall have the right to check that a demand facility or a distribution system complies with the requirements of this Regulation by carrying out its own compliance simulations based on the provided simulation reports, simulation models and compliance test measurements. |  | ü |  |  | ü
6. The relevant system operator shall provide the demand facility owner, the DSO or the CDSO with technical data and a simulation model of the network, to the extent necessary to carry out the requested simulations in accordance with Articles 43, 44 and 45. |  | ü |  |  | ü
Article 43 Compliance simulations for transmission-connected distribution facilities
1. With regard to the reactive power capability simulation of a transmission-connected distribution facility:
(a) a steady-state load flow simulation model of the network of the transmission-connected distribution system shall be used in order to calculate the reactive power demand under different load and generation conditions;
(b) a combination of steady-state minimum and maximum load and generation conditions resulting in the lowest and highest reactive power demand shall be part of the simulations;
© calculating the reactive power export at an active power flow of less than 25% of the maximum import capability at the connection point shall be part of the simulations in accordance with Article 15.
2. The relevant TSO may specify the method for compliance simulation of the active control of reactive power set out in Article 15(3). |  | ü |  |  | ü
3. The simulation shall be deemed passed if the results demonstrate compliance with the requirements set out in Article 15.
Article 44 Compliance simulations for transmission-connected demand facilities
1. With regard to the reactive power capability simulation of a transmission-connected demand facility without onsite generation:
(a) the transmission-connected demand facility without onsite generation's reactive power capability at the connection point shall be demonstrated;
(b) a load flow simulation model of the transmission-connected demand facility shall be used to calculate the reactive power demand under different load conditions. Minimum and maximum load conditions resulting in the lowest and highest reactive power demand at the connection point shall be part of the simulations;
(c) the simulation shall be deemed passed if the results demonstrate compliance with the requirements set out in Article 15(1) and (2).
2. With regard to the reactive power capability simulation of a transmission-connected demand facility with onsite generation:
(a) a load flow simulation model of the transmission-connected demand facility shall be used to calculate the reactive power demand under different load conditions and under different generation conditions;
(b) a combination of minimum and maximum load and generation conditions resulting in the lowest and highest reactive power capability at the connection point shall be part of the simulations;
(c) the simulation shall be deemed passed if the results demonstrate compliance with the requirements set out in Article 15(1) and (2).
Article 45 Compliance simulations for demand units with demand response very fast active power control
1. The model of the demand unit used by a demand facility owner or a closed distribution system operator to provide demand response very fast active power control shall demonstrate the technical capability of the demand unit to provide very fast active power control to a low frequency event in the conditions set out in Article 30.
2. The simulation shall be deemed passed provided that the model demonstrates compliance with the conditions set out in Article 30.
CHAPTER 4 COMPLIANCE MONITORING
Article 46 Compliance monitoring for transmission-connected distribution facilities
With regard to compliance monitoring of the reactive power requirements applicable to transmission-connected distribution facilities:
(a) the transmission-connected distribution facility shall be equipped with necessary equipment to measure the active and reactive power, in accordance with Article 15; and
(b) the relevant system operator shall specify the time frame for compliance monitoring. |  | ü |  |  | ü
Article 47 Compliance monitoring for transmission-connected demand facilities
With regard to compliance monitoring of the reactive power requirements applicable to transmission-connected demand facilities:
(a) the transmission-connected demand facility shall be equipped with necessary equipment to measure the active and reactive power, in accordance with Article 15; and
(b) the relevant system operator shall specify the time frame for compliance monitoring. |  | ü |  |  | ü
TITLE V APPLICATIONS AND DEROGATIONS CHAPTER 1 COST-BENEFIT ANALYSIS
Article 48 Identification of costs and benefits of application of requirements to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units
1. Prior to the application of any requirement set out in this Regulation to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units in accordance with Article 4(3), the relevant TSO shall undertake a qualitative comparison of costs and benefits related to the requirement under consideration. This comparison shall take into account available network-based or market-based alternatives. The relevant TSO may only proceed to undertake a quantitative cost-benefit analysis in accordance with paragraphs 2 to 5, if the qualitative comparison indicates that the likely benefits exceed the likely costs. If, however, the cost is deemed high or the benefit is deemed low, then the relevant TSO shall not proceed further. |  | ü |  |  | ü
2. Following a preparatory stage undertaken in accordance with paragraph 1, the relevant TSO shall carry out a quantitative cost-benefit analysis of any requirement under consideration for application to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units that have demonstrated potential benefits as a result of the preparatory stage according to paragraph 1. |  | ü |  |  | ü
3. Within three months of concluding the cost-benefit analysis, the relevant TSO shall summarise the findings in a report which shall: |  | ü |  |  | ü
(a) include the cost-benefit analysis and a recommendation on how to proceed;
(b) include a proposal for a transitional period for applying the requirement to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units. That transitional period shall not be more than two years from the date of the decision of the regulatory authority or where applicable the Member State on the requirement’s applicability;
(c) be subject to public consultation in accordance with Article 9.
4. No later than six months after the end of the public consultation, the relevant TSO shall prepare a report explaining the outcome of the consultation and making a proposal on the applicability of the requirement under consideration to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units. The report and proposal shall be notified to the regulatory authority or, where applicable, the Member State, and the demand facility owner, DSO, CDSO or, where applicable, third party shall be informed on its content. |  | ü |  |  | ü
5. The proposal made by the relevant TSO to the regulatory authority or, where applicable, the Member State pursuant to paragraph 4 shall include the following: |  | ü |  |  | ü
(a) an operational notification procedure for demonstrating the implementation of the requirements by the existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs; |  | ü |  |  | ü
(b) a transitional period for implementing the requirements which shall take into account the classes of transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs and any underlying obstacles to the efficient implementation of the equipment modification/refitting. |  | ü |  |  | ü
Article 49 Principles of cost-benefit analysis
1. Demand facility owners, DSOs and CDSOs shall assist and contribute to the cost-benefit analysis undertaken according to Articles 48 and 53 and provide the necessary data as requested by the relevant system operator or relevant TSO within three months of receiving a request, unless agreed otherwise by the relevant TSO. For the preparation of a cost-benefit-analysis by a demand facility owner or prospective owner, or by a DSO/CDSO or prospective operator, assessing a potential derogation pursuant to Article 52, the relevant TSO and DSO shall assist and contribute to the cost-benefit analysis and provide the necessary data as requested by the demand facility owner or prospective owner, or by the DSO/CDSO or prospective operator, within three months of receiving a request, unless agreed otherwise by the demand facility owner or prospective owner, or by the DSO/CDSO or prospective operator. |  | ü |  |  | ü
2. A cost-benefit analysis shall be in line with the following principles:
(a) the relevant TSO, demand facility owner or prospective owner, DSO/CDSO or prospective operator, shall base its cost-benefit analysis on one or more of the following calculating principles: |  | ü |  |  | ü
(i) the net present value;
(ii) the return on investment
(iii) the rate of return
(iv) the time needed to break even
(b) the relevant TSO, demand facility owner or prospective owner, DSO/CDSO or prospective operator, shall also quantify socio-economic benefits in terms of improvement in security of supply and shall include at least: |  | ü |  |  | ü
(i) the associated reduction in probability of loss of supply over the lifetime of the modification;
(ii) the probable extent and duration of such loss of supply;
(iii) the societal cost per hour of such loss of
(c) the relevant TSO, demand facility owner or prospective owner, DSO/CDSO or prospective operator, shall quantify the benefits to the internal market in electricity, cross-border trade and integration of renewable energies, including at least: |  | ü |  |  | ü
(i) the active power frequecy response
(ii) the balancing reserves
(iii) the reactive power provision;
(iv) congestion management
(v) defence meaures
(d) the relevant TSO shall quantify the costs of applying the necessary rules to existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems, or existing demand units, including at least: |  | ü |  |  | ü
(i) the direct costs incurred in implementing a requirement;
(ii) the costs associated with attributable loss of opportunity;
(iii) the costs associated with resulting changes in maintenance and operation.
CHAPTER 2 DEROGATIONS
Article 50 Power to grant derogations
1. Regulatory authorities may, at the request of a demand facility owner or prospective owner, and a DSO/CDSO or prospective operator, relevant system operator or relevant TSO, grant demand facility owners or prospective owners, and DSOs/CDSOs or prospective operators,, relevant system operators or relevant TSOs derogations from one or more provisions of this Regulation for new and existing transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units in accordance with Articles 51 to 53. |  | ü |  |  | ü
2. Where applicable in a Member State, derogations may be granted and revoked in accordance with Articles 51 to 53 by other authorities than the regulatory authority.
Article 51 General provisions
1. Each regulatory authority shall specify, after consulting relevant system operators, demand facility owners, DSOs, CDSOs, and other stakeholders whom it deems affected by this Regulation, the criteria for granting derogations pursuant to Articles 52 and 53. It shall publish those criteria on its website and notify them to the Commission within nine months of the entry into force of this Regulation. The Commission may require a regulatory authority to amend the criteria if it considers that they are not in line with this Regulation. This possibility to review and amend the criteria for granting derogations shall not affect the derogations already granted which shall continue to apply until the scheduled expiry date as detailed in the decision granting the exemption.
2. If the regulatory authority deems that it is necessary due to a change in circumstances relating to the evolution of system requirements, it may review and amend at most once every year the criteria for granting derogations in accordance with paragraph 1. Any changes to the criteria shall not apply to derogations for which a request has already been made.
3. The regulatory authority may decide that transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units for which a request for a derogation has been filed pursuant to Articles 52 or 53 do not need to comply with the requirements of this Regulation from which a derogation has been sought from the day of filing the request until the regulatory authority’s decision is issued.
Article 52 Request for a derogation by a demand facility owner, a distribution system operator or a closed distribution system operator
1. Demand facility owners or prospective owners, and DSOs/CDSOs or prospective operators, may request a derogation to one or several requirements of this Regulation for transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems, or demand units used by a demand facility or a closed distribution system to provide demand response services to a relevant system operator and a relevant TSO. |  | ü |  |  | ü
2. A request for a derogation shall be filed with the relevant system operator and include: |  | ü |  |  | ü
(a) an identification of the demand facility owner or prospective owner, the DSO/CDSO or prospective operator, and a contact person for any communications;
(b) a description of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit for which a derogation is requested;
(c) a reference to the provisions of this Regulation from which a derogation is requested and a detailed description of the requested derogation;
(d) detailed reasoning, with relevant supporting documents and cost-benefit analysis pursuant to the requirements of Article 49;
(e) demonstration that the requested derogation would have no adverse effect on cross-border trade.
3. Within two weeks of receipt of a request for a derogation, the relevant system operator shall confirm to the demand facility owner or prospective owner, or to the DSO/CDSO or prospective operator, whether the request is complete. If the relevant system operator considers that the request is incomplete, the demand facility owner or prospective owner, or the DSO/CDSO or prospective operator, shall submit the additional required information within one month from the receipt of the request for additional information. If the demand facility owner or prospective owner, or if the DSO/CDSO or prospective operator, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn. |  | ü |  |  | ü
4. The relevant system operator shall, in coordination with the relevant TSO and any affected adjacent DSO, assess the request for a derogation and the provided cost-benefit analysis, taking into account the criteria determined by the regulatory authority pursuant to Article 51. |  | ü |  |  | ü
5. Within six months of receipt of a request for a derogation, the relevant system operator shall forward the request to the regulatory authority and submit the assessment(s) prepared in accordance with paragraphs 4. That period may be extended by one month where the relevant system operator seeks further information from the demand facility owner or prospective owner, or from the DSO/CDSO or prospective operator, and by two months where the relevant system operator requests the relevant TSO to submit an assessment of the request for a derogation. |  | ü |  |  | ü
6. The regulatory authority shall adopt a decision concerning any request for a derogation within six months from the day after it receives the request. That time limit may be extended by three months before its expiry where the regulatory authority requires further information from the demand facility owner or prospective owner, or from the DSO/CDSO or prospective operator, or from any other interested parties. The additional period shall begin when the complete information has been received.
7. The demand facility owner or prospective owner, or the DSO/CDSO or prospective operator, shall submit any additional information requested by the regulatory authority within two months of such request. If the demand facility owner or prospective owner, or if the DSO/CDSO or prospective operator, does not supply the requested information within that time limit, the request for a derogation shall be deemed withdrawn unless, before its expiry:
(a) the regulatory authority decides to provide an extension; or
(b) the demand facility owner or prospective owner, or the DSO/CDSO or prospective operator, informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete.
8. The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants a derogation, it shall specify its duration.
9. The regulatory authority shall notify its decision to the relevant demand facility owner or prospective owner, the DSO/CDSO or prospective operator, the relevant system operator and the relevant TSO. |  | ü |  |  | ü
10. A regulatory authority may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply or upon a reasoned recommendation of the Commission or reasoned recommendation by the Agency pursuant to Article 55(2).
11. For demand units within a demand facility or a closed distribution system connected at a voltage level of or below 1000V, a request for a derogation under this Article may be made by a third party on behalf of the demand facility owner or prospective owner, or on behalf of the CDSO or prospective operator. Such a request may be for a single demand unit or multiple demand units within the same demand facility or closed distribution system. In the case of the latter, and provided the cumulative maximum capacity is specified, the third party may substitute the details required by point (a) of paragraph 2 with their details.
Article 53 Request for a derogation by a relevant system operator or relevant TSO
1. Relevant system operators or relevant TSOs may request derogations for transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems, or demand units within a demand facility or a closed distribution system connected or to be connected to their network. |  | ü |  |  | ü
2. Relevant system operators or relevant TSOs shall submit their requests for a derogation to the regulatory authority. Each request for a derogation shall include: |  | ü |  |  | ü
(a) identification of the relevant system operator or relevant TSO, and a contact person for any communications; |  | ü |  |  | ü
(b) a description of the transmission-connected demand facility, the transmission-connected distribution facility, the distribution system, or the demand unit for which a derogation is requested and the total installed capacity and number of transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems, or demand units;
(c) the requirement or requirements of this Regulation for which a derogation is requested, with a detailed description of the requested derogation;
(d) detailed reasoning, with all relevant supporting documents;
(e) demonstration that the requested derogation would have no adverse effect on cross-border trade;
(f) a cost-benefit analysis pursuant to the requirements of Article 49. If applicable, the cost-benefit analysis shall be carried out in coordination with the relevant TSO and any adjacent DSO. |  | ü |  |  | ü
3. Where the request for a derogation is submitted by a relevant DSO, the regulatory authority shall, within two weeks from the day after receipt of that request, ask the relevant TSO to assess the request for a derogation in the light of the criteria determined by the regulatory authority pursuant to Article 51. |  | ü |  |  | ü
4. Within two weeks from the day after the receipt of such request for assessment, the relevant TSO shall confirm to the relevant DSO whether the request for a derogation is complete. If the relevant TSO considers that it is incomplete, the relevant DSO shall submit the required additional information within one month from the receipt of the request for additional information. |  | ü |  |  | ü
5. Within six months of receipt of a request for a derogation, the relevant TSO shall submit to the regulatory authority its assessment, including any relevant documentation. The six-month time limit may be extended by one month where the relevant TSO seeks further information from the relevant DSO. |  | ü |  |  | ü
6. The regulatory authority shall adopt a decision concerning a request for a derogation within six months from the day after it receives the request. Where the request for a derogation is submitted by the relevant DSO, the six-month time limit runs from the day following receipt of the relevant TSO’s assessment pursuant to paragraph 5. |  | ü |  |  | ü
7. The six-month time limit referred to in paragraph 6 may, before its expiry, be extended by an additional three months where the regulatory authority requests further information from the relevant system operator requesting the derogation or from any other interested parties. That additional period shall run from the day following the date of receipt of the complete information. |  | ü |  |  | ü
The relevant system operator shall provide any additional information requested by the regulatory authority within two months from the date of the request. If the relevant system operator does not provide the requested additional information within that time limit, the request for a derogation shall be deemed withdrawn unless, before expiry of the time limit: |  | ü |  |  | ü
(a) the regulatory authority decides to provide an extension; or
(b) the relevant system operator informs the regulatory authority by means of a reasoned submission that the request for a derogation is complete. |  | ü |  |  | ü
8. The regulatory authority shall issue a reasoned decision concerning a request for a derogation. Where the regulatory authority grants derogation, it shall specify its duration.
9. The regulatory authority shall notify its decision to the relevant system operator requesting the derogation, the relevant TSO and the Agency. |  | ü |  |  | ü
10. Regulatory authorities may lay down further requirements concerning the preparation of requests for a derogation by relevant system operators. In doing so, regulatory authorities shall take into account the delineation between the transmission system and the distribution system at the national level and shall consult with system operators, demand facility owners and stakeholders, including manufacturers. |  | ü |  |  | ü
11. A regulatory authority may revoke a decision granting a derogation if the circumstances and underlying reasons no longer apply or upon a reasoned recommendation of the Commission or reasoned recommendation by the Agency pursuant to Article 55(2).
Article 54 Register of derogations from the requirements of this Regulation
1. Regulatory authorities shall maintain a register of all derogations they have granted or refused and shall provide the Agency with an updated and consolidated register at least once every six months, a copy of which shall be given to ENTSO for Electricity.
2. The register shall contain, in particular:
(a) the requirement or requirements for which the derogation is granted or refused;
(b) the content of the derogation;
(c) the reasons for granting or refusing the derogation;
(d) the consequences resulting from granting the derogation.
Article 55 Monitoring of derogations
1. The Agency shall monitor the procedure of granting derogations with the cooperation of the regulatory authorities or relevant authorities of the Member State. Those authorities or relevant authorities of the Member State shall provide the Agency with all the information necessary for that purpose.
2. The Agency may issue a reasoned recommendation to a regulatory authority to revoke a derogation due to a lack of justification. The Commission may issue a reasoned recommendation to a regulatory authority or relevant authority of the Member State to revoke a derogation due to a lack of justification.
3. The Commission may request the Agency to report on the application of paragraphs 1 and 2 and to provide reasons for requesting or not requesting derogations to be revoked.
TITLE VI NON-BINDING GUIDANCE AND MONITORING OF IMPLEMENTATION
Article 56 Non-binding guidance on implementation
1. No later than six months after the entry into force of this Regulation, the ENTSO for Electricity shall prepare and thereafter every two years provide non-binding written guidance to its members and other system operators concerning the elements of this Regulation requiring national decisions. The ENTSO for Electricity shall publish this guidance on its website.
2. ENTSO for Electricity shall consult stakeholders when providing non-binding guidance.
3. The non-binding guidance shall explain the technical issues, conditions and interdependencies which need to be considered when complying with the requirements of this Regulation at national level.
Article 57 Monitoring
1. ENTSO for Electricity shall monitor the implementation of this Regulation in accordance with Article 8(8) of Regulation (EC) No 714/2009. Monitoring shall cover in particular the following matters:
(a) identification of any divergences in the national implementation of this Regulation;
(b) assessment of whether the choice of values and ranges in the requirements applicable to transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units under this Regulation continues to be valid.
2. The Agency, in cooperation with ENTSO for Electricity, shall produce by 12 months after the entry into force of this Regulation a list of the relevant information to be communicated by ENTSO for Electricity to the Agency in accordance with Article 8(9) and Article 9(1) of Regulation (EC) No 714/2009. The list of relevant information may be subject to updates. ENTSO for Electricity shall maintain a comprehensive, standardised format, digital data archive of the information required by the Agency.
3. Relevant TSOs shall submit to ENTSO for Electricity the information required to perform the tasks referred to in paragraphs 1 and 2. |  | ü |  |  | ü
Based on a request of the regulatory authority, DSOs shall provide TSOs with information under paragraph 2 unless the information is already obtained by regulatory authorities, the Agency or ENTSO-E in relation to their respective implementation monitoring tasks, with the objective of avoiding duplication of information. |  | ü |  |  | ü
4. Where ENTSO for Electricity or the Agency establish areas subject to this Regulation where, based on market developments or experience gathered in the application of this Regulation, further harmonisation of the requirements under this Regulation is advisable to promote market integration, they shall propose draft amendments to this Regulation pursuant to Article 7(1) of Regulation (EC) No 714/2009.
TITLE VII FINAL PROVISIONS
Article 58 Amendment of contracts and general terms and conditions
1. Regulatory authorities shall ensure that all relevant clauses in contracts and general terms and conditions relating to the grid connection of new transmission-connected demand facilities, new transmission-connected distribution facilities, new distribution systems and new demand units are brought into compliance with the requirements of this Regulation.
2. All relevant clauses in contracts and relevant clauses of general terms and conditions relating to the grid connection of existing transmission-connected demand facilities, existing transmission-connected distribution facilities, existing distribution systems and existing demand units subject to all or some of the requirements of this Regulation in accordance with paragraph 1 of Article 4 shall be amended in order to comply with the requirements of this Regulation. The relevant clauses shall be amended within three years following the decision of the regulatory authority or Member State as referred to in Article 4(1).
3. Regulatory authorities shall ensure that agreements between system operators and owners of new or existing demand facilities or operators of new or existing distribution systems subject to this Regulation and relating to grid connection requirements for transmission-connected demand facilities, transmission-connected distribution facilities, distribution systems and demand units used by a demand facility or a closed distribution system to provide demand response services to relevant system operators and relevant TSOs, in particular in national network codes, reflect the requirements set out in this Regulation. |  | ü |  |  | ü
Article 59 Entry into force
This Regulation shall enter into force on the twentieth day following that of its publication in the Official Journal of the European Union.
Without prejudice to Article 4(2)(b), Article 6, Article 51, Article 56 and Article 57, the requirements of this Regulation shall apply from three years after publication. This Regulation shall be binding in its entirety and directly applicable in all Member States.
Done at Brussels,
For the Commission
The President
ANNEXES to the Commission Regulation No [000/2015 - DCC] establishing a Network Code on Demand Connection Annex I Frequency ranges and time periods referred to in Article 12(1) |  | ü |  |  | ü
Annex II Voltage ranges and time periods referred to in Article 13(1) |  | ü |  |  | ü

## FCA
Title | Chapter | Section | Article Name | Article | Article Description | OFTOs | TOs | I/C | SO | Ofgem Comment
|  | Recitals | Recitals | n/a | Sets out the high level aims of the regulation. |  |  |  |  | Interpretive text. Does not contain any TSO obligations.
1. General Provisions |  | General Provisions | Subject Matter and Scope | 1 | [5 empty] | This Article does not address TSOs.
|  | General Provisions | Definitions | 2 | This Article sets out the definitions used in the FCA Regulation which are not already defined in previous European Directives or Regulations. | P | P | P | P | Definitions need to apply to anyone undertaking a role within the Regulation, so apply to all parties
|  | General Provisions | Objectives of Forward Capacity Allocation | 3 | This Article states the high level objectives that govern all processes in the Regulation. | P | P | P | P | Applicable to all TSOs as it sets the context for all actions undertaken by anyone complying with the Regulation
|  | General Provisions | Adoption of Terms Conditions and Methodologies | 4 | This Article explains the process that the regulatory authorities will need to comply with in order to make decisions on proposals. |  | P | P | P | This Article is relevant to any party that has a function relevant to the development of any methodology.
|  | General Provisions | Stakeholder Involvement | 5 | This Article specifies an ENTSOE obligation and as such, has not been individually allocated to the TSOs, however it is expected that they will contribute as EC 714/2009 Article 4 states "All transmission system operators shall cooperate at Community level through the ENTSO for Electricity..... to promote the completion and functioning of the internal market..." |  |  |  |  | We currently don't consider that these articles put direct obligations on TSOs.
|  | General Provisions | Consultation | 6 | This Article specifies the consultation procedures that TSOs must comply with. |  | P | P | P | This Article is relevant to any party taking part in the development of any methodology.
|  | General Provisions | Confidentiality Obligations | 7 | This Article refers to the confidentiality of information received, transmitted or exchanged under the FCA Regulation. | P | P | P | P | This Article is essential to make sure that all parties have due regard for confidentiality.
2. Requirements for terms, conditions and methodologies | 1. Forward Capacity Allocation | General Requirements | Capacity Calculation Regions | 8 | This Article states that the CCRs shall be those established in CACM Article 15. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 15.
|  | General Requirements | Capacity Calculation Timeframes | 9 | This Article states that all TSOs in each CCR shall ensure that long term cross zonal capacity is calculated for each forward capacity allocation and at least on annual and monthly timeframes |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows.
|  | Capacity Calculation Methodology | Capacity Calculation Methodology | 10 | This Article requires TSOs to submit a proposal for a common coordinated capacity calculation methodology. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Articles 20 and 21.
|  | Capacity Calculation Methodology | Reliability Margin Methodology | 11 | This Article is based on CACM Article 22 which sets out the process and criteria to be included in the reliability margin methodology. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 22.
|  | Capacity Calculation Methodology | Methodologies for Operational Security Limits and Contingencies | 12 | This Article is based on CACM Article 23 which states that all TSOs must respect certain limits and contingencies to ensure acceptable operating boundaries for secure grid operation. |  | P | P | P | We consider this Sub Article to be applicable to the SO in its capacity as the real time system operator, the ICs in their capacity as managers of cross border electricity flows and the TOs due to their maintenance and development of part of the GB grid. This is consistent with our assignment of responsibilities for CACM Article 23.
|  | Capacity Calculation Methodology | Generation Shift Keys Methodologies | 13 | This Article states that generation shift keys shall the meet requirements set out in CACM Article 24. |  |  |  | P | The estimation of generation shift keys will be done by the SOs with input from generating units relevant to the capacity calculation, there we consider this Article applicable to the SO only. This is consistent with our assignment of responsibilities for CACM Article 24.
|  | Capacity Calculation Methodology | Methodology for remedial actions | 14 | This Article requires TSOs to have remedial actions available in real time when necessary, which meet requirements set out in CACM Article 25. |  | P | P | P | We consider this Article to be applicable to the SO in its capacity as the real time system operator, the ICs in their capacity as managers of cross border electricity flows and the TOs due to their maintenance and development of part of the GB grid. This is consistent with our assignment of responsibilities for CACM Article 25.
|  | Capacity Calculation Methodology | Cross Zonal Capacity Validation Methodology | 15 | This Article states that the proposal for a common CCR methodology shall include a cross zonal validation methodology which shall meet the requirements set out in CACM Article 26. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 26.
|  | Capacity Calculation Methodology | Methodology for Splitting Long-Term Cross-Zonal Capacity | 16 | This Article requires TSOs to develop a methodology for splitting long-term cross-zonal capacity. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. We note that the SO should be appropriately consulted through the process.
|  | Common Grid Model | Generation and Load Data Provision Methodology | 17 | This Article requires TSOs to propose a common generation and load data provision methodology for the data required for long term timeframes. The Article also states that this shall be done in accordance with CACM Article 16. |  |  |  | P | Generators provide generation and load data to the SO only so this Article is not applicable to OFTOs, TOs or ICs. This is consistent with our assignment of responsibilities for CACM Article 16.
|  | Common Grid Model | Common Grid Model Methodology | 18 | This Article requires TSOs to develop a common grid methodology. |  |  | P | P | The Common Grid Model will include the relevant parts of European Grids with forecasted production and consumption patterns for each market time unit. We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 17.
|  | Common Grid Model | Scenarios | 19 | This Article requires all TSOs in a CCR to jointly develop a common set of scenarios to be used in the common grid model for each long-term capacity calculation timeframe. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 18.
|  | Common Grid Model | Individual Grid Model | 20 | This Article requires TSOs to submit a proposal for a common coordinated capacity calculation methodology . TSOs must develop this, pursuant to CACM Article 19. | P | P | P | P | We consider this Article to be applicable to the SO in its capacity as the real time system operator, the ICs in their capacity as managers of cross border electricity flows, and TOs due to their maintenance and development of part of the GB grid. OFTOs will need to provide relevant data. This is consistent with our assignment of responsibilities for CACM Article 19.
|  | Capacity Calculation Process | General Provisions | 21 | This Article states that merging individual grid models should be done in accordance with CACM Article 27, and sets out the timeframe for the process. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and therefore the responsible parties for network security and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 27.
|  | Capacity Calculation Process | Creation of a Common Grid Model | 22 | This Article states that the process for creation of a Common Grid Model shall be done as pursuant to CACM Article 28. | P | P | P | P | All TSOs will need to provide data to facilitate in relation to the individual grid model they will create in relation to Article 20. The SO will have additional responsibilities, as the SOs' individual grid models will be merged to form the common grid model. Please also refer to the MTSO decision for CACM article 28.
|  | Capacity Calculation Process | Regional Calculation of long-term Cross Zonal Capacity | 23 (1),(2) | Sub Articles (1) and (2) state conditions for the process of the calculation of long term cross zonal capacity when TSOs apply the statistical approach pursuant to Article 10, and states that the requirements of CACM Article 29 shall apply where relevant. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 29.
|  |  |  | 23 (3),(4) | These Sub Articles state that the coordinated capacity calculator shall split the calculated long-term cross-zonal capacity pursuant to Article 16, and that they shall submit it to each TSO within the capacity calculation regions. |  |  |  | P | The entity which will perform the role of the coordinated capacity calculator has yet to be determined, however existing capacity calculation is an SO role and so we consider it logical that this obligation will either become an SO function at regional level or it will be a function delivered by a third party.
|  | Capacity Calculation Process | Validation and Delivery of Cross Zonal Capacity and Split Cross-Zonal Capacity | 24 (1),(2), (3), (5) | Sub Articles (1), (2) , (3) and (5) require each TSO to validate results of calculation for long term cross -zonal capacity, for delivery and for splitting, pursuant to Articles 16 and 17. TSOs shall send these validations to the coordinated capacity calculator and to the other TSOs of the relevant CCR. Sub Article 5 requires TSOs to be able to provide the methodology for this validation on request. |  |  | P | P | We consider this Sub Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows.
|  |  |  | 24 (4) | Sub Article (4) requires coordinated capacity calculator to provide validated splitting of long-term cross-zonal capacity. |  |  |  | P | The entity which will perform the role of the coordinated capacity calculator has yet to be determined, however existing capacity calculation is an SO role and so we consider it logical that this obligation will either become an SO function at regional level or it will be a function delivered by a third party.
|  | Capacity Calculation Process | Coordinated Curtailment of Cross-Zonal Capacity | 25 (1) | Sub Article (1) requires TSOs to coordinate curtailments of allocated long-term cross-zonal capacity if the curtailments occur more than 48 hours ahead of the delivery date, and apply the capacity calculation process required by CACM Article 29 if the curtailments occur within 48 hours of the start of the delivery date. |  |  | P | P | We consider this Sub Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 29.
|  |  |  | 25 (2),(4) | Sub Articles (2) and (4) require TSOs to send requests for coordinated capacity curtailments to the coordinated capacity calculator, and to validate the updated cross-zonal capacity on its bidding borders or critical network areas pursuant to Article 24. |  |  | P | P | We consider these Sub Articles to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows.
|  |  |  | 25 (3),(5) | Sub Articles (3) and (5) require the coordinated capacity calculator to provide the updated cross zonal capacity to the relevant TSOs for validation, and to provide the validated updated cross zonal capacity to the relevant TSOs and SAP to perform curtailment pursuant to Article 53. |  |  |  | P | The entity which will perform the role of the coordinated capacity calculator has yet to be determined, however existing capacity calculation is an SO role and so we consider it logical that this obligation will either become an SO function at regional level or it will be a function delivered by a third party.
|  | Biennial Report on Capacity Calculation | Biennial Report on Capacity Calculation and Allocation | 26 (1) - (3) | Sub Articles (1) - (3) and (5) describe an ENTSOE task, and as such have not been individually allocated to TSOs. However, it is expected they will contribute as EC 714/2009 Article 4 states "All transmission system operators shall cooperate at community level through the ENTSO for electricity... to promote the completion of the internal market..." |  |  |  |  | We currently don't consider that these sub-articles put direct obligations on TSOs. This is consistent with our assignment of responsibilities for CACM Article 31.
|  |  |  | 26(4) | Sub Article (4) requires TSOs to agree on the statistical and quality indicators in their report. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 31.
|  |  |  | 26 (5) | Sub Article (5) requires the Agency to decide whether to publish all or part of the report. |  |  |  |  | This Sub Article does not address TSOs. This is consistent with our assignment of responsibilities for CACM Article 31.
| 2. Bidding Zones | General Provisions | General Provisions | 27 | This Article states that the bidding zones applicable to day ahead and intra day trading shall apply to forward capacity calculation and allocation. Where a bidding zone border no longer exists, holders of LTTR on this border shall be entitled to reimbursement by the concerned TSOs based on the initial price paid for the LTTR. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows.
| 3. Forward Capacity Allocation | General Provisions | General Principles | 28 | This Article sets out general principles for forward capacity allocation. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | General Provisions | Inputs and Results | 29 | This Article states the inputs that the SAP shall use to determine the allocation of forward capacity, and the outputs that it must determine. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Options for Cross Zonal Transmission Risk Hedging | Decision on Cross Zonal Risk Hedging Opportunities | 30 | This Article states that TSOs on bidding zone borders shall issue LTTRs unless agreed by the competent regulatory authorities of the bidding zone border. The Article describes how the relevant authorities shall make their assessment, and describes how the process for TSOs developing the necessary arrangements shall take place in case they are requested by the relevant authorities. This Article also states that upon the joint request of the relevant TSOs or at least every four years, the competent regulatory authorities shall make an assessment. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Options for Cross Zonal Transmission Risk Hedging | Regional Design of Long-Term Transmission Rights | 31 | Sub Article (1) requires long term cross zonal capacity to be allocated in the form of Physical Transmission Rights (PTR) subject to UIOSI or in the form of Financial Transmission Rights (FTR) (options or obligations). Sub Articles (2) - (6) outline the process that TSOs offering LTTR shall undertake in creating the regional design of these rights at a bidding zone border. Sub article (7) states how regulatory authorities may launch a review of LTTRs offered at a bidding zone border. Sub Articles (8) - (10) set out how TSOs in a CCR shall conduct a review or consultation pursuant to Sub Articles (4) and (9). |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Options for Cross Zonal Transmission Risk Hedging | Physical Transmission Rights | 32 | This Article entitles each holder of a PTR to nominate all or part of its PTR pursuant to Article 35, and states that where the holders do not make this nomination they are entitled to remuneration in accordance with Article 35. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Options for Cross Zonal Transmission Risk Hedging | Financial Transmission Rights - Options | 33 | This Article requires that holders of FTR-options shall be entitled to obtain remuneration in accordance with Article 35, and states that the implementation of FTRs shall be subject to the application of day-ahead price coupling in accordance with CACM Articles 38 to 50. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Articles 38-50.
|  | Options for Cross Zonal Transmission Risk Hedging | Financial Transmission Rights - Obligations | 34 | This Article requires that holders of FTR-obligations shall be entitled to receive or obliged to pay the financial remuneration in accordance with Article 35, and states that the implementation of FTRs shall be subject to the application of day-ahead price coupling in accordance with CACM Articles 38-50. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Articles 38-50.
|  | Options for Cross Zonal Transmission Risk Hedging | Principles for Long-Term Transmission Rights Remuneration | 35 | This Article states how the relevant TSOs performing the allocation of transmission rights on a bidding zone border through the SAP shall remunerate LTTR holders. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 23.
|  | Nomination Procedures for Physical Transmission Rights | General Provisions for Physical Transmission Rights Nomination | 36 | This Article states the general principles and provisions for TSOs issuing physical transmission rights on bidding zone borders. The Article states that TSOs issuing physical transmission rights shall submit to the relevant regulatory authorities a proposal for nomination rules for electricity exchange schedules between bidding zones. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 23.
|  | Nomination Procedures for Physical Transmission Rights | Terms and Conditions for Participation in the Forward Capacity Allocation | 37 (1), (3), | These Sub Articles state the terms and conditions that market participants must fulfil in order to participate in Forward Capacity Allocation, and states some requirements for market participants for complying with the HAR and for working with the SAP. |  |  |  |  | These Sub Articles address market participants, and do not place direct obligations on TSOs
|  |  |  | 37 (2), (4),(5) | These Sub Articles states how the SAP shall register a new sign up, and deal with a breach of contractual obligations under the HAR. |  |  | P |  | We consider this Sub Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Submission of Input Data to the Single Allocation Platform. | 38 | This Article requires each TSO shall ensure that validated splitting of long-term cross-zonal capacity is submitted to the SAP prior to the publication of the auction in accordance with Article 39. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Operation of the Forward Capacity Allocation | 39 | This Article requires that an auction should be published on the SAP, describes what should be included in the auction, and describes how the auction must take place. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Pricing of the Long Term Transmission Rights | 40 | This Article states that the price, direction of utilization, and market time unit of a LTTR on a bidding zone border shall be determined based on the marginal price principle and expressed in Euros/ MW, and describes the market conditions in which prices will be zero. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Financial Requirements and Settlement | 41 | This Article states how the SAP shall settle debits or credits resulting from the allocation of LTTR, and states a minimum required collateral for market participants to participate in the auctions. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Establishment of Fallback Procedures | 42 | This Article states that the default fall back procedure is the postponement of the forward capacity allocation, but also states that all TSOs in a CCR are entitled to implement alternative coordinated fall back solutions. In these cases, they should jointly develop a robust coordinated proposal. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Return of Long-Term Transmission Rights | 43 (1), (2) | These Sub Articles describe how LTTR holders can return their LTTR. |  |  |  |  | We currently don't consider that these Sub Articles put direct obligations on TSOs.
|  |  |  | 43 (3) | This Sub Article requires that the relevant TSO shall remunerate market participants who return their LTTR through the SAP, and states that the price shall be the one from the auction where the LTTR are reallocated. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Transfer of Long-Term Transmission Rights | 44 (1),(3), (4) | These Sub Articles state the manner in which holders of LTTR can transfer these rights. |  |  |  |  | We currently don't consider that these sub-articles put direct obligations on TSOs.
|  |  |  | 44 (2) | This Sub Article requires that a list of market participants who are eligible to transfer LTTR shall be published on the SAP. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Delivery of Results | 45 | This Article requires that the SAP notify the relevant market participants at bidding zone border about the result of the forward capacity allocation within the timeframe provided in the auction specification, and requires the SAP to make participants aware about the execution status and clearing prices of the bids. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Initiation of Fallback Procedures | 46 | This Article states that if the SAP cannot deliver the auction or the results of the forward capacity allocation within the timeframe set by the HAR, the relevant TSOs shall initiate the fallback procedure pursuant to Article 42. This article also states that the SAP shall notify market participants when fallback procedures will be applied. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  | Nomination Procedures for Physical Transmission Rights | Publication of Market Information | 47 | This Article states the market information that the SAP must make available. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
| 4. Single Allocation Platform |  | Establishment | 48 | This Article requires TSOs to set up the SAP. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Functional Requirements | 49 | This Article requires TSOs to submit a common proposal for a set of requirements, and for the establishment of the SAP. This Article also includes a list of the minimum functional requirements that the SAP must include. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | General Tasks | 50 | This Article describes the tasks that at a minimum the relevant TSOs must use the SAP for. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
| 5. Harmonised Allocation Rules |  | Introduction of Harmonised Allocation Rules | 51 | This Article requires TSOs to develop a proposal for HARs for LTTR pursuant to Article 52. The proposal shall include any regional and bidding zone border specific requirements if developed by the TSOs of a CCR. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Requirements for the Harmonised Allocation Rules | 52 | This Article describes the general requirements that the HAR for LTTR shall fulfil. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
| 6. Firmness of Allocated Cross-Zonal Capacity |  | General Firmness Provisions | 53 | This Article states that TSOs are allowed to curtail LTTRs in certain conditions, and states that they must report this to the relevant regulatory authorities if they do this. This Article also states that when such a curtailment occurs, TSOs on a bidding zone border shall compensate the holders of the curtailed LTTR with the market spread. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Definition of Caps | 54 | This Article states that the relevant TSOs may propose a cap on the total amount of compensation paid to holders of curtailed LTTR over a given time period. The Article also states a minimum value for this cap, and how to determine this if there are multiple interconnectors and regulatory regimes involved. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Compensation Rules | 55 | This Article states that where TSOs propose to apply a cap, they shall jointly propose a set of compensation rules with regard to the cap. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Firmness in the Event of Force Majeure | 56 (1),(2), (3), (4) | These Sub Articles describe how TSOs should act in a case of force majeure. They must coordinate, issue a notification and provide compensation where appropriate. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows.
|  |  |  | 56 (5) | This Sub Article states that where the member state has so provided, upon request from the concerned TSO, NRAs shall assess whether an event qualifies as a force majure. |  |  |  |  | We currently don't consider that this Sub Article put direct obligations on TSOs.
| 7. Congestion Income Distribution |  | Congestion Income Distribution Methodology | 57 | This Article states that within six months after the approval of the methodology for sharing congestion income referred to in Article 9 (6) of CACM, all TSOs shall jointly develop a methodology for sharing congestion income from forward capacity allocation, and states conditions that the methodology must fulfil, which are from CACM article 73. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows. Please also refer to the MTSO decision for CACM Article 73.
| 8. Cost Recovery |  | General Provisions on Cost Recovery | 58 | This Article states that costs incurred by TSOs arising from this regulation shall be assessed by the regulatory authorities, who should allow reasonable costs incurred to be recovered through an appropriate mechanism. | P | P | P | P | Applicable to all TSOs, as it is possible that all TSOs may incur some costs associate with this network code.
|  |  | Costs of Establishing, Developing and Operating the Single Allocation Platform | 59 | This Article states that all TSOs issuing LTTR on the SAP shall jointly bear the costs of establishment and operation of the SAP. This Article also states that within six months of entry into force, TSOs will propose a methodology for sharing these costs. |  |  | P |  | We consider this Article to be applicable to the ICs in their capacity as managers of cross border electricity flows.
|  |  | Costs of Establishing and Operating the Coordinated Capacity Calculation Process | 60 | This Article states that each TSO shall individually bear the costs related to the provision of inputs to the capacity calculation process, and that all TSOs shall jointly bear the costs related to merging individual grid models, and that all TSOs in a CCR shall bear the costs of the coordinated capacity calculators. | P | P | P | P | Applicable to all TSOs, as it is possible that all TSOs may incur some costs associate with this network code.
|  |  | Costs of Ensuring Firmness and Remuneration of Long-Term Transmission Rights | 61 | This Article states that the costs of ensuring firmness shall be borne by TSOs to the extent possible in accordance with Article 16 (6)(a) of Regulation (EC) No 714/2009, and that regulatory authorities shall consider compensation payments as eligible costs provided they are reasonable, efficient and proportionate, The Article also states that TSOs shall jointly develop a methodology for sharing costs to ensure firmness and remuneration of LTTR, which is consistent with Article 57. |  |  | P | P | We consider this Article to be applicable to both the SO in its capacity as the real time system operator and the ICs in their capacity as managers of cross border electricity flows. This is consistent with our assignment of responsibilities for CACM Article 79.
3. Delegation of Tasks and Monitoring |  |  | Delegation of Tasks | 62 | This Article sets out the conditions under which a TSO may delegate any of its tasks to a third party | P | P | P | P | Applicable to all TSOs, as it is possible that all TSOs may want to delegate to a third party. This is consistent with our assignment of responsibilities for CACM Article 81.
|  |  | Monitoring | 63 (1), (2), (3) | These Sub Articles specify an ENTSOE obligation and as such, has not been individually allocated to the TSOs, however it is expected that they will contribute as EC 714/2009 Article 4 states "All transmission system operators shall cooperate at Community level through the ENTSO for Electricity..... to promote the completion and functioning of the internal market...". They also state that The Agency, in cooperation with ENTSOe shall draw up a list of relevant information to provided to ENTSOe. |  |  |  |  | We currently don't consider that these Sub Articles put direct obligations on TSOs. This is consistent with our assignment of responsibilities for CACM Article 82 (1)-(4).
|  |  |  | 63 (4) | This Sub Article states that market participants and other relevant organisations shall submit to ENTSOE, upon request, information required for monitoring. | P | P | P | P | Applicable to all TSOs as it is possible that all TSOs maybe required to provide information. This is consistent with our assignment of responsibilities for CACM Article 82 (5)-(6).
4. Final Provisions |  |  | Entry into Force | 64 | This Article states that the FCA Guideline will enter into force the day after its publication in the Official Journal of the European Union. |  |  |  |  | We currently don't consider that these Sub Articles put direct obligations on TSOs.
|  | Subgroup | TSOs
|  | OFTO | Blue Transmission Investments Ltd, Balfour Beatty Investments, Transmission Capital Partners.
|  | TO | Scottish Hydro Electric Transmission plc, SP Transmission plc, NGET (TO)
|  | I/C | National Grid Interconnectors, Britned Development Ltd, Eirgrid IC Ltd, Moyle Interconnector Ltd
|  | SO | National Grid (SO)