## Note
This is a workbook summarising the document of testing, validation and calibration plan (the plan) for the NOMs methdology
Draft version 0.1 | work in progress
Any inconsistencies with the plan will be resolved baselining the plan
The time scale and resource is only an indication without anything committed
Some of the calibration cases might not be performed if the validation cases are proved to be satisfactory
All the time scales are resouces assuming the model and framework in the NOMs methdology is developed in a reasonable quality. This time scale does not include re-development or heaviy re-iteration needed upon negative testing and validation results.
The time scales and resources also assuming highly skilled and motivated modeller and analytics, and work in a collobrative and efficient way. It does not include project management resource requirement, etc. Other assumptions are the same with the assumption for the time scale.

## Section2
CALIBRATION, TESTING, AND VALIDATION PLAN WORKBOOK | [13 empty] | Non-committed indicative, and current understanding, need further refinements and discussions
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail | Column1 | Expected time scale (weeks) | Resource expected (No. of FTE or equivalent) | comments
2.2.1 | Health score | TBA | coefficents for the health score calculation | Input | All Licensees | Calibration | Maximise the compatibility between the health score and the asset health index | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | High degree of compatibility, with differences reviewed and justified. | If the maximium compatibility is low by going through all the parametric space, it might need to review the model itself and re-develop the health score formulae |  | 2 | 4 | This time scale assume the data that used to calculate the health score is available, and the time scale does not include the model re-development and re-calibration. Propose one person for each asset type
2.2.2 | Health score | TBA | Anticipated asset life | Input | All Licensees | Calibration | Use end-of-life data to calibrate the anticipated asset life for each asset type, where possible | Statistical analysis facilitated by some bias correction techniques, some envelope estimation may also be possible, some machine learning techniques can be used, some simulations are also possible to simulate the anticipated asset life | asset end of life data plus foresenic data. if using simulations, the model derived from case 2.2.1 can be used, the current asset life may be also used as part of the inputs if there is no data available | Yes | It is an calibration exercise - pass as long as the anticipated asset life can be justified by data and the method - subject to review and agreements (e.g., TOs and Ofgem) | Where reasonable, the TOs should align the anticipated asset life with data, followed by updating where affected and impact assessments |  | 3 | 4 | there will be data collection, cleanse and data manipulation, combination exercises, the scale of which is considered as moderate. Propose one person for each asset type
2.2.3 | Health score | TBA | Anticipated asset life | Input | All Licensees | Calibration | Make sure the same asset type have similar asset life across the TOs, under a reasonable and like-for-like comparison | Comparison studies facilitated by expert review | Each TO's asset life data for each asset ype - subjecting to confidentiality issues | Yes | A comprehensive study with differences justified - may lead to change of TOs' asset life | Where reasonable, actions should be taken to unify TOs' asset life, followed by updating where affected and some impact assessment |  | 2 | 4 | changing asset life may take much longer than expected due to its impact on investments, etc. The time scale here is only to deliver recommendations with sufficient justifications. Propose one person for each asset type
2.3.1 | Health score | TBA | Factors and ingredients included in the formulae | Process | All Licensees | Testing | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Comparison study between the current process and the formulae, different ingredients used should be justified | Each TO's asset health process; subject matter experts; where possible international standard might be also considered | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the health score formulae |  | 2 | 2 | assuming the asset health processes are well documented for each TO and minimum data collection required - the time scale does not include any re-development work
2.3.2 | Health score | TBA | The formats of the formulae | Process | All Licensees | Testing | To test the formats of the formulae captures the underlying interactions between different condition measures of the assets | Coefficient calculation (see 2.2.1) across different datasets (calibration and validation use different parts of the data) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae |  | 2 | 4 | providing the calibration model is developed in 2.2.1, propose one person for each asset type
2.3.3 | Health score | TBA | Assumption: the number of defects (instead of the severity of defects) is representative to the impact of the defect to the asset condition. | Process | All Licensees | Testing | To understand the assumption and the material impact of making the assumption | Data deep dive followed by subject matter review, also, compare the number of defects with the asset health index | defect database | yes | Defect severity can be ignored (or averaged out in some way) when using number of defects | Re-develop the health score formulae if the assumption is proved to be invalid |  | 4 | 1 | considerable data cleanse effort required, it can stop when negative results can be proved or positive results are satisfactory
2.3.4 | Health score | TBA | Assumption: the correlations and interactions between each condition factor in the health score | Process | All Licensees | Testing | To understand the rationale behind the formulae - this is already tested (in some degree) by 2.3.2 | correlation analysis of the condition data where possible + workshops | expert opinions, data behind the health score formulae | yes | A documentation supporting the correlations and interactions between the factors in the formulae - approved by the TOs and Ofgem | Re-develop the health score formulae |  | 2 | 4 | part of the formats of the formulae already tested by case 2.3.2. If it passed, it highly likely this case will pass. One person for each asset type
2.4.1 | Health score | TBA | General | Output | All Licensees | Validation | To verify that the model is constructed according to designed specifications | Independent review | data used in the NOMs methodology (both current and the modified) | yes | All the designed specifications are covered by the health score model | Re-develop the health score model |  | 2 | 1 | this should be straightforward however require someone independent/impartial while understand the TOs' assets (or able to seek for asset experts support, e.g. Ofgem may be in the position to review this)
2.4.2 | Health score | TBA | health scores and forecast | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | case study using data manipulation, categorisation, and visualisation | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model |  | 2 | 1 | providing the functionalities of the NOMs model are developed, all the scenarios and the health score can be calculated in a straightforward manner
2.4.3 | Health score | TBA | uncertainties from inputs | Output | All Licensees | Validation | Understand the impact of uncertainties from input on the outputs (health scores) | Monte Carlo method | Estimation of the uncertainties; or some uncertainties can be drawn directly from the data (e.g. the same condition factor may vary with time, etc.) | yes | The impact of uncertainty is understood and acceptable | Take consideration of uncertainties more explicitly in the health score models |  | 4 | 1 | this is a relatively straightforward task but require some coding skills - some data exercise may be required to infer the level of uncertainties from each input
2.4.4 | Health score | TBA | material impact of the uncertainties | Output | All Licensees | Validation | Validate whether uncertainties have material impact | Established techniques and references regarding uncertainty cost, together with TOs activities to reduced uncertainties (e.g. inspection cost, etc.) | cost data and technical regimes for inspections, external references, etc. | yes | The uncertainty is regarded as no material impact or minimal material impact | Take consideration of uncertainties more explicitly in the health score models |  | 4 | 2 | it is not aiming to provide how much uncertainty cost - significant longer time scale needed for the development work (as it might impact other parts of the methodology)
2.4.5 | Health score | TBA | uncertainties of the model | Output | All Licensees | Validation | Make sure the model is robust enough to cope with possible scenarios and identify gaps in the model (that might lead to risk management options) | Stress test | assumed scenarios unless there are data available in a public domain regarding a deteriorated network, etc. | no | The model performs the desired functionality under stressed condition (e.g. worse asset health) | Establish some risk management framework to manage those uncertainties, including making sure the model is used in the designed domain |  | 4 | 3 | This might be an important area - to establish a risk framework that is aiming to capture those outliers?
-
[6 empty] | - | [7 empty] | Time (weeks) | Resouce (FTE weeks)
[6 empty] | - | [6 empty] | total | 33 | 80
-
-
Note on C3: National Grid: Will be updated against the final version of the methdology
Note on D3: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F3: National Grid: This will be more apparent when we know where the specific appendices look like
Note on O3: National Grid: assuming the model and framework in the NOMs methdology is developed in a reasonable quality. This time scale does not include re-development or heaviy re-iteration needed upon negative testing and validation results.
Note on P3: National Grid: assuming highly skilled and motivated modeller and analytics, and work in a collobrative and efficient way. It does not include project management resource requirement, etc. Other assumptions are the same with the assumption for the time scale.

## Section 3
CALIBRATION, TESTING, AND VALIDATION PLAN WORKBOOK | [13 empty] | Non-committed indicative, and current understanding, need further refinements and discussions
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail |  | Expected time scale (weeks) | Resource expected (No. of FTE or equivalent) | comments |  | worse case (some of the cases will be only triggered if a tesing/validation case is failed) | better case (assume all the cases are not triggered - pass all the testing/valdation cases)
3.1.1 | FMEA | TBA | failure mode, failure rate (indicative), freuquency of events (indicative), and detection | Output | NGET Only | Validation | To use the failure, fault and defect database to validate those used in the FMEA workshops | Data cleanse and data manipulation, may be facilitated by machine learning techniques, guided by subject matte expert | asset data with asset type, fault, failure and defect data, and data deep dive, data from the FMEA workshop | Yes | results from the fault, failure, and defect database is compatible with those from FEMA workshops | Trigger calibration case 3.1.2 |  | 8 | 4 | This is probably the most time consuming exercises in the NOMs methodology - data cleanse and manipulation is not a trivial task and require significant database and engineering knowledge plus the understanding of the NOMs methodology (what those data is used for and how to test and whether the outcomes are credible, bias and gaps from the data, any alternative approach, etc.). If possible, data gaps and future data collection ideas should also be recorded. It might be a worthwhile to do so as the outcome from this data exercise can be used as a basis for a large number of following cases. Proposing 4 people working on it each responsible for an asset type | 8 | 1 | 1 | 32
3.1.1a | FMEA | TBA | failure mode effect, failure rate (historic failures and defects) from TO's and ITOMS (International Transmission Operations & Maintenance Study) failure and defect data. | Output | SHE-T & SPT Only | Validation | Determine applicable failure rates for the Failure Effect categories to set the C and K parameters used to determin POF | Data cleanse and data manipulation, may be facilitated by machine learning techniques, guided by subject matte expert | asset data with asset type, fault, failure and defect data, and data deep dive, data from TO's Failure or Defect databases and ITOMS datasets and/or expert judgement from data review sessions | No | results from the fault, failure, and defect database is compatible with those from ITOMS datasets | Trigger calibration case 3.1.2a |  |  |  | Part of the CBRM Calibration process requires collection of failure data classified/grouped by Failure Effect so this test can be aligned with the CBRM Calibration step of extracting data to match the Failure Effect categories desriptions (DEFECT /MINOR/ SIGNIFICANT/ MAJOR/ REBUILD) which in turn will be used for the calculation of a Failure Effect specific K value which will be used in conjuction with the condition data derived equivilant age in the 3rd Order Polynomial calculation to calculate a PoF value for the Failure Effect. As with the NGET data the sources will be a mixture of failure data / expert judgement and industry understanding. Note that Failure Mode data is not collected. However it may be possible to determine asset type based consquence templates which can be used in the NOMS Methodology going forward which can be validated also.
3.1.2 | FMEA | TBA | failure mode, failure rate (indicative), freuquency of events (indicative), and detection | Input | NGET Only | Calibration | review guided by subject matter experts and possibly re-calibration of the failure modes, event types, and corresponding probabilities, based on the data analyses performed in case 3.1.1 | Same with above, the FMEA workshop data might be used to fill data gaps (in an informed way) | same as above | Yes | It is an calibration exercise - pass as long as the failure modes, probabilities, etc. can be justified by data and the method - subject to review and agreements (e.g., TOs and Ofgem) | Failing those calibration case will lead to significant delay towards to NOMs methodology development - some further data collection exercise may be triggered (e.g. another round of FMEA workshops by explaining why the previous ones fail) |  | 8 | 4 |  | 0 | 1 | 0 | 0
3.1.2a | FMEA | TBA | failure mode effect, failure rate | Input | SHE-T & SPT Only | Calibration | review guided by subject matter experts and possibly re-calibration of the failure modes event types and failure rates, based on the failure of data analyses performed in case 3.1.1 using Structured Expert Judgement Techniques | Structured Expert Judgement Techniques (for example using The SHeffield ELicitation Framework or Classic Model. | same with above | No | It is an calibration exercise - pass as long as the failure modes, probabilities, etc. can be justified by data and the method - subject to review and agreements (e.g., TOs and Ofgem)
3.1.3 | FMEA | TBA | end of life failure mode | Output | All Licensees | Validation | Compare the end-of-life failure mode between the current NOMs methodology and the modified NOMs methodology to validate those end-of-life curves obtained from the FMEA for NGET and CBRM in Scottish TOs | Comparison studies facilitated by expert review | data used in the current NOMs methodology and data in the modified NOMs methodology, regarding end of life curves | Yes | A comprehensive study with differences sufficiently justified | Trigger calibration case 3.1.5 |  | 4 | 1 |  | 4 | 1 | 1 | 4
3.1.4 | FMEA | TBA | end of life failure mode | Output | All Licensees | Validation | where possible, validate the end-of-life failure mode for each asset type using data-driven methods | Combine the failure database and the replacement database and possibly forensic database to calculate probability of failure curve or its lower bound | failure database and replacement database and possibly forensic database | Yes | the database support the end of life failure mode (probabilities for earliest, anticipated, and latest onset) | Trigger calibration case 3.1.5 |  | 4 | 1 | most time spent on identifying and collecting what data is available and what can be done using limited data source (e.g. upper/lower bound estimation, etc.) | 4 | 1 | 1 | 4
3.1.5 | FMEA | TBA | end of life failure mode | Input | All Licensees | Calibration | make sure the end of life failure mode is sufficiently justified | as per case 3.1.3 and case 3.1.4 | as per case 3.1.3 and case 3.1.4 | yes | It is an calibration exercise - pass as long as the re-calibrated values can be justified by the above two validation cases - subject to review and agreements (e.g., TOs and Ofgem) | It is unlikely to fail if the all the actions suggested in the above 2 cases are carried out - when it has been demonstrated to be unable to calibrate, a decision has to be made by understanding the impact of the end-of-life mode on the final outcomes (i.e. impact on the monetised risks) |  | 4 | 4 | only needed to be done when the above 2 cases fail, and the time scale is by assuming reasonable number (~50%) of asset types will pass the above 2 validation cases, Proposing 4 people working on it each responsible for an asset type | 0 | 1 | 0 | 0
3.1.6 | FMEA | TBA | disruptive failure | Output | All Licensees | Validation | while the probability of disrutpive failures used, the failure database should be used to validate the probabilities | statistical analysis where data is available and implied failure probability when data is not available, reviewed by engineering experts | failure database and forensic data where possible, end of life failure (mode) data | yes | The disruptive failure mode is appropriately addressed in the methodology with validated probabilities, in order to correctly model the scenarios associated with the disruptive failures | update the probability of failure for the disruptive cases |  | 2 | 1 | This should not be too difficult as the disruptive failure is relatively well understood and recorded. The problem might be how it is modelled and incorporated in the monetised risk - i.e. the risk of an asset is associated with steady replacement programme or associated with what worst can happen to those assets - assumptions need to be clarified and agreement need to be obtained across the TOs and with Ofgem | 2 | 1 | 1 | 2
3.1.7 | FMEA | TBA | disruptive failure | Input | All Licensees | Calibration | while the probability of disrupive failures used, the failure database should be used to calibrate the probabilities | as above | as bove | yes | as above | Re-develop the disruptive failure model and update all elements that are affected |  | 3 | 1 | see above | 3 | 1 | 1 | 3
3.1.8 | FMEA | TBA | none end-of-life failure modes | Output | NGET Only | Validation | to use the cost information to validate the maintenance related probabilities and failure modes | equivalent annual cost calculation | maintenance cycle, maintenance cost, maintenance script, the non end of life failure modes and the interventions from the FEMA workshops | yes | the maintenance cycle is relatively optimised and the maintenance cost is comparable with the risk cost | trigger calibration case 3.1.9 |  | 6 | 2 | there is very limited information regarding none end-of-life failure modes at the moment. When the details are clearer, there might be other ways of validation and calibration the methodology. On the other hand, the method proposed here is only treated as indicative as maintenance may be determined by other factors instead of cost efficiency, which needs to be further understood | 6 | 1 | 1 | 12
3.1.9 | FMEA | TBA | none end-of-life failure modes | Input | NGET Only | Calibration | to use the cost information to calibrate the maintenance related probabilities and failure modes | as above | as above | yes | it is a calibration case, pass as long as the validation case above can be achieved using the re-calibrated values | re-visit and re-held the FMEA workshops if possible, or seek alternatives, e.g. make assumptions towards the relationships between end of life mode and none end of life mode, etc. |  | 6 | 2 | see above | 0 | 1 | 0 | 0
3.1.10 | FMEA | TBA | none end-of-life failure modes | Output | All Licensees | Validation | make sure the non-end-of life failure modes are of reasonable values and comparable between TOs | Comparison studies facilitated by expert review, Note that translation between definitions from different TOs might be essential to enable a like-for-like comparison. | non-end-of life failure modes and values of each TO (subjecting confidentiality agreement) | yes | where comparable, the non end of life failure modes are within reasonable range between TOs | Trigger calibration case 3.1.9 after identifying the cause of the discrepencies |  | 2 | 1 | assuming all the non end of life modes are appropriately developed and detailed in each TOs NOMs methodology | 2 | 1 | 1 | 2
3.2.1 | FMEA | TBA | assumption of independence | Process | NGET Only | Testing | the assumptions of inter-dependence (or "after processing") is heavily assumed when the model combines different failure modes and events together, it is crucial to test those assumptions using data facilitated by engineering knowledge and experience | Data categorisation and data mining, facilitated by engineering knowledge. This should be easier as long as some previous data work (3.1.1, and 3.1.2) has been done. Tests also need to be performed to confirm that those are truthfully reflected in the model | same with 3.1.1 and 3.1.2 | yes | the events can be modelled as "independent after processing" and this is truthfully reflected in the FMEA modelling | Refine or re-develop the model |  | 2 | 2 | Assuming the data is already in a reasonable state from the previous case, while the model is readily available to review with sufficient documentations on details of modelling. It is not designed to go to the code to check whether there is bugs in the code or whether the code and documentation are consistent. These should be covered by standard testing in the area of e.g. software development. | 2 | 1 | 1 | 4
3.2.2 | FMEA | TBA | data needed to model inter-dependence | Input | NGET Only | Calibration | In the case some of the inter-dependent failure modes has to be modelled, there are chances the data above is not sufficient to address those inter-dependence. Further justification, including impact study, workshops, etc. may be needed to model/ignore those inter-dependence | workshops, sensitivity test | Extra information souces from e.g. engineering experience and workshops, data from other companies, sectors, etc. | no | The inter-dependence is deemed as non-material and/or data can be drawn from additional information sources | It is unlikely to fail on this case - the worst situation is that the data is not accurate enough and may lead to some non-credible outputs. However this should be demonstrated using the sensitivity tests, etc. |  | 2 | 2 | one person do the extra data another do the sensitivity test - again, this assumes all the model, tools, documentations are in appropriate place | 2 | 1 | 1 | 4
3.2.3 | FMEA | TBA | the modelling of probability of failure (as a function of age) | Output | NGET Only | Validation | To demonstrate different types of models are considered | statistical analysis with data cleanse and manipulation | Case study data for end of life failure data | yes | the current model explains well the data in the case study - we do not expected a "hard" pass criterion here but to demonstrate this area has been considered | The risk of failing this is relatively low because NGET has performed similar type of case studies before - as a flexible and widely used model, the Weibull's failure model is expected to give reasonable good performance. If failed to validate case 3.2.4 will be triggered |  | 1 | 1 | In theory all the TOs should be able to perform this exercise however some of the models may be subjecting to IP agreement with EATL. On the other hand, the credibility from EATL might be providing some sorts of validation | 1 | 1 | 1 | 1
3.2.4 | FMEA | TBA | the modelling of probability of failure (as a function of age) | Input | NGET Only | Calibration | To find a suitable (analytical) probability distribution model if the above case failed | use known analytical probability functions and compare their performance | same as above | yes | demonstrate the best performance probability function, with the consideration of simplicity and applicability | n/a |  | 2 | 1 | as above | 0 | 1 | 0 | 0
3.2.5 | FMEA | TBA | intervetion - the assumption of perfect intervention | Process | NGET Only | Testing | to test and understand the assumption that all the intervention types are assumed as perfect (i.e. reset the corresponding risk to zero) | expertise survey, data deep dive, or scenario test (to compare the outcomes of perfect and imperfect interventions) | link the repair data and maintenance data with the performance data (defect, fault, and failure rate) and understand the model performance before and after those type of interventions | yes | the assumption is regarded as suitable or non-material | refine the modelling to introduce imperfect modelling (and subsequence calibration activities, see below) |  | 3 | 1 | it will be focusing on the non-end-of life type of modes that require intervention - the end of life - replacement type of intervention can be safely regarded as perfect intervention. The time scale assumes the fault, defect and failure data is in a reasonable state from exercises such as 3.1.1 | 3 | 1 | 1 | 3
3.2.6 | FMEA | TBA | intervention - the calibrate of imperfect intervention | Input | NGET Only | Calibration | To quantify the level imperfection if the imperfect intervention is deemed as important | use the data obtained above (may need more data but following the same data process technique) to work out an "equivalent imperfection level" that can be relatively easy to be incorporated in the risk model | same with above | yes | the imperfection of intervention can be addressed sufficiently using a relatively simple model | Other techniques will be explored if it can't be modelled in a relatively simple way |  | 6 | 1 | further validation on the model may be needed | 0 | 1 | 0 | 0
3.2.7 | FMEA | TBA | model functionality - asset replacement (none like-for-like replacements) | Process | NGET Only | Testing | different asset types may have different failure modes and probability of failure curves, the model should address this appropriately (for example, replace an oil filled cable with a XLPE cable) This should be relatively easy to model | model review and confirm the logic | n/a | no | the model address this specification sufficiently | further development of the model (should be relatively straightforward) |  | 1 | 1 | n/a | 1 | 1 | 1 | 1
3.3.1 | FMEA | TBA | failures modes - the assumption of mutual exclusitivity | Process | NGET Only | Testing | the model used in the NGET methodology requires (assumes) the failure modes are independent but not mutually exclusive, i.e. in theory those modes can fail at the same time. This assumption needs to be carefully tested by reviewing the definitions and physical process of the failure modes in the FMEA spreadsheet. If inconsistencies found, either case 3.3.2 needs to be triggered or some justifications needed to demonstration non-materiality | subject matter experts and collective opinion | FMEA spreadsheet to review the assumption. The defect, fault and failure data needed to demonstrate non-materiality | yes | either the assumption is valid or non-material | alternative modelling method required, a number of parts of the overall model will be affected, see case 3.3.2 |  | 2 | 1 | assume the data required is ready to use based on data cleanse exercise in e.g. case 3.1.1 | 2 | 1 | 1 | 2
3.3.2 | FMEA | TBA | probability of events | Input | NGET Only | Calibration | if the above case 3.3.1 fails, this case is required to re-establish a model that can be used in calculating the probability of events | On top of the FMEA sheet, a full list needed to address which failure modes are mutual exclusive which can not be ignored. Then it is straightforward to model the mutual exclusivity using simple probability manipulation | FMEA spreadsheet | yes | the relationship between the model and the failure modes is fully understood/clarified | an unlikely event that this will not go anywhere, the FMEA spreadsheet might need to be modified, and workshops need to be re-held. This will impact a large number of areas on the established models |  | 4 | 1 | Most of the time will be consumed to make the rest of the methodology align with the new model | 0 | 1 | 0 | 0
3.3.3 | FMEA | TBA | probability of failure (Scottish TOs) and probability of events (NGET) | Output | All Licensees | Validation | where possible compare the probability of failure and probability of events between different TOs | comparison case study for same the asset types | no extra data is needed as long as those probabilities are tested and validated in the previous cases | yes | for the same asset type for the similar event/failure type, the probabilities should be in the same order of magnitude | root cause needs to be identified to understand the different - it is important the comparisons are like-for-like |  | 4 | 1 | deep understandings of both methodologies are needed (NGET vs. Scottish TOs) - it is a good exercise also for regulatory and performance benchmarking purposes. Some confidentiality issues need to be resolved beforehand | 4 | 1 | 1 | 4
3.4.1 | FMEA | TBA | the probability of detection and (act accordingly) | Process | NGET Only | Testing | make sure the modelling for probability of detection and act accordingly include the cost of detection and act according, at the same time, various assumption, e.g. fixed probability of detection, and identify probability of detection and probability of acting accordingly, etc. | review and test the model under different scenarios, some data may be needed especially successful detection and act accordingly cases and unsuccessful cases in the history | historical detection cases, inspection regime, and asset management guidelines and activities (act accordingly) around this area | yes | the model truthfully reflects what the TOs asset management practices while quantitatively address the detection activities, at the same time, various assumption around this area are deemed as valid | re-develop or refine the way the detection is modelled |  | 2.5 | 1 | the detection and acting accordingly is not a trivial task to model - this is to do with uncertainties and prior and posterior probabilities. There are some of literatures/text books in this area which can be referred. The time scale is to review the model and assumptions instead of re-develop the model, which is a much bigger task | 2.5 | 1 | 1 | 2.5
3.4.2 | FMEA | TBA | the probability of detection and (act accordingly) | Output | NGET Only | Validation | to validate the value of the probability of detections (and act accordingly). | The direct data mining can be hard (it is possible new data source can be identified to mitigate this problem). It is proposed here to use the cost of inspection and the risk avoidance due to inspection to provide validation and assurance to the probability of detection (and act accordingly) | The cost of inspection, risk avoided (historical interventions triggered by inspections), as well as the indication from the FMEA spreadsheets | yes | the cost of inspection can be justified by the risk avoidance (in the same ballpark), and also consistent with FMEA spreadsheets | trigger case 3.4.3 |  | 4 | 1 | The inspection regime might not be optimised so this exercise might not be as valid as an ideal case. If this is the case, some sensitivity tests can be done while ALL other factors in the risk model is fixed. the probability of detection can be then drawn from the cases similar to case 3.1.8. Anyhow much understanding can be drawn from this exercise, for example, how to further optimise the inspection regime. | 4 | 1 | 1 | 4
3.4.3 | FMEA | TBA | the probability of detection and (act accordingly) | Input | NGET Only | Calibration | to calibrate the value of the probability of detections (and act accordingly). | Assuming the inspection is optimised, the calibration can be done by comparing the inspection regime and the risk avoidance. See the notes for the case if it is not optimised | same as above - NB. The above case might not need to cover all asset types as long as validity can be demonstrated however this case might need cover all asset types if the validity can not be justified | yes | appropriate detection probability can be obtained and can be used to produce credible risk-related outputs from the model | see the note in column Q |  | 4 | 4 | see above, Proposing 4 people working on it each responsible for an asset type | 0 | 1 | 0 | 0
3.5.1 | FMEA | TBA | compatibility - health score and probability of failure (and/or probability of events) | Output | All Licensees | Validation | to validate that the probability of failure (or probability of events) is compatible with the health score modelling, for each asset type. | compare with the probability of failure (and/or probability of events) - health score curve with the fault, failure and defect data, by assigning the underlying assets with the health score. Direct data plotting may not be possible (due to sparse data or data availibility) but a small amount of data should be able to form a basis for the following review by subject matter experts, and/or comparison with industrial normalised information. | fault, defect and failure data established in 3.1.1, together with historical health score information, as well as subject matter experiences and published (nominal) information for the industry | yes | the comparison studies returns positive outcomes | trigger case 3.5.3 |  | 4 | 4 | the compatibility between the health score - ageing model and probability of failure - ageing model is not guaranteed judging from the current version of the methodology. Assigning historical health score, searching industrial information, and running workshops takes time. Proposing 4 people working on it each responsible for an asset type | 4 | 1 | 1 | 16
3.5.2 | FMEA | TBA | compatibility - health score and probability of failure (and/or probability of events) | Output | All Licensees | Validation | same as above | Compare the probability of failure (or probability of events) - health score curve between the NGET approach and the Scottish TOs’ approach, for the same asset type and same failure mode or event, where possible. | the detailed methdologies of all the TOs, including the numeric values | no | the comparison studies returns positive outcomes | trigger case 3.5.3 |  | 2 | 4 | the health score - probability function is consistent between the NGET and Scottish TO approach, providing the failure modes/events are like-for-like comparison. This is an important exercise and in fact provide an additional dimension to compensate the problem of sparse data, etc. | 2 | 1 | 1 | 8
3.5.3 | FMEA | TBA | compatibility - health score and probability of failure (and/or probability of events) | Input | All Licensees | Calibration | to re-calibrate the health score - age model (assuming the probability of failure (or events) - age model is already validated/calibrated from previous exercises) | Align the different models and also align the models with data/engineering experience as detailed in the above two cases | a combination of the above two cases | yes | the above two validation cases can be satisfied | seek for roots cause of the inconsistencies and alternative methods. For example, some more information may be obtained from the study proposed by case 3.5.4 (using extra information borrowed from current NOMs methodology) |  | 4 | 4 | once the above cases are established, the calibration process should not be too difficult and may be run parallel with the validation case, if planned efficiently | 0 | 1 | 0 | 0
3.5.4 | FMEA | TBA | health score and ageing (end of life modifier) | Output | All Licensees | Validation | use the current NOMs methodology to validate (or provide some sense of assurance) regarding the health score - ageing model | use the health score, age plotting for all asset types and all assets. Historical health score can also be used. The plotting can be super-imposed with the current NOMs methodology deterioration model to visualise the comparison | current NOMs methodology, asset inventory, health score (calculated from the modified methodology), and /or historical information of all above | yes | the health score- age plot and the current deterioration model is comparable and the difference can be explained | trigger case 3.5.3 |  | 2 | 4 | Note: the modified NOMs methodology should not be constrained by the existing methodology however such comparison study is very meaningful by providing reassurance that the new development is on the right track. It would be also useful that the discrepancies can be understood and explained. Also, it should be ok to do for all licensees although the context is mainly NGET based | 2 | 1 | 1 | 8
3.5.5 | FMEA | TBA | health score (focusing on the age element and end of life modifier) | Output | All Licensees | Validation | make sure assets will be prioritised appropriately according to the health score, with as little outliers as possible | Extreme value testing, and if possible, compare with known physical condition criteria (for example, strength criteria for overheald lines) | known (physical) condition measures if possible | yes | the number of outliers are minimised | refine the health score model, using methods proposed in section2, and development a method to highlighting outliers |  | 2 | 4 | one person for each asset type - this case is closely linked with the health score discussions in section 2 | 2 | 1 | 1 | 8
3.5.6 | FMEA | TBA | forecast model for the health score | Output | All Licensees | Validation | validate the deterioration forecast model, for the health score | data driven modelling using e.g. probalistic methods | use historical health score information and age information to compare against the deterioration model of health score (note the there might be some statistical bias in the data regarding e.g., de-commissioned assets, i.e. data censor). The current deterioation model can also be used for reference/comparison purposes | yes | the health score data supports the health score deterioration model in the modified NOMs methodology | trigger case 3.5.7 |  | 2 | 4 | This is a direct comparison and data plotting task, which should be relatively straightforward. One person for each asset type is proposed | 2 | 1 | 1 | 8
3.5.7 | FMEA | TBA | forecast model for the health score | Input | All Licensees | Calibration | calibrate the deterioration forecast model, for the health score | as above | as above | yes | calibrate the deterioration model to a satisfactory level | in a rare case that the health score data can not be modelled (in theory this should not happen), expert opninion may be used to agree a deterioraiton model using visualised, trial and error type of approach |  | 4 | 4 | one person for each asset type - it is likely that the data is more scattered instead of converged. In those case, some advanced modelling apprach such as machine learning can be used to establish a refined deterioration model | 0 | 1 | 0 | 0
3.6.1 | FMEA | TBA | probability of events | Output | All Licensees | Validation | validate the probability of events using known risk assessment | data manipulation based on understanding on known risks, to enable the comparison between low risk and high risk assets | probability of events from NOMs methdology; known risk assessments | yes | the probability of events reflects the known risks (e.g. known high risk assets will have high probability of events) | various elements contributing to probability of events need to be reviewed to find root cause. Corresponding re-calibration extercises will be triggered |  | 2 | 4 | not necessarily cover all known risks but generics ones such as using the existing intervention plan, or strategic spare holdings, etc. | 2 | 1 | 1 | 8
3.6.2 | FMEA | TBA | probability of events - end of life | Output | All Licensees | Validation | validate the probability of events using established models | portfolio risk modelling to infer intervention (replacement) volumes to manage the portfolio risk level | the one above + establised models (e.g. Ofgem's survivor model) | yes | the two models suggest similar level of replacement volume required | as above |  | 1 | 4 | one week should be enough providing both model are already available. One person per asset type | 1 | 1 | 1 | 4
3.6.3 | FMEA | TBA | probability of events - maintenance | Output | All Licensees | Validation | validate the probability of events against deferred maintenance risk assessments | similar with 3.6.1 plus historical deferred maintenance risk assessment information | the one above + establised models (e.g. Ofgem's survivor model) | yes | the probability of events as a function of time truly reflect the suggested risk from the deferred maintenace risk assesment | as above |  | 4 | 4 | the reason for a longer period of time is because there are much more maintenance related failure modes and events than end of life modes and events, one person for each asset type | 4 | 1 | 1 | 16
[14 empty] | worse case |  |  | Better case
[14 empty] | Time (weeks) | Resouce (FTE weeks) |  | Time (weeks) |  |  | Resouce (FTE weeks)
[13 empty] | total | 111.5 | 280.5 |  | 69.5 |  |  | 160.5
Note on C3: National Grid: Will be updated against the final version of the methdology
Note on D3: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F3: National Grid: This will be more apparent when we know where the specific appendices look like
Note on O3: National Grid: assuming the model and framework in the NOMs methdology is developed in a reasonable quality. This time scale does not include re-development or heaviy re-iteration needed upon negative testing and validation results.
Note on P3: National Grid: assuming highly skilled and motivated modeller and analytics, and work in a collobrative and efficient way. It does not include project management resource requirement, etc. Other assumptions are the same with the assumption for the time scale.

## Section 4
CALIBRATION, TESTING, AND VALIDATION PLAN WORKBOOK | [13 empty] | Non-committed indicative, and current understanding, need further refinements and discussions
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail |  | Expected time scale (weeks) | Resource expected (No. of FTE or equivalent) | comments |  | worse case (some of the cases will be only triggered if a tesing/validation case is failed) | better case (assume all the cases are not triggered - pass all the testing/valdation cases)
4.1.1 | FMECA | TBA | cost of (material) consequence - the model | Process | All Licensees | Testing | Review and understand the validity of using a representative value to model the cost of (material) consequences. Special care is needed when modelling the events that have got no material consequence (in order to reflect probability of (material) consequence). | independent review using existing process and data | using the cost of events data to review whether the cost of (material) consequence fit the purpose - i.e. taking consideration the variability and the no material consequence events. | Yes | Equivalent monetised risk should be obtained using the with/without variability modelling. Plus the "zero consequence events" are sufficiently addressed | refine the approach of obtaining material consequence cost in the NOMs methodology |  | 4 | 1 | the logic and the detailed methodology should be reviewed using available data. One or two asset types and failure modes and event types will be used instead of going through all asset types, etc. It is unclear about the details in this approach for the modified NOMs methodology, which is one of the bigger risks. | 4 | 1 | 1 | 4
4.1.2 | FMECA | TBA | cost of (material) consequence - the model | Process | All Licensees | Testing | Review the process when introducing criticality (or any other asset specific information) into the cost of (material) consequence. At the same time, make sure the current criticality definition is appropriately translated into the probability of (material) consequence. | independent review + comparison study, e.g. the definitions between the cost of (material) consequence and criticality | data used in the above case + the current criticality related documentation and the methodology to incorporate criticality into the cost of (material) consequence | Yes | the definitions and approach are compatible and can be justified. And the cost of material consequence is compatible with the current criticality data (for example, criticality is currently represented by exposure and vulnerability, which might be duplicated with the probability of material consequence) | refine the approach of incorporating criticality in the cost of (material) consequence in the NOMs methodology |  | 4 | 1 | as above | 4 | 1 | 1 | 4
4.1.3 | FMECA | TBA | cost of (material) consequence - the values for the disruptive failure | Output | All Licensees | Validation | make sure the cost of (material) consequence values are in the right magnitude of order, and this exercise also helps to pin down the most suitable values that can be used for the monetised risk modelling | comparison study + report | current NOMs methodology and modified NOMs methodology | Yes | the current NOMs methodology should be the upper bound of the modified NOMs methodology, in terms of disruptive failure type of consequences | refine the cost of material consequence values |  | 2 | 1 | providing the values in the modified MOMs methodology is explicitly available (including those values) | 2 | 1 | 1 | 2
4.1.3 (due to a indexing error in the document, will be amended in a later version) | FMECA | TBA | cost of (material) consequence - general values | Output | All Licensees | Validation | provide further assurance on the values of cost of (material) consequences | comparison study + report | DNO methodology, modified NOMs methodology, and values developed independent between TOs | Yes | the values are in the same ballpark for like for like comparisons, any differences can be justified | refine the cost of material consequence values |  | 3 | 4 | comparison with DNOs requires re-categorisation and substantial understanding of both methodologies. Comparison across TOs requires the confidentiality issues can be resolved - this might only be applicable for the cost of recovery (financial consequence) type of consequence (which is expected to be developed independently for each TO). Propose one person working on each asset type | 3 | 1 | 1 | 12
4.1.4 | FMECA | TBA | financial consequence | Output | All Licensees | Validation | validate the financial consequence values using cost data | data cleanse and data manipulation, statistical analysis | cost data such as work orders, scheme costs, defect, fault, and failure database, etc., and combine with asset data and FMEA data | yes | the cost data supports the values of the cost of financial consequence data retained by the TOs | trigger case 4.1.5 |  | 5 | 4 | the cost data should be readily available - other data needs to be bring together to perform this study, such as asset information and event information (cost categorisation) | 5 | 1 | 1 | 20
4.1.5 | FMECA | TBA | financial consequence | Input | All Licensees | Calibration | calibrate the financial consequence values using cost data | as above | as above | yes | all event types and asset types are assigned with appropriate financial consequences that can be justified by data/evidence | seek for alternative techniques such as cross reading and expert estimation |  | 4 | 4 | assume the above exercise has got the outcome of a useable database. The above comparison studies can also provide some insights into the financial consequence values. | 0 | 1 | 0 | 0
4.1.6 | FMECA | TBA | "impact" of events | Output | All Licensees | Validation | provide further reassurance to all aspects of the cost of (material) consequence values using extra information from the FMEA workshops | cross-referencing from the available information using the FMEA ratio information. It is also important to compare like-for-like (i.e. same definition). For example, similarity and difference between "impact" and "consequence", and the "zero impact events", etc. | the data from the cost data base (case 4.1.4) + the outcomes from the FMEA workshops | yes | the cost of material consequence in NOMs methodology is generally consistent with those from FMEA workshop, providing like-for-like comparison | review the difference and find the root cause, case 4.1.7 will also provide further information regarding this case. This exercise need to be performed together with other exercises that calculates to cost of (material) consequences. |  | 3 | 4 | This exercise is considered as supplimentary to use an additional data from the FMEA workshop. It should be performed together with other exercises | 3 | 1 | 1 | 12
4.1.7 | FMECA | TBA | "impact" of events | Input | All Licensees | Calibration | using the additional information to calibrate some "difficult to obtain" impact (cost) of events | as above | as above | yes | those "difficult-to-obtain" cost information can be obtained in a justified manner | held another workshop to review the FMEA data |  | 3 | 4 | The FMEA data may be less accurate or of less confidence. This exercise needs to proceed with caution, together with substantial understanding of the asset information and cost information. Those understandings can be achieved by first analysing the hard evidence (data) in 4.1.4. | 3 | 1 | 1 | 12
4.2.1 | FMECA | TBA | safety and environmental consequences | Output | All Licensees | Validation | to validate the safety and environmental consequence values that are proposed in the modified NOMs methodology | compare the probability of events and cost of events from the modified NOMs methodology with the historical events over the whole network for environmental and safety related events | explicit probabilities and costs from NOMs methodology, plus historical events on safety and environmental cases of the whole network | yes | the comparison study provides consistent outcomes (from the model and the historical records) | trigger case 4.2.2 |  | 4 | 1 | This exercise should be straightforward providing the probability information and the cost information are explicitly detailed in the NOMs methodology | 4 | 1 | 1 | 4
4.2.2 | FMECA | TBA | safety and environmental consequences | Input | All Licensees | Calibration | to calibrate the safety and environmental consequence values that are proposed in the modified NOMs methodology | use various calibration cases in this section to meet the requirement in 4.2.1 | as above | yes | meet the requirements above | if the calibration is not possible, some expert judgement or public available information about safety and environments may be used. Also comparison with DNOs cost of consequence may also give some insights into those values |  | 2 | 1 | assume the above data is already prepared and cleansed. Also assume the probability information in previous sections are validated and calibrated | 0 | 1 | 0 | 0
4.3.1 | FMECA | TBA | the return to service time - system consequence | Output | All Licensees | Validation | to validate the return to service time that is used to calculate the system consequence | data collection, manipulation and statistical analysis | outage data plus the asset types, event types and asset health and health score data that are collected and cleansed in exercises above | yes | The RTS time in the NOMs methodology (used to calculate the system consequence) is consistent with the RTS time calculated from the outage database | trigger case 4.3.3, the system consequence needs to be re-calculated |  | 6 | 2 | The outage database is in a reasonable state but assigning event type may require further engineering judgements. Considering the volume of the data, six month for two people is deemed as reasonable | 6 | 1 | 1 | 12
4.3.2 | FMECA | TBA | the return to service time - system consequence | Process | All Licensees | Testing | to review and test the assumptions over the return to service time that is examined in the FMEA workshops | review the assumptions with the modelling and data, e.g. the RTS modelling use a single value to represent all the events/assets of this type; the RTS time is insensitive to asset condition, etc. | as above | yes | those assumptions are supported by the data and the modelling (i.e. no material impact) | refine the logic that is used in FMEA workshop and this might impact the calculation of the system consequence |  | 3 | 2 | Most assumptions should be OK as the RTS time is widely used in many applications of reliability studies. However the logic in the FMEA workshop needs to be reviewed regarding the RTS time. | 3 | 1 | 1 | 6
4.3.3 | FMECA | TBA | the return to service time - system consequence | Input | All Licensees | Calibration | to calibrate the return to service time that is used to calculate the system consequence | data collection, manipulation and statistical analysis | as above | yes | the RTS time after the calibration meets the requirements in cases 4.3.1 and 4.3.2 | It is unlikely that an RTS time can not be obtained from various calibration methods. A wider information source, e.g. external database may be considered if this case is failed to be completed |  | 3 | 2 | as above | 0 | 1 | 0 | 0
4.3.4 | FMECA | TBA | direct customer connection - system consequence | Output | All Licensees | Validation | to validate the cost of system consequence toward the direct customer connection | compare the probability of events and cost of events from the modified NOMs methodology with the historical events over the whole network for disconnection of customers (supply and demand sides) related events | historical records regarding customer disconnection (supply and demand) + explicit probabilities and costs and durations (RTS) in the NOMs methodology | yes | the probability of events and the consequence of events provides are reasonable agreements between NOMs methodology and data, over the whole network | re-calibration of the system consequence regarding direct disconnection of customers |  | 2 | 2 | one person on demand side one person on supply side, providing the all the required elements in the NOMs methodology is established explicitly | 2 | 1 | 1 | 4
4.3.5 | FMECA | TBA | direct customer connection - system consequence | Output | All Licensees | Validation | to validate the cost of system consequence toward the direct customer connection | use case studies to validate the system consequence (customer disconnection) using established reliability models | established models + explicit probabilities and costs and durations (RTS) in the NOMs methodology | yes | the outcomes using the established models and the inputs in the NOMs methodology gives similar results to previous/known cases studies | review the model, and inputs used to calculate the system consequence regarding direct customer disconnection |  | 2 | 1 | Two case studies required | 2 | 1 | 1 | 2
4.3.6 | FMECA | TBA | direct customer connection - system consequence | Process | All Licensees | Testing | to test the process of calculating system consequence toward the direct customer connection | compare the established system reliability modelling with the process to calculate the system consequence | as above | yes | for the identical problem, and the same inputs, the established model and the process in the NOMs methodology lead to the same results | review the model, and process used to calculate the system consequence regarding direct customer disconnection |  | 2 | 1 | this should be relatively straightforward providing the NOMs methodology is fully developed | 2 | 1 | 1 | 2
4.3.7 | FMECA | TBA | constraint cost - system consequence | Output | All Licensees | Validation | to validate the cost of system consequence values towards the constraint cost | envelope calculation using linear approximations | system topology plus the NOMs methodology for the corresponding elements | yes | the envelope calculation is proved to be positive | understanding the root cause and the NOMs methodology may be reviewed |  | 2 | 2 | a report may be required to justify the calculation methodology and the findings; one person working on the data another working on the methodology | 2 | 1 | 1 | 4
4.3.8 | FMECA | TBA | Constraint cost, reserve cost and auxiliary service cost - system consequence | Output | All Licensees | Validation | to validate the cost of system consequence values towards reserve cost and auxiliary service cost | Use the historical events associated with constraint costs, reserve cost and auxiliary service cost to validate those aspects of system consequences from the modified NOMs methodology. | historical records regarding those events, plus the corresponding parts of the NOMs methodology | yes | the probability of events and the consequence of events provides are reasonable agreements between NOMs methodology and data, over the whole network | re-calibration of the system consequence regarding constraint costs, reserve cost and auxiliary service cost |  | 2 | 3 | three person working one three different aspects (constraint costs, reserve cost and auxiliary service cost) | 2 | 1 | 1 | 6
4.3.9 | FMECA | TBA | Loss of supply to vital infrastructures - system consequence | Process | All Licensees | Testing | to test the assumption that the cost per minute is an appropriate measure for the vital infrastructure related events | data analysis on the external referenced information on the cost of consequence of those events | external referenced information | yes | the cost per minute is an appropriate measure, or can be modelled using some equivalent measures | trigger case 4.3.10 |  | 2 | 2 | review the methodology with the data support - an report is expected | 2 | 1 | 1 | 4
4.3.10 | FMECA | TBA | Loss of supply to vital infrastructures - system consequence | Output | All Licensees | Validation | to validate the cost of system consequence values towards the cost of loss supply to vital infrastructures | as above | as above | yes | the values of the cost of consequence can be justified using external referenced information, or the differences can be explained | refine the methodology of the cost of consequence on loss of supply to vital infrastructures |  | 2 | 2 | Two person work collaboratively, one search the external referenced information (take advantage of the existing NOMs methodology); another working on modelling using the information detailed in the modified NOMs methodology | 2 | 1 | 1 | 4
[14 empty] | Worse case |  |  | Better case
[14 empty] | Time (weeks) | Resouce (FTE weeks) |  | Time (weeks) |  |  | Resouce (FTE weeks)
[13 empty] | total | 60 | 138 |  | 51 |  |  | 114
Note on C3: National Grid: Will be updated against the final version of the methdology
Note on D3: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F3: National Grid: This will be more apparent when we know where the specific appendices look like
Note on O3: National Grid: assuming the model and framework in the NOMs methdology is developed in a reasonable quality. This time scale does not include re-development or heaviy re-iteration needed upon negative testing and validation results.
Note on P3: National Grid: assuming highly skilled and motivated modeller and analytics, and work in a collobrative and efficient way. It does not include project management resource requirement, etc. Other assumptions are the same with the assumption for the time scale.

## Section 5
CALIBRATION, TESTING, AND VALIDATION PLAN WORKBOOK | [13 empty] | Non-committed indicative, and current understanding, need further refinements and discussions
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail |  | Expected time scale (weeks) | Resource expected (No. of FTE or equivalent) | comments
5.2.1 | Risk Trading model | TBA | overall methdology | Output | All Licensees | Validation | validate the overall NOMs methodology | life cycle costing modelling | probability elements and cost elements in the NOMs methodology, plus established outcomes from those life cycle costing studies | Yes | the values in the NOMs methodology returns consistent outcomes with previous case studies | review the root cause and perform relevant actions in the previous sections (re-calibration, refine the model, etc.) |  | 3 | 1.5 | some data collection effort needed to dig out previous studies and perform like for like study using the values in the NOMs methodology
5.3.1 | Risk Trading model | TBA | overall methdology | Output | All Licensees | Validation | validate the overall NOMs methodology | Compare the existing risk measure and the monetised risk measure in a portfolio sense | historical RRP data + probability elements and cost elements in the NOMs methodology | Yes | the monetised risk shows consistent outcomes with known risk assessments, when broken down in different ways | as above |  | 3 | 2 | This exercise can also be seen as a exploratory study towards future RRP
5.3.2 | Risk Trading model | TBA | overall methdology | Output | All Licensees | Validation | validate the overall NOMs methodology | Compare the existing risk measure and the monetised risk measure, from the known intervention list | Current intervention plan + probability elements and cost elements in the NOMs methodology | Yes | the assets in the current intervention plan sits on top of the list when assets are ranked using the monetised risk | as above |  | 4 | 2 | most time may be spent to understand the reasons of inconsistencies (inevitably the model can not cover all the factors that contributing to the asset management planning process)
5.4.1 | Risk Trading model | TBA | overall methdology | Process | All Licensees | Testing | test the designed functionalities of the trade off model | An independent review report to verify the logic and the functionalities using the methodology documentations, the design specifications, and the outcomes of the testing, validation and calibration exercise | all data involved in the methodology, subjecting to level of details the report is designed to | Yes | A report that is delivered in a satisfactory way, subjecting to the level of completeness of the NOMs methodology | as above |  | 8 | 1 | it is important this report is independent - it might duplicate some review report from Ofgem
5.4.2 | Risk Trading model | TBA | overall methdology | Process | All Licensees | Testing | test the scenarios that the trade off model will be used, as well as understand what does it means for the regulatory framework | Develop scenarios under the guidance of the NOMs methodology: justified and unjustified over and under delivery. Evaluate the impact of those scenarios on the overall network risk and review the validities. | the NOMs methodology itself + asset information since 2010 | Yes | The scenarios and treatment of scenarios including the regulatory implications are agreed between TOs and Ofgem | If this is not possible, some guidance from Ofgem will be needed |  | 12 | 1 | This can be an enduring process that can be continuously improved before the review of the price control
[14 empty] | Time (weeks) | Resouce (FTE weeks)
[13 empty] | total | 30 | 38.5
Note on C3: National Grid: Will be updated against the final version of the methdology
Note on D3: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F3: National Grid: This will be more apparent when we know where the specific appendices look like
Note on O3: National Grid: assuming the model and framework in the NOMs methdology is developed in a reasonable quality. This time scale does not include re-development or heaviy re-iteration needed upon negative testing and validation results.
Note on P3: National Grid: assuming highly skilled and motivated modeller and analytics, and work in a collobrative and efficient way. It does not include project management resource requirement, etc. Other assumptions are the same with the assumption for the time scale.

## CBRM Specific Calibration
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail
2.3.1 | Health Score | 1.1 | Asset Age | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.2 | Average Age | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Comparison study between the current process and the formulae, different ingredients used should be justified | Each TO's asset health process; subject matter experts; where possible international standard might be also considered | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.3 | Duty Factor | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.4 | LSE Factor | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.5 | Refurbished Assets | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.6 | Condition | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.7 | Defects | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.8 | Generic Reliability | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.9 | Oil Condition | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.10 | Operating Restrictions | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.11 | Tests | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.12 | Gas Condition | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.13 | Gas Leaks | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.14 | Cable Length Leak History (oil cables only) | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.15 | Cable Length Fault Rate | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.16 | ESQCR Rating | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.17 | Severe Weather (potential exposure to) | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.18 | Proximity to Wind Turbine | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.19 | Load at Risk | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.20 | Generation At Risk | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.21 | Maximum Demand | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.22 | Rating | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.23 | Generation infeed-Firm | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.24 | Generation infeed-Non-Firm | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.25 | Busbar Capacity | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.26 | % Busbar Capacity Lost | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.27 | Firm | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.28 | Non-Firm | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.29 | Level of Security | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.30 | Commercially Sensitive Customers | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.31 | Cables Circuit rating | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.32 | Critical Circuit | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.33 | Nature of cable route | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.34 | Cables Difficult Access | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.35 | Cables High cost location | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.36 | Cables Number of cores | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.37 | Cables Type of Ground | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.38 | Cables As Laid Depth (m) | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.39 | Cables Termination Type | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.40 | Cables Low Smoke Cable | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.41 | Cables Situation | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.42 | Cables Cable underwater | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.43 | Sensitive Location | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.44 | Major Transport Crossing | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.45 | Crosses another OHL | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.46 | SOPs | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.47 | Obsolescence | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.48 | Maintenance Time | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.49 | Part of Main Interconnected Transmission System | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.50 | Restricted Access | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.51 | Consequence Severity | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.52 | Probability of Consequence Severity for each Failure Mode (May also include voltage levels) | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.53 | Proximity to Customers | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.54 | Land Usage | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.55 | Bushing Type | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.56 | Situation | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.57 | Type of Fire Supression System | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.58 | Presence of Blast Walls | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.59 | Local or Remote Switching | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.60 | Intenally Arc Tested | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.61 | Locational Risk | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.62 | Major Crossing | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.63 | Span From Substation | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.64 | OHL Crosses another OHL | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.65 | Difficult Access | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.66 | OHL Fibre Optics Present | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.67 | Auxiliary OHLs | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.68 | Number of Circuits | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.69 | Tower Design | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.70 | Construction Specification | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.71 | Number of Earthwires | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.72 | Number of Conductors per phase | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.73 | Opex Consequences Calibration | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.74 | Capex Consequences Calibration | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.75 | Reporting Voltage | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.76 | Operating Voltage | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.77 | Fire Barrier | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.78 | Site Specific Cost Rating | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.79 | Busbar insulation | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.80 | Existence of Fire compartments (oil filled CBs only) | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.81 | Oil | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.82 | SF6 | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.83 | Fire | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.84 | Waste | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.85 | Disturbance | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.86 | Insulating Medium | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.87 | Proximity to water course | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.88 | Bunded transformer/Switchgear | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.89 | Oil Volume | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.90 | Gas Quantity | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.91 | SF6 design weight | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.92 | Building Type | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
2.3.1 | Health Score | 1.93 | Auxilliary Equipment | Input | All Licensees | Calibration | Make sure the health score formulae include appropriate ingredients that reflect the asset condition | Computer aided parametric search | existing asset health index, data behind health scores, and review by subject matter experts | Yes | The ingredients used in the health score formulae reflect the asset condition in a satisfactory manner | Re-develop the condition based modifiers or health score formulae
Note on C1: National Grid: Will be updated against the final version of the methdology
Note on D1: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F1: National Grid: This will be more apparent when we know where the specific appendices look like

## CBRM Specific Testing
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail
2.3.2 | Health score | TBA | OVERALL Health Index | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Current Health Index | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Initial Health Based Health Index | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Duty Factor | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | LSE Factor | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Modified Age Based Health Index | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Condition Factor | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Test Factor | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Specific Health Indices | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Future Health Indices | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Failure Nodes | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Probability of Failure | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Future Probability of Failure | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Criticality Index | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Network Performance | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Risk of Reduction in System Transfer Capacity | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Network Performance Criticallity | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Safety | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Average Safety Consequences | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Safety Criticality | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Financial | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Average Financial Consequences | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Financial Criticalities | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Environmental | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Average Environmental Consequences | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Environmental Consequence Severity | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
2.3.2 | Health score | TBA | Consequences Environmental Criticality | Process | All Licensees | Testing | To test the formats of the formulea caputures the underlying interactions between different condition measures of the assets | Coefficent calculation (see 2.2.1) across different datasets (calibration part and validation part) | existing asset health index, data behind health scores, and review by subject matter experts | yes | The validation part of the data can be predicted by the formulae together with the coefficients determined from the calibration part of the data | Re-develop the health score formulae
Note on C1: National Grid: Will be updated against the final version of the methdology
Note on D1: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F1: National Grid: This will be more apparent when we know where the specific appendices look like

## CBRM Specific Validation
No. | Methodology Section | Reference | Element(s) | Category | Licensees | Interrogation Type | Aim | Proposed Technique | Test Data Required | Required data held by licensee(s) | Pass Measure | Proposed action in event of fail
2.4.2 | Health score | TBA | OVERALL Health Index | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Current Health Index | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Initial Health Based Health Index | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Modified Age Based Health Index | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Specific Health Indices | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Future Health Indices | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Failure Nodes | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Probability of Failure | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Future Probability of Failure | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Criticality Index | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Consequences Network Performance | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Consequences Safety | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Consequences Financial | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
2.4.2 | Health score | TBA | Consequences Environmental | Output | All Licensees | Validation | to validate the health score (asset condition) against known risks | Qualativie validation, different scenarios, visualisaiton - similar to those used in the DNOs' validation methdology | data used in the NOMs methodology (current and the modified), known risk assessments | yes | A case study similar to that in the DNO's validation methodology | Re-develop the health score model
Note on C1: National Grid: Will be updated against the final version of the methdology
Note on D1: National Grid: It is possible a testing, etc case is testing, etc more than one element in the methdology. Only the main element is written here
Note on F1: National Grid: This will be more apparent when we know where the specific appendices look like