## Cover
Feeder 9 Cost Benefit Analysis - adapted from NGGT's traditional CBA
Version | 2.01
Date | 2018-09-28
Team | Systems & Networks
Purpose | This spreadsheet implements an adapted version of NGGT's traditional CBA to support our assessment of NGGT's request for funding for a replacement to Feeder 9 as part of the 2018 RIIO-T1 reopener. We submitted v 1.01 alongside our consultation document. Since then NGGT has provided further information. We have reflected the new information in our revised CBA.

## Contents
TABLE OF CONTENTS
Worksheet names
Contents | Worksheet names, keys, acronyms
INPUT1 | Inputs for Scenario 1.
INPUT2 | Inputs for Scenario 2.
INPUT3 | Inputs for Scenario 3.
CALC¦1 | Calculations for Scenario 1
CALC¦2 | Calculations for Scenario 2
CALC¦3 | Calculations for Scenario 3
OUTPUT¦ Summary results | Key results from different scenarios presented.
FOOTNOTES | Footnotes that are hyperlinked in the remainder of the model.
KEY
Text
Input
Calculation / formula
Explanatory text
Acronyms
NGGT | National Grid Gas Transmission
TPI | Third Party Incident
WACC | Weighted Average Cost of Capital

## INPUT1
Scenario 1
| Tunnel efficient costs, £m (2009/10 prices) | 139.887
| Probabilities | NGGT
| Enduring WACC | 4.375%
| Item | Unit | Index | Source | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[7 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
General note: We have used the assumptions used by NGGT unless otherwise specified. This does not imply endorsement of these assumptions.
1 | Discount rate
| Discount rate for future costs (up to 30 years) | % |  | Treasury Green Book 2018 |  | 3.5%
| Discount rate for future costs (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 3%
| Discount rate for loss of life (up to 30 years) | % |  | Treasury Green Book 2018 |  | 1.5%
| Discount rate for loss of life (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 1.29%
2 | Capital Expenditure
2.1 | Tunnel capital expenditure
| NGGT proposed expenditure profile | £m | 09/10 | NGGT |  |  | 1 2013/14: 0.072393; 2 2014/15: 3.8383; 3 2015/16: 2.4318; 4 2016/17: 25.0318; 5 2017/18: 42.9279; 6 2018/19: 50.8127; 7 2019/20: 11.7378; 8 2020/21: 3.0342
| Adjustment factor to reflect outcome of Ofgem's efficiency challenge (if the needs case were to be approved) | % |  | NGGT |  | 1
2.1 | Revenue profile
| NGGT estimate of revenue profile for tunnel option (before efficiency challenge) | £m | 09/10 | NGGT |  |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ofgem estimate of revenue profile (after efficiency challenge) | £m | 09/10 | Ofgem calculations |  |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Operating Expenediture
3.1 | Option: Mitigation
| Annual cost of regular inspections of the riverbed/pipeline | £m | 09/10 | NGGT |  | 0.28599
| Annual cost of pigging | £m | 09/10 | NGGT |  | 0.013516
| Cost minor mattressing work | £m | 09/10 | NGGT |  | 0.882
| Cost of major mattressing work | £m | 09/10 | NGGT |  | 7.081
3.2 | Option: Tunnel
| Annual cost of regular inspections/pigging | £m | 09/10 | NGGT |  | 0.059745
4 | Probabilities |  |  |  | See footnote 1
4.1 | Probability of scouring, freespan and third party incidents (TPI)
| Probability that a section of the pipeline is exposed (scouring) | % |  | Various |  | 35%
| Probability that major work is required following exposure | % |  | NGGT |  | 20%
| Probability that minor work is required following exposure | % |  | NGGT |  | 80%
| Probability of freespan of less than 20m developing | % |  | Various |  | 12.3%
| Probability of freespan of between 20m and 55m developing | % |  | Various |  | 2.4%
| Probability of freespan greater than 55m developing | % |  | Various |  | 0.511%
| Probability of TPI/anchor strike on the pipeline | % |  | NGGT |  | 0.03125%
4.2 | Loss of lease
| Probability of loss of lease | % |  | NGGT, Ofgem | See footnote 2 | 0.965%
4.3 | Probability of third party incidents (TPI)
| Estimated casualties following TPI - base case | fraction |  | NGGT | Number/year | 0.00221
| Estimated casualties following TPI - worst case | fraction |  | NGGT | Number/year | 0.0155
4.4 | Probability of energy price impact and constraint costs
| Probability that loss of Feeder 9 occurs during winter peak | % |  | Various | See footnote 3 | 50%
| Maximum days of constraint following loss of Feeder 9 | days |  | NGGT |  | 103
5 | Potential delays from damage to existing pipeline
5.1 | Delays from damage
| Repair clamp following localised mechanical/impact damage | weeks |  | NGGT |  | 48
| Probability minor | % |  | NGGT |  | 90%
| Probability of major | % |  | NGGT |  | 50%
| Short replacement spool following localised failure | weeks |  | NGGT |  | 69
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 30%
| Long replacement spool following extensive failure | weeks |  | NGGT |  | 75
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 10%
| Tunnel replacement following extensive failure | weeks |  | NGGT |  | 312
| Probability minor | % |  | NGGT |  | 0%
| Probability of major | % |  | NGGT |  | 10%
6 | Costs of adverse events
6.1 | Gas price impact
| Total annual domestic gas consumption | kWh |  | NGGT |  | 297563000000
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of gas price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of gas price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Gas price impact in first month (summer) (to 2024) | p/therm | 16/17 | NGGT |  | 2
| Gas price impact in first month (winter) (to 2024) | p/therm | 16/17 | NGGT |  | 25
| Gas price impact in subsequent months (to 2024) | p/therm | 16/17 | NGGT |  | 7.8
| Gas price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | NGGT |  | 1.5
| Gas price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | NGGT |  | 18.75
| Gas price impact in subsequent months (2024 onwards) | p/therm | 16/17 | NGGT |  | 5.85
6.2 | Electricity price impact
| Total annual domestic electricity consumption | kWh |  | NGGT |  | 84628524400
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of electricity price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of electricity price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Electricity price impact in first month (summer) (to 2024) | p/therm | 16/17 | NGGT |  | 5.8
| Electricity price impact in first month (winter) (to 2024) | p/therm | 16/17 | NGGT |  | 72.5
| Electricity price impact in subsequent months (to 2024) | p/therm | 16/17 | NGGT |  | 22.62
| Electricity price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | NGGT |  | 4.35
| Electricity price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | NGGT |  | 54.375
| Electricity price impact in subsequent months (2024 onwards) | p/therm | 16/17 | NGGT |  | 16.965
6.3 | Constraint costs
| Daily constraint cost | £m | 16/17 | NGGT |  | 28
6.3 | Value of lost load (VOLL)
| Cost of VOLL over a 10-day period per isolation | £m | 09/10 | NGGT |  | 33.5
6.4 | Possible loss of life
| Assumed cost of a life | £m | 16/17 | NGGT |  | 1.6
| Disproportionality factor | No. |  | NGGT |  | 10
6.5 | Cost of pipeline repair/replacement following damage
| Repair clamp following localised mechanical/impact damage | £m | 16/17 | NGGT |  | 2.61
| Short replacement spool following localised failure | £m | 16/17 | NGGT |  | 12.6
| Long replacement spool following extensive failure | £m | 16/17 | NGGT |  | 18.14
| Tunnel replacement following extensive failure | £m | 16/17 | NGGT |  | 181.717
6.6 | Other adverse consequences
| Daily cost of estuary disruption following TPI | £m | 16/17 | NGGT |  | 8.5
| Ship clear up costs following accident | £m | 16/17 | NGGT |  | 241
7 | General
| Conversion factor from 09/10 to 16/17 prices |  |  | Ofgem calculation |  | 1.2281
| Tunnel construction time | years |  | NGGT |  | 8

## INPUT2
Scenario 2
| Tunnel efficient costs, £m (2009/10 prices) | 111.299
| Probabilities | High
| Enduring WACC | 1.27%
| Item | Unit | Index | Source | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[7 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
General note: We have used the assumptions used by NGGT unless otherwise specified. This does not imply endorsement of these assumptions.
1 | Discount rate
| Discount rate for future costs (up to 30 years) | % |  | Treasury Green Book 2018 |  | 3.5%
| Discount rate for future costs (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 3%
| Discount rate for loss of life (up to 30 years) | % |  | Treasury Green Book 2018 |  | 1.5%
| Discount rate for loss of life (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 1.29%
2 | Capital Expenditure
2.1 | Tunnel capital expenditure
| NGGT proposed expenditure profile | £m | 09/10 | NGGT |  |  | 1 2013/14: 0.072393; 2 2014/15: 3.8383; 3 2015/16: 2.4318; 4 2016/17: 25.0318; 5 2017/18: 42.9279; 6 2018/19: 50.8127; 7 2019/20: 11.7378; 8 2020/21: 3.0342
| Adjustment factor to reflect outcome of Ofgem's efficiency challenge (if the needs case were to be approved) | % |  | NGGT |  | 0.79564
2.1 | Revenue profile
| NGGT estimate of revenue profile for tunnel option (before efficiency challenge) | £m | 09/10 | NGGT |  |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ofgem estimate of revenue profile (after efficiency challenge) | £m | 09/10 | Ofgem calculations |  |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 2.5743 | 2.671 | 2.7546 | 2.8265 | 2.888 | 2.9402 | 2.9842 | 3.0207 | 3.0507 | 3.0748 | 3.0937 | 3.1079 | 3.118 | 3.1244 | 3.1275 | 3.1276 | 3.1251 | 3.1203 | 3.1133 | 3.1046 | 3.0941 | 3.0822 | 3.069 | 3.0546 | 3.0392 | 3.0228 | 3.0056 | 2.9876 | 2.969 | 2.9498 | 2.9301 | 2.9099 | 2.8893 | 2.8684 | 2.847 | 2.8254 | 2.8036 | 2.7815 | 2.7578 | 2.662 | 2.5936 | 2.0941 | 1.2572 | 0.27707 | -0.028007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Operating Expenediture
3.1 | Option: Mitigation
| Annual cost of regular inspections of the riverbed/pipeline | £m | 09/10 | NGGT |  | 0.28599
| Annual cost of pigging | £m | 09/10 | NGGT |  | 0.013516
| Cost minor mattressing work | £m | 09/10 | NGGT |  | 0.882
| Cost of major mattressing work | £m | 09/10 | NGGT |  | 7.081
3.2 | Option: Tunnel
| Annual cost of regular inspections/pigging | £m | 09/10 | NGGT |  | 0.059745
4 | Probabilities |  |  |  | See footnote 1
4.1 | Probability of scouring, freespan and third party incidents (TPI)
| Probability that a section of the pipeline is exposed (scouring) | % |  | Various |  | 20%
| Probability that major work is required following exposure | % |  | NGGT |  | 20%
| Probability that minor work is required following exposure | % |  | NGGT |  | 80%
| Probability of freespan of less than 20m developing | % |  | Various |  | 2%
| Probability of freespan of between 20m and 55m developing | % |  | Various |  | 0.4%
| Probability of freespan greater than 55m developing | % |  | Various |  | 0.08%
| Probability of TPI/anchor strike on the pipeline | % |  | NGGT |  | 0.03125%
4.2 | Loss of lease
| Probability of loss of lease | % |  | NGGT, Ofgem | See footnote 2 | 0.965%
4.3 | Probability of third party incidents (TPI)
| Estimated casualties following TPI - base case | fraction |  | NGGT | Number/year | 0.00221
| Estimated casualties following TPI - worst case | fraction |  | NGGT | Number/year | 0.0155
4.4 | Probability of energy price impact and constraint costs
| Probability that loss of Feeder 9 occurs during winter peak | % |  | Various | See footnote 3 | 28.22%
| Maximum days of constraint following loss of Feeder 9 | days |  | NGGT |  | 103
5 | Potential delays from damage to existing pipeline
5.1 | Delays from damage
| Repair clamp following localised mechanical/impact damage | weeks |  | NGGT |  | 48
| Probability minor | % |  | NGGT |  | 90%
| Probability of major | % |  | NGGT |  | 50%
| Short replacement spool following localised failure | weeks |  | NGGT |  | 69
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 30%
| Long replacement spool following extensive failure | weeks |  | NGGT |  | 75
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 10%
| Tunnel replacement following extensive failure | weeks |  | NGGT |  | 312
| Probability minor | % |  | NGGT |  | 0%
| Probability of major | % |  | NGGT |  | 10%
6 | Costs of adverse events
6.1 | Gas price impact
| Total annual domestic gas consumption | kWh |  | NGGT |  | 297563000000
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of gas price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of gas price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Gas price impact in first month (summer) (to 2024) | p/therm | 16/17 | NGGT |  | 2
| Gas price impact in first month (winter) (to 2024) | p/therm | 16/17 | NGGT |  | 25
| Gas price impact in subsequent months (to 2024) | p/therm | 16/17 | NGGT |  | 7.8
| Gas price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | NGGT |  | 1.5
| Gas price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | NGGT |  | 18.75
| Gas price impact in subsequent months (2024 onwards) | p/therm | 16/17 | NGGT |  | 5.85
6.2 | Electricity price impact
| Total annual domestic electricity consumption | kWh |  | NGGT |  | 84628524400
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of electricity price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of electricity price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Electricity price impact in first month (summer) (to 2024) | p/therm | 16/17 | NGGT |  | 5.8
| Electricity price impact in first month (winter) (to 2024) | p/therm | 16/17 | NGGT |  | 72.5
| Electricity price impact in subsequent months (to 2024) | p/therm | 16/17 | NGGT |  | 22.62
| Electricity price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | NGGT |  | 4.35
| Electricity price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | NGGT |  | 54.375
| Electricity price impact in subsequent months (2024 onwards) | p/therm | 16/17 | NGGT |  | 16.965
6.3 | Constraint costs
| Daily constraint cost | £m | 16/17 | NGGT |  | 28
6.3 | Value of lost load (VOLL)
| Cost of VOLL over a 10-day period per isolation | £m | 09/10 | NGGT |  | 33.5
6.4 | Possible loss of life
| Assumed cost of a life | £m | 16/17 | NGGT |  | 1.6
| Disproportionality factor | No. |  | NGGT |  | 10
6.5 | Cost of pipeline repair/replacement following damage
| Repair clamp following localised mechanical/impact damage | £m | 16/17 | NGGT |  | 2.61
| Short replacement spool following localised failure | £m | 16/17 | NGGT |  | 12.6
| Long replacement spool following extensive failure | £m | 16/17 | NGGT |  | 18.14
| Tunnel replacement following extensive failure | £m | 16/17 | NGGT |  | 181.717
6.6 | Other adverse consequences
| Daily cost of estuary disruption following TPI | £m | 16/17 | NGGT |  | 8.5
| Ship clear up costs following accident | £m | 16/17 | NGGT |  | 241
7 | General
| Conversion factor from 09/10 to 16/17 prices |  |  | Ofgem calculation |  | 1.2281
| Tunnel construction time | years |  | NGGT |  | 8

## INPUT3
Scenario 3
| Tunnel efficient costs, £m (2009/10 prices) | 111.299
| Probabilities | Low
| Enduring WACC | 3.615%
| Item | Unit | Index | Source | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[7 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
General note: We have used the assumptions used by NGGT unless otherwise specified. This does not imply endorsement of these assumptions.
1 | Discount rate
| Discount rate for future costs (up to 30 years) | % |  | Treasury Green Book 2018 |  | 3.5%
| Discount rate for future costs (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 3%
| Discount rate for loss of life (up to 30 years) | % |  | Treasury Green Book 2018 |  | 1.5%
| Discount rate for loss of life (beyond 30 years) | % |  | Treasury Green Book 2018 |  | 1.29%
2 | Capital Expenditure
2.1 | Tunnel capital expenditure
| NGGT proposed expenditure profile | £m | 09/10 | NGGT |  |  | 1 2013/14: 0.072393; 2 2014/15: 3.8383; 3 2015/16: 2.4318; 4 2016/17: 25.0318; 5 2017/18: 42.9279; 6 2018/19: 50.8127; 7 2019/20: 11.7378; 8 2020/21: 3.0342
| Adjustment factor to reflect outcome of Ofgem's efficiency challenge (if the needs case were to be approved) | % |  | NGGT |  | 0.79564
2.1 | Revenue profile
| NGGT estimate of revenue profile for tunnel option (before efficiency challenge) | £m | 09/10 | NGGT |  |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Ofgem estimate of revenue profile (after efficiency challenge) | £m | 09/10 | Ofgem calculations |  |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 5.0555 | 5.0929 | 5.1172 | 5.1297 | 5.1319 | 5.1248 | 5.1094 | 5.0866 | 5.0572 | 5.022 | 4.9815 | 4.9364 | 4.8871 | 4.8342 | 4.7779 | 4.7187 | 4.6568 | 4.5926 | 4.5264 | 4.4583 | 4.3885 | 4.3172 | 4.2447 | 4.1709 | 4.0961 | 4.0204 | 3.9439 | 3.8666 | 3.7886 | 3.7101 | 3.631 | 3.5515 | 3.4715 | 3.3912 | 3.3106 | 3.2296 | 3.1484 | 3.067 | 2.9839 | 2.8297 | 2.7041 | 2.1531 | 1.279 | 0.28157 | -0.027348 | 0 | 0 | 0 | 0 | 0 | 0 | 0
3 | Operating Expenediture
3.1 | Option: Mitigation
| Annual cost of regular inspections of the riverbed/pipeline | £m | 09/10 | NGGT |  | 0.28599
| Annual cost of pigging | £m | 09/10 | NGGT |  | 0.013516
| Cost minor mattressing work | £m | 09/10 | NGGT |  | 0.882
| Cost of major mattressing work | £m | 09/10 | NGGT |  | 7.081
3.2 | Option: Tunnel
| Annual cost of regular inspections/pigging | £m | 09/10 | NGGT |  | 0.059745
4 | Probabilities |  |  |  | See footnote 1
4.1 | Probability of scouring, freespan and third party incidents (TPI)
| Probability that a section of the pipeline is exposed (scouring) | % |  | Various |  | 10%
| Probability that major work is required following exposure | % |  | NGGT |  | 20%
| Probability that minor work is required following exposure | % |  | NGGT |  | 80%
| Probability of freespan of less than 20m developing | % |  | Various |  | 0.58%
| Probability of freespan of between 20m and 55m developing | % |  | Various |  | 0.117%
| Probability of freespan greater than 55m developing | % |  | Various |  | 0.023%
| Probability of TPI/anchor strike on the pipeline | % |  | NGGT |  | 0.03125%
4.2 | Loss of lease
| Probability of loss of lease | % |  | NGGT, Ofgem | See footnote 2 | 0.965%
4.3 | Probability of third party incidents (TPI)
| Estimated casualties following TPI - base case | fraction |  | NGGT | Number/year | 0.00221
| Estimated casualties following TPI - worst case | fraction |  | NGGT | Number/year | 0.0155
4.4 | Probability of energy price impact and constraint costs
| Probability that loss of Feeder 9 occurs during winter peak | % |  | Various | See footnote 3 | 21.37%
| Maximum days of constraint following loss of Feeder 9 | days |  | NGGT |  | 78
5 | Potential delays from damage to existing pipeline
5.1 | Delays from damage
| Repair clamp following localised mechanical/impact damage | weeks |  | NGGT |  | 48
| Probability minor | % |  | NGGT |  | 90%
| Probability of major | % |  | NGGT |  | 50%
| Short replacement spool following localised failure | weeks |  | NGGT |  | 69
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 30%
| Long replacement spool following extensive failure | weeks |  | NGGT |  | 75
| Probability minor | % |  | NGGT |  | 5%
| Probability of major | % |  | NGGT |  | 10%
| Tunnel replacement following extensive failure | weeks |  | NGGT |  | 312
| Probability minor | % |  | NGGT |  | 0%
| Probability of major | % |  | NGGT |  | 10%
6 | Costs of adverse events
6.1 | Gas price impact
| Total annual domestic gas consumption | kWh |  | NGGT |  | 297563000000
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of gas price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of gas price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Gas price impact in first month (summer) (to 2024) | p/therm | 16/17 | NGGT |  | 2
| Gas price impact in first month (winter) (to 2024) | p/therm | 16/17 | NGGT |  | 25
| Gas price impact in subsequent months (to 2024) | p/therm | 16/17 | NGGT |  | 7.8
| Gas price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | NGGT |  | 1.5
| Gas price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | NGGT |  | 18.75
| Gas price impact in subsequent months (2024 onwards) | p/therm | 16/17 | NGGT |  | 5.85
6.2 | Electricity price impact
| Total annual domestic electricity consumption | kWh |  | NGGT |  | 84628524400
| kWh to Therm conversion factor | kWh/therm |  | NGGT |  | 29.3
| Duration of electricity price increase following a 20-55m freespan (months) | Months |  | NGGT |  | 3
| Duration of electricity price increase following a >55m freespan (months) | Months |  | NGGT |  | 16
| Electricity price impact in first month (summer) (to 2024) | p/therm | 16/17 | Ofgem |  | 4
| Electricity price impact in first month (winter) (to 2024) | p/therm | 16/17 | Ofgem |  | 50
| Electricity price impact in subsequent months (to 2024) | p/therm | 16/17 | Ofgem |  | 15.6
| Electricity price impact in first month (summer) (2024 onwards) | p/therm | 16/17 | Ofgem |  | 3
| Electricity price impact in first month (winter) (2024 onwards) | p/therm | 16/17 | Ofgem |  | 37.5
| Electricity price impact in subsequent months (2024 onwards) | p/therm | 16/17 | Ofgem |  | 11.7
6.3 | Constraint costs
| Daily constraint cost | £m | 16/17 | NGGT |  | 28
6.3 | Value of lost load (VOLL)
| Cost of VOLL over a 10-day period per isolation | £m | 09/10 | NGGT |  | 33.5
6.4 | Possible loss of life
| Assumed cost of a life | £m | 16/17 | NGGT |  | 1.6
| Disproportionality factor | No. |  | NGGT |  | 10
6.5 | Cost of pipeline repair/replacement following damage
| Repair clamp following localised mechanical/impact damage | £m | 16/17 | NGGT |  | 2.61
| Short replacement spool following localised failure | £m | 16/17 | NGGT |  | 12.6
| Long replacement spool following extensive failure | £m | 16/17 | NGGT |  | 18.14
| Tunnel replacement following extensive failure | £m | 16/17 | NGGT |  | 181.717
6.6 | Other adverse consequences
| Daily cost of estuary disruption following TPI | £m | 16/17 | NGGT |  | 8.5
| Ship clear up costs following accident | £m | 16/17 | NGGT |  | 241
7 | General
| Conversion factor from 09/10 to 16/17 prices |  |  | Ofgem calculation |  | 1.2281
| Tunnel construction time | years |  | NGGT |  | 8

## CALC¦1
| Item | Unit | Index | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[6 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Costs and expenditure profile Tunnel
| Tunnel construction period | years |  |  | 8
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.059745
| Expenditure profile after Ofgem efficiency challenge | £m | 09/10 |  |  | 0.072393 | 3.8383 | 2.4318 | 25.0318 | 42.9279 | 50.8127 | 11.7378 | 3.0342 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tunnel revenue profile to be used for modelling | £m | 09/10 |  |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Costs and expenditure profile Mitigation
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.29951
2.1 | Probablity adjusted cost of losing lease in any year
| Cost of replacing pipeline with a tunnel (after Ofgem efficiency challenge) | £m | 09/10 |  | 139.887
| Cost of loss of lease | £m | 09/10 |  |  | 1 2013/14: 1.2511; 2 2014/15: 1.239; 3 2015/16: 1.2271; 4 2016/17: 1.2152; 5 2017/18: 1.2035; 6 2018/19: 1.1919; 7 2019/20: 1.1804; 8 2020/21: 1.169; 9 2021/22: 1.1577; 10 2022/23: 1.1465; 11 2023/24: 1.1355; 12 2024/25: 1.1245; 13 2025/26: 1.1137; 14 2026/27: 1.1029; 15 2027/28: 1.0923; 16 2028/29: 1.0817; 17 2029/30: 1.0713; 18 2030/31: 1.061; 19 2031/32: 1.0507; 20 2032/33: 1.0406; 21 2033/34: 1.0305; 22 2034/35: 1.0206; 23 2035/36: 1.0107; 24 2036/37: 1.001; 25 2037/38: 0.99133; 26 2038/39: 0.98176; 27 2039/40: 0.97229; 28 2040/41: 0.96291; 29 2041/42: 0.95361; 30 2042/43: 0.94441; 31 2043/44: 0.9353; 32 2044/45: 0.92627
| Probability that the lease is still in force and current pipeline is operational | % |  |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.53% | 97.08% | 95.65% | 94.24% | 92.86% | 91.49% | 90.15% | 88.82% | 87.51% | 86.23% | 84.96% | 83.71% | 82.48% | 81.26% | 80.07% | 78.89% | 77.73% | 76.59% | 75.46% | 74.35% | 73.26% | 72.18% | 71.12% | 70.07% | 69.04% | 68.02% | 67.02% | 66.04% | 65.07% | 64.11% | 63.17%
2.2 | Cost of mattressing
| Probability adjusted annual cost of mattressing | £m | 09/10 |  | 0.74263
2.3 | Freespan develops despite mattressing (less than 20m section)
| Probability of event | % |  |  | 12.3%
| Cost of emergency mattressing | £m | 09/10 | see footnote 4 | 0.26098
2.4 | Freespan develops despite mattressing (between 20m and 55m section)
| Probability of event |  |  |  | 2.4%
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.16994
| Constraint costs | £m | 09/10 |  | 14.0896
| Value of lost load (VOLL) | £m | 09/10 |  | 0.804
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 8.782
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 6.5865
2.5 | Freespan develops despite mattressing (greater than 55m section)
| Probability of event | % |  |  | 0.511%
| Cost of building a tunnel replacement | £m | 09/10 |  |  | 1 2013/14: 0.66249; 2 2014/15: 0.65911; 3 2015/16: 0.65574; 4 2016/17: 0.65239; 5 2017/18: 0.64906; 6 2018/19: 0.64574; 7 2019/20: 0.64244; 8 2020/21: 0.63916; 9 2021/22: 0.63589; 10 2022/23: 0.63264; 11 2023/24: 0.62941; 12 2024/25: 0.62619; 13 2025/26: 0.62299; 14 2026/27: 0.61981; 15 2027/28: 0.61664; 16 2028/29: 0.61349; 17 2029/30: 0.61036; 18 2030/31: 0.60724; 19 2031/32: 0.60413; 20 2032/33: 0.60105; 21 2033/34: 0.59798; 22 2034/35: 0.59492; 23 2035/36: 0.59188; 24 2036/37: 0.58886; 25 2037/38: 0.58585; 26 2038/39: 0.58285; 27 2039/40: 0.57987; 28 2040/41: 0.57691; 29 2041/42: 0.57396; 30 2042/43: 0.57103; 31 2043/44: 0.56811; 32 2044/45: 0.56521
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.036184
| Constraint costs | £m | 09/10 |  | 2.9999
| Value of lost load (VOLL) | £m | 09/10 |  | 0.17119
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 8.3854
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 6.289
2.6 | Third party interference
| Probability of event | % |  |  | 0.03125%
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 0.11536
| Cost of intervention | £m | 09/10 |  | 0.0035579
| Constraint costs | £m | 09/10 |  | 0.18346
| Value of lost load (VOLL) | £m | 09/10 |  | 0.010469
| Wholesale gas and electricity price impact for 16 months up to 2024 | £m | 09/10 |  | 0.5128
| Wholesale gas and electricity price impact for 16 months beyond 2024 | £m | 09/10 |  | 0.3846
| Disruption costs | £m | 09/10 |  | 0.0021628
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322
3 | Detailed Working: Constraint costs
3.1 | Constraint costs
| Total constraint costs following isolation/rupture | £m | 16/17 | See footnote 6 | 721
4 | Detailed Workings: Wholesale Gas and Electricity Price Impacts
4.1 | Energy consumption
| Monthy domestic gas consumption | therm |  |  | 846311149.033
| Monthly domestic electricity consumption | therm |  |  | 240695461.8885
4.2 | To 2024
| First month average | £m | 16/17 |  | 208.4843
| Monthly average (excluding first month) | £m | 16/17 |  | 120.4576
4.3 | From 2024 to 2072
| First month average | £m | 16/17 |  | 156.3632
| Monthly average (excluding first month) | £m | 16/17 |  | 90.3432
4.4 | Damage intervention
4.4.1 | Localised mechanical/impact damage leading to repair clamp
| Probability | % |  |  | 0.7
| Expected duration | weeks |  |  | 33.6
| Expected cost | £m | 09/10 |  | 1.4876
4.4.2 | Localised failure leading to short replacement spool
| Probability | % |  |  | 0.175
| Expected duration | weeks |  |  | 12.075
| Expected cost | £m | 09/10 |  | 1.7954
4.4.3 | Extensive failure over pipeline span /rupture leading to long replacement spool
| Probability | % |  |  | 0.075
| Expected duration | weeks |  |  | 5.625
| Expected cost | £m | 09/10 |  | 1.1078
4.4.4 | Tunnel replacement
| Probability | % |  |  | 0.05
| Expected duration | weeks |  |  | 15.6
| Expected cost | £m | 09/10 |  | 6.9943
4.4.4 | Average cost of intervention | £m | 09/10 |  | 11.3851
| Item | Unit | Index | Notes | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[5 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Option: Tunnel 2012
| Revenue impact of construction cost | £m | 09/10 |  | 0.56455 | 0.57303 | 2.8901 | 5.2498 | 5.648 | 6.7417 | 5.0916 | 5.1811 | 7.6863 | 7.5661 | 7.4459 | 7.3258 | 7.2056 | 7.0855 | 6.9653 | 6.8451 | 6.725 | 6.6048 | 6.4847 | 6.3645 | 6.2443 | 6.1242 | 6.004 | 5.8839 | 5.7637 | 5.6435 | 5.5234 | 5.4032 | 5.2831 | 5.1629 | 5.0427 | 4.9226 | 4.8024 | 4.6823 | 4.5621 | 4.4419 | 4.3218 | 4.2016 | 4.0815 | 3.9613 | 3.8411 | 3.721 | 3.6008 | 3.4807 | 3.3605 | 3.2403 | 2.9572 | 2.7549 | 1.9131 | 1.172 | 0.59855 | 0.032968 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational costs | £m | 09/10 |  | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Mattressing cost | £m | 09/10 |  | 0.74263 | 0.74263 | 0.74263 | 0.74263 | 0.74263 | 0.74263 | 0.74263 | 0.74263 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 0.26098 | 0.26098 | 0.26098 | 0.26098 | 0.26098 | 0.26098 | 0.26098 | 0.26098 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.16994 | 0.16994 | 0.16994 | 0.16994 | 0.16994 | 0.16994 | 0.16994 | 0.16994 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 14.0896 | 14.0896 | 14.0896 | 14.0896 | 14.0896 | 14.0896 | 14.0896 | 14.0896 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0.804 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 8.782 | 8.782 | 8.782 | 8.782 | 8.782 | 8.782 | 8.782 | 8.782 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (>55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.036184 | 0.036184 | 0.036184 | 0.036184 | 0.036184 | 0.036184 | 0.036184 | 0.036184 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 2.9999 | 2.9999 | 2.9999 | 2.9999 | 2.9999 | 2.9999 | 2.9999 | 2.9999 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.17119 | 0.17119 | 0.17119 | 0.17119 | 0.17119 | 0.17119 | 0.17119 | 0.17119 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 8.3854 | 8.3854 | 8.3854 | 8.3854 | 8.3854 | 8.3854 | 8.3854 | 8.3854 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
Third party impact
| Probability adjusted cost associated with possible loss of life |  |  |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost of intervention |  |  |  | 0.0035579 | 0.0035579 | 0.0035579 | 0.0035579 | 0.0035579 | 0.0035579 | 0.0035579 | 0.0035579 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.18346 | 0.18346 | 0.18346 | 0.18346 | 0.18346 | 0.18346 | 0.18346 | 0.18346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.5128 | 0.5128 | 0.5128 | 0.5128 | 0.5128 | 0.5128 | 0.5128 | 0.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
| Estuary disruption costs | £m | 09/10 |  | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total tunnel construction and operation cost | £m | 09/10 |  | 0.86406 | 0.87254 | 3.1896 | 5.5493 | 5.9475 | 7.0412 | 5.3911 | 5.4806 | 7.746 | 7.6258 | 7.5057 | 7.3855 | 7.2654 | 7.1452 | 7.025 | 6.9049 | 6.7847 | 6.6646 | 6.5444 | 6.4242 | 6.3041 | 6.1839 | 6.0638 | 5.9436 | 5.8234 | 5.7033 | 5.5831 | 5.463 | 5.3428 | 5.2226 | 5.1025 | 4.9823 | 4.8622 | 4.742 | 4.6218 | 4.5017 | 4.3815 | 4.2614 | 4.1412 | 4.021 | 3.9009 | 3.7807 | 3.6606 | 3.5404 | 3.4202 | 3.3001 | 3.017 | 2.8147 | 1.9729 | 1.2318 | 0.65829 | 0.092713 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Total costs (excluding loss of life) | £m | 09/10 |  | 38.0797 | 38.0881 | 40.4052 | 42.7649 | 43.1631 | 44.2568 | 42.6067 | 42.6962 | 7.746 | 7.6258 | 7.5057 | 7.3855 | 7.2654 | 7.1452 | 7.025 | 6.9049 | 6.7847 | 6.6646 | 6.5444 | 6.4242 | 6.3041 | 6.1839 | 6.0638 | 5.9436 | 5.8234 | 5.7033 | 5.5831 | 5.463 | 5.3428 | 5.2226 | 5.1025 | 4.9823 | 4.8622 | 4.742 | 4.6218 | 4.5017 | 4.3815 | 4.2614 | 4.1412 | 4.021 | 3.9009 | 3.7807 | 3.6606 | 3.5404 | 3.4202 | 3.3001 | 3.017 | 2.8147 | 1.9729 | 1.2318 | 0.65829 | 0.092713 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted total tunnel construction and operation cost | £m | 09/10 |  | 0.83484 | 0.81452 | 2.8768 | 4.8359 | 5.0076 | 5.728 | 4.2373 | 4.1621 | 5.6835 | 5.4061 | 5.141 | 4.8876 | 4.6455 | 4.4142 | 4.1932 | 3.9821 | 3.7805 | 3.5879 | 3.4041 | 3.2286 | 3.0611 | 2.9012 | 2.7486 | 2.603 | 2.4642 | 2.3317 | 2.2054 | 2.085 | 1.9701 | 1.8607 | 2.0409 | 1.9348 | 1.8332 | 1.7358 | 1.6425 | 1.5532 | 1.4677 | 1.3859 | 1.3076 | 1.2327 | 1.161 | 1.0925 | 1.0269 | 0.9643 | 0.90444 | 0.84725 | 0.752 | 0.68114 | 0.46353 | 0.28098 | 0.14579 | 0.019935 | 0.012472 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 36.7919 | 35.5557 | 36.4432 | 37.2671 | 36.3422 | 36.003 | 33.4885 | 32.424 | 5.6835 | 5.4061 | 5.141 | 4.8876 | 4.6455 | 4.4142 | 4.1932 | 3.9821 | 3.7805 | 3.5879 | 3.4041 | 3.2286 | 3.0611 | 2.9012 | 2.7486 | 2.603 | 2.4642 | 2.3317 | 2.2054 | 2.085 | 1.9701 | 1.8607 | 2.0409 | 1.9348 | 1.8332 | 1.7358 | 1.6425 | 1.5532 | 1.4677 | 1.3859 | 1.3076 | 1.2327 | 1.161 | 1.0925 | 1.0269 | 0.9643 | 0.90444 | 0.84725 | 0.752 | 0.68114 | 0.46353 | 0.28098 | 0.14579 | 0.019935 | 0.012472 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 36.9056 | 35.6677 | 36.5535 | 37.3758 | 36.4492 | 36.1085 | 33.5924 | 32.5264 | 5.6835 | 5.4061 | 5.141 | 4.8876 | 4.6455 | 4.4142 | 4.1932 | 3.9821 | 3.7805 | 3.5879 | 3.4041 | 3.2286 | 3.0611 | 2.9012 | 2.7486 | 2.603 | 2.4642 | 2.3317 | 2.2054 | 2.085 | 1.9701 | 1.8607 | 2.0409 | 1.9348 | 1.8332 | 1.7358 | 1.6425 | 1.5532 | 1.4677 | 1.3859 | 1.3076 | 1.2327 | 1.161 | 1.0925 | 1.0269 | 0.9643 | 0.90444 | 0.84725 | 0.752 | 0.68114 | 0.46353 | 0.28098 | 0.14579 | 0.019935 | 0.012472 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Cumulative discounted tunnel construction and operation cost | £m | 09/10 |  | 0.83484 | 1.6494 | 4.5262 | 9.3621 | 14.3697 | 20.0977 | 24.3351 | 28.4971 | 34.1806 | 39.5867 | 44.7277 | 49.6153 | 54.2608 | 58.675 | 62.8682 | 66.8502 | 70.6307 | 74.2187 | 77.6228 | 80.8514 | 83.9124 | 86.8136 | 89.5622 | 92.1653 | 94.6295 | 96.9612 | 99.1666 | 101.2515 | 103.2217 | 105.0824 | 107.1233 | 109.0581 | 110.8913 | 112.6271 | 114.2696 | 115.8228 | 117.2906 | 118.6765 | 119.9841 | 121.2168 | 122.3778 | 123.4702 | 124.4972 | 125.4615 | 126.3659 | 127.2132 | 127.9652 | 128.6463 | 129.1099 | 129.3908 | 129.5366 | 129.5566 | 129.569 | 129.5811 | 129.5929 | 129.6043 | 129.6154 | 129.6261 | 129.6366 | 129.6467
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 36.7919 | 72.3476 | 108.7908 | 146.058 | 182.4001 | 218.4031 | 251.8915 | 284.3156 | 289.999 | 295.4051 | 300.5461 | 305.4337 | 310.0792 | 314.4934 | 318.6866 | 322.6687 | 326.4491 | 330.0371 | 333.4412 | 336.6698 | 339.7309 | 342.6321 | 345.3807 | 347.9837 | 350.4479 | 352.7796 | 354.985 | 357.07 | 359.0401 | 360.9008 | 362.9418 | 364.8766 | 366.7097 | 368.4455 | 370.088 | 371.6413 | 373.109 | 374.4949 | 375.8025 | 377.0352 | 378.1962 | 379.2887 | 380.3156 | 381.2799 | 382.1844 | 383.0316 | 383.7836 | 384.4648 | 384.9283 | 385.2093 | 385.355 | 385.375 | 385.3875 | 385.3996 | 385.4113 | 385.4227 | 385.4338 | 385.4446 | 385.455 | 385.4652
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359
| Cumulative total discounted cost | £m | 09/10 |  | 36.9056 | 72.5733 | 109.1268 | 146.5026 | 182.9518 | 219.0603 | 252.6527 | 285.1791 | 290.8626 | 296.2687 | 301.4097 | 306.2973 | 310.9428 | 315.357 | 319.5502 | 323.5323 | 327.3127 | 330.9007 | 334.3048 | 337.5334 | 340.5945 | 343.4956 | 346.2443 | 348.8473 | 351.3115 | 353.6432 | 355.8486 | 357.9335 | 359.9037 | 361.7644 | 363.8053 | 365.7402 | 367.5733 | 369.3091 | 370.9516 | 372.5049 | 373.9726 | 375.3585 | 376.6661 | 377.8988 | 379.0598 | 380.1523 | 381.1792 | 382.1435 | 383.0479 | 383.8952 | 384.6472 | 385.3283 | 385.7919 | 386.0728 | 386.2186 | 386.2386 | 386.251 | 386.2632 | 386.2749 | 386.2863 | 386.2974 | 386.3082 | 386.3186 | 386.3287
2 | Option: Mitigate 2044
| Operational costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.29951; 11.3851 2 2014/15: 0.29951; 11.3851 3 2015/16: 0.29951; 11.3851 4 2016/17: 0.29951; 11.3851 5 2017/18: 0.29951; 11.3851 6 2018/19: 0.29951; 11.3851 7 2019/20: 0.29951; 11.3851 8 2020/21: 0.29951; 11.3851 9 2021/22: 0.29598; 11.3851 10 2022/23: 0.29251; 11.3851 11 2023/24: 0.28908; 11.3851 12 2024/25: 0.28571; 11.3851 13 2025/26: 0.28239; 11.3851 14 2026/27: 0.27911; 11.3851 15 2027/28: 0.27588; 11.3851 16 2028/29: 0.2727; 11.3851 17 2029/30: 0.26957; 11.3851 18 2030/31: 0.26648; 11.3851 19 2031/32: 0.26344; 11.3851 20 2032/33: 0.26045; 11.3851 21 2033/34: 0.25749; 11.3851 22 2034/35: 0.25458; 11.3851 23 2035/36: 0.25172; 11.3851 24 2036/37: 0.24889; 11.3851 25 2037/38: 0.24611; 11.3851 26 2038/39: 0.24337; 11.3851 27 2039/40: 0.24067; 11.3851 28 2040/41: 0.23801; 11.3851 29 2041/42: 0.23539; 11.3851 30 2042/43: 0.2328; 11.3851 31 2043/44: 0.23026; 11.3851 32 2044/45: 0.22775
| Loss of lease | £m | 09/10 |  | 11.3851 1 2013/14: 1.2511; 11.3851 2 2014/15: 1.239; 11.3851 3 2015/16: 1.2271; 11.3851 4 2016/17: 1.2152; 11.3851 5 2017/18: 1.2035; 11.3851 6 2018/19: 1.1919; 11.3851 7 2019/20: 1.1804; 11.3851 8 2020/21: 1.169; 11.3851 9 2021/22: 1.1577; 11.3851 10 2022/23: 1.1465; 11.3851 11 2023/24: 1.1355; 11.3851 12 2024/25: 1.1245; 11.3851 13 2025/26: 1.1137; 11.3851 14 2026/27: 1.1029; 11.3851 15 2027/28: 1.0923; 11.3851 16 2028/29: 1.0817; 11.3851 17 2029/30: 1.0713; 11.3851 18 2030/31: 1.061; 11.3851 19 2031/32: 1.0507; 11.3851 20 2032/33: 1.0406; 11.3851 21 2033/34: 1.0305; 11.3851 22 2034/35: 1.0206; 11.3851 23 2035/36: 1.0107; 11.3851 24 2036/37: 1.001; 11.3851 25 2037/38: 0.99133; 11.3851 26 2038/39: 0.98176; 11.3851 27 2039/40: 0.97229; 11.3851 28 2040/41: 0.96291; 11.3851 29 2041/42: 0.95361; 11.3851 30 2042/43: 0.94441; 11.3851 31 2043/44: 0.9353; 11.3851 32 2044/45: 0.92627
| Mattressing cost | £m | 09/10 |  | 11.3851 1 2013/14: 0.74263; 11.3851 2 2014/15: 0.74263; 11.3851 3 2015/16: 0.74263; 11.3851 4 2016/17: 0.74263; 11.3851 5 2017/18: 0.74263; 11.3851 6 2018/19: 0.74263; 11.3851 7 2019/20: 0.74263; 11.3851 8 2020/21: 0.74263; 11.3851 9 2021/22: 0.73171; 11.3851 10 2022/23: 0.72094; 11.3851 11 2023/24: 0.71034; 11.3851 12 2024/25: 0.69989; 11.3851 13 2025/26: 0.68959; 11.3851 14 2026/27: 0.67945; 11.3851 15 2027/28: 0.66945; 11.3851 16 2028/29: 0.6596; 11.3851 17 2029/30: 0.6499; 11.3851 18 2030/31: 0.64034; 11.3851 19 2031/32: 0.63092; 11.3851 20 2032/33: 0.62164; 11.3851 21 2033/34: 0.61249; 11.3851 22 2034/35: 0.60348; 11.3851 23 2035/36: 0.59461; 11.3851 24 2036/37: 0.58586; 11.3851 25 2037/38: 0.57724; 11.3851 26 2038/39: 0.56875; 11.3851 27 2039/40: 0.56038; 11.3851 28 2040/41: 0.55214; 11.3851 29 2041/42: 0.54402; 11.3851 30 2042/43: 0.53601; 11.3851 31 2043/44: 0.52813; 11.3851 32 2044/45: 0.52036
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 11.3851 1 2013/14: 0.26098; 11.3851 2 2014/15: 0.26098; 11.3851 3 2015/16: 0.26098; 11.3851 4 2016/17: 0.26098; 11.3851 5 2017/18: 0.26098; 11.3851 6 2018/19: 0.26098; 11.3851 7 2019/20: 0.26098; 11.3851 8 2020/21: 0.26098; 11.3851 9 2021/22: 0.25714; 11.3851 10 2022/23: 0.25336; 11.3851 11 2023/24: 0.24963; 11.3851 12 2024/25: 0.24596; 11.3851 13 2025/26: 0.24234; 11.3851 14 2026/27: 0.23878; 11.3851 15 2027/28: 0.23526; 11.3851 16 2028/29: 0.2318; 11.3851 17 2029/30: 0.22839; 11.3851 18 2030/31: 0.22503; 11.3851 19 2031/32: 0.22172; 11.3851 20 2032/33: 0.21846; 11.3851 21 2033/34: 0.21525; 11.3851 22 2034/35: 0.21208; 11.3851 23 2035/36: 0.20896; 11.3851 24 2036/37: 0.20589; 11.3851 25 2037/38: 0.20286; 11.3851 26 2038/39: 0.19987; 11.3851 27 2039/40: 0.19693; 11.3851 28 2040/41: 0.19404; 11.3851 29 2041/42: 0.19118; 11.3851 30 2042/43: 0.18837; 11.3851 31 2043/44: 0.1856; 11.3851 32 2044/45: 0.18287
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 11.3851 1 2013/14: 0.16994; 11.3851 2 2014/15: 0.16994; 11.3851 3 2015/16: 0.16994; 11.3851 4 2016/17: 0.16994; 11.3851 5 2017/18: 0.16994; 11.3851 6 2018/19: 0.16994; 11.3851 7 2019/20: 0.16994; 11.3851 8 2020/21: 0.16994; 11.3851 9 2021/22: 0.16744; 11.3851 10 2022/23: 0.16498; 11.3851 11 2023/24: 0.16255; 11.3851 12 2024/25: 0.16016; 11.3851 13 2025/26: 0.15781; 11.3851 14 2026/27: 0.15548; 11.3851 15 2027/28: 0.1532; 11.3851 16 2028/29: 0.15094; 11.3851 17 2029/30: 0.14872; 11.3851 18 2030/31: 0.14654; 11.3851 19 2031/32: 0.14438; 11.3851 20 2032/33: 0.14226; 11.3851 21 2033/34: 0.14016; 11.3851 22 2034/35: 0.1381; 11.3851 23 2035/36: 0.13607; 11.3851 24 2036/37: 0.13407; 11.3851 25 2037/38: 0.1321; 11.3851 26 2038/39: 0.13015; 11.3851 27 2039/40: 0.12824; 11.3851 28 2040/41: 0.12635; 11.3851 29 2041/42: 0.12449; 11.3851 30 2042/43: 0.12266; 11.3851 31 2043/44: 0.12086; 11.3851 32 2044/45: 0.11908
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 14.0896; 11.3851 2 2014/15: 14.0896; 11.3851 3 2015/16: 14.0896; 11.3851 4 2016/17: 14.0896; 11.3851 5 2017/18: 14.0896; 11.3851 6 2018/19: 14.0896; 11.3851 7 2019/20: 14.0896; 11.3851 8 2020/21: 14.0896; 11.3851 9 2021/22: 13.8823; 11.3851 10 2022/23: 13.6781; 11.3851 11 2023/24: 13.4769; 11.3851 12 2024/25: 13.2786; 11.3851 13 2025/26: 13.0833; 11.3851 14 2026/27: 12.8908; 11.3851 15 2027/28: 12.7012; 11.3851 16 2028/29: 12.5144; 11.3851 17 2029/30: 12.3303; 11.3851 18 2030/31: 12.1489; 11.3851 19 2031/32: 11.9702; 11.3851 20 2032/33: 11.7941; 11.3851 21 2033/34: 11.6206; 11.3851 22 2034/35: 11.4496; 11.3851 23 2035/36: 11.2812; 11.3851 24 2036/37: 11.1152; 11.3851 25 2037/38: 10.9517; 11.3851 26 2038/39: 10.7906; 11.3851 27 2039/40: 10.6319; 11.3851 28 2040/41: 10.4755; 11.3851 29 2041/42: 10.3214; 11.3851 30 2042/43: 10.1695; 11.3851 31 2043/44: 10.0199; 11.3851 32 2044/45: 9.8725
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.804; 11.3851 2 2014/15: 0.804; 11.3851 3 2015/16: 0.804; 11.3851 4 2016/17: 0.804; 11.3851 5 2017/18: 0.804; 11.3851 6 2018/19: 0.804; 11.3851 7 2019/20: 0.804; 11.3851 8 2020/21: 0.804; 11.3851 9 2021/22: 0.79217; 11.3851 10 2022/23: 0.78052; 11.3851 11 2023/24: 0.76904; 11.3851 12 2024/25: 0.75772; 11.3851 13 2025/26: 0.74658; 11.3851 14 2026/27: 0.73559; 11.3851 15 2027/28: 0.72477; 11.3851 16 2028/29: 0.71411; 11.3851 17 2029/30: 0.70361; 11.3851 18 2030/31: 0.69326; 11.3851 19 2031/32: 0.68306; 11.3851 20 2032/33: 0.67301; 11.3851 21 2033/34: 0.66311; 11.3851 22 2034/35: 0.65335; 11.3851 23 2035/36: 0.64374; 11.3851 24 2036/37: 0.63427; 11.3851 25 2037/38: 0.62494; 11.3851 26 2038/39: 0.61575; 11.3851 27 2039/40: 0.60669; 11.3851 28 2040/41: 0.59777; 11.3851 29 2041/42: 0.58897; 11.3851 30 2042/43: 0.58031; 11.3851 31 2043/44: 0.57177; 11.3851 32 2044/45: 0.56336
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 8.782; 11.3851 2 2014/15: 8.782; 11.3851 3 2015/16: 8.782; 11.3851 4 2016/17: 8.782; 11.3851 5 2017/18: 8.782; 11.3851 6 2018/19: 8.782; 11.3851 7 2019/20: 8.782; 11.3851 8 2020/21: 8.782; 11.3851 9 2021/22: 8.6529; 11.3851 10 2022/23: 8.5256; 11.3851 11 2023/24: 8.4001; 11.3851 12 2024/25: 8.2766
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 6.1161; 11.3851 14 2026/27: 6.0261; 11.3851 15 2027/28: 5.9375; 11.3851 16 2028/29: 5.8501; 11.3851 17 2029/30: 5.7641; 11.3851 18 2030/31: 5.6793; 11.3851 19 2031/32: 5.5957; 11.3851 20 2032/33: 5.5134; 11.3851 21 2033/34: 5.4323; 11.3851 22 2034/35: 5.3524; 11.3851 23 2035/36: 5.2737; 11.3851 24 2036/37: 5.1961; 11.3851 25 2037/38: 5.1197; 11.3851 26 2038/39: 5.0443; 11.3851 27 2039/40: 4.9701; 11.3851 28 2040/41: 4.897; 11.3851 29 2041/42: 4.825; 11.3851 30 2042/43: 4.754; 11.3851 31 2043/44: 4.6841; 11.3851 32 2044/45: 4.6152
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 11.3851 1 2013/14: 0.66249; 11.3851 2 2014/15: 0.65911; 11.3851 3 2015/16: 0.65574; 11.3851 4 2016/17: 0.65239; 11.3851 5 2017/18: 0.64906; 11.3851 6 2018/19: 0.64574; 11.3851 7 2019/20: 0.64244; 11.3851 8 2020/21: 0.63916; 11.3851 9 2021/22: 0.63589; 11.3851 10 2022/23: 0.63264; 11.3851 11 2023/24: 0.62941; 11.3851 12 2024/25: 0.62619; 11.3851 13 2025/26: 0.62299; 11.3851 14 2026/27: 0.61981; 11.3851 15 2027/28: 0.61664; 11.3851 16 2028/29: 0.61349; 11.3851 17 2029/30: 0.61036; 11.3851 18 2030/31: 0.60724; 11.3851 19 2031/32: 0.60413; 11.3851 20 2032/33: 0.60105; 11.3851 21 2033/34: 0.59798; 11.3851 22 2034/35: 0.59492; 11.3851 23 2035/36: 0.59188; 11.3851 24 2036/37: 0.58886; 11.3851 25 2037/38: 0.58585; 11.3851 26 2038/39: 0.58285; 11.3851 27 2039/40: 0.57987; 11.3851 28 2040/41: 0.57691; 11.3851 29 2041/42: 0.57396; 11.3851 30 2042/43: 0.57103; 11.3851 31 2043/44: 0.56811; 11.3851 32 2044/45: 0.56521
| Cost of emergency mattressing - major | £m | 09/10 |  | 11.3851 1 2013/14: 0.036184; 11.3851 2 2014/15: 0.036184; 11.3851 3 2015/16: 0.036184; 11.3851 4 2016/17: 0.036184; 11.3851 5 2017/18: 0.036184; 11.3851 6 2018/19: 0.036184; 11.3851 7 2019/20: 0.036184; 11.3851 8 2020/21: 0.036184; 11.3851 9 2021/22: 0.035652; 11.3851 10 2022/23: 0.035127; 11.3851 11 2023/24: 0.03461; 11.3851 12 2024/25: 0.034101; 11.3851 13 2025/26: 0.0336; 11.3851 14 2026/27: 0.033105; 11.3851 15 2027/28: 0.032618; 11.3851 16 2028/29: 0.032139; 11.3851 17 2029/30: 0.031666; 11.3851 18 2030/31: 0.0312; 11.3851 19 2031/32: 0.030741; 11.3851 20 2032/33: 0.030289; 11.3851 21 2033/34: 0.029843; 11.3851 22 2034/35: 0.029404; 11.3851 23 2035/36: 0.028972; 11.3851 24 2036/37: 0.028545; 11.3851 25 2037/38: 0.028125; 11.3851 26 2038/39: 0.027712; 11.3851 27 2039/40: 0.027304; 11.3851 28 2040/41: 0.026902; 11.3851 29 2041/42: 0.026507; 11.3851 30 2042/43: 0.026117; 11.3851 31 2043/44: 0.025733; 11.3851 32 2044/45: 0.025354
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 2.9999; 11.3851 2 2014/15: 2.9999; 11.3851 3 2015/16: 2.9999; 11.3851 4 2016/17: 2.9999; 11.3851 5 2017/18: 2.9999; 11.3851 6 2018/19: 2.9999; 11.3851 7 2019/20: 2.9999; 11.3851 8 2020/21: 2.9999; 11.3851 9 2021/22: 2.9558; 11.3851 10 2022/23: 2.9123; 11.3851 11 2023/24: 2.8695; 11.3851 12 2024/25: 2.8272; 11.3851 13 2025/26: 2.7857; 11.3851 14 2026/27: 2.7447; 11.3851 15 2027/28: 2.7043; 11.3851 16 2028/29: 2.6645; 11.3851 17 2029/30: 2.6253; 11.3851 18 2030/31: 2.5867; 11.3851 19 2031/32: 2.5486; 11.3851 20 2032/33: 2.5112; 11.3851 21 2033/34: 2.4742; 11.3851 22 2034/35: 2.4378; 11.3851 23 2035/36: 2.402; 11.3851 24 2036/37: 2.3666; 11.3851 25 2037/38: 2.3318; 11.3851 26 2038/39: 2.2975; 11.3851 27 2039/40: 2.2637; 11.3851 28 2040/41: 2.2304; 11.3851 29 2041/42: 2.1976; 11.3851 30 2042/43: 2.1653; 11.3851 31 2043/44: 2.1334; 11.3851 32 2044/45: 2.102
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.17119; 11.3851 2 2014/15: 0.17119; 11.3851 3 2015/16: 0.17119; 11.3851 4 2016/17: 0.17119; 11.3851 5 2017/18: 0.17119; 11.3851 6 2018/19: 0.17119; 11.3851 7 2019/20: 0.17119; 11.3851 8 2020/21: 0.17119; 11.3851 9 2021/22: 0.16867; 11.3851 10 2022/23: 0.16619; 11.3851 11 2023/24: 0.16374; 11.3851 12 2024/25: 0.16133; 11.3851 13 2025/26: 0.15896; 11.3851 14 2026/27: 0.15662; 11.3851 15 2027/28: 0.15432; 11.3851 16 2028/29: 0.15205; 11.3851 17 2029/30: 0.14981; 11.3851 18 2030/31: 0.14761; 11.3851 19 2031/32: 0.14543; 11.3851 20 2032/33: 0.14329; 11.3851 21 2033/34: 0.14119; 11.3851 22 2034/35: 0.13911; 11.3851 23 2035/36: 0.13706; 11.3851 24 2036/37: 0.13505; 11.3851 25 2037/38: 0.13306; 11.3851 26 2038/39: 0.1311; 11.3851 27 2039/40: 0.12917; 11.3851 28 2040/41: 0.12727; 11.3851 29 2041/42: 0.1254; 11.3851 30 2042/43: 0.12356; 11.3851 31 2043/44: 0.12174; 11.3851 32 2044/45: 0.11995
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 8.3854; 11.3851 2 2014/15: 8.3854; 11.3851 3 2015/16: 8.3854; 11.3851 4 2016/17: 8.3854; 11.3851 5 2017/18: 8.3854; 11.3851 6 2018/19: 8.3854; 11.3851 7 2019/20: 8.3854; 11.3851 8 2020/21: 8.3854; 11.3851 9 2021/22: 8.262; 11.3851 10 2022/23: 8.1405; 11.3851 11 2023/24: 8.0207; 11.3851 12 2024/25: 7.9027
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 5.8399; 11.3851 14 2026/27: 5.754; 11.3851 15 2027/28: 5.6693; 11.3851 16 2028/29: 5.5859; 11.3851 17 2029/30: 5.5037; 11.3851 18 2030/31: 5.4228; 11.3851 19 2031/32: 5.343; 11.3851 20 2032/33: 5.2644; 11.3851 21 2033/34: 5.187; 11.3851 22 2034/35: 5.1107; 11.3851 23 2035/36: 5.0355; 11.3851 24 2036/37: 4.9614; 11.3851 25 2037/38: 4.8884; 11.3851 26 2038/39: 4.8165; 11.3851 27 2039/40: 4.7456; 11.3851 28 2040/41: 4.6758; 11.3851 29 2041/42: 4.6071; 11.3851 30 2042/43: 4.5393; 11.3851 31 2043/44: 4.4725; 11.3851 32 2044/45: 4.4067
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 11.3851 1 2013/14: 0.11536; 11.3851 2 2014/15: 0.11536; 11.3851 3 2015/16: 0.11536; 11.3851 4 2016/17: 0.11536; 11.3851 5 2017/18: 0.11536; 11.3851 6 2018/19: 0.11536; 11.3851 7 2019/20: 0.11536; 11.3851 8 2020/21: 0.11536; 11.3851 9 2021/22: 0.11366; 11.3851 10 2022/23: 0.11199; 11.3851 11 2023/24: 0.11034; 11.3851 12 2024/25: 0.10872; 11.3851 13 2025/26: 0.10712; 11.3851 14 2026/27: 0.10555; 11.3851 15 2027/28: 0.10399; 11.3851 16 2028/29: 0.10246; 11.3851 17 2029/30: 0.10096; 11.3851 18 2030/31: 0.099471; 11.3851 19 2031/32: 0.098008; 11.3851 20 2032/33: 0.096566; 11.3851 21 2033/34: 0.095146; 11.3851 22 2034/35: 0.093746; 11.3851 23 2035/36: 0.092367; 11.3851 24 2036/37: 0.091008; 11.3851 25 2037/38: 0.089669; 11.3851 26 2038/39: 0.08835; 11.3851 27 2039/40: 0.087051; 11.3851 28 2040/41: 0.08577; 11.3851 29 2041/42: 0.084508; 11.3851 30 2042/43: 0.083265; 11.3851 31 2043/44: 0.08204; 11.3851 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 11.3851 1 2013/14: 0.0035579; 11.3851 2 2014/15: 0.0035579; 11.3851 3 2015/16: 0.0035579; 11.3851 4 2016/17: 0.0035579; 11.3851 5 2017/18: 0.0035579; 11.3851 6 2018/19: 0.0035579; 11.3851 7 2019/20: 0.0035579; 11.3851 8 2020/21: 0.0035579; 11.3851 9 2021/22: 0.0035055; 11.3851 10 2022/23: 0.0034539; 11.3851 11 2023/24: 0.0034031; 11.3851 12 2024/25: 0.0033531; 11.3851 13 2025/26: 0.0033037; 11.3851 14 2026/27: 0.0032551; 11.3851 15 2027/28: 0.0032073; 11.3851 16 2028/29: 0.0031601; 11.3851 17 2029/30: 0.0031136; 11.3851 18 2030/31: 0.0030678; 11.3851 19 2031/32: 0.0030227; 11.3851 20 2032/33: 0.0029782; 11.3851 21 2033/34: 0.0029344; 11.3851 22 2034/35: 0.0028912; 11.3851 23 2035/36: 0.0028487; 11.3851 24 2036/37: 0.0028068; 11.3851 25 2037/38: 0.0027655; 11.3851 26 2038/39: 0.0027248; 11.3851 27 2039/40: 0.0026847; 11.3851 28 2040/41: 0.0026452; 11.3851 29 2041/42: 0.0026063; 11.3851 30 2042/43: 0.002568; 11.3851 31 2043/44: 0.0025302; 11.3851 32 2044/45: 0.002493
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.18346; 11.3851 2 2014/15: 0.18346; 11.3851 3 2015/16: 0.18346; 11.3851 4 2016/17: 0.18346; 11.3851 5 2017/18: 0.18346; 11.3851 6 2018/19: 0.18346; 11.3851 7 2019/20: 0.18346; 11.3851 8 2020/21: 0.18346; 11.3851 9 2021/22: 0.18076; 11.3851 10 2022/23: 0.1781; 11.3851 11 2023/24: 0.17548; 11.3851 12 2024/25: 0.1729; 11.3851 13 2025/26: 0.17036; 11.3851 14 2026/27: 0.16785; 11.3851 15 2027/28: 0.16538; 11.3851 16 2028/29: 0.16295; 11.3851 17 2029/30: 0.16055; 11.3851 18 2030/31: 0.15819; 11.3851 19 2031/32: 0.15586; 11.3851 20 2032/33: 0.15357; 11.3851 21 2033/34: 0.15131; 11.3851 22 2034/35: 0.14908; 11.3851 23 2035/36: 0.14689; 11.3851 24 2036/37: 0.14473; 11.3851 25 2037/38: 0.1426; 11.3851 26 2038/39: 0.1405; 11.3851 27 2039/40: 0.13844; 11.3851 28 2040/41: 0.1364; 11.3851 29 2041/42: 0.13439; 11.3851 30 2042/43: 0.13242; 11.3851 31 2043/44: 0.13047; 11.3851 32 2044/45: 0.12855
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.010469; 11.3851 2 2014/15: 0.010469; 11.3851 3 2015/16: 0.010469; 11.3851 4 2016/17: 0.010469; 11.3851 5 2017/18: 0.010469; 11.3851 6 2018/19: 0.010469; 11.3851 7 2019/20: 0.010469; 11.3851 8 2020/21: 0.010469; 11.3851 9 2021/22: 0.010315; 11.3851 10 2022/23: 0.010163; 11.3851 11 2023/24: 0.010014; 11.3851 12 2024/25: 0.0098662; 11.3851 13 2025/26: 0.0097211; 11.3851 14 2026/27: 0.0095781; 11.3851 15 2027/28: 0.0094372; 11.3851 16 2028/29: 0.0092983; 11.3851 17 2029/30: 0.0091615; 11.3851 18 2030/31: 0.0090268; 11.3851 19 2031/32: 0.008894; 11.3851 20 2032/33: 0.0087631; 11.3851 21 2033/34: 0.0086342; 11.3851 22 2034/35: 0.0085072; 11.3851 23 2035/36: 0.0083821; 11.3851 24 2036/37: 0.0082588; 11.3851 25 2037/38: 0.0081373; 11.3851 26 2038/39: 0.0080176; 11.3851 27 2039/40: 0.0078996; 11.3851 28 2040/41: 0.0077834; 11.3851 29 2041/42: 0.0076689; 11.3851 30 2042/43: 0.0075561; 11.3851 31 2043/44: 0.0074449; 11.3851 32 2044/45: 0.0073354
|  | £m | 09/10
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 0.5128; 11.3851 2 2014/15: 0.5128; 11.3851 3 2015/16: 0.5128; 11.3851 4 2016/17: 0.5128; 11.3851 5 2017/18: 0.5128; 11.3851 6 2018/19: 0.5128; 11.3851 7 2019/20: 0.5128; 11.3851 8 2020/21: 0.5128; 11.3851 9 2021/22: 0.50526; 11.3851 10 2022/23: 0.49783; 11.3851 11 2023/24: 0.4905; 11.3851 12 2024/25: 0.48329
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 0.35713; 11.3851 14 2026/27: 0.35188; 11.3851 15 2027/28: 0.3467; 11.3851 16 2028/29: 0.3416; 11.3851 17 2029/30: 0.33658; 11.3851 18 2030/31: 0.33163; 11.3851 19 2031/32: 0.32675; 11.3851 20 2032/33: 0.32194; 11.3851 21 2033/34: 0.31721; 11.3851 22 2034/35: 0.31254; 11.3851 23 2035/36: 0.30794; 11.3851 24 2036/37: 0.30341; 11.3851 25 2037/38: 0.29895; 11.3851 26 2038/39: 0.29455; 11.3851 27 2039/40: 0.29022; 11.3851 28 2040/41: 0.28595; 11.3851 29 2041/42: 0.28174; 11.3851 30 2042/43: 0.2776; 11.3851 31 2043/44: 0.27351; 11.3851 32 2044/45: 0.26949
| Estuary disruption costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.0021628; 11.3851 2 2014/15: 0.0021628; 11.3851 3 2015/16: 0.0021628; 11.3851 4 2016/17: 0.0021628; 11.3851 5 2017/18: 0.0021628; 11.3851 6 2018/19: 0.0021628; 11.3851 7 2019/20: 0.0021628; 11.3851 8 2020/21: 0.0021628; 11.3851 9 2021/22: 0.002131; 11.3851 10 2022/23: 0.0020997; 11.3851 11 2023/24: 0.0020688; 11.3851 12 2024/25: 0.0020383; 11.3851 13 2025/26: 0.0020084; 11.3851 14 2026/27: 0.0019788; 11.3851 15 2027/28: 0.0019497; 11.3851 16 2028/29: 0.001921; 11.3851 17 2029/30: 0.0018928; 11.3851 18 2030/31: 0.0018649; 11.3851 19 2031/32: 0.0018375; 11.3851 20 2032/33: 0.0018104; 11.3851 21 2033/34: 0.0017838; 11.3851 22 2034/35: 0.0017576; 11.3851 23 2035/36: 0.0017317; 11.3851 24 2036/37: 0.0017062; 11.3851 25 2037/38: 0.0016811; 11.3851 26 2038/39: 0.0016564; 11.3851 27 2039/40: 0.001632; 11.3851 28 2040/41: 0.001608; 11.3851 29 2041/42: 0.0015844; 11.3851 30 2042/43: 0.0015611; 11.3851 31 2043/44: 0.0015381; 11.3851 32 2044/45: 0.0015155
| Shipwreck clear up costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.061322; 11.3851 2 2014/15: 0.061322; 11.3851 3 2015/16: 0.061322; 11.3851 4 2016/17: 0.061322; 11.3851 5 2017/18: 0.061322; 11.3851 6 2018/19: 0.061322; 11.3851 7 2019/20: 0.061322; 11.3851 8 2020/21: 0.061322; 11.3851 9 2021/22: 0.06042; 11.3851 10 2022/23: 0.059531; 11.3851 11 2023/24: 0.058656; 11.3851 12 2024/25: 0.057793; 11.3851 13 2025/26: 0.056943; 11.3851 14 2026/27: 0.056105; 11.3851 15 2027/28: 0.05528; 11.3851 16 2028/29: 0.054466; 11.3851 17 2029/30: 0.053665; 11.3851 18 2030/31: 0.052876; 11.3851 19 2031/32: 0.052098; 11.3851 20 2032/33: 0.051332; 11.3851 21 2033/34: 0.050576; 11.3851 22 2034/35: 0.049832; 11.3851 23 2035/36: 0.049099; 11.3851 24 2036/37: 0.048377; 11.3851 25 2037/38: 0.047665; 11.3851 26 2038/39: 0.046964; 11.3851 27 2039/40: 0.046273; 11.3851 28 2040/41: 0.045593; 11.3851 29 2041/42: 0.044922; 11.3851 30 2042/43: 0.044261; 11.3851 31 2043/44: 0.04361; 11.3851 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 11.3851 1 2013/14: 39.4287; 11.3851 2 2014/15: 39.4132; 11.3851 3 2015/16: 39.3979; 11.3851 4 2016/17: 39.3827; 11.3851 5 2017/18: 39.3677; 11.3851 6 2018/19: 39.3527; 11.3851 7 2019/20: 39.3379; 11.3851 8 2020/21: 39.3233; 11.3851 9 2021/22: 38.7577; 11.3851 10 2022/23: 38.2004; 11.3851 11 2023/24: 37.6512; 11.3851 12 2024/25: 37.11; 11.3851 13 2025/26: 32.4723; 11.3851 14 2026/27: 32.0071; 11.3851 15 2027/28: 31.5487; 11.3851 16 2028/29: 31.0969; 11.3851 17 2029/30: 30.6517; 11.3851 18 2030/31: 30.2129; 11.3851 19 2031/32: 29.7806; 11.3851 20 2032/33: 29.3545; 11.3851 21 2033/34: 28.9346; 11.3851 22 2034/35: 28.5207; 11.3851 23 2035/36: 28.1129; 11.3851 24 2036/37: 27.7111; 11.3851 25 2037/38: 27.315; 11.3851 26 2038/39: 26.9247; 11.3851 27 2039/40: 26.5401; 11.3851 28 2040/41: 26.161; 11.3851 29 2041/42: 25.7875; 11.3851 30 2042/43: 25.4193; 11.3851 31 2043/44: 25.0565; 11.3851 32 2044/45: 24.699
| Cost of possible loss of life | £m | 09/10 |  | 11.3851 1 2013/14: 0.11536; 11.3851 2 2014/15: 0.11536; 11.3851 3 2015/16: 0.11536; 11.3851 4 2016/17: 0.11536; 11.3851 5 2017/18: 0.11536; 11.3851 6 2018/19: 0.11536; 11.3851 7 2019/20: 0.11536; 11.3851 8 2020/21: 0.11536; 11.3851 9 2021/22: 0.11366; 11.3851 10 2022/23: 0.11199; 11.3851 11 2023/24: 0.11034; 11.3851 12 2024/25: 0.10872; 11.3851 13 2025/26: 0.10712; 11.3851 14 2026/27: 0.10555; 11.3851 15 2027/28: 0.10399; 11.3851 16 2028/29: 0.10246; 11.3851 17 2029/30: 0.10096; 11.3851 18 2030/31: 0.099471; 11.3851 19 2031/32: 0.098008; 11.3851 20 2032/33: 0.096566; 11.3851 21 2033/34: 0.095146; 11.3851 22 2034/35: 0.093746; 11.3851 23 2035/36: 0.092367; 11.3851 24 2036/37: 0.091008; 11.3851 25 2037/38: 0.089669; 11.3851 26 2038/39: 0.08835; 11.3851 27 2039/40: 0.087051; 11.3851 28 2040/41: 0.08577; 11.3851 29 2041/42: 0.084508; 11.3851 30 2042/43: 0.083265; 11.3851 31 2043/44: 0.08204; 11.3851 32 2044/45: 0.080833
| Discount factor for other costs |  |  |  | 11.3851 1 2013/14: 0.96618; 11.3851 2 2014/15: 0.93351; 11.3851 3 2015/16: 0.90194; 11.3851 4 2016/17: 0.87144; 11.3851 5 2017/18: 0.84197; 11.3851 6 2018/19: 0.8135; 11.3851 7 2019/20: 0.78599; 11.3851 8 2020/21: 0.75941; 11.3851 9 2021/22: 0.73373; 11.3851 10 2022/23: 0.70892; 11.3851 11 2023/24: 0.68495; 11.3851 12 2024/25: 0.66178; 11.3851 13 2025/26: 0.6394; 11.3851 14 2026/27: 0.61778; 11.3851 15 2027/28: 0.59689; 11.3851 16 2028/29: 0.57671; 11.3851 17 2029/30: 0.5572; 11.3851 18 2030/31: 0.53836; 11.3851 19 2031/32: 0.52016; 11.3851 20 2032/33: 0.50257; 11.3851 21 2033/34: 0.48557; 11.3851 22 2034/35: 0.46915; 11.3851 23 2035/36: 0.45329; 11.3851 24 2036/37: 0.43796; 11.3851 25 2037/38: 0.42315; 11.3851 26 2038/39: 0.40884; 11.3851 27 2039/40: 0.39501; 11.3851 28 2040/41: 0.38165; 11.3851 29 2041/42: 0.36875; 11.3851 30 2042/43: 0.35628; 11.3851 31 2043/44: 0.39999; 11.3851 32 2044/45: 0.38834
| Discount factor for loss of life costs |  |  |  | 11.3851 1 2013/14: 0.98522; 11.3851 2 2014/15: 0.97066; 11.3851 3 2015/16: 0.95632; 11.3851 4 2016/17: 0.94218; 11.3851 5 2017/18: 0.92826; 11.3851 6 2018/19: 0.91454; 11.3851 7 2019/20: 0.90103; 11.3851 8 2020/21: 0.88771; 11.3851 9 2021/22: 0.87459; 11.3851 10 2022/23: 0.86167; 11.3851 11 2023/24: 0.84893; 11.3851 12 2024/25: 0.83639; 11.3851 13 2025/26: 0.82403; 11.3851 14 2026/27: 0.81185; 11.3851 15 2027/28: 0.79985; 11.3851 16 2028/29: 0.78803; 11.3851 17 2029/30: 0.77639; 11.3851 18 2030/31: 0.76491; 11.3851 19 2031/32: 0.75361; 11.3851 20 2032/33: 0.74247; 11.3851 21 2033/34: 0.7315; 11.3851 22 2034/35: 0.72069; 11.3851 23 2035/36: 0.71004; 11.3851 24 2036/37: 0.69954; 11.3851 25 2037/38: 0.68921; 11.3851 26 2038/39: 0.67902; 11.3851 27 2039/40: 0.66899; 11.3851 28 2040/41: 0.6591; 11.3851 29 2041/42: 0.64936; 11.3851 30 2042/43: 0.63976; 11.3851 31 2043/44: 0.6721; 11.3851 32 2044/45: 0.66354
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 11.3851 1 2013/14: 38.0954; 11.3851 2 2014/15: 36.7927; 11.3851 3 2015/16: 35.5347; 11.3851 4 2016/17: 34.3198; 11.3851 5 2017/18: 33.1465; 11.3851 6 2018/19: 32.0135; 11.3851 7 2019/20: 30.9193; 11.3851 8 2020/21: 29.8625; 11.3851 9 2021/22: 28.4377; 11.3851 10 2022/23: 27.081; 11.3851 11 2023/24: 25.789; 11.3851 12 2024/25: 24.5588; 11.3851 13 2025/26: 20.7629; 11.3851 14 2026/27: 19.7734; 11.3851 15 2027/28: 18.8311; 11.3851 16 2028/29: 17.9338; 11.3851 17 2029/30: 17.0792; 11.3851 18 2030/31: 16.2655; 11.3851 19 2031/32: 15.4905; 11.3851 20 2032/33: 14.7526; 11.3851 21 2033/34: 14.0498; 11.3851 22 2034/35: 13.3805; 11.3851 23 2035/36: 12.7432; 11.3851 24 2036/37: 12.1363; 11.3851 25 2037/38: 11.5583; 11.3851 26 2038/39: 11.0078; 11.3851 27 2039/40: 10.4836; 11.3851 28 2040/41: 9.9845; 11.3851 29 2041/42: 9.5091; 11.3851 30 2042/43: 9.0564; 11.3851 31 2043/44: 10.0223; 11.3851 32 2044/45: 9.5915
| Discounted cost of loss of life | £m | 09/10 |  | 11.3851 1 2013/14: 0.11366; 11.3851 2 2014/15: 0.11198; 11.3851 3 2015/16: 0.11032; 11.3851 4 2016/17: 0.10869; 11.3851 5 2017/18: 0.10709; 11.3851 6 2018/19: 0.1055; 11.3851 7 2019/20: 0.10394; 11.3851 8 2020/21: 0.10241; 11.3851 9 2021/22: 0.09941; 11.3851 10 2022/23: 0.0965; 11.3851 11 2023/24: 0.093675; 11.3851 12 2024/25: 0.090933; 11.3851 13 2025/26: 0.088272; 11.3851 14 2026/27: 0.085688; 11.3851 15 2027/28: 0.083179; 11.3851 16 2028/29: 0.080745; 11.3851 17 2029/30: 0.078381; 11.3851 18 2030/31: 0.076087; 11.3851 19 2031/32: 0.07386; 11.3851 20 2032/33: 0.071698; 11.3851 21 2033/34: 0.069599; 11.3851 22 2034/35: 0.067562; 11.3851 23 2035/36: 0.065584; 11.3851 24 2036/37: 0.063664; 11.3851 25 2037/38: 0.061801; 11.3851 26 2038/39: 0.059992; 11.3851 27 2039/40: 0.058236; 11.3851 28 2040/41: 0.056531; 11.3851 29 2041/42: 0.054876; 11.3851 30 2042/43: 0.05327; 11.3851 31 2043/44: 0.05514; 11.3851 32 2044/45: 0.053637
| Total discounted cost | £m | 09/10 |  | 11.3851 1 2013/14: 38.209; 11.3851 2 2014/15: 36.9047; 11.3851 3 2015/16: 35.645; 11.3851 4 2016/17: 34.4285; 11.3851 5 2017/18: 33.2536; 11.3851 6 2018/19: 32.119; 11.3851 7 2019/20: 31.0232; 11.3851 8 2020/21: 29.9649; 11.3851 9 2021/22: 28.5371; 11.3851 10 2022/23: 27.1775; 11.3851 11 2023/24: 25.8827; 11.3851 12 2024/25: 24.6497; 11.3851 13 2025/26: 20.8512; 11.3851 14 2026/27: 19.8591; 11.3851 15 2027/28: 18.9143; 11.3851 16 2028/29: 18.0145; 11.3851 17 2029/30: 17.1576; 11.3851 18 2030/31: 16.3416; 11.3851 19 2031/32: 15.5644; 11.3851 20 2032/33: 14.8242; 11.3851 21 2033/34: 14.1194; 11.3851 22 2034/35: 13.4481; 11.3851 23 2035/36: 12.8088; 11.3851 24 2036/37: 12.1999; 11.3851 25 2037/38: 11.6201; 11.3851 26 2038/39: 11.0678; 11.3851 27 2039/40: 10.5419; 11.3851 28 2040/41: 10.041; 11.3851 29 2041/42: 9.564; 11.3851 30 2042/43: 9.1096; 11.3851 31 2043/44: 10.0774; 11.3851 32 2044/45: 9.6452
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 11.3851 1 2013/14: 38.0954; 11.3851 2 2014/15: 74.888; 11.3851 3 2015/16: 110.4227; 11.3851 4 2016/17: 144.7425; 11.3851 5 2017/18: 177.889; 11.3851 6 2018/19: 209.9025; 11.3851 7 2019/20: 240.8217; 11.3851 8 2020/21: 270.6843; 11.3851 9 2021/22: 299.122; 11.3851 10 2022/23: 326.203; 11.3851 11 2023/24: 351.992; 11.3851 12 2024/25: 376.5508; 11.3851 13 2025/26: 397.3138; 11.3851 14 2026/27: 417.0872; 11.3851 15 2027/28: 435.9183; 11.3851 16 2028/29: 453.852; 11.3851 17 2029/30: 470.9313; 11.3851 18 2030/31: 487.1967; 11.3851 19 2031/32: 502.6873; 11.3851 20 2032/33: 517.4398; 11.3851 21 2033/34: 531.4896; 11.3851 22 2034/35: 544.8701; 11.3851 23 2035/36: 557.6133; 11.3851 24 2036/37: 569.7496; 11.3851 25 2037/38: 581.3078; 11.3851 26 2038/39: 592.3157; 11.3851 27 2039/40: 602.7993; 11.3851 28 2040/41: 612.7838; 11.3851 29 2041/42: 622.2928; 11.3851 30 2042/43: 631.3492; 11.3851 31 2043/44: 641.3715; 11.3851 32 2044/45: 650.963
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 11.3851 1 2013/14: 0.11366; 11.3851 2 2014/15: 0.22563; 11.3851 3 2015/16: 0.33596; 11.3851 4 2016/17: 0.44465; 11.3851 5 2017/18: 0.55173; 11.3851 6 2018/19: 0.65724; 11.3851 7 2019/20: 0.76118; 11.3851 8 2020/21: 0.86359; 11.3851 9 2021/22: 0.963; 11.3851 10 2022/23: 1.0595; 11.3851 11 2023/24: 1.1532; 11.3851 12 2024/25: 1.2441; 11.3851 13 2025/26: 1.3324; 11.3851 14 2026/27: 1.4181; 11.3851 15 2027/28: 1.5012; 11.3851 16 2028/29: 1.582; 11.3851 17 2029/30: 1.6604; 11.3851 18 2030/31: 1.7365; 11.3851 19 2031/32: 1.8103; 11.3851 20 2032/33: 1.882; 11.3851 21 2033/34: 1.9516; 11.3851 22 2034/35: 2.0192; 11.3851 23 2035/36: 2.0848; 11.3851 24 2036/37: 2.1484; 11.3851 25 2037/38: 2.2102; 11.3851 26 2038/39: 2.2702; 11.3851 27 2039/40: 2.3284; 11.3851 28 2040/41: 2.385; 11.3851 29 2041/42: 2.4399; 11.3851 30 2042/43: 2.4931; 11.3851 31 2043/44: 2.5483; 11.3851 32 2044/45: 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 11.3851 1 2013/14: 38.209; 11.3851 2 2014/15: 75.1137; 11.3851 3 2015/16: 110.7587; 11.3851 4 2016/17: 145.1871; 11.3851 5 2017/18: 178.4407; 11.3851 6 2018/19: 210.5597; 11.3851 7 2019/20: 241.5829; 11.3851 8 2020/21: 271.5479; 11.3851 9 2021/22: 300.085; 11.3851 10 2022/23: 327.2625; 11.3851 11 2023/24: 353.1452; 11.3851 12 2024/25: 377.7949; 11.3851 13 2025/26: 398.6461; 11.3851 14 2026/27: 418.5052; 11.3851 15 2027/28: 437.4195; 11.3851 16 2028/29: 455.434; 11.3851 17 2029/30: 472.5916; 11.3851 18 2030/31: 488.9332; 11.3851 19 2031/32: 504.4976; 11.3851 20 2032/33: 519.3218; 11.3851 21 2033/34: 533.4412; 11.3851 22 2034/35: 546.8893; 11.3851 23 2035/36: 559.6981; 11.3851 24 2036/37: 571.898; 11.3851 25 2037/38: 583.518; 11.3851 26 2038/39: 594.5859; 11.3851 27 2039/40: 605.1278; 11.3851 28 2040/41: 615.1687; 11.3851 29 2041/42: 624.7327; 11.3851 30 2042/43: 633.8423; 11.3851 31 2043/44: 643.9197; 11.3851 32 2044/45: 653.5649
3 | Option: Mitigate with tunnel replacement in 2044
| Revenue impact of tunnel commissioned in 2045/46 | £m | 09/10 | See footnote 5 | 11.3851 25 2037/38: 0.44537; 11.3851 26 2038/39: 0.45206; 11.3851 27 2039/40: 2.28; 11.3851 28 2040/41: 4.1415; 11.3851 29 2041/42: 4.4557; 11.3851 30 2042/43: 5.3185; 11.3851 31 2043/44: 4.0167; 11.3851 32 2044/45: 4.0874; 11.3851 33 2045/46: 6.0637; 11.3851 34 2046/47: 5.9689; 11.3851 35 2047/48: 5.8741; 11.3851 36 2048/49: 5.7793; 11.3851 37 2049/50: 5.6845; 11.3851 38 2050/51: 5.5897; 11.3851 39 2051/52: 5.4949; 11.3851 40 2052/53: 5.4001; 11.3851 41 2053/54: 5.3053; 11.3851 42 2054/55: 5.2105; 11.3851 43 2055/56: 5.1157; 11.3851 44 2056/57: 5.0209; 11.3851 45 2057/58: 4.9261; 11.3851 46 2058/59: 4.8313; 11.3851 47 2059/60: 4.7365; 11.3851 48 2060/61: 4.6418; 11.3851 49 2061/62: 4.547; 11.3851 50 2062/63: 4.4522; 11.3851 51 2063/64: 4.3574; 11.3851 52 2064/65: 4.2626; 11.3851 53 2065/66: 4.1678; 11.3851 54 2066/67: 4.073; 11.3851 55 2067/68: 3.9782; 11.3851 56 2068/69: 3.8834; 11.3851 57 2069/70: 3.7886; 11.3851 58 2070/71: 3.6938; 11.3851 59 2071/72: 3.599; 11.3851 60 2072/73: 3.5042
| Operational costs untill 2044/45 | £m | 09/10 |  | 11.3851 1 2013/14: 0.29951; 11.3851 2 2014/15: 0.29951; 11.3851 3 2015/16: 0.29951; 11.3851 4 2016/17: 0.29951; 11.3851 5 2017/18: 0.29951; 11.3851 6 2018/19: 0.29951; 11.3851 7 2019/20: 0.29951; 11.3851 8 2020/21: 0.29951; 11.3851 9 2021/22: 0.29598; 11.3851 10 2022/23: 0.29251; 11.3851 11 2023/24: 0.28908; 11.3851 12 2024/25: 0.28571; 11.3851 13 2025/26: 0.28239; 11.3851 14 2026/27: 0.27911; 11.3851 15 2027/28: 0.27588; 11.3851 16 2028/29: 0.2727; 11.3851 17 2029/30: 0.26957; 11.3851 18 2030/31: 0.26648; 11.3851 19 2031/32: 0.26344; 11.3851 20 2032/33: 0.26045; 11.3851 21 2033/34: 0.25749; 11.3851 22 2034/35: 0.25458; 11.3851 23 2035/36: 0.25172; 11.3851 24 2036/37: 0.24889; 11.3851 25 2037/38: 0.24611; 11.3851 26 2038/39: 0.24337; 11.3851 27 2039/40: 0.24067; 11.3851 28 2040/41: 0.23801; 11.3851 29 2041/42: 0.23539; 11.3851 30 2042/43: 0.2328; 11.3851 31 2043/44: 0.23026; 11.3851 32 2044/45: 0.22775
| Operational costs for tunnel commissioned in 2045/46 |  |  |  | 11.3851 33 2045/46: 0.059745; 11.3851 34 2046/47: 0.059745; 11.3851 35 2047/48: 0.059745; 11.3851 36 2048/49: 0.059745; 11.3851 37 2049/50: 0.059745; 11.3851 38 2050/51: 0.059745; 11.3851 39 2051/52: 0.059745; 11.3851 40 2052/53: 0.059745; 11.3851 41 2053/54: 0.059745; 11.3851 42 2054/55: 0.059745; 11.3851 43 2055/56: 0.059745; 11.3851 44 2056/57: 0.059745; 11.3851 45 2057/58: 0.059745; 11.3851 46 2058/59: 0.059745; 11.3851 47 2059/60: 0.059745; 11.3851 48 2060/61: 0.059745; 11.3851 49 2061/62: 0.059745; 11.3851 50 2062/63: 0.059745; 11.3851 51 2063/64: 0.059745; 11.3851 52 2064/65: 0.059745; 11.3851 53 2065/66: 0.059745; 11.3851 54 2066/67: 0.059745; 11.3851 55 2067/68: 0.059745; 11.3851 56 2068/69: 0.059745; 11.3851 57 2069/70: 0.059745; 11.3851 58 2070/71: 0.059745; 11.3851 59 2071/72: 0.059745; 11.3851 60 2072/73: 0.059745
| Loss of lease | £m | 09/10 |  | 11.3851 1 2013/14: 1.2511; 11.3851 2 2014/15: 1.239; 11.3851 3 2015/16: 1.2271; 11.3851 4 2016/17: 1.2152; 11.3851 5 2017/18: 1.2035; 11.3851 6 2018/19: 1.1919; 11.3851 7 2019/20: 1.1804; 11.3851 8 2020/21: 1.169; 11.3851 9 2021/22: 1.1577; 11.3851 10 2022/23: 1.1465; 11.3851 11 2023/24: 1.1355; 11.3851 12 2024/25: 1.1245; 11.3851 13 2025/26: 1.1137; 11.3851 14 2026/27: 1.1029; 11.3851 15 2027/28: 1.0923; 11.3851 16 2028/29: 1.0817; 11.3851 17 2029/30: 1.0713; 11.3851 18 2030/31: 1.061; 11.3851 19 2031/32: 1.0507; 11.3851 20 2032/33: 1.0406; 11.3851 21 2033/34: 1.0305; 11.3851 22 2034/35: 1.0206; 11.3851 23 2035/36: 1.0107; 11.3851 24 2036/37: 1.001; 11.3851 25 2037/38: 0.99133; 11.3851 26 2038/39: 0.98176; 11.3851 27 2039/40: 0.97229; 11.3851 28 2040/41: 0.96291; 11.3851 29 2041/42: 0.95361; 11.3851 30 2042/43: 0.94441; 11.3851 31 2043/44: 0.9353; 11.3851 32 2044/45: 0.92627
| Mattressing cost | £m | 09/10 |  | 11.3851 1 2013/14: 0.74263; 11.3851 2 2014/15: 0.74263; 11.3851 3 2015/16: 0.74263; 11.3851 4 2016/17: 0.74263; 11.3851 5 2017/18: 0.74263; 11.3851 6 2018/19: 0.74263; 11.3851 7 2019/20: 0.74263; 11.3851 8 2020/21: 0.74263; 11.3851 9 2021/22: 0.73171; 11.3851 10 2022/23: 0.72094; 11.3851 11 2023/24: 0.71034; 11.3851 12 2024/25: 0.69989; 11.3851 13 2025/26: 0.68959; 11.3851 14 2026/27: 0.67945; 11.3851 15 2027/28: 0.66945; 11.3851 16 2028/29: 0.6596; 11.3851 17 2029/30: 0.6499; 11.3851 18 2030/31: 0.64034; 11.3851 19 2031/32: 0.63092; 11.3851 20 2032/33: 0.62164; 11.3851 21 2033/34: 0.61249; 11.3851 22 2034/35: 0.60348; 11.3851 23 2035/36: 0.59461; 11.3851 24 2036/37: 0.58586; 11.3851 25 2037/38: 0.57724; 11.3851 26 2038/39: 0.56875; 11.3851 27 2039/40: 0.56038; 11.3851 28 2040/41: 0.55214; 11.3851 29 2041/42: 0.54402; 11.3851 30 2042/43: 0.53601; 11.3851 31 2043/44: 0.52813; 11.3851 32 2044/45: 0.52036
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 11.3851 1 2013/14: 0.26098; 11.3851 2 2014/15: 0.26098; 11.3851 3 2015/16: 0.26098; 11.3851 4 2016/17: 0.26098; 11.3851 5 2017/18: 0.26098; 11.3851 6 2018/19: 0.26098; 11.3851 7 2019/20: 0.26098; 11.3851 8 2020/21: 0.26098; 11.3851 9 2021/22: 0.25714; 11.3851 10 2022/23: 0.25336; 11.3851 11 2023/24: 0.24963; 11.3851 12 2024/25: 0.24596; 11.3851 13 2025/26: 0.24234; 11.3851 14 2026/27: 0.23878; 11.3851 15 2027/28: 0.23526; 11.3851 16 2028/29: 0.2318; 11.3851 17 2029/30: 0.22839; 11.3851 18 2030/31: 0.22503; 11.3851 19 2031/32: 0.22172; 11.3851 20 2032/33: 0.21846; 11.3851 21 2033/34: 0.21525; 11.3851 22 2034/35: 0.21208; 11.3851 23 2035/36: 0.20896; 11.3851 24 2036/37: 0.20589; 11.3851 25 2037/38: 0.20286; 11.3851 26 2038/39: 0.19987; 11.3851 27 2039/40: 0.19693; 11.3851 28 2040/41: 0.19404; 11.3851 29 2041/42: 0.19118; 11.3851 30 2042/43: 0.18837; 11.3851 31 2043/44: 0.1856; 11.3851 32 2044/45: 0.18287
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 11.3851 1 2013/14: 0.16994; 11.3851 2 2014/15: 0.16994; 11.3851 3 2015/16: 0.16994; 11.3851 4 2016/17: 0.16994; 11.3851 5 2017/18: 0.16994; 11.3851 6 2018/19: 0.16994; 11.3851 7 2019/20: 0.16994; 11.3851 8 2020/21: 0.16994; 11.3851 9 2021/22: 0.16744; 11.3851 10 2022/23: 0.16498; 11.3851 11 2023/24: 0.16255; 11.3851 12 2024/25: 0.16016; 11.3851 13 2025/26: 0.15781; 11.3851 14 2026/27: 0.15548; 11.3851 15 2027/28: 0.1532; 11.3851 16 2028/29: 0.15094; 11.3851 17 2029/30: 0.14872; 11.3851 18 2030/31: 0.14654; 11.3851 19 2031/32: 0.14438; 11.3851 20 2032/33: 0.14226; 11.3851 21 2033/34: 0.14016; 11.3851 22 2034/35: 0.1381; 11.3851 23 2035/36: 0.13607; 11.3851 24 2036/37: 0.13407; 11.3851 25 2037/38: 0.1321; 11.3851 26 2038/39: 0.13015; 11.3851 27 2039/40: 0.12824; 11.3851 28 2040/41: 0.12635; 11.3851 29 2041/42: 0.12449; 11.3851 30 2042/43: 0.12266; 11.3851 31 2043/44: 0.12086; 11.3851 32 2044/45: 0.11908
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 14.0896; 11.3851 2 2014/15: 14.0896; 11.3851 3 2015/16: 14.0896; 11.3851 4 2016/17: 14.0896; 11.3851 5 2017/18: 14.0896; 11.3851 6 2018/19: 14.0896; 11.3851 7 2019/20: 14.0896; 11.3851 8 2020/21: 14.0896; 11.3851 9 2021/22: 13.8823; 11.3851 10 2022/23: 13.6781; 11.3851 11 2023/24: 13.4769; 11.3851 12 2024/25: 13.2786; 11.3851 13 2025/26: 13.0833; 11.3851 14 2026/27: 12.8908; 11.3851 15 2027/28: 12.7012; 11.3851 16 2028/29: 12.5144; 11.3851 17 2029/30: 12.3303; 11.3851 18 2030/31: 12.1489; 11.3851 19 2031/32: 11.9702; 11.3851 20 2032/33: 11.7941; 11.3851 21 2033/34: 11.6206; 11.3851 22 2034/35: 11.4496; 11.3851 23 2035/36: 11.2812; 11.3851 24 2036/37: 11.1152; 11.3851 25 2037/38: 10.9517; 11.3851 26 2038/39: 10.7906; 11.3851 27 2039/40: 10.6319; 11.3851 28 2040/41: 10.4755; 11.3851 29 2041/42: 10.3214; 11.3851 30 2042/43: 10.1695; 11.3851 31 2043/44: 10.0199; 11.3851 32 2044/45: 9.8725
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.804; 11.3851 2 2014/15: 0.804; 11.3851 3 2015/16: 0.804; 11.3851 4 2016/17: 0.804; 11.3851 5 2017/18: 0.804; 11.3851 6 2018/19: 0.804; 11.3851 7 2019/20: 0.804; 11.3851 8 2020/21: 0.804; 11.3851 9 2021/22: 0.79217; 11.3851 10 2022/23: 0.78052; 11.3851 11 2023/24: 0.76904; 11.3851 12 2024/25: 0.75772; 11.3851 13 2025/26: 0.74658; 11.3851 14 2026/27: 0.73559; 11.3851 15 2027/28: 0.72477; 11.3851 16 2028/29: 0.71411; 11.3851 17 2029/30: 0.70361; 11.3851 18 2030/31: 0.69326; 11.3851 19 2031/32: 0.68306; 11.3851 20 2032/33: 0.67301; 11.3851 21 2033/34: 0.66311; 11.3851 22 2034/35: 0.65335; 11.3851 23 2035/36: 0.64374; 11.3851 24 2036/37: 0.63427; 11.3851 25 2037/38: 0.62494; 11.3851 26 2038/39: 0.61575; 11.3851 27 2039/40: 0.60669; 11.3851 28 2040/41: 0.59777; 11.3851 29 2041/42: 0.58897; 11.3851 30 2042/43: 0.58031; 11.3851 31 2043/44: 0.57177; 11.3851 32 2044/45: 0.56336
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 8.782; 11.3851 2 2014/15: 8.782; 11.3851 3 2015/16: 8.782; 11.3851 4 2016/17: 8.782; 11.3851 5 2017/18: 8.782; 11.3851 6 2018/19: 8.782; 11.3851 7 2019/20: 8.782; 11.3851 8 2020/21: 8.782; 11.3851 9 2021/22: 8.6529; 11.3851 10 2022/23: 8.5256; 11.3851 11 2023/24: 8.4001; 11.3851 12 2024/25: 8.2766
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 6.1161; 11.3851 14 2026/27: 6.0261; 11.3851 15 2027/28: 5.9375; 11.3851 16 2028/29: 5.8501; 11.3851 17 2029/30: 5.7641; 11.3851 18 2030/31: 5.6793; 11.3851 19 2031/32: 5.5957; 11.3851 20 2032/33: 5.5134; 11.3851 21 2033/34: 5.4323; 11.3851 22 2034/35: 5.3524; 11.3851 23 2035/36: 5.2737; 11.3851 24 2036/37: 5.1961; 11.3851 25 2037/38: 5.1197; 11.3851 26 2038/39: 5.0443; 11.3851 27 2039/40: 4.9701; 11.3851 28 2040/41: 4.897; 11.3851 29 2041/42: 4.825; 11.3851 30 2042/43: 4.754; 11.3851 31 2043/44: 4.6841; 11.3851 32 2044/45: 4.6152
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 11.3851 1 2013/14: 0.66249; 11.3851 2 2014/15: 0.65911; 11.3851 3 2015/16: 0.65574; 11.3851 4 2016/17: 0.65239; 11.3851 5 2017/18: 0.64906; 11.3851 6 2018/19: 0.64574; 11.3851 7 2019/20: 0.64244; 11.3851 8 2020/21: 0.63916; 11.3851 9 2021/22: 0.63589; 11.3851 10 2022/23: 0.63264; 11.3851 11 2023/24: 0.62941; 11.3851 12 2024/25: 0.62619; 11.3851 13 2025/26: 0.62299; 11.3851 14 2026/27: 0.61981; 11.3851 15 2027/28: 0.61664; 11.3851 16 2028/29: 0.61349; 11.3851 17 2029/30: 0.61036; 11.3851 18 2030/31: 0.60724; 11.3851 19 2031/32: 0.60413; 11.3851 20 2032/33: 0.60105; 11.3851 21 2033/34: 0.59798; 11.3851 22 2034/35: 0.59492; 11.3851 23 2035/36: 0.59188; 11.3851 24 2036/37: 0.58886; 11.3851 25 2037/38: 0.58585; 11.3851 26 2038/39: 0.58285; 11.3851 27 2039/40: 0.57987; 11.3851 28 2040/41: 0.57691; 11.3851 29 2041/42: 0.57396; 11.3851 30 2042/43: 0.57103; 11.3851 31 2043/44: 0.56811; 11.3851 32 2044/45: 0.56521
| Cost of emergency mattressing - major | £m | 09/10 |  | 11.3851 1 2013/14: 0.036184; 11.3851 2 2014/15: 0.036184; 11.3851 3 2015/16: 0.036184; 11.3851 4 2016/17: 0.036184; 11.3851 5 2017/18: 0.036184; 11.3851 6 2018/19: 0.036184; 11.3851 7 2019/20: 0.036184; 11.3851 8 2020/21: 0.036184; 11.3851 9 2021/22: 0.035652; 11.3851 10 2022/23: 0.035127; 11.3851 11 2023/24: 0.03461; 11.3851 12 2024/25: 0.034101; 11.3851 13 2025/26: 0.0336; 11.3851 14 2026/27: 0.033105; 11.3851 15 2027/28: 0.032618; 11.3851 16 2028/29: 0.032139; 11.3851 17 2029/30: 0.031666; 11.3851 18 2030/31: 0.0312; 11.3851 19 2031/32: 0.030741; 11.3851 20 2032/33: 0.030289; 11.3851 21 2033/34: 0.029843; 11.3851 22 2034/35: 0.029404; 11.3851 23 2035/36: 0.028972; 11.3851 24 2036/37: 0.028545; 11.3851 25 2037/38: 0.028125; 11.3851 26 2038/39: 0.027712; 11.3851 27 2039/40: 0.027304; 11.3851 28 2040/41: 0.026902; 11.3851 29 2041/42: 0.026507; 11.3851 30 2042/43: 0.026117; 11.3851 31 2043/44: 0.025733; 11.3851 32 2044/45: 0.025354
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 2.9999; 11.3851 2 2014/15: 2.9999; 11.3851 3 2015/16: 2.9999; 11.3851 4 2016/17: 2.9999; 11.3851 5 2017/18: 2.9999; 11.3851 6 2018/19: 2.9999; 11.3851 7 2019/20: 2.9999; 11.3851 8 2020/21: 2.9999; 11.3851 9 2021/22: 2.9558; 11.3851 10 2022/23: 2.9123; 11.3851 11 2023/24: 2.8695; 11.3851 12 2024/25: 2.8272; 11.3851 13 2025/26: 2.7857; 11.3851 14 2026/27: 2.7447; 11.3851 15 2027/28: 2.7043; 11.3851 16 2028/29: 2.6645; 11.3851 17 2029/30: 2.6253; 11.3851 18 2030/31: 2.5867; 11.3851 19 2031/32: 2.5486; 11.3851 20 2032/33: 2.5112; 11.3851 21 2033/34: 2.4742; 11.3851 22 2034/35: 2.4378; 11.3851 23 2035/36: 2.402; 11.3851 24 2036/37: 2.3666; 11.3851 25 2037/38: 2.3318; 11.3851 26 2038/39: 2.2975; 11.3851 27 2039/40: 2.2637; 11.3851 28 2040/41: 2.2304; 11.3851 29 2041/42: 2.1976; 11.3851 30 2042/43: 2.1653; 11.3851 31 2043/44: 2.1334; 11.3851 32 2044/45: 2.102
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.17119; 11.3851 2 2014/15: 0.17119; 11.3851 3 2015/16: 0.17119; 11.3851 4 2016/17: 0.17119; 11.3851 5 2017/18: 0.17119; 11.3851 6 2018/19: 0.17119; 11.3851 7 2019/20: 0.17119; 11.3851 8 2020/21: 0.17119; 11.3851 9 2021/22: 0.16867; 11.3851 10 2022/23: 0.16619; 11.3851 11 2023/24: 0.16374; 11.3851 12 2024/25: 0.16133; 11.3851 13 2025/26: 0.15896; 11.3851 14 2026/27: 0.15662; 11.3851 15 2027/28: 0.15432; 11.3851 16 2028/29: 0.15205; 11.3851 17 2029/30: 0.14981; 11.3851 18 2030/31: 0.14761; 11.3851 19 2031/32: 0.14543; 11.3851 20 2032/33: 0.14329; 11.3851 21 2033/34: 0.14119; 11.3851 22 2034/35: 0.13911; 11.3851 23 2035/36: 0.13706; 11.3851 24 2036/37: 0.13505; 11.3851 25 2037/38: 0.13306; 11.3851 26 2038/39: 0.1311; 11.3851 27 2039/40: 0.12917; 11.3851 28 2040/41: 0.12727; 11.3851 29 2041/42: 0.1254; 11.3851 30 2042/43: 0.12356; 11.3851 31 2043/44: 0.12174; 11.3851 32 2044/45: 0.11995
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 8.3854; 11.3851 2 2014/15: 8.3854; 11.3851 3 2015/16: 8.3854; 11.3851 4 2016/17: 8.3854; 11.3851 5 2017/18: 8.3854; 11.3851 6 2018/19: 8.3854; 11.3851 7 2019/20: 8.3854; 11.3851 8 2020/21: 8.3854; 11.3851 9 2021/22: 8.262; 11.3851 10 2022/23: 8.1405; 11.3851 11 2023/24: 8.0207; 11.3851 12 2024/25: 7.9027
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 5.8399; 11.3851 14 2026/27: 5.754; 11.3851 15 2027/28: 5.6693; 11.3851 16 2028/29: 5.5859; 11.3851 17 2029/30: 5.5037; 11.3851 18 2030/31: 5.4228; 11.3851 19 2031/32: 5.343; 11.3851 20 2032/33: 5.2644; 11.3851 21 2033/34: 5.187; 11.3851 22 2034/35: 5.1107; 11.3851 23 2035/36: 5.0355; 11.3851 24 2036/37: 4.9614; 11.3851 25 2037/38: 4.8884; 11.3851 26 2038/39: 4.8165; 11.3851 27 2039/40: 4.7456; 11.3851 28 2040/41: 4.6758; 11.3851 29 2041/42: 4.6071; 11.3851 30 2042/43: 4.5393; 11.3851 31 2043/44: 4.4725; 11.3851 32 2044/45: 4.4067
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 11.3851 1 2013/14: 0.11536; 11.3851 2 2014/15: 0.11536; 11.3851 3 2015/16: 0.11536; 11.3851 4 2016/17: 0.11536; 11.3851 5 2017/18: 0.11536; 11.3851 6 2018/19: 0.11536; 11.3851 7 2019/20: 0.11536; 11.3851 8 2020/21: 0.11536; 11.3851 9 2021/22: 0.11366; 11.3851 10 2022/23: 0.11199; 11.3851 11 2023/24: 0.11034; 11.3851 12 2024/25: 0.10872; 11.3851 13 2025/26: 0.10712; 11.3851 14 2026/27: 0.10555; 11.3851 15 2027/28: 0.10399; 11.3851 16 2028/29: 0.10246; 11.3851 17 2029/30: 0.10096; 11.3851 18 2030/31: 0.099471; 11.3851 19 2031/32: 0.098008; 11.3851 20 2032/33: 0.096566; 11.3851 21 2033/34: 0.095146; 11.3851 22 2034/35: 0.093746; 11.3851 23 2035/36: 0.092367; 11.3851 24 2036/37: 0.091008; 11.3851 25 2037/38: 0.089669; 11.3851 26 2038/39: 0.08835; 11.3851 27 2039/40: 0.087051; 11.3851 28 2040/41: 0.08577; 11.3851 29 2041/42: 0.084508; 11.3851 30 2042/43: 0.083265; 11.3851 31 2043/44: 0.08204; 11.3851 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 11.3851 1 2013/14: 0.0035579; 11.3851 2 2014/15: 0.0035579; 11.3851 3 2015/16: 0.0035579; 11.3851 4 2016/17: 0.0035579; 11.3851 5 2017/18: 0.0035579; 11.3851 6 2018/19: 0.0035579; 11.3851 7 2019/20: 0.0035579; 11.3851 8 2020/21: 0.0035579; 11.3851 9 2021/22: 0.0035055; 11.3851 10 2022/23: 0.0034539; 11.3851 11 2023/24: 0.0034031; 11.3851 12 2024/25: 0.0033531; 11.3851 13 2025/26: 0.0033037; 11.3851 14 2026/27: 0.0032551; 11.3851 15 2027/28: 0.0032073; 11.3851 16 2028/29: 0.0031601; 11.3851 17 2029/30: 0.0031136; 11.3851 18 2030/31: 0.0030678; 11.3851 19 2031/32: 0.0030227; 11.3851 20 2032/33: 0.0029782; 11.3851 21 2033/34: 0.0029344; 11.3851 22 2034/35: 0.0028912; 11.3851 23 2035/36: 0.0028487; 11.3851 24 2036/37: 0.0028068; 11.3851 25 2037/38: 0.0027655; 11.3851 26 2038/39: 0.0027248; 11.3851 27 2039/40: 0.0026847; 11.3851 28 2040/41: 0.0026452; 11.3851 29 2041/42: 0.0026063; 11.3851 30 2042/43: 0.002568; 11.3851 31 2043/44: 0.0025302; 11.3851 32 2044/45: 0.002493
| Constraint costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.18346; 11.3851 2 2014/15: 0.18346; 11.3851 3 2015/16: 0.18346; 11.3851 4 2016/17: 0.18346; 11.3851 5 2017/18: 0.18346; 11.3851 6 2018/19: 0.18346; 11.3851 7 2019/20: 0.18346; 11.3851 8 2020/21: 0.18346; 11.3851 9 2021/22: 0.18076; 11.3851 10 2022/23: 0.1781; 11.3851 11 2023/24: 0.17548; 11.3851 12 2024/25: 0.1729; 11.3851 13 2025/26: 0.17036; 11.3851 14 2026/27: 0.16785; 11.3851 15 2027/28: 0.16538; 11.3851 16 2028/29: 0.16295; 11.3851 17 2029/30: 0.16055; 11.3851 18 2030/31: 0.15819; 11.3851 19 2031/32: 0.15586; 11.3851 20 2032/33: 0.15357; 11.3851 21 2033/34: 0.15131; 11.3851 22 2034/35: 0.14908; 11.3851 23 2035/36: 0.14689; 11.3851 24 2036/37: 0.14473; 11.3851 25 2037/38: 0.1426; 11.3851 26 2038/39: 0.1405; 11.3851 27 2039/40: 0.13844; 11.3851 28 2040/41: 0.1364; 11.3851 29 2041/42: 0.13439; 11.3851 30 2042/43: 0.13242; 11.3851 31 2043/44: 0.13047; 11.3851 32 2044/45: 0.12855
| VOLL | £m | 09/10 |  | 11.3851 1 2013/14: 0.010469; 11.3851 2 2014/15: 0.010469; 11.3851 3 2015/16: 0.010469; 11.3851 4 2016/17: 0.010469; 11.3851 5 2017/18: 0.010469; 11.3851 6 2018/19: 0.010469; 11.3851 7 2019/20: 0.010469; 11.3851 8 2020/21: 0.010469; 11.3851 9 2021/22: 0.010315; 11.3851 10 2022/23: 0.010163; 11.3851 11 2023/24: 0.010014; 11.3851 12 2024/25: 0.0098662; 11.3851 13 2025/26: 0.0097211; 11.3851 14 2026/27: 0.0095781; 11.3851 15 2027/28: 0.0094372; 11.3851 16 2028/29: 0.0092983; 11.3851 17 2029/30: 0.0091615; 11.3851 18 2030/31: 0.0090268; 11.3851 19 2031/32: 0.008894; 11.3851 20 2032/33: 0.0087631; 11.3851 21 2033/34: 0.0086342; 11.3851 22 2034/35: 0.0085072; 11.3851 23 2035/36: 0.0083821; 11.3851 24 2036/37: 0.0082588; 11.3851 25 2037/38: 0.0081373; 11.3851 26 2038/39: 0.0080176; 11.3851 27 2039/40: 0.0078996; 11.3851 28 2040/41: 0.0077834; 11.3851 29 2041/42: 0.0076689; 11.3851 30 2042/43: 0.0075561; 11.3851 31 2043/44: 0.0074449; 11.3851 32 2044/45: 0.0073354
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 11.3851 1 2013/14: 0.5128; 11.3851 2 2014/15: 0.5128; 11.3851 3 2015/16: 0.5128; 11.3851 4 2016/17: 0.5128; 11.3851 5 2017/18: 0.5128; 11.3851 6 2018/19: 0.5128; 11.3851 7 2019/20: 0.5128; 11.3851 8 2020/21: 0.5128; 11.3851 9 2021/22: 0.50526; 11.3851 10 2022/23: 0.49783; 11.3851 11 2023/24: 0.4905; 11.3851 12 2024/25: 0.48329
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 11.3851 13 2025/26: 0.35713; 11.3851 14 2026/27: 0.35188; 11.3851 15 2027/28: 0.3467; 11.3851 16 2028/29: 0.3416; 11.3851 17 2029/30: 0.33658; 11.3851 18 2030/31: 0.33163; 11.3851 19 2031/32: 0.32675; 11.3851 20 2032/33: 0.32194; 11.3851 21 2033/34: 0.31721; 11.3851 22 2034/35: 0.31254; 11.3851 23 2035/36: 0.30794; 11.3851 24 2036/37: 0.30341; 11.3851 25 2037/38: 0.29895; 11.3851 26 2038/39: 0.29455; 11.3851 27 2039/40: 0.29022; 11.3851 28 2040/41: 0.28595; 11.3851 29 2041/42: 0.28174; 11.3851 30 2042/43: 0.2776; 11.3851 31 2043/44: 0.27351; 11.3851 32 2044/45: 0.26949
| Estuary disruption costs | £m | 09/10 |  | 11.3851 1 2013/14: 0.0021628; 11.3851 2 2014/15: 0.0021628; 11.3851 3 2015/16: 0.0021628; 11.3851 4 2016/17: 0.0021628; 11.3851 5 2017/18: 0.0021628; 11.3851 6 2018/19: 0.0021628; 11.3851 7 2019/20: 0.0021628; 11.3851 8 2020/21: 0.0021628; 11.3851 9 2021/22: 0.002131; 11.3851 10 2022/23: 0.0020997; 11.3851 11 2023/24: 0.0020688; 11.3851 12 2024/25: 0.0020383; 11.3851 13 2025/26: 0.0020084; 11.3851 14 2026/27: 0.0019788; 11.3851 15 2027/28: 0.0019497; 11.3851 16 2028/29: 0.001921; 11.3851 17 2029/30: 0.0018928; 11.3851 18 2030/31: 0.0018649; 11.3851 19 2031/32: 0.0018375; 11.3851 20 2032/33: 0.0018104; 11.3851 21 2033/34: 0.0017838; 11.3851 22 2034/35: 0.0017576; 11.3851 23 2035/36: 0.0017317; 11.3851 24 2036/37: 0.0017062; 11.3851 25 2037/38: 0.0016811; 11.3851 26 2038/39: 0.0016564; 11.3851 27 2039/40: 0.001632; 11.3851 28 2040/41: 0.001608; 11.3851 29 2041/42: 0.0015844; 11.3851 30 2042/43: 0.0015611; 11.3851 31 2043/44: 0.0015381; 11.3851 32 2044/45: 0.0015155
| Shipwreck clear up costs (£m) (09/10 prices) | £m | 09/10 |  | 11.3851 1 2013/14: 0.061322; 11.3851 2 2014/15: 0.061322; 11.3851 3 2015/16: 0.061322; 11.3851 4 2016/17: 0.061322; 11.3851 5 2017/18: 0.061322; 11.3851 6 2018/19: 0.061322; 11.3851 7 2019/20: 0.061322; 11.3851 8 2020/21: 0.061322; 11.3851 9 2021/22: 0.06042; 11.3851 10 2022/23: 0.059531; 11.3851 11 2023/24: 0.058656; 11.3851 12 2024/25: 0.057793; 11.3851 13 2025/26: 0.056943; 11.3851 14 2026/27: 0.056105; 11.3851 15 2027/28: 0.05528; 11.3851 16 2028/29: 0.054466; 11.3851 17 2029/30: 0.053665; 11.3851 18 2030/31: 0.052876; 11.3851 19 2031/32: 0.052098; 11.3851 20 2032/33: 0.051332; 11.3851 21 2033/34: 0.050576; 11.3851 22 2034/35: 0.049832; 11.3851 23 2035/36: 0.049099; 11.3851 24 2036/37: 0.048377; 11.3851 25 2037/38: 0.047665; 11.3851 26 2038/39: 0.046964; 11.3851 27 2039/40: 0.046273; 11.3851 28 2040/41: 0.045593; 11.3851 29 2041/42: 0.044922; 11.3851 30 2042/43: 0.044261; 11.3851 31 2043/44: 0.04361; 11.3851 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 39.4287 | 39.4132 | 39.3979 | 39.3827 | 39.3677 | 39.3527 | 39.3379 | 39.3233 | 38.7577 | 38.2004 | 37.6512 | 37.11 | 32.4723 | 32.0071 | 31.5487 | 31.0969 | 30.6517 | 30.2129 | 29.7806 | 29.3545 | 28.9346 | 28.5207 | 28.1129 | 27.7111 | 27.7604 | 27.3768 | 28.82 | 30.3026 | 30.2431 | 30.7378 | 29.0732 | 28.7864 | 6.1234 | 6.0286 | 5.9338 | 5.839 | 5.7442 | 5.6494 | 5.5546 | 5.4599 | 5.3651 | 5.2703 | 5.1755 | 5.0807 | 4.9859 | 4.8911 | 4.7963 | 4.7015 | 4.6067 | 4.5119 | 4.4171 | 4.3223 | 4.2275 | 4.1327 | 4.0379 | 3.9431 | 3.8484 | 3.7536 | 3.6588 | 3.564
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11366 | 0.11199 | 0.11034 | 0.10872 | 0.10712 | 0.10555 | 0.10399 | 0.10246 | 0.10096 | 0.099471 | 0.098008 | 0.096566 | 0.095146 | 0.093746 | 0.092367 | 0.091008 | 0.089669 | 0.08835 | 0.087051 | 0.08577 | 0.084508 | 0.083265 | 0.08204 | 0.080833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 38.0954 | 36.7927 | 35.5347 | 34.3198 | 33.1465 | 32.0135 | 30.9193 | 29.8625 | 28.4377 | 27.081 | 25.789 | 24.5588 | 20.7629 | 19.7734 | 18.8311 | 17.9338 | 17.0792 | 16.2655 | 15.4905 | 14.7526 | 14.0498 | 13.3805 | 12.7432 | 12.1363 | 11.7467 | 11.1927 | 11.3843 | 11.5651 | 11.1521 | 10.9512 | 11.6289 | 11.1788 | 2.3087 | 2.2067 | 2.1088 | 2.0147 | 1.9242 | 1.8373 | 1.7539 | 1.6738 | 1.5968 | 1.5229 | 1.4519 | 1.3838 | 1.3185 | 1.2557 | 1.1955 | 1.1378 | 1.0823 | 1.0292 | 0.97823 | 0.92936 | 0.8825 | 0.83758 | 0.79453 | 0.75328 | 0.71376 | 0.6759 | 0.63964 | 0.60492
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0.09941 | 0.0965 | 0.093675 | 0.090933 | 0.088272 | 0.085688 | 0.083179 | 0.080745 | 0.078381 | 0.076087 | 0.07386 | 0.071698 | 0.069599 | 0.067562 | 0.065584 | 0.063664 | 0.061801 | 0.059992 | 0.058236 | 0.056531 | 0.054876 | 0.05327 | 0.05514 | 0.053637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 38.209 | 36.9047 | 35.645 | 34.4285 | 33.2536 | 32.119 | 31.0232 | 29.9649 | 28.5371 | 27.1775 | 25.8827 | 24.6497 | 20.8512 | 19.8591 | 18.9143 | 18.0145 | 17.1576 | 16.3416 | 15.5644 | 14.8242 | 14.1194 | 13.4481 | 12.8088 | 12.1999 | 11.8085 | 11.2526 | 11.4425 | 11.6216 | 11.207 | 11.0045 | 11.6841 | 11.2324 | 2.3087 | 2.2067 | 2.1088 | 2.0147 | 1.9242 | 1.8373 | 1.7539 | 1.6738 | 1.5968 | 1.5229 | 1.4519 | 1.3838 | 1.3185 | 1.2557 | 1.1955 | 1.1378 | 1.0823 | 1.0292 | 0.97823 | 0.92936 | 0.8825 | 0.83758 | 0.79453 | 0.75328 | 0.71376 | 0.6759 | 0.63964 | 0.60492
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 38.0954 | 74.888 | 110.4227 | 144.7425 | 177.889 | 209.9025 | 240.8217 | 270.6843 | 299.122 | 326.203 | 351.992 | 376.5508 | 397.3138 | 417.0872 | 435.9183 | 453.852 | 470.9313 | 487.1967 | 502.6873 | 517.4398 | 531.4896 | 544.8701 | 557.6133 | 569.7496 | 581.4963 | 592.6889 | 604.0732 | 615.6383 | 626.7904 | 637.7416 | 649.3705 | 660.5493 | 662.858 | 665.0648 | 667.1736 | 669.1882 | 671.1124 | 672.9498 | 674.7037 | 676.3774 | 677.9742 | 679.4971 | 680.9491 | 682.3329 | 683.6513 | 684.9071 | 686.1026 | 687.2403 | 688.3227 | 689.3519 | 690.3301 | 691.2595 | 692.142 | 692.9796 | 693.7741 | 694.5274 | 695.2411 | 695.917 | 696.5567 | 697.1616
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.963 | 1.0595 | 1.1532 | 1.2441 | 1.3324 | 1.4181 | 1.5012 | 1.582 | 1.6604 | 1.7365 | 1.8103 | 1.882 | 1.9516 | 2.0192 | 2.0848 | 2.1484 | 2.2102 | 2.2702 | 2.3284 | 2.385 | 2.4399 | 2.4931 | 2.5483 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 38.209 | 75.1137 | 110.7587 | 145.1871 | 178.4407 | 210.5597 | 241.5829 | 271.5479 | 300.085 | 327.2625 | 353.1452 | 377.7949 | 398.6461 | 418.5052 | 437.4195 | 455.434 | 472.5916 | 488.9332 | 504.4976 | 519.3218 | 533.4412 | 546.8893 | 559.6981 | 571.898 | 583.7065 | 594.9591 | 606.4016 | 618.0233 | 629.2302 | 640.2347 | 651.9188 | 663.1513 | 665.4599 | 667.6667 | 669.7755 | 671.7901 | 673.7143 | 675.5517 | 677.3056 | 678.9793 | 680.5761 | 682.099 | 683.551 | 684.9348 | 686.2533 | 687.509 | 688.7045 | 689.8422 | 690.9246 | 691.9538 | 692.932 | 693.8614 | 694.7439 | 695.5815 | 696.376 | 697.1293 | 697.843 | 698.5189 | 699.1586 | 699.7635

## CALC¦2
| Item | Unit | Index | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[6 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Costs and expenditure profile Tunnel
| Tunnel construction period | years |  |  | 8
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.059745
| Expenditure profile after Ofgem efficiency challenge | £m | 09/10 |  |  | 0.057598 | 3.0539 | 1.9348 | 19.9162 | 34.155 | 40.4284 | 9.339 | 2.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tunnel revenue profile to be used for modelling | £m | 09/10 |  |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 2.5743 | 2.671 | 2.7546 | 2.8265 | 2.888 | 2.9402 | 2.9842 | 3.0207 | 3.0507 | 3.0748 | 3.0937 | 3.1079 | 3.118 | 3.1244 | 3.1275 | 3.1276 | 3.1251 | 3.1203 | 3.1133 | 3.1046 | 3.0941 | 3.0822 | 3.069 | 3.0546 | 3.0392 | 3.0228 | 3.0056 | 2.9876 | 2.969 | 2.9498 | 2.9301 | 2.9099 | 2.8893 | 2.8684 | 2.847 | 2.8254 | 2.8036 | 2.7815 | 2.7578 | 2.662 | 2.5936 | 2.0941 | 1.2572 | 0.27707 | -0.028007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Costs and expenditure profile Mitigation
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.29951
2.1 | Probablity adjusted cost of losing lease in any year
| Cost of replacing pipeline with a tunnel (after Ofgem efficiency challenge) | £m | 09/10 |  | 111.299
| Cost of loss of lease | £m | 09/10 |  |  | 1 2013/14: 0.72155; 2 2014/15: 0.71458; 3 2015/16: 0.70769; 4 2016/17: 0.70086; 5 2017/18: 0.69409; 6 2018/19: 0.6874; 7 2019/20: 0.68076; 8 2020/21: 0.67419; 9 2021/22: 0.66769; 10 2022/23: 0.66124; 11 2023/24: 0.65486; 12 2024/25: 0.64854; 13 2025/26: 0.64229; 14 2026/27: 0.63609; 15 2027/28: 0.62995; 16 2028/29: 0.62387; 17 2029/30: 0.61785; 18 2030/31: 0.61189; 19 2031/32: 0.60598; 20 2032/33: 0.60014; 21 2033/34: 0.59434; 22 2034/35: 0.58861; 23 2035/36: 0.58293; 24 2036/37: 0.5773; 25 2037/38: 0.57173; 26 2038/39: 0.56621; 27 2039/40: 0.56075; 28 2040/41: 0.55534; 29 2041/42: 0.54998; 30 2042/43: 0.54467; 31 2043/44: 0.53942; 32 2044/45: 0.53421
| Probability that the lease is still in force and current pipeline is operational | % |  |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.53% | 97.08% | 95.65% | 94.24% | 92.86% | 91.49% | 90.15% | 88.82% | 87.51% | 86.23% | 84.96% | 83.71% | 82.48% | 81.26% | 80.07% | 78.89% | 77.73% | 76.59% | 75.46% | 74.35% | 73.26% | 72.18% | 71.12% | 70.07% | 69.04% | 68.02% | 67.02% | 66.04% | 65.07% | 64.11% | 63.17%
2.2 | Cost of mattressing
| Probability adjusted annual cost of mattressing | £m | 09/10 |  | 0.42436
2.3 | Freespan develops despite mattressing (less than 20m section)
| Probability of event | % |  |  | 2%
| Cost of emergency mattressing | £m | 09/10 | see footnote 4 | 0.042436
2.4 | Freespan develops despite mattressing (between 20m and 55m section)
| Probability of event |  |  |  | 0.4%
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.028324
| Constraint costs | £m | 09/10 |  | 1.3253
| Value of lost load (VOLL) | £m | 09/10 |  | 0.134
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 1.2117
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 0.90878
2.5 | Freespan develops despite mattressing (greater than 55m section)
| Probability of event | % |  |  | 0.08%
| Cost of building a tunnel replacement | £m | 09/10 |  |  | 1 2013/14: 0.059817; 2 2014/15: 0.059769; 3 2015/16: 0.059722; 4 2016/17: 0.059674; 5 2017/18: 0.059626; 6 2018/19: 0.059578; 7 2019/20: 0.059531; 8 2020/21: 0.059483; 9 2021/22: 0.059435; 10 2022/23: 0.059388; 11 2023/24: 0.05934; 12 2024/25: 0.059293; 13 2025/26: 0.059246; 14 2026/27: 0.059198; 15 2027/28: 0.059151; 16 2028/29: 0.059103; 17 2029/30: 0.059056; 18 2030/31: 0.059009; 19 2031/32: 0.058962; 20 2032/33: 0.058915; 21 2033/34: 0.058867; 22 2034/35: 0.05882; 23 2035/36: 0.058773; 24 2036/37: 0.058726; 25 2037/38: 0.058679; 26 2038/39: 0.058632; 27 2039/40: 0.058585; 28 2040/41: 0.058539; 29 2041/42: 0.058492; 30 2042/43: 0.058445; 31 2043/44: 0.058398; 32 2044/45: 0.058351
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0056648
| Constraint costs | £m | 09/10 |  | 0.26506
| Value of lost load (VOLL) | £m | 09/10 |  | 0.0268
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 1.2624
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 0.94679
2.6 | Third party interference
| Probability of event | % |  |  | 0.03125%
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 0.11536
| Cost of intervention | £m | 09/10 |  | 0.0031112
| Constraint costs | £m | 09/10 |  | 0.10354
| Value of lost load (VOLL) | £m | 09/10 |  | 0.010469
| Wholesale gas and electricity price impact for 16 months up to 2024 | £m | 09/10 |  | 0.49312
| Wholesale gas and electricity price impact for 16 months beyond 2024 | £m | 09/10 |  | 0.36984
| Disruption costs | £m | 09/10 |  | 0.0021628
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322
3 | Detailed Working: Constraint costs
3.1 | Constraint costs
| Total constraint costs following isolation/rupture | £m | 16/17 | See footnote 6 | 406.9205
4 | Detailed Workings: Wholesale Gas and Electricity Price Impacts
4.1 | Energy consumption
| Monthy domestic gas consumption | therm |  |  | 846311149.033
| Monthly domestic electricity consumption | therm |  |  | 240695461.8885
4.2 | To 2024
| First month average | £m | 16/17 |  | 131.1198
| Monthly average (excluding first month) | £m | 16/17 |  | 120.4576
4.3 | From 2024 to 2072
| First month average | £m | 16/17 |  | 98.3398
| Monthly average (excluding first month) | £m | 16/17 |  | 90.3432
4.4 | Damage intervention
4.4.1 | Localised mechanical/impact damage leading to repair clamp
| Probability | % |  |  | 0.7
| Expected duration | weeks |  |  | 33.6
| Expected cost | £m | 09/10 |  | 1.4876
4.4.2 | Localised failure leading to short replacement spool
| Probability | % |  |  | 0.175
| Expected duration | weeks |  |  | 12.075
| Expected cost | £m | 09/10 |  | 1.7954
4.4.3 | Extensive failure over pipeline span /rupture leading to long replacement spool
| Probability | % |  |  | 0.075
| Expected duration | weeks |  |  | 5.625
| Expected cost | £m | 09/10 |  | 1.1078
4.4.4 | Tunnel replacement
| Probability | % |  |  | 0.05
| Expected duration | weeks |  |  | 15.6
| Expected cost | £m | 09/10 |  | 5.5649
4.4.4 | Average cost of intervention | £m | 09/10 |  | 9.9557
| Item | Unit | Index | Notes | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[5 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Option: Tunnel 2012
| Revenue impact of construction cost | £m | 09/10 |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 2.5743 | 2.671 | 2.7546 | 2.8265 | 2.888 | 2.9402 | 2.9842 | 3.0207 | 3.0507 | 3.0748 | 3.0937 | 3.1079 | 3.118 | 3.1244 | 3.1275 | 3.1276 | 3.1251 | 3.1203 | 3.1133 | 3.1046 | 3.0941 | 3.0822 | 3.069 | 3.0546 | 3.0392 | 3.0228 | 3.0056 | 2.9876 | 2.969 | 2.9498 | 2.9301 | 2.9099 | 2.8893 | 2.8684 | 2.847 | 2.8254 | 2.8036 | 2.7815 | 2.7578 | 2.662 | 2.5936 | 2.0941 | 1.2572 | 0.27707 | -0.028007 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational costs | £m | 09/10 |  | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Mattressing cost | £m | 09/10 |  | 0.42436 | 0.42436 | 0.42436 | 0.42436 | 0.42436 | 0.42436 | 0.42436 | 0.42436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 0.042436 | 0.042436 | 0.042436 | 0.042436 | 0.042436 | 0.042436 | 0.042436 | 0.042436 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.028324 | 0.028324 | 0.028324 | 0.028324 | 0.028324 | 0.028324 | 0.028324 | 0.028324 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 1.3253 | 1.3253 | 1.3253 | 1.3253 | 1.3253 | 1.3253 | 1.3253 | 1.3253 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0.134 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 1.2117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (>55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0056648 | 0.0056648 | 0.0056648 | 0.0056648 | 0.0056648 | 0.0056648 | 0.0056648 | 0.0056648 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.26506 | 0.26506 | 0.26506 | 0.26506 | 0.26506 | 0.26506 | 0.26506 | 0.26506 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.0268 | 0.0268 | 0.0268 | 0.0268 | 0.0268 | 0.0268 | 0.0268 | 0.0268 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 1.2624 | 1.2624 | 1.2624 | 1.2624 | 1.2624 | 1.2624 | 1.2624 | 1.2624 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
Third party impact
| Probability adjusted cost associated with possible loss of life |  |  |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost of intervention |  |  |  | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.10354 | 0.10354 | 0.10354 | 0.10354 | 0.10354 | 0.10354 | 0.10354 | 0.10354 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.49312 | 0.49312 | 0.49312 | 0.49312 | 0.49312 | 0.49312 | 0.49312 | 0.49312 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
| Estuary disruption costs | £m | 09/10 |  | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total tunnel construction and operation cost | £m | 09/10 |  | 0.30513 | 0.60592 | 0.63712 | 2.5173 | 4.861 | 6.923 | 5.2881 | 5.0303 | 2.634 | 2.7307 | 2.8143 | 2.8863 | 2.9478 | 3 | 3.0439 | 3.0805 | 3.1105 | 3.1346 | 3.1535 | 3.1677 | 3.1778 | 3.1841 | 3.1872 | 3.1873 | 3.1848 | 3.18 | 3.1731 | 3.1643 | 3.1539 | 3.142 | 3.1287 | 3.1144 | 3.0989 | 3.0825 | 3.0653 | 3.0474 | 3.0288 | 3.0096 | 2.9899 | 2.9697 | 2.9491 | 2.9281 | 2.9068 | 2.8852 | 2.8633 | 2.8412 | 2.8175 | 2.7218 | 2.6534 | 2.1539 | 1.317 | 0.33682 | 0.031738 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Total costs (excluding loss of life) | £m | 09/10 |  | 5.7049 | 6.0057 | 6.0369 | 7.9171 | 10.2607 | 12.3228 | 10.6879 | 10.4301 | 2.634 | 2.7307 | 2.8143 | 2.8863 | 2.9478 | 3 | 3.0439 | 3.0805 | 3.1105 | 3.1346 | 3.1535 | 3.1677 | 3.1778 | 3.1841 | 3.1872 | 3.1873 | 3.1848 | 3.18 | 3.1731 | 3.1643 | 3.1539 | 3.142 | 3.1287 | 3.1144 | 3.0989 | 3.0825 | 3.0653 | 3.0474 | 3.0288 | 3.0096 | 2.9899 | 2.9697 | 2.9491 | 2.9281 | 2.9068 | 2.8852 | 2.8633 | 2.8412 | 2.8175 | 2.7218 | 2.6534 | 2.1539 | 1.317 | 0.33682 | 0.031738 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted total tunnel construction and operation cost | £m | 09/10 |  | 0.29481 | 0.56564 | 0.57464 | 2.1937 | 4.0928 | 5.6319 | 4.1564 | 3.8201 | 1.9327 | 1.9359 | 1.9277 | 1.9101 | 1.8848 | 1.8533 | 1.8169 | 1.7765 | 1.7332 | 1.6875 | 1.6403 | 1.592 | 1.543 | 1.4938 | 1.4447 | 1.3959 | 1.3477 | 1.3001 | 1.2534 | 1.2077 | 1.163 | 1.1194 | 1.2515 | 1.2094 | 1.1684 | 1.1283 | 1.0894 | 1.0514 | 1.0146 | 0.9788 | 0.94406 | 0.91037 | 0.87773 | 0.8461 | 0.81548 | 0.78584 | 0.75717 | 0.72945 | 0.70229 | 0.65867 | 0.62341 | 0.49132 | 0.29166 | 0.07242 | 0.0066252 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 5.512 | 5.6064 | 5.4449 | 6.8993 | 8.6393 | 10.0246 | 8.4006 | 7.9207 | 1.9327 | 1.9359 | 1.9277 | 1.9101 | 1.8848 | 1.8533 | 1.8169 | 1.7765 | 1.7332 | 1.6875 | 1.6403 | 1.592 | 1.543 | 1.4938 | 1.4447 | 1.3959 | 1.3477 | 1.3001 | 1.2534 | 1.2077 | 1.163 | 1.1194 | 1.2515 | 1.2094 | 1.1684 | 1.1283 | 1.0894 | 1.0514 | 1.0146 | 0.9788 | 0.94406 | 0.91037 | 0.87773 | 0.8461 | 0.81548 | 0.78584 | 0.75717 | 0.72945 | 0.70229 | 0.65867 | 0.62341 | 0.49132 | 0.29166 | 0.07242 | 0.0066252 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 5.6257 | 5.7184 | 5.5553 | 7.008 | 8.7463 | 10.1301 | 8.5045 | 8.0231 | 1.9327 | 1.9359 | 1.9277 | 1.9101 | 1.8848 | 1.8533 | 1.8169 | 1.7765 | 1.7332 | 1.6875 | 1.6403 | 1.592 | 1.543 | 1.4938 | 1.4447 | 1.3959 | 1.3477 | 1.3001 | 1.2534 | 1.2077 | 1.163 | 1.1194 | 1.2515 | 1.2094 | 1.1684 | 1.1283 | 1.0894 | 1.0514 | 1.0146 | 0.9788 | 0.94406 | 0.91037 | 0.87773 | 0.8461 | 0.81548 | 0.78584 | 0.75717 | 0.72945 | 0.70229 | 0.65867 | 0.62341 | 0.49132 | 0.29166 | 0.07242 | 0.0066252 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Cumulative discounted tunnel construction and operation cost | £m | 09/10 |  | 0.29481 | 0.86045 | 1.4351 | 3.6288 | 7.7216 | 13.3534 | 17.5098 | 21.3299 | 23.2626 | 25.1984 | 27.1261 | 29.0362 | 30.921 | 32.7743 | 34.5912 | 36.3678 | 38.1009 | 39.7885 | 41.4287 | 43.0207 | 44.5637 | 46.0576 | 47.5023 | 48.8982 | 50.2459 | 51.546 | 52.7994 | 54.007 | 55.17 | 56.2895 | 57.5409 | 58.7503 | 59.9187 | 61.0471 | 62.1364 | 63.1879 | 64.2025 | 65.1813 | 66.1253 | 67.0357 | 67.9134 | 68.7595 | 69.575 | 70.3608 | 71.118 | 71.8475 | 72.5497 | 73.2084 | 73.8318 | 74.3231 | 74.6148 | 74.6872 | 74.6938 | 74.706 | 74.7177 | 74.7291 | 74.7402 | 74.751 | 74.7614 | 74.7716
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 5.512 | 11.1184 | 16.5633 | 23.4626 | 32.1018 | 42.1264 | 50.527 | 58.4478 | 60.3804 | 62.3163 | 64.244 | 66.1541 | 68.0389 | 69.8922 | 71.7091 | 73.4856 | 75.2188 | 76.9063 | 78.5466 | 80.1386 | 81.6816 | 83.1754 | 84.6202 | 86.0161 | 87.3637 | 88.6638 | 89.9172 | 91.1249 | 92.2879 | 93.4073 | 94.6588 | 95.8682 | 97.0366 | 98.1649 | 99.2543 | 100.3057 | 101.3203 | 102.2991 | 103.2432 | 104.1535 | 105.0313 | 105.8774 | 106.6928 | 107.4787 | 108.2359 | 108.9653 | 109.6676 | 110.3263 | 110.9497 | 111.441 | 111.7327 | 111.8051 | 111.8117 | 111.8238 | 111.8356 | 111.847 | 111.8581 | 111.8688 | 111.8793 | 111.8894
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359
| Cumulative total discounted cost | £m | 09/10 |  | 5.6257 | 11.344 | 16.8993 | 23.9072 | 32.6536 | 42.7837 | 51.2882 | 59.3114 | 61.244 | 63.1799 | 65.1076 | 67.0176 | 68.9025 | 70.7558 | 72.5727 | 74.3492 | 76.0824 | 77.7699 | 79.4102 | 81.0022 | 82.5452 | 84.039 | 85.4837 | 86.8797 | 88.2273 | 89.5274 | 90.7808 | 91.9885 | 93.1515 | 94.2709 | 95.5224 | 96.7318 | 97.9001 | 99.0285 | 100.1179 | 101.1693 | 102.1839 | 103.1627 | 104.1068 | 105.0171 | 105.8949 | 106.741 | 107.5564 | 108.3423 | 109.0995 | 109.8289 | 110.5312 | 111.1899 | 111.8133 | 112.3046 | 112.5962 | 112.6687 | 112.6753 | 112.6874 | 112.6992 | 112.7106 | 112.7216 | 112.7324 | 112.7429 | 112.753
2 | Option: Mitigate 2044
| Operational costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.29951; 9.9557 2 2014/15: 0.29951; 9.9557 3 2015/16: 0.29951; 9.9557 4 2016/17: 0.29951; 9.9557 5 2017/18: 0.29951; 9.9557 6 2018/19: 0.29951; 9.9557 7 2019/20: 0.29951; 9.9557 8 2020/21: 0.29951; 9.9557 9 2021/22: 0.29598; 9.9557 10 2022/23: 0.29251; 9.9557 11 2023/24: 0.28908; 9.9557 12 2024/25: 0.28571; 9.9557 13 2025/26: 0.28239; 9.9557 14 2026/27: 0.27911; 9.9557 15 2027/28: 0.27588; 9.9557 16 2028/29: 0.2727; 9.9557 17 2029/30: 0.26957; 9.9557 18 2030/31: 0.26648; 9.9557 19 2031/32: 0.26344; 9.9557 20 2032/33: 0.26045; 9.9557 21 2033/34: 0.25749; 9.9557 22 2034/35: 0.25458; 9.9557 23 2035/36: 0.25172; 9.9557 24 2036/37: 0.24889; 9.9557 25 2037/38: 0.24611; 9.9557 26 2038/39: 0.24337; 9.9557 27 2039/40: 0.24067; 9.9557 28 2040/41: 0.23801; 9.9557 29 2041/42: 0.23539; 9.9557 30 2042/43: 0.2328; 9.9557 31 2043/44: 0.23026; 9.9557 32 2044/45: 0.22775
| Loss of lease | £m | 09/10 |  | 9.9557 1 2013/14: 0.72155; 9.9557 2 2014/15: 0.71458; 9.9557 3 2015/16: 0.70769; 9.9557 4 2016/17: 0.70086; 9.9557 5 2017/18: 0.69409; 9.9557 6 2018/19: 0.6874; 9.9557 7 2019/20: 0.68076; 9.9557 8 2020/21: 0.67419; 9.9557 9 2021/22: 0.66769; 9.9557 10 2022/23: 0.66124; 9.9557 11 2023/24: 0.65486; 9.9557 12 2024/25: 0.64854; 9.9557 13 2025/26: 0.64229; 9.9557 14 2026/27: 0.63609; 9.9557 15 2027/28: 0.62995; 9.9557 16 2028/29: 0.62387; 9.9557 17 2029/30: 0.61785; 9.9557 18 2030/31: 0.61189; 9.9557 19 2031/32: 0.60598; 9.9557 20 2032/33: 0.60014; 9.9557 21 2033/34: 0.59434; 9.9557 22 2034/35: 0.58861; 9.9557 23 2035/36: 0.58293; 9.9557 24 2036/37: 0.5773; 9.9557 25 2037/38: 0.57173; 9.9557 26 2038/39: 0.56621; 9.9557 27 2039/40: 0.56075; 9.9557 28 2040/41: 0.55534; 9.9557 29 2041/42: 0.54998; 9.9557 30 2042/43: 0.54467; 9.9557 31 2043/44: 0.53942; 9.9557 32 2044/45: 0.53421
| Mattressing cost | £m | 09/10 |  | 9.9557 1 2013/14: 0.42436; 9.9557 2 2014/15: 0.42436; 9.9557 3 2015/16: 0.42436; 9.9557 4 2016/17: 0.42436; 9.9557 5 2017/18: 0.42436; 9.9557 6 2018/19: 0.42436; 9.9557 7 2019/20: 0.42436; 9.9557 8 2020/21: 0.42436; 9.9557 9 2021/22: 0.41812; 9.9557 10 2022/23: 0.41197; 9.9557 11 2023/24: 0.40591; 9.9557 12 2024/25: 0.39994; 9.9557 13 2025/26: 0.39405; 9.9557 14 2026/27: 0.38826; 9.9557 15 2027/28: 0.38254; 9.9557 16 2028/29: 0.37692; 9.9557 17 2029/30: 0.37137; 9.9557 18 2030/31: 0.36591; 9.9557 19 2031/32: 0.36053; 9.9557 20 2032/33: 0.35522; 9.9557 21 2033/34: 0.35; 9.9557 22 2034/35: 0.34485; 9.9557 23 2035/36: 0.33977; 9.9557 24 2036/37: 0.33478; 9.9557 25 2037/38: 0.32985; 9.9557 26 2038/39: 0.325; 9.9557 27 2039/40: 0.32022; 9.9557 28 2040/41: 0.31551; 9.9557 29 2041/42: 0.31087; 9.9557 30 2042/43: 0.30629; 9.9557 31 2043/44: 0.30179; 9.9557 32 2044/45: 0.29735
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 9.9557 1 2013/14: 0.042436; 9.9557 2 2014/15: 0.042436; 9.9557 3 2015/16: 0.042436; 9.9557 4 2016/17: 0.042436; 9.9557 5 2017/18: 0.042436; 9.9557 6 2018/19: 0.042436; 9.9557 7 2019/20: 0.042436; 9.9557 8 2020/21: 0.042436; 9.9557 9 2021/22: 0.041812; 9.9557 10 2022/23: 0.041197; 9.9557 11 2023/24: 0.040591; 9.9557 12 2024/25: 0.039994; 9.9557 13 2025/26: 0.039405; 9.9557 14 2026/27: 0.038826; 9.9557 15 2027/28: 0.038254; 9.9557 16 2028/29: 0.037692; 9.9557 17 2029/30: 0.037137; 9.9557 18 2030/31: 0.036591; 9.9557 19 2031/32: 0.036053; 9.9557 20 2032/33: 0.035522; 9.9557 21 2033/34: 0.035; 9.9557 22 2034/35: 0.034485; 9.9557 23 2035/36: 0.033977; 9.9557 24 2036/37: 0.033478; 9.9557 25 2037/38: 0.032985; 9.9557 26 2038/39: 0.0325; 9.9557 27 2039/40: 0.032022; 9.9557 28 2040/41: 0.031551; 9.9557 29 2041/42: 0.031087; 9.9557 30 2042/43: 0.030629; 9.9557 31 2043/44: 0.030179; 9.9557 32 2044/45: 0.029735
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.028324; 9.9557 2 2014/15: 0.028324; 9.9557 3 2015/16: 0.028324; 9.9557 4 2016/17: 0.028324; 9.9557 5 2017/18: 0.028324; 9.9557 6 2018/19: 0.028324; 9.9557 7 2019/20: 0.028324; 9.9557 8 2020/21: 0.028324; 9.9557 9 2021/22: 0.027907; 9.9557 10 2022/23: 0.027497; 9.9557 11 2023/24: 0.027092; 9.9557 12 2024/25: 0.026694; 9.9557 13 2025/26: 0.026301; 9.9557 14 2026/27: 0.025914; 9.9557 15 2027/28: 0.025533; 9.9557 16 2028/29: 0.025157; 9.9557 17 2029/30: 0.024787; 9.9557 18 2030/31: 0.024423; 9.9557 19 2031/32: 0.024063; 9.9557 20 2032/33: 0.023709; 9.9557 21 2033/34: 0.023361; 9.9557 22 2034/35: 0.023017; 9.9557 23 2035/36: 0.022678; 9.9557 24 2036/37: 0.022345; 9.9557 25 2037/38: 0.022016; 9.9557 26 2038/39: 0.021692; 9.9557 27 2039/40: 0.021373; 9.9557 28 2040/41: 0.021059; 9.9557 29 2041/42: 0.020749; 9.9557 30 2042/43: 0.020444; 9.9557 31 2043/44: 0.020143; 9.9557 32 2044/45: 0.019847
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 1.3253; 9.9557 2 2014/15: 1.3253; 9.9557 3 2015/16: 1.3253; 9.9557 4 2016/17: 1.3253; 9.9557 5 2017/18: 1.3253; 9.9557 6 2018/19: 1.3253; 9.9557 7 2019/20: 1.3253; 9.9557 8 2020/21: 1.3253; 9.9557 9 2021/22: 1.3058; 9.9557 10 2022/23: 1.2866; 9.9557 11 2023/24: 1.2677; 9.9557 12 2024/25: 1.249; 9.9557 13 2025/26: 1.2307; 9.9557 14 2026/27: 1.2126; 9.9557 15 2027/28: 1.1947; 9.9557 16 2028/29: 1.1771; 9.9557 17 2029/30: 1.1598; 9.9557 18 2030/31: 1.1428; 9.9557 19 2031/32: 1.126; 9.9557 20 2032/33: 1.1094; 9.9557 21 2033/34: 1.0931; 9.9557 22 2034/35: 1.077; 9.9557 23 2035/36: 1.0612; 9.9557 24 2036/37: 1.0455; 9.9557 25 2037/38: 1.0302; 9.9557 26 2038/39: 1.015; 9.9557 27 2039/40: 1.0001; 9.9557 28 2040/41: 0.98536; 9.9557 29 2041/42: 0.97087; 9.9557 30 2042/43: 0.95659; 9.9557 31 2043/44: 0.94251; 9.9557 32 2044/45: 0.92865
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.134; 9.9557 2 2014/15: 0.134; 9.9557 3 2015/16: 0.134; 9.9557 4 2016/17: 0.134; 9.9557 5 2017/18: 0.134; 9.9557 6 2018/19: 0.134; 9.9557 7 2019/20: 0.134; 9.9557 8 2020/21: 0.134; 9.9557 9 2021/22: 0.13203; 9.9557 10 2022/23: 0.13009; 9.9557 11 2023/24: 0.12817; 9.9557 12 2024/25: 0.12629; 9.9557 13 2025/26: 0.12443; 9.9557 14 2026/27: 0.1226; 9.9557 15 2027/28: 0.1208; 9.9557 16 2028/29: 0.11902; 9.9557 17 2029/30: 0.11727; 9.9557 18 2030/31: 0.11554; 9.9557 19 2031/32: 0.11384; 9.9557 20 2032/33: 0.11217; 9.9557 21 2033/34: 0.11052; 9.9557 22 2034/35: 0.10889; 9.9557 23 2035/36: 0.10729; 9.9557 24 2036/37: 0.10571; 9.9557 25 2037/38: 0.10416; 9.9557 26 2038/39: 0.10262; 9.9557 27 2039/40: 0.10112; 9.9557 28 2040/41: 0.099628; 9.9557 29 2041/42: 0.098162; 9.9557 30 2042/43: 0.096718; 9.9557 31 2043/44: 0.095295; 9.9557 32 2044/45: 0.093893
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 1.2117; 9.9557 2 2014/15: 1.2117; 9.9557 3 2015/16: 1.2117; 9.9557 4 2016/17: 1.2117; 9.9557 5 2017/18: 1.2117; 9.9557 6 2018/19: 1.2117; 9.9557 7 2019/20: 1.2117; 9.9557 8 2020/21: 1.2117; 9.9557 9 2021/22: 1.1939; 9.9557 10 2022/23: 1.1763; 9.9557 11 2023/24: 1.159; 9.9557 12 2024/25: 1.142
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.84387; 9.9557 14 2026/27: 0.83146; 9.9557 15 2027/28: 0.81922; 9.9557 16 2028/29: 0.80717; 9.9557 17 2029/30: 0.7953; 9.9557 18 2030/31: 0.7836; 9.9557 19 2031/32: 0.77207; 9.9557 20 2032/33: 0.76071; 9.9557 21 2033/34: 0.74952; 9.9557 22 2034/35: 0.7385; 9.9557 23 2035/36: 0.72763; 9.9557 24 2036/37: 0.71693; 9.9557 25 2037/38: 0.70638; 9.9557 26 2038/39: 0.69599; 9.9557 27 2039/40: 0.68575; 9.9557 28 2040/41: 0.67567; 9.9557 29 2041/42: 0.66573; 9.9557 30 2042/43: 0.65593; 9.9557 31 2043/44: 0.64628; 9.9557 32 2044/45: 0.63678
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 9.9557 1 2013/14: 0.059817; 9.9557 2 2014/15: 0.059769; 9.9557 3 2015/16: 0.059722; 9.9557 4 2016/17: 0.059674; 9.9557 5 2017/18: 0.059626; 9.9557 6 2018/19: 0.059578; 9.9557 7 2019/20: 0.059531; 9.9557 8 2020/21: 0.059483; 9.9557 9 2021/22: 0.059435; 9.9557 10 2022/23: 0.059388; 9.9557 11 2023/24: 0.05934; 9.9557 12 2024/25: 0.059293; 9.9557 13 2025/26: 0.059246; 9.9557 14 2026/27: 0.059198; 9.9557 15 2027/28: 0.059151; 9.9557 16 2028/29: 0.059103; 9.9557 17 2029/30: 0.059056; 9.9557 18 2030/31: 0.059009; 9.9557 19 2031/32: 0.058962; 9.9557 20 2032/33: 0.058915; 9.9557 21 2033/34: 0.058867; 9.9557 22 2034/35: 0.05882; 9.9557 23 2035/36: 0.058773; 9.9557 24 2036/37: 0.058726; 9.9557 25 2037/38: 0.058679; 9.9557 26 2038/39: 0.058632; 9.9557 27 2039/40: 0.058585; 9.9557 28 2040/41: 0.058539; 9.9557 29 2041/42: 0.058492; 9.9557 30 2042/43: 0.058445; 9.9557 31 2043/44: 0.058398; 9.9557 32 2044/45: 0.058351
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0056648; 9.9557 2 2014/15: 0.0056648; 9.9557 3 2015/16: 0.0056648; 9.9557 4 2016/17: 0.0056648; 9.9557 5 2017/18: 0.0056648; 9.9557 6 2018/19: 0.0056648; 9.9557 7 2019/20: 0.0056648; 9.9557 8 2020/21: 0.0056648; 9.9557 9 2021/22: 0.0055815; 9.9557 10 2022/23: 0.0054994; 9.9557 11 2023/24: 0.0054185; 9.9557 12 2024/25: 0.0053388; 9.9557 13 2025/26: 0.0052602; 9.9557 14 2026/27: 0.0051828; 9.9557 15 2027/28: 0.0051066; 9.9557 16 2028/29: 0.0050315; 9.9557 17 2029/30: 0.0049575; 9.9557 18 2030/31: 0.0048845; 9.9557 19 2031/32: 0.0048127; 9.9557 20 2032/33: 0.0047419; 9.9557 21 2033/34: 0.0046721; 9.9557 22 2034/35: 0.0046034; 9.9557 23 2035/36: 0.0045357; 9.9557 24 2036/37: 0.0044689; 9.9557 25 2037/38: 0.0044032; 9.9557 26 2038/39: 0.0043384; 9.9557 27 2039/40: 0.0042746; 9.9557 28 2040/41: 0.0042117; 9.9557 29 2041/42: 0.0041498; 9.9557 30 2042/43: 0.0040887; 9.9557 31 2043/44: 0.0040286; 9.9557 32 2044/45: 0.0039693
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.26506; 9.9557 2 2014/15: 0.26506; 9.9557 3 2015/16: 0.26506; 9.9557 4 2016/17: 0.26506; 9.9557 5 2017/18: 0.26506; 9.9557 6 2018/19: 0.26506; 9.9557 7 2019/20: 0.26506; 9.9557 8 2020/21: 0.26506; 9.9557 9 2021/22: 0.26117; 9.9557 10 2022/23: 0.25732; 9.9557 11 2023/24: 0.25354; 9.9557 12 2024/25: 0.24981; 9.9557 13 2025/26: 0.24613; 9.9557 14 2026/27: 0.24251; 9.9557 15 2027/28: 0.23894; 9.9557 16 2028/29: 0.23543; 9.9557 17 2029/30: 0.23197; 9.9557 18 2030/31: 0.22855; 9.9557 19 2031/32: 0.22519; 9.9557 20 2032/33: 0.22188; 9.9557 21 2033/34: 0.21862; 9.9557 22 2034/35: 0.2154; 9.9557 23 2035/36: 0.21223; 9.9557 24 2036/37: 0.20911; 9.9557 25 2037/38: 0.20603; 9.9557 26 2038/39: 0.203; 9.9557 27 2039/40: 0.20002; 9.9557 28 2040/41: 0.19707; 9.9557 29 2041/42: 0.19417; 9.9557 30 2042/43: 0.19132; 9.9557 31 2043/44: 0.1885; 9.9557 32 2044/45: 0.18573
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.0268; 9.9557 2 2014/15: 0.0268; 9.9557 3 2015/16: 0.0268; 9.9557 4 2016/17: 0.0268; 9.9557 5 2017/18: 0.0268; 9.9557 6 2018/19: 0.0268; 9.9557 7 2019/20: 0.0268; 9.9557 8 2020/21: 0.0268; 9.9557 9 2021/22: 0.026406; 9.9557 10 2022/23: 0.026017; 9.9557 11 2023/24: 0.025635; 9.9557 12 2024/25: 0.025257; 9.9557 13 2025/26: 0.024886; 9.9557 14 2026/27: 0.02452; 9.9557 15 2027/28: 0.024159; 9.9557 16 2028/29: 0.023804; 9.9557 17 2029/30: 0.023454; 9.9557 18 2030/31: 0.023109; 9.9557 19 2031/32: 0.022769; 9.9557 20 2032/33: 0.022434; 9.9557 21 2033/34: 0.022104; 9.9557 22 2034/35: 0.021778; 9.9557 23 2035/36: 0.021458; 9.9557 24 2036/37: 0.021142; 9.9557 25 2037/38: 0.020831; 9.9557 26 2038/39: 0.020525; 9.9557 27 2039/40: 0.020223; 9.9557 28 2040/41: 0.019926; 9.9557 29 2041/42: 0.019632; 9.9557 30 2042/43: 0.019344; 9.9557 31 2043/44: 0.019059; 9.9557 32 2044/45: 0.018779
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 1.2624; 9.9557 2 2014/15: 1.2624; 9.9557 3 2015/16: 1.2624; 9.9557 4 2016/17: 1.2624; 9.9557 5 2017/18: 1.2624; 9.9557 6 2018/19: 1.2624; 9.9557 7 2019/20: 1.2624; 9.9557 8 2020/21: 1.2624; 9.9557 9 2021/22: 1.2438; 9.9557 10 2022/23: 1.2255; 9.9557 11 2023/24: 1.2075; 9.9557 12 2024/25: 1.1897
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.87917; 9.9557 14 2026/27: 0.86623; 9.9557 15 2027/28: 0.85349; 9.9557 16 2028/29: 0.84094; 9.9557 17 2029/30: 0.82857; 9.9557 18 2030/31: 0.81638; 9.9557 19 2031/32: 0.80437; 9.9557 20 2032/33: 0.79253; 9.9557 21 2033/34: 0.78088; 9.9557 22 2034/35: 0.76939; 9.9557 23 2035/36: 0.75807; 9.9557 24 2036/37: 0.74692; 9.9557 25 2037/38: 0.73593; 9.9557 26 2038/39: 0.7251; 9.9557 27 2039/40: 0.71444; 9.9557 28 2040/41: 0.70393; 9.9557 29 2041/42: 0.69357; 9.9557 30 2042/43: 0.68337; 9.9557 31 2043/44: 0.67332; 9.9557 32 2044/45: 0.66341
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 9.9557 1 2013/14: 0.0031112; 9.9557 2 2014/15: 0.0031112; 9.9557 3 2015/16: 0.0031112; 9.9557 4 2016/17: 0.0031112; 9.9557 5 2017/18: 0.0031112; 9.9557 6 2018/19: 0.0031112; 9.9557 7 2019/20: 0.0031112; 9.9557 8 2020/21: 0.0031112; 9.9557 9 2021/22: 0.0030654; 9.9557 10 2022/23: 0.0030203; 9.9557 11 2023/24: 0.0029759; 9.9557 12 2024/25: 0.0029321; 9.9557 13 2025/26: 0.002889; 9.9557 14 2026/27: 0.0028465; 9.9557 15 2027/28: 0.0028046; 9.9557 16 2028/29: 0.0027633; 9.9557 17 2029/30: 0.0027227; 9.9557 18 2030/31: 0.0026826; 9.9557 19 2031/32: 0.0026432; 9.9557 20 2032/33: 0.0026043; 9.9557 21 2033/34: 0.002566; 9.9557 22 2034/35: 0.0025282; 9.9557 23 2035/36: 0.002491; 9.9557 24 2036/37: 0.0024544; 9.9557 25 2037/38: 0.0024183; 9.9557 26 2038/39: 0.0023827; 9.9557 27 2039/40: 0.0023477; 9.9557 28 2040/41: 0.0023131; 9.9557 29 2041/42: 0.0022791; 9.9557 30 2042/43: 0.0022456; 9.9557 31 2043/44: 0.0022125; 9.9557 32 2044/45: 0.00218
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.10354; 9.9557 2 2014/15: 0.10354; 9.9557 3 2015/16: 0.10354; 9.9557 4 2016/17: 0.10354; 9.9557 5 2017/18: 0.10354; 9.9557 6 2018/19: 0.10354; 9.9557 7 2019/20: 0.10354; 9.9557 8 2020/21: 0.10354; 9.9557 9 2021/22: 0.10202; 9.9557 10 2022/23: 0.10052; 9.9557 11 2023/24: 0.099038; 9.9557 12 2024/25: 0.097581; 9.9557 13 2025/26: 0.096146; 9.9557 14 2026/27: 0.094731; 9.9557 15 2027/28: 0.093338; 9.9557 16 2028/29: 0.091965; 9.9557 17 2029/30: 0.090612; 9.9557 18 2030/31: 0.089279; 9.9557 19 2031/32: 0.087966; 9.9557 20 2032/33: 0.086672; 9.9557 21 2033/34: 0.085397; 9.9557 22 2034/35: 0.08414; 9.9557 23 2035/36: 0.082903; 9.9557 24 2036/37: 0.081683; 9.9557 25 2037/38: 0.080481; 9.9557 26 2038/39: 0.079297; 9.9557 27 2039/40: 0.078131; 9.9557 28 2040/41: 0.076982; 9.9557 29 2041/42: 0.075849; 9.9557 30 2042/43: 0.074733; 9.9557 31 2043/44: 0.073634; 9.9557 32 2044/45: 0.072551
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.010469; 9.9557 2 2014/15: 0.010469; 9.9557 3 2015/16: 0.010469; 9.9557 4 2016/17: 0.010469; 9.9557 5 2017/18: 0.010469; 9.9557 6 2018/19: 0.010469; 9.9557 7 2019/20: 0.010469; 9.9557 8 2020/21: 0.010469; 9.9557 9 2021/22: 0.010315; 9.9557 10 2022/23: 0.010163; 9.9557 11 2023/24: 0.010014; 9.9557 12 2024/25: 0.0098662; 9.9557 13 2025/26: 0.0097211; 9.9557 14 2026/27: 0.0095781; 9.9557 15 2027/28: 0.0094372; 9.9557 16 2028/29: 0.0092983; 9.9557 17 2029/30: 0.0091615; 9.9557 18 2030/31: 0.0090268; 9.9557 19 2031/32: 0.008894; 9.9557 20 2032/33: 0.0087631; 9.9557 21 2033/34: 0.0086342; 9.9557 22 2034/35: 0.0085072; 9.9557 23 2035/36: 0.0083821; 9.9557 24 2036/37: 0.0082588; 9.9557 25 2037/38: 0.0081373; 9.9557 26 2038/39: 0.0080176; 9.9557 27 2039/40: 0.0078996; 9.9557 28 2040/41: 0.0077834; 9.9557 29 2041/42: 0.0076689; 9.9557 30 2042/43: 0.0075561; 9.9557 31 2043/44: 0.0074449; 9.9557 32 2044/45: 0.0073354
|  | £m | 09/10
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.49312; 9.9557 2 2014/15: 0.49312; 9.9557 3 2015/16: 0.49312; 9.9557 4 2016/17: 0.49312; 9.9557 5 2017/18: 0.49312; 9.9557 6 2018/19: 0.49312; 9.9557 7 2019/20: 0.49312; 9.9557 8 2020/21: 0.49312; 9.9557 9 2021/22: 0.48586; 9.9557 10 2022/23: 0.47872; 9.9557 11 2023/24: 0.47168; 9.9557 12 2024/25: 0.46474
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.34342; 9.9557 14 2026/27: 0.33837; 9.9557 15 2027/28: 0.3334; 9.9557 16 2028/29: 0.32849; 9.9557 17 2029/30: 0.32366; 9.9557 18 2030/31: 0.3189; 9.9557 19 2031/32: 0.31421; 9.9557 20 2032/33: 0.30958; 9.9557 21 2033/34: 0.30503; 9.9557 22 2034/35: 0.30054; 9.9557 23 2035/36: 0.29612; 9.9557 24 2036/37: 0.29177; 9.9557 25 2037/38: 0.28747; 9.9557 26 2038/39: 0.28324; 9.9557 27 2039/40: 0.27908; 9.9557 28 2040/41: 0.27497; 9.9557 29 2041/42: 0.27093; 9.9557 30 2042/43: 0.26694; 9.9557 31 2043/44: 0.26301; 9.9557 32 2044/45: 0.25915
| Estuary disruption costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.0021628; 9.9557 2 2014/15: 0.0021628; 9.9557 3 2015/16: 0.0021628; 9.9557 4 2016/17: 0.0021628; 9.9557 5 2017/18: 0.0021628; 9.9557 6 2018/19: 0.0021628; 9.9557 7 2019/20: 0.0021628; 9.9557 8 2020/21: 0.0021628; 9.9557 9 2021/22: 0.002131; 9.9557 10 2022/23: 0.0020997; 9.9557 11 2023/24: 0.0020688; 9.9557 12 2024/25: 0.0020383; 9.9557 13 2025/26: 0.0020084; 9.9557 14 2026/27: 0.0019788; 9.9557 15 2027/28: 0.0019497; 9.9557 16 2028/29: 0.001921; 9.9557 17 2029/30: 0.0018928; 9.9557 18 2030/31: 0.0018649; 9.9557 19 2031/32: 0.0018375; 9.9557 20 2032/33: 0.0018104; 9.9557 21 2033/34: 0.0017838; 9.9557 22 2034/35: 0.0017576; 9.9557 23 2035/36: 0.0017317; 9.9557 24 2036/37: 0.0017062; 9.9557 25 2037/38: 0.0016811; 9.9557 26 2038/39: 0.0016564; 9.9557 27 2039/40: 0.001632; 9.9557 28 2040/41: 0.001608; 9.9557 29 2041/42: 0.0015844; 9.9557 30 2042/43: 0.0015611; 9.9557 31 2043/44: 0.0015381; 9.9557 32 2044/45: 0.0015155
| Shipwreck clear up costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.061322; 9.9557 2 2014/15: 0.061322; 9.9557 3 2015/16: 0.061322; 9.9557 4 2016/17: 0.061322; 9.9557 5 2017/18: 0.061322; 9.9557 6 2018/19: 0.061322; 9.9557 7 2019/20: 0.061322; 9.9557 8 2020/21: 0.061322; 9.9557 9 2021/22: 0.06042; 9.9557 10 2022/23: 0.059531; 9.9557 11 2023/24: 0.058656; 9.9557 12 2024/25: 0.057793; 9.9557 13 2025/26: 0.056943; 9.9557 14 2026/27: 0.056105; 9.9557 15 2027/28: 0.05528; 9.9557 16 2028/29: 0.054466; 9.9557 17 2029/30: 0.053665; 9.9557 18 2030/31: 0.052876; 9.9557 19 2031/32: 0.052098; 9.9557 20 2032/33: 0.051332; 9.9557 21 2033/34: 0.050576; 9.9557 22 2034/35: 0.049832; 9.9557 23 2035/36: 0.049099; 9.9557 24 2036/37: 0.048377; 9.9557 25 2037/38: 0.047665; 9.9557 26 2038/39: 0.046964; 9.9557 27 2039/40: 0.046273; 9.9557 28 2040/41: 0.045593; 9.9557 29 2041/42: 0.044922; 9.9557 30 2042/43: 0.044261; 9.9557 31 2043/44: 0.04361; 9.9557 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 6.4807; 9.9557 2 2014/15: 6.4736; 9.9557 3 2015/16: 6.4667; 9.9557 4 2016/17: 6.4598; 9.9557 5 2017/18: 6.453; 9.9557 6 2018/19: 6.4463; 9.9557 7 2019/20: 6.4396; 9.9557 8 2020/21: 6.433; 9.9557 9 2021/22: 6.3435; 9.9557 10 2022/23: 6.2552; 9.9557 11 2023/24: 6.1683; 9.9557 12 2024/25: 6.0825; 9.9557 13 2025/26: 5.3092; 9.9557 14 2026/27: 5.2361; 9.9557 15 2027/28: 5.164; 9.9557 16 2028/29: 5.0929; 9.9557 17 2029/30: 5.0228; 9.9557 18 2030/31: 4.9538; 9.9557 19 2031/32: 4.8857; 9.9557 20 2032/33: 4.8186; 9.9557 21 2033/34: 4.7524; 9.9557 22 2034/35: 4.6872; 9.9557 23 2035/36: 4.623; 9.9557 24 2036/37: 4.5596; 9.9557 25 2037/38: 4.4971; 9.9557 26 2038/39: 4.4356; 9.9557 27 2039/40: 4.3749; 9.9557 28 2040/41: 4.315; 9.9557 29 2041/42: 4.2561; 9.9557 30 2042/43: 4.1979; 9.9557 31 2043/44: 4.1406; 9.9557 32 2044/45: 4.0841
| Cost of possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Discount factor for other costs |  |  |  | 9.9557 1 2013/14: 0.96618; 9.9557 2 2014/15: 0.93351; 9.9557 3 2015/16: 0.90194; 9.9557 4 2016/17: 0.87144; 9.9557 5 2017/18: 0.84197; 9.9557 6 2018/19: 0.8135; 9.9557 7 2019/20: 0.78599; 9.9557 8 2020/21: 0.75941; 9.9557 9 2021/22: 0.73373; 9.9557 10 2022/23: 0.70892; 9.9557 11 2023/24: 0.68495; 9.9557 12 2024/25: 0.66178; 9.9557 13 2025/26: 0.6394; 9.9557 14 2026/27: 0.61778; 9.9557 15 2027/28: 0.59689; 9.9557 16 2028/29: 0.57671; 9.9557 17 2029/30: 0.5572; 9.9557 18 2030/31: 0.53836; 9.9557 19 2031/32: 0.52016; 9.9557 20 2032/33: 0.50257; 9.9557 21 2033/34: 0.48557; 9.9557 22 2034/35: 0.46915; 9.9557 23 2035/36: 0.45329; 9.9557 24 2036/37: 0.43796; 9.9557 25 2037/38: 0.42315; 9.9557 26 2038/39: 0.40884; 9.9557 27 2039/40: 0.39501; 9.9557 28 2040/41: 0.38165; 9.9557 29 2041/42: 0.36875; 9.9557 30 2042/43: 0.35628; 9.9557 31 2043/44: 0.39999; 9.9557 32 2044/45: 0.38834
| Discount factor for loss of life costs |  |  |  | 9.9557 1 2013/14: 0.98522; 9.9557 2 2014/15: 0.97066; 9.9557 3 2015/16: 0.95632; 9.9557 4 2016/17: 0.94218; 9.9557 5 2017/18: 0.92826; 9.9557 6 2018/19: 0.91454; 9.9557 7 2019/20: 0.90103; 9.9557 8 2020/21: 0.88771; 9.9557 9 2021/22: 0.87459; 9.9557 10 2022/23: 0.86167; 9.9557 11 2023/24: 0.84893; 9.9557 12 2024/25: 0.83639; 9.9557 13 2025/26: 0.82403; 9.9557 14 2026/27: 0.81185; 9.9557 15 2027/28: 0.79985; 9.9557 16 2028/29: 0.78803; 9.9557 17 2029/30: 0.77639; 9.9557 18 2030/31: 0.76491; 9.9557 19 2031/32: 0.75361; 9.9557 20 2032/33: 0.74247; 9.9557 21 2033/34: 0.7315; 9.9557 22 2034/35: 0.72069; 9.9557 23 2035/36: 0.71004; 9.9557 24 2036/37: 0.69954; 9.9557 25 2037/38: 0.68921; 9.9557 26 2038/39: 0.67902; 9.9557 27 2039/40: 0.66899; 9.9557 28 2040/41: 0.6591; 9.9557 29 2041/42: 0.64936; 9.9557 30 2042/43: 0.63976; 9.9557 31 2043/44: 0.6721; 9.9557 32 2044/45: 0.66354
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 6.2615; 9.9557 2 2014/15: 6.0432; 9.9557 3 2015/16: 5.8326; 9.9557 4 2016/17: 5.6294; 9.9557 5 2017/18: 5.4333; 9.9557 6 2018/19: 5.244; 9.9557 7 2019/20: 5.0615; 9.9557 8 2020/21: 4.8853; 9.9557 9 2021/22: 4.6544; 9.9557 10 2022/23: 4.4344; 9.9557 11 2023/24: 4.2249; 9.9557 12 2024/25: 4.0253; 9.9557 13 2025/26: 3.3947; 9.9557 14 2026/27: 3.2347; 9.9557 15 2027/28: 3.0823; 9.9557 16 2028/29: 2.9371; 9.9557 17 2029/30: 2.7987; 9.9557 18 2030/31: 2.6669; 9.9557 19 2031/32: 2.5413; 9.9557 20 2032/33: 2.4217; 9.9557 21 2033/34: 2.3076; 9.9557 22 2034/35: 2.199; 9.9557 23 2035/36: 2.0955; 9.9557 24 2036/37: 1.9969; 9.9557 25 2037/38: 1.9029; 9.9557 26 2038/39: 1.8134; 9.9557 27 2039/40: 1.7281; 9.9557 28 2040/41: 1.6469; 9.9557 29 2041/42: 1.5694; 9.9557 30 2042/43: 1.4956; 9.9557 31 2043/44: 1.6562; 9.9557 32 2044/45: 1.586
| Discounted cost of loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11366; 9.9557 2 2014/15: 0.11198; 9.9557 3 2015/16: 0.11032; 9.9557 4 2016/17: 0.10869; 9.9557 5 2017/18: 0.10709; 9.9557 6 2018/19: 0.1055; 9.9557 7 2019/20: 0.10394; 9.9557 8 2020/21: 0.10241; 9.9557 9 2021/22: 0.09941; 9.9557 10 2022/23: 0.0965; 9.9557 11 2023/24: 0.093675; 9.9557 12 2024/25: 0.090933; 9.9557 13 2025/26: 0.088272; 9.9557 14 2026/27: 0.085688; 9.9557 15 2027/28: 0.083179; 9.9557 16 2028/29: 0.080745; 9.9557 17 2029/30: 0.078381; 9.9557 18 2030/31: 0.076087; 9.9557 19 2031/32: 0.07386; 9.9557 20 2032/33: 0.071698; 9.9557 21 2033/34: 0.069599; 9.9557 22 2034/35: 0.067562; 9.9557 23 2035/36: 0.065584; 9.9557 24 2036/37: 0.063664; 9.9557 25 2037/38: 0.061801; 9.9557 26 2038/39: 0.059992; 9.9557 27 2039/40: 0.058236; 9.9557 28 2040/41: 0.056531; 9.9557 29 2041/42: 0.054876; 9.9557 30 2042/43: 0.05327; 9.9557 31 2043/44: 0.05514; 9.9557 32 2044/45: 0.053637
| Total discounted cost | £m | 09/10 |  | 9.9557 1 2013/14: 6.3752; 9.9557 2 2014/15: 6.1552; 9.9557 3 2015/16: 5.9429; 9.9557 4 2016/17: 5.7381; 9.9557 5 2017/18: 5.5403; 9.9557 6 2018/19: 5.3495; 9.9557 7 2019/20: 5.1654; 9.9557 8 2020/21: 4.9877; 9.9557 9 2021/22: 4.7538; 9.9557 10 2022/23: 4.5309; 9.9557 11 2023/24: 4.3186; 9.9557 12 2024/25: 4.1163; 9.9557 13 2025/26: 3.483; 9.9557 14 2026/27: 3.3204; 9.9557 15 2027/28: 3.1655; 9.9557 16 2028/29: 3.0178; 9.9557 17 2029/30: 2.8771; 9.9557 18 2030/31: 2.743; 9.9557 19 2031/32: 2.6152; 9.9557 20 2032/33: 2.4934; 9.9557 21 2033/34: 2.3772; 9.9557 22 2034/35: 2.2666; 9.9557 23 2035/36: 2.1611; 9.9557 24 2036/37: 2.0606; 9.9557 25 2037/38: 1.9647; 9.9557 26 2038/39: 1.8734; 9.9557 27 2039/40: 1.7864; 9.9557 28 2040/41: 1.7034; 9.9557 29 2041/42: 1.6243; 9.9557 30 2042/43: 1.5489; 9.9557 31 2043/44: 1.7113; 9.9557 32 2044/45: 1.6397
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 6.2615; 9.9557 2 2014/15: 12.3047; 9.9557 3 2015/16: 18.1373; 9.9557 4 2016/17: 23.7667; 9.9557 5 2017/18: 29.1999; 9.9557 6 2018/19: 34.444; 9.9557 7 2019/20: 39.5054; 9.9557 8 2020/21: 44.3907; 9.9557 9 2021/22: 49.0451; 9.9557 10 2022/23: 53.4795; 9.9557 11 2023/24: 57.7044; 9.9557 12 2024/25: 61.7298; 9.9557 13 2025/26: 65.1245; 9.9557 14 2026/27: 68.3592; 9.9557 15 2027/28: 71.4416; 9.9557 16 2028/29: 74.3787; 9.9557 17 2029/30: 77.1774; 9.9557 18 2030/31: 79.8443; 9.9557 19 2031/32: 82.3856; 9.9557 20 2032/33: 84.8073; 9.9557 21 2033/34: 87.1149; 9.9557 22 2034/35: 89.314; 9.9557 23 2035/36: 91.4095; 9.9557 24 2036/37: 93.4064; 9.9557 25 2037/38: 95.3093; 9.9557 26 2038/39: 97.1228; 9.9557 27 2039/40: 98.8509; 9.9557 28 2040/41: 100.4977; 9.9557 29 2041/42: 102.0672; 9.9557 30 2042/43: 103.5628; 9.9557 31 2043/44: 105.219; 9.9557 32 2044/45: 106.805
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11366; 9.9557 2 2014/15: 0.22563; 9.9557 3 2015/16: 0.33596; 9.9557 4 2016/17: 0.44465; 9.9557 5 2017/18: 0.55173; 9.9557 6 2018/19: 0.65724; 9.9557 7 2019/20: 0.76118; 9.9557 8 2020/21: 0.86359; 9.9557 9 2021/22: 0.963; 9.9557 10 2022/23: 1.0595; 9.9557 11 2023/24: 1.1532; 9.9557 12 2024/25: 1.2441; 9.9557 13 2025/26: 1.3324; 9.9557 14 2026/27: 1.4181; 9.9557 15 2027/28: 1.5012; 9.9557 16 2028/29: 1.582; 9.9557 17 2029/30: 1.6604; 9.9557 18 2030/31: 1.7365; 9.9557 19 2031/32: 1.8103; 9.9557 20 2032/33: 1.882; 9.9557 21 2033/34: 1.9516; 9.9557 22 2034/35: 2.0192; 9.9557 23 2035/36: 2.0848; 9.9557 24 2036/37: 2.1484; 9.9557 25 2037/38: 2.2102; 9.9557 26 2038/39: 2.2702; 9.9557 27 2039/40: 2.3284; 9.9557 28 2040/41: 2.385; 9.9557 29 2041/42: 2.4399; 9.9557 30 2042/43: 2.4931; 9.9557 31 2043/44: 2.5483; 9.9557 32 2044/45: 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 9.9557 1 2013/14: 6.3752; 9.9557 2 2014/15: 12.5303; 9.9557 3 2015/16: 18.4733; 9.9557 4 2016/17: 24.2113; 9.9557 5 2017/18: 29.7517; 9.9557 6 2018/19: 35.1012; 9.9557 7 2019/20: 40.2666; 9.9557 8 2020/21: 45.2543; 9.9557 9 2021/22: 50.0081; 9.9557 10 2022/23: 54.539; 9.9557 11 2023/24: 58.8576; 9.9557 12 2024/25: 62.9739; 9.9557 13 2025/26: 66.4569; 9.9557 14 2026/27: 69.7773; 9.9557 15 2027/28: 72.9428; 9.9557 16 2028/29: 75.9607; 9.9557 17 2029/30: 78.8378; 9.9557 18 2030/31: 81.5808; 9.9557 19 2031/32: 84.196; 9.9557 20 2032/33: 86.6893; 9.9557 21 2033/34: 89.0666; 9.9557 22 2034/35: 91.3331; 9.9557 23 2035/36: 93.4942; 9.9557 24 2036/37: 95.5548; 9.9557 25 2037/38: 97.5196; 9.9557 26 2038/39: 99.393; 9.9557 27 2039/40: 101.1793; 9.9557 28 2040/41: 102.8827; 9.9557 29 2041/42: 104.507; 9.9557 30 2042/43: 106.0559; 9.9557 31 2043/44: 107.7673; 9.9557 32 2044/45: 109.4069
3 | Option: Mitigate with tunnel replacement in 2044
| Revenue impact of tunnel commissioned in 2045/46 | £m | 09/10 | See footnote 5 | 9.9557 25 2037/38: 0.0044358; 9.9557 26 2038/39: 0.24173; 9.9557 27 2039/40: 0.26634; 9.9557 28 2040/41: 1.7496; 9.9557 29 2041/42: 3.5985; 9.9557 30 2042/43: 5.2253; 9.9557 31 2043/44: 3.9355; 9.9557 32 2044/45: 3.7321; 9.9557 33 2045/46: 2.0308; 9.9557 34 2046/47: 2.1071; 9.9557 35 2047/48: 2.1731; 9.9557 36 2048/49: 2.2298; 9.9557 37 2049/50: 2.2784; 9.9557 38 2050/51: 2.3195; 9.9557 39 2051/52: 2.3542; 9.9557 40 2052/53: 2.383; 9.9557 41 2053/54: 2.4067; 9.9557 42 2054/55: 2.4257; 9.9557 43 2055/56: 2.4406; 9.9557 44 2056/57: 2.4518; 9.9557 45 2057/58: 2.4598; 9.9557 46 2058/59: 2.4648; 9.9557 47 2059/60: 2.4672; 9.9557 48 2060/61: 2.4673; 9.9557 49 2061/62: 2.4654; 9.9557 50 2062/63: 2.4616; 9.9557 51 2063/64: 2.4561; 9.9557 52 2064/65: 2.4492; 9.9557 53 2065/66: 2.441; 9.9557 54 2066/67: 2.4316; 9.9557 55 2067/68: 2.4211; 9.9557 56 2068/69: 2.4098; 9.9557 57 2069/70: 2.3976; 9.9557 58 2070/71: 2.3847; 9.9557 59 2071/72: 2.3711; 9.9557 60 2072/73: 2.3569
| Operational costs untill 2044/45 | £m | 09/10 |  | 9.9557 1 2013/14: 0.29951; 9.9557 2 2014/15: 0.29951; 9.9557 3 2015/16: 0.29951; 9.9557 4 2016/17: 0.29951; 9.9557 5 2017/18: 0.29951; 9.9557 6 2018/19: 0.29951; 9.9557 7 2019/20: 0.29951; 9.9557 8 2020/21: 0.29951; 9.9557 9 2021/22: 0.29598; 9.9557 10 2022/23: 0.29251; 9.9557 11 2023/24: 0.28908; 9.9557 12 2024/25: 0.28571; 9.9557 13 2025/26: 0.28239; 9.9557 14 2026/27: 0.27911; 9.9557 15 2027/28: 0.27588; 9.9557 16 2028/29: 0.2727; 9.9557 17 2029/30: 0.26957; 9.9557 18 2030/31: 0.26648; 9.9557 19 2031/32: 0.26344; 9.9557 20 2032/33: 0.26045; 9.9557 21 2033/34: 0.25749; 9.9557 22 2034/35: 0.25458; 9.9557 23 2035/36: 0.25172; 9.9557 24 2036/37: 0.24889; 9.9557 25 2037/38: 0.24611; 9.9557 26 2038/39: 0.24337; 9.9557 27 2039/40: 0.24067; 9.9557 28 2040/41: 0.23801; 9.9557 29 2041/42: 0.23539; 9.9557 30 2042/43: 0.2328; 9.9557 31 2043/44: 0.23026; 9.9557 32 2044/45: 0.22775
| Operational costs for tunnel commissioned in 2045/46 |  |  |  | 9.9557 33 2045/46: 0.059745; 9.9557 34 2046/47: 0.059745; 9.9557 35 2047/48: 0.059745; 9.9557 36 2048/49: 0.059745; 9.9557 37 2049/50: 0.059745; 9.9557 38 2050/51: 0.059745; 9.9557 39 2051/52: 0.059745; 9.9557 40 2052/53: 0.059745; 9.9557 41 2053/54: 0.059745; 9.9557 42 2054/55: 0.059745; 9.9557 43 2055/56: 0.059745; 9.9557 44 2056/57: 0.059745; 9.9557 45 2057/58: 0.059745; 9.9557 46 2058/59: 0.059745; 9.9557 47 2059/60: 0.059745; 9.9557 48 2060/61: 0.059745; 9.9557 49 2061/62: 0.059745; 9.9557 50 2062/63: 0.059745; 9.9557 51 2063/64: 0.059745; 9.9557 52 2064/65: 0.059745; 9.9557 53 2065/66: 0.059745; 9.9557 54 2066/67: 0.059745; 9.9557 55 2067/68: 0.059745; 9.9557 56 2068/69: 0.059745; 9.9557 57 2069/70: 0.059745; 9.9557 58 2070/71: 0.059745; 9.9557 59 2071/72: 0.059745; 9.9557 60 2072/73: 0.059745
| Loss of lease | £m | 09/10 |  | 9.9557 1 2013/14: 0.72155; 9.9557 2 2014/15: 0.71458; 9.9557 3 2015/16: 0.70769; 9.9557 4 2016/17: 0.70086; 9.9557 5 2017/18: 0.69409; 9.9557 6 2018/19: 0.6874; 9.9557 7 2019/20: 0.68076; 9.9557 8 2020/21: 0.67419; 9.9557 9 2021/22: 0.66769; 9.9557 10 2022/23: 0.66124; 9.9557 11 2023/24: 0.65486; 9.9557 12 2024/25: 0.64854; 9.9557 13 2025/26: 0.64229; 9.9557 14 2026/27: 0.63609; 9.9557 15 2027/28: 0.62995; 9.9557 16 2028/29: 0.62387; 9.9557 17 2029/30: 0.61785; 9.9557 18 2030/31: 0.61189; 9.9557 19 2031/32: 0.60598; 9.9557 20 2032/33: 0.60014; 9.9557 21 2033/34: 0.59434; 9.9557 22 2034/35: 0.58861; 9.9557 23 2035/36: 0.58293; 9.9557 24 2036/37: 0.5773; 9.9557 25 2037/38: 0.57173; 9.9557 26 2038/39: 0.56621; 9.9557 27 2039/40: 0.56075; 9.9557 28 2040/41: 0.55534; 9.9557 29 2041/42: 0.54998; 9.9557 30 2042/43: 0.54467; 9.9557 31 2043/44: 0.53942; 9.9557 32 2044/45: 0.53421
| Mattressing cost | £m | 09/10 |  | 9.9557 1 2013/14: 0.42436; 9.9557 2 2014/15: 0.42436; 9.9557 3 2015/16: 0.42436; 9.9557 4 2016/17: 0.42436; 9.9557 5 2017/18: 0.42436; 9.9557 6 2018/19: 0.42436; 9.9557 7 2019/20: 0.42436; 9.9557 8 2020/21: 0.42436; 9.9557 9 2021/22: 0.41812; 9.9557 10 2022/23: 0.41197; 9.9557 11 2023/24: 0.40591; 9.9557 12 2024/25: 0.39994; 9.9557 13 2025/26: 0.39405; 9.9557 14 2026/27: 0.38826; 9.9557 15 2027/28: 0.38254; 9.9557 16 2028/29: 0.37692; 9.9557 17 2029/30: 0.37137; 9.9557 18 2030/31: 0.36591; 9.9557 19 2031/32: 0.36053; 9.9557 20 2032/33: 0.35522; 9.9557 21 2033/34: 0.35; 9.9557 22 2034/35: 0.34485; 9.9557 23 2035/36: 0.33977; 9.9557 24 2036/37: 0.33478; 9.9557 25 2037/38: 0.32985; 9.9557 26 2038/39: 0.325; 9.9557 27 2039/40: 0.32022; 9.9557 28 2040/41: 0.31551; 9.9557 29 2041/42: 0.31087; 9.9557 30 2042/43: 0.30629; 9.9557 31 2043/44: 0.30179; 9.9557 32 2044/45: 0.29735
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 9.9557 1 2013/14: 0.042436; 9.9557 2 2014/15: 0.042436; 9.9557 3 2015/16: 0.042436; 9.9557 4 2016/17: 0.042436; 9.9557 5 2017/18: 0.042436; 9.9557 6 2018/19: 0.042436; 9.9557 7 2019/20: 0.042436; 9.9557 8 2020/21: 0.042436; 9.9557 9 2021/22: 0.041812; 9.9557 10 2022/23: 0.041197; 9.9557 11 2023/24: 0.040591; 9.9557 12 2024/25: 0.039994; 9.9557 13 2025/26: 0.039405; 9.9557 14 2026/27: 0.038826; 9.9557 15 2027/28: 0.038254; 9.9557 16 2028/29: 0.037692; 9.9557 17 2029/30: 0.037137; 9.9557 18 2030/31: 0.036591; 9.9557 19 2031/32: 0.036053; 9.9557 20 2032/33: 0.035522; 9.9557 21 2033/34: 0.035; 9.9557 22 2034/35: 0.034485; 9.9557 23 2035/36: 0.033977; 9.9557 24 2036/37: 0.033478; 9.9557 25 2037/38: 0.032985; 9.9557 26 2038/39: 0.0325; 9.9557 27 2039/40: 0.032022; 9.9557 28 2040/41: 0.031551; 9.9557 29 2041/42: 0.031087; 9.9557 30 2042/43: 0.030629; 9.9557 31 2043/44: 0.030179; 9.9557 32 2044/45: 0.029735
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.028324; 9.9557 2 2014/15: 0.028324; 9.9557 3 2015/16: 0.028324; 9.9557 4 2016/17: 0.028324; 9.9557 5 2017/18: 0.028324; 9.9557 6 2018/19: 0.028324; 9.9557 7 2019/20: 0.028324; 9.9557 8 2020/21: 0.028324; 9.9557 9 2021/22: 0.027907; 9.9557 10 2022/23: 0.027497; 9.9557 11 2023/24: 0.027092; 9.9557 12 2024/25: 0.026694; 9.9557 13 2025/26: 0.026301; 9.9557 14 2026/27: 0.025914; 9.9557 15 2027/28: 0.025533; 9.9557 16 2028/29: 0.025157; 9.9557 17 2029/30: 0.024787; 9.9557 18 2030/31: 0.024423; 9.9557 19 2031/32: 0.024063; 9.9557 20 2032/33: 0.023709; 9.9557 21 2033/34: 0.023361; 9.9557 22 2034/35: 0.023017; 9.9557 23 2035/36: 0.022678; 9.9557 24 2036/37: 0.022345; 9.9557 25 2037/38: 0.022016; 9.9557 26 2038/39: 0.021692; 9.9557 27 2039/40: 0.021373; 9.9557 28 2040/41: 0.021059; 9.9557 29 2041/42: 0.020749; 9.9557 30 2042/43: 0.020444; 9.9557 31 2043/44: 0.020143; 9.9557 32 2044/45: 0.019847
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 1.3253; 9.9557 2 2014/15: 1.3253; 9.9557 3 2015/16: 1.3253; 9.9557 4 2016/17: 1.3253; 9.9557 5 2017/18: 1.3253; 9.9557 6 2018/19: 1.3253; 9.9557 7 2019/20: 1.3253; 9.9557 8 2020/21: 1.3253; 9.9557 9 2021/22: 1.3058; 9.9557 10 2022/23: 1.2866; 9.9557 11 2023/24: 1.2677; 9.9557 12 2024/25: 1.249; 9.9557 13 2025/26: 1.2307; 9.9557 14 2026/27: 1.2126; 9.9557 15 2027/28: 1.1947; 9.9557 16 2028/29: 1.1771; 9.9557 17 2029/30: 1.1598; 9.9557 18 2030/31: 1.1428; 9.9557 19 2031/32: 1.126; 9.9557 20 2032/33: 1.1094; 9.9557 21 2033/34: 1.0931; 9.9557 22 2034/35: 1.077; 9.9557 23 2035/36: 1.0612; 9.9557 24 2036/37: 1.0455; 9.9557 25 2037/38: 1.0302; 9.9557 26 2038/39: 1.015; 9.9557 27 2039/40: 1.0001; 9.9557 28 2040/41: 0.98536; 9.9557 29 2041/42: 0.97087; 9.9557 30 2042/43: 0.95659; 9.9557 31 2043/44: 0.94251; 9.9557 32 2044/45: 0.92865
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.134; 9.9557 2 2014/15: 0.134; 9.9557 3 2015/16: 0.134; 9.9557 4 2016/17: 0.134; 9.9557 5 2017/18: 0.134; 9.9557 6 2018/19: 0.134; 9.9557 7 2019/20: 0.134; 9.9557 8 2020/21: 0.134; 9.9557 9 2021/22: 0.13203; 9.9557 10 2022/23: 0.13009; 9.9557 11 2023/24: 0.12817; 9.9557 12 2024/25: 0.12629; 9.9557 13 2025/26: 0.12443; 9.9557 14 2026/27: 0.1226; 9.9557 15 2027/28: 0.1208; 9.9557 16 2028/29: 0.11902; 9.9557 17 2029/30: 0.11727; 9.9557 18 2030/31: 0.11554; 9.9557 19 2031/32: 0.11384; 9.9557 20 2032/33: 0.11217; 9.9557 21 2033/34: 0.11052; 9.9557 22 2034/35: 0.10889; 9.9557 23 2035/36: 0.10729; 9.9557 24 2036/37: 0.10571; 9.9557 25 2037/38: 0.10416; 9.9557 26 2038/39: 0.10262; 9.9557 27 2039/40: 0.10112; 9.9557 28 2040/41: 0.099628; 9.9557 29 2041/42: 0.098162; 9.9557 30 2042/43: 0.096718; 9.9557 31 2043/44: 0.095295; 9.9557 32 2044/45: 0.093893
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 1.2117; 9.9557 2 2014/15: 1.2117; 9.9557 3 2015/16: 1.2117; 9.9557 4 2016/17: 1.2117; 9.9557 5 2017/18: 1.2117; 9.9557 6 2018/19: 1.2117; 9.9557 7 2019/20: 1.2117; 9.9557 8 2020/21: 1.2117; 9.9557 9 2021/22: 1.1939; 9.9557 10 2022/23: 1.1763; 9.9557 11 2023/24: 1.159; 9.9557 12 2024/25: 1.142
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.84387; 9.9557 14 2026/27: 0.83146; 9.9557 15 2027/28: 0.81922; 9.9557 16 2028/29: 0.80717; 9.9557 17 2029/30: 0.7953; 9.9557 18 2030/31: 0.7836; 9.9557 19 2031/32: 0.77207; 9.9557 20 2032/33: 0.76071; 9.9557 21 2033/34: 0.74952; 9.9557 22 2034/35: 0.7385; 9.9557 23 2035/36: 0.72763; 9.9557 24 2036/37: 0.71693; 9.9557 25 2037/38: 0.70638; 9.9557 26 2038/39: 0.69599; 9.9557 27 2039/40: 0.68575; 9.9557 28 2040/41: 0.67567; 9.9557 29 2041/42: 0.66573; 9.9557 30 2042/43: 0.65593; 9.9557 31 2043/44: 0.64628; 9.9557 32 2044/45: 0.63678
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 9.9557 1 2013/14: 0.059817; 9.9557 2 2014/15: 0.059769; 9.9557 3 2015/16: 0.059722; 9.9557 4 2016/17: 0.059674; 9.9557 5 2017/18: 0.059626; 9.9557 6 2018/19: 0.059578; 9.9557 7 2019/20: 0.059531; 9.9557 8 2020/21: 0.059483; 9.9557 9 2021/22: 0.059435; 9.9557 10 2022/23: 0.059388; 9.9557 11 2023/24: 0.05934; 9.9557 12 2024/25: 0.059293; 9.9557 13 2025/26: 0.059246; 9.9557 14 2026/27: 0.059198; 9.9557 15 2027/28: 0.059151; 9.9557 16 2028/29: 0.059103; 9.9557 17 2029/30: 0.059056; 9.9557 18 2030/31: 0.059009; 9.9557 19 2031/32: 0.058962; 9.9557 20 2032/33: 0.058915; 9.9557 21 2033/34: 0.058867; 9.9557 22 2034/35: 0.05882; 9.9557 23 2035/36: 0.058773; 9.9557 24 2036/37: 0.058726; 9.9557 25 2037/38: 0.058679; 9.9557 26 2038/39: 0.058632; 9.9557 27 2039/40: 0.058585; 9.9557 28 2040/41: 0.058539; 9.9557 29 2041/42: 0.058492; 9.9557 30 2042/43: 0.058445; 9.9557 31 2043/44: 0.058398; 9.9557 32 2044/45: 0.058351
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0056648; 9.9557 2 2014/15: 0.0056648; 9.9557 3 2015/16: 0.0056648; 9.9557 4 2016/17: 0.0056648; 9.9557 5 2017/18: 0.0056648; 9.9557 6 2018/19: 0.0056648; 9.9557 7 2019/20: 0.0056648; 9.9557 8 2020/21: 0.0056648; 9.9557 9 2021/22: 0.0055815; 9.9557 10 2022/23: 0.0054994; 9.9557 11 2023/24: 0.0054185; 9.9557 12 2024/25: 0.0053388; 9.9557 13 2025/26: 0.0052602; 9.9557 14 2026/27: 0.0051828; 9.9557 15 2027/28: 0.0051066; 9.9557 16 2028/29: 0.0050315; 9.9557 17 2029/30: 0.0049575; 9.9557 18 2030/31: 0.0048845; 9.9557 19 2031/32: 0.0048127; 9.9557 20 2032/33: 0.0047419; 9.9557 21 2033/34: 0.0046721; 9.9557 22 2034/35: 0.0046034; 9.9557 23 2035/36: 0.0045357; 9.9557 24 2036/37: 0.0044689; 9.9557 25 2037/38: 0.0044032; 9.9557 26 2038/39: 0.0043384; 9.9557 27 2039/40: 0.0042746; 9.9557 28 2040/41: 0.0042117; 9.9557 29 2041/42: 0.0041498; 9.9557 30 2042/43: 0.0040887; 9.9557 31 2043/44: 0.0040286; 9.9557 32 2044/45: 0.0039693
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.26506; 9.9557 2 2014/15: 0.26506; 9.9557 3 2015/16: 0.26506; 9.9557 4 2016/17: 0.26506; 9.9557 5 2017/18: 0.26506; 9.9557 6 2018/19: 0.26506; 9.9557 7 2019/20: 0.26506; 9.9557 8 2020/21: 0.26506; 9.9557 9 2021/22: 0.26117; 9.9557 10 2022/23: 0.25732; 9.9557 11 2023/24: 0.25354; 9.9557 12 2024/25: 0.24981; 9.9557 13 2025/26: 0.24613; 9.9557 14 2026/27: 0.24251; 9.9557 15 2027/28: 0.23894; 9.9557 16 2028/29: 0.23543; 9.9557 17 2029/30: 0.23197; 9.9557 18 2030/31: 0.22855; 9.9557 19 2031/32: 0.22519; 9.9557 20 2032/33: 0.22188; 9.9557 21 2033/34: 0.21862; 9.9557 22 2034/35: 0.2154; 9.9557 23 2035/36: 0.21223; 9.9557 24 2036/37: 0.20911; 9.9557 25 2037/38: 0.20603; 9.9557 26 2038/39: 0.203; 9.9557 27 2039/40: 0.20002; 9.9557 28 2040/41: 0.19707; 9.9557 29 2041/42: 0.19417; 9.9557 30 2042/43: 0.19132; 9.9557 31 2043/44: 0.1885; 9.9557 32 2044/45: 0.18573
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.0268; 9.9557 2 2014/15: 0.0268; 9.9557 3 2015/16: 0.0268; 9.9557 4 2016/17: 0.0268; 9.9557 5 2017/18: 0.0268; 9.9557 6 2018/19: 0.0268; 9.9557 7 2019/20: 0.0268; 9.9557 8 2020/21: 0.0268; 9.9557 9 2021/22: 0.026406; 9.9557 10 2022/23: 0.026017; 9.9557 11 2023/24: 0.025635; 9.9557 12 2024/25: 0.025257; 9.9557 13 2025/26: 0.024886; 9.9557 14 2026/27: 0.02452; 9.9557 15 2027/28: 0.024159; 9.9557 16 2028/29: 0.023804; 9.9557 17 2029/30: 0.023454; 9.9557 18 2030/31: 0.023109; 9.9557 19 2031/32: 0.022769; 9.9557 20 2032/33: 0.022434; 9.9557 21 2033/34: 0.022104; 9.9557 22 2034/35: 0.021778; 9.9557 23 2035/36: 0.021458; 9.9557 24 2036/37: 0.021142; 9.9557 25 2037/38: 0.020831; 9.9557 26 2038/39: 0.020525; 9.9557 27 2039/40: 0.020223; 9.9557 28 2040/41: 0.019926; 9.9557 29 2041/42: 0.019632; 9.9557 30 2042/43: 0.019344; 9.9557 31 2043/44: 0.019059; 9.9557 32 2044/45: 0.018779
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 1.2624; 9.9557 2 2014/15: 1.2624; 9.9557 3 2015/16: 1.2624; 9.9557 4 2016/17: 1.2624; 9.9557 5 2017/18: 1.2624; 9.9557 6 2018/19: 1.2624; 9.9557 7 2019/20: 1.2624; 9.9557 8 2020/21: 1.2624; 9.9557 9 2021/22: 1.2438; 9.9557 10 2022/23: 1.2255; 9.9557 11 2023/24: 1.2075; 9.9557 12 2024/25: 1.1897
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.87917; 9.9557 14 2026/27: 0.86623; 9.9557 15 2027/28: 0.85349; 9.9557 16 2028/29: 0.84094; 9.9557 17 2029/30: 0.82857; 9.9557 18 2030/31: 0.81638; 9.9557 19 2031/32: 0.80437; 9.9557 20 2032/33: 0.79253; 9.9557 21 2033/34: 0.78088; 9.9557 22 2034/35: 0.76939; 9.9557 23 2035/36: 0.75807; 9.9557 24 2036/37: 0.74692; 9.9557 25 2037/38: 0.73593; 9.9557 26 2038/39: 0.7251; 9.9557 27 2039/40: 0.71444; 9.9557 28 2040/41: 0.70393; 9.9557 29 2041/42: 0.69357; 9.9557 30 2042/43: 0.68337; 9.9557 31 2043/44: 0.67332; 9.9557 32 2044/45: 0.66341
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 9.9557 1 2013/14: 0.0031112; 9.9557 2 2014/15: 0.0031112; 9.9557 3 2015/16: 0.0031112; 9.9557 4 2016/17: 0.0031112; 9.9557 5 2017/18: 0.0031112; 9.9557 6 2018/19: 0.0031112; 9.9557 7 2019/20: 0.0031112; 9.9557 8 2020/21: 0.0031112; 9.9557 9 2021/22: 0.0030654; 9.9557 10 2022/23: 0.0030203; 9.9557 11 2023/24: 0.0029759; 9.9557 12 2024/25: 0.0029321; 9.9557 13 2025/26: 0.002889; 9.9557 14 2026/27: 0.0028465; 9.9557 15 2027/28: 0.0028046; 9.9557 16 2028/29: 0.0027633; 9.9557 17 2029/30: 0.0027227; 9.9557 18 2030/31: 0.0026826; 9.9557 19 2031/32: 0.0026432; 9.9557 20 2032/33: 0.0026043; 9.9557 21 2033/34: 0.002566; 9.9557 22 2034/35: 0.0025282; 9.9557 23 2035/36: 0.002491; 9.9557 24 2036/37: 0.0024544; 9.9557 25 2037/38: 0.0024183; 9.9557 26 2038/39: 0.0023827; 9.9557 27 2039/40: 0.0023477; 9.9557 28 2040/41: 0.0023131; 9.9557 29 2041/42: 0.0022791; 9.9557 30 2042/43: 0.0022456; 9.9557 31 2043/44: 0.0022125; 9.9557 32 2044/45: 0.00218
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.10354; 9.9557 2 2014/15: 0.10354; 9.9557 3 2015/16: 0.10354; 9.9557 4 2016/17: 0.10354; 9.9557 5 2017/18: 0.10354; 9.9557 6 2018/19: 0.10354; 9.9557 7 2019/20: 0.10354; 9.9557 8 2020/21: 0.10354; 9.9557 9 2021/22: 0.10202; 9.9557 10 2022/23: 0.10052; 9.9557 11 2023/24: 0.099038; 9.9557 12 2024/25: 0.097581; 9.9557 13 2025/26: 0.096146; 9.9557 14 2026/27: 0.094731; 9.9557 15 2027/28: 0.093338; 9.9557 16 2028/29: 0.091965; 9.9557 17 2029/30: 0.090612; 9.9557 18 2030/31: 0.089279; 9.9557 19 2031/32: 0.087966; 9.9557 20 2032/33: 0.086672; 9.9557 21 2033/34: 0.085397; 9.9557 22 2034/35: 0.08414; 9.9557 23 2035/36: 0.082903; 9.9557 24 2036/37: 0.081683; 9.9557 25 2037/38: 0.080481; 9.9557 26 2038/39: 0.079297; 9.9557 27 2039/40: 0.078131; 9.9557 28 2040/41: 0.076982; 9.9557 29 2041/42: 0.075849; 9.9557 30 2042/43: 0.074733; 9.9557 31 2043/44: 0.073634; 9.9557 32 2044/45: 0.072551
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.010469; 9.9557 2 2014/15: 0.010469; 9.9557 3 2015/16: 0.010469; 9.9557 4 2016/17: 0.010469; 9.9557 5 2017/18: 0.010469; 9.9557 6 2018/19: 0.010469; 9.9557 7 2019/20: 0.010469; 9.9557 8 2020/21: 0.010469; 9.9557 9 2021/22: 0.010315; 9.9557 10 2022/23: 0.010163; 9.9557 11 2023/24: 0.010014; 9.9557 12 2024/25: 0.0098662; 9.9557 13 2025/26: 0.0097211; 9.9557 14 2026/27: 0.0095781; 9.9557 15 2027/28: 0.0094372; 9.9557 16 2028/29: 0.0092983; 9.9557 17 2029/30: 0.0091615; 9.9557 18 2030/31: 0.0090268; 9.9557 19 2031/32: 0.008894; 9.9557 20 2032/33: 0.0087631; 9.9557 21 2033/34: 0.0086342; 9.9557 22 2034/35: 0.0085072; 9.9557 23 2035/36: 0.0083821; 9.9557 24 2036/37: 0.0082588; 9.9557 25 2037/38: 0.0081373; 9.9557 26 2038/39: 0.0080176; 9.9557 27 2039/40: 0.0078996; 9.9557 28 2040/41: 0.0077834; 9.9557 29 2041/42: 0.0076689; 9.9557 30 2042/43: 0.0075561; 9.9557 31 2043/44: 0.0074449; 9.9557 32 2044/45: 0.0073354
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.49312; 9.9557 2 2014/15: 0.49312; 9.9557 3 2015/16: 0.49312; 9.9557 4 2016/17: 0.49312; 9.9557 5 2017/18: 0.49312; 9.9557 6 2018/19: 0.49312; 9.9557 7 2019/20: 0.49312; 9.9557 8 2020/21: 0.49312; 9.9557 9 2021/22: 0.48586; 9.9557 10 2022/23: 0.47872; 9.9557 11 2023/24: 0.47168; 9.9557 12 2024/25: 0.46474
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.34342; 9.9557 14 2026/27: 0.33837; 9.9557 15 2027/28: 0.3334; 9.9557 16 2028/29: 0.32849; 9.9557 17 2029/30: 0.32366; 9.9557 18 2030/31: 0.3189; 9.9557 19 2031/32: 0.31421; 9.9557 20 2032/33: 0.30958; 9.9557 21 2033/34: 0.30503; 9.9557 22 2034/35: 0.30054; 9.9557 23 2035/36: 0.29612; 9.9557 24 2036/37: 0.29177; 9.9557 25 2037/38: 0.28747; 9.9557 26 2038/39: 0.28324; 9.9557 27 2039/40: 0.27908; 9.9557 28 2040/41: 0.27497; 9.9557 29 2041/42: 0.27093; 9.9557 30 2042/43: 0.26694; 9.9557 31 2043/44: 0.26301; 9.9557 32 2044/45: 0.25915
| Estuary disruption costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.0021628; 9.9557 2 2014/15: 0.0021628; 9.9557 3 2015/16: 0.0021628; 9.9557 4 2016/17: 0.0021628; 9.9557 5 2017/18: 0.0021628; 9.9557 6 2018/19: 0.0021628; 9.9557 7 2019/20: 0.0021628; 9.9557 8 2020/21: 0.0021628; 9.9557 9 2021/22: 0.002131; 9.9557 10 2022/23: 0.0020997; 9.9557 11 2023/24: 0.0020688; 9.9557 12 2024/25: 0.0020383; 9.9557 13 2025/26: 0.0020084; 9.9557 14 2026/27: 0.0019788; 9.9557 15 2027/28: 0.0019497; 9.9557 16 2028/29: 0.001921; 9.9557 17 2029/30: 0.0018928; 9.9557 18 2030/31: 0.0018649; 9.9557 19 2031/32: 0.0018375; 9.9557 20 2032/33: 0.0018104; 9.9557 21 2033/34: 0.0017838; 9.9557 22 2034/35: 0.0017576; 9.9557 23 2035/36: 0.0017317; 9.9557 24 2036/37: 0.0017062; 9.9557 25 2037/38: 0.0016811; 9.9557 26 2038/39: 0.0016564; 9.9557 27 2039/40: 0.001632; 9.9557 28 2040/41: 0.001608; 9.9557 29 2041/42: 0.0015844; 9.9557 30 2042/43: 0.0015611; 9.9557 31 2043/44: 0.0015381; 9.9557 32 2044/45: 0.0015155
| Shipwreck clear up costs (£m) (09/10 prices) | £m | 09/10 |  | 9.9557 1 2013/14: 0.061322; 9.9557 2 2014/15: 0.061322; 9.9557 3 2015/16: 0.061322; 9.9557 4 2016/17: 0.061322; 9.9557 5 2017/18: 0.061322; 9.9557 6 2018/19: 0.061322; 9.9557 7 2019/20: 0.061322; 9.9557 8 2020/21: 0.061322; 9.9557 9 2021/22: 0.06042; 9.9557 10 2022/23: 0.059531; 9.9557 11 2023/24: 0.058656; 9.9557 12 2024/25: 0.057793; 9.9557 13 2025/26: 0.056943; 9.9557 14 2026/27: 0.056105; 9.9557 15 2027/28: 0.05528; 9.9557 16 2028/29: 0.054466; 9.9557 17 2029/30: 0.053665; 9.9557 18 2030/31: 0.052876; 9.9557 19 2031/32: 0.052098; 9.9557 20 2032/33: 0.051332; 9.9557 21 2033/34: 0.050576; 9.9557 22 2034/35: 0.049832; 9.9557 23 2035/36: 0.049099; 9.9557 24 2036/37: 0.048377; 9.9557 25 2037/38: 0.047665; 9.9557 26 2038/39: 0.046964; 9.9557 27 2039/40: 0.046273; 9.9557 28 2040/41: 0.045593; 9.9557 29 2041/42: 0.044922; 9.9557 30 2042/43: 0.044261; 9.9557 31 2043/44: 0.04361; 9.9557 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 6.4807 | 6.4736 | 6.4667 | 6.4598 | 6.453 | 6.4463 | 6.4396 | 6.433 | 6.3435 | 6.2552 | 6.1683 | 6.0825 | 5.3092 | 5.2361 | 5.164 | 5.0929 | 5.0228 | 4.9538 | 4.8857 | 4.8186 | 4.7524 | 4.6872 | 4.623 | 4.5596 | 4.5016 | 4.6773 | 4.6412 | 6.0646 | 7.8546 | 9.4232 | 8.0761 | 7.8163 | 2.0906 | 2.1669 | 2.2328 | 2.2896 | 2.3381 | 2.3793 | 2.414 | 2.4428 | 2.4664 | 2.4855 | 2.5004 | 2.5116 | 2.5195 | 2.5246 | 2.527 | 2.5271 | 2.5251 | 2.5213 | 2.5159 | 2.5089 | 2.5007 | 2.4913 | 2.4809 | 2.4695 | 2.4573 | 2.4444 | 2.4308 | 2.4167
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11366 | 0.11199 | 0.11034 | 0.10872 | 0.10712 | 0.10555 | 0.10399 | 0.10246 | 0.10096 | 0.099471 | 0.098008 | 0.096566 | 0.095146 | 0.093746 | 0.092367 | 0.091008 | 0.089669 | 0.08835 | 0.087051 | 0.08577 | 0.084508 | 0.083265 | 0.08204 | 0.080833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 6.2615 | 6.0432 | 5.8326 | 5.6294 | 5.4333 | 5.244 | 5.0615 | 4.8853 | 4.6544 | 4.4344 | 4.2249 | 4.0253 | 3.3947 | 3.2347 | 3.0823 | 2.9371 | 2.7987 | 2.6669 | 2.5413 | 2.4217 | 2.3076 | 2.199 | 2.0955 | 1.9969 | 1.9048 | 1.9123 | 1.8333 | 2.3146 | 2.8964 | 3.3573 | 3.2304 | 3.0353 | 0.7882 | 0.79318 | 0.79351 | 0.78998 | 0.78322 | 0.77381 | 0.76221 | 0.74885 | 0.73408 | 0.7182 | 0.70146 | 0.68409 | 0.66626 | 0.64815 | 0.62987 | 0.61155 | 0.59328 | 0.57513 | 0.55717 | 0.53945 | 0.52202 | 0.50491 | 0.48815 | 0.47177 | 0.45577 | 0.44017 | 0.42497 | 0.41019
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0.09941 | 0.0965 | 0.093675 | 0.090933 | 0.088272 | 0.085688 | 0.083179 | 0.080745 | 0.078381 | 0.076087 | 0.07386 | 0.071698 | 0.069599 | 0.067562 | 0.065584 | 0.063664 | 0.061801 | 0.059992 | 0.058236 | 0.056531 | 0.054876 | 0.05327 | 0.05514 | 0.053637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 6.3752 | 6.1552 | 5.9429 | 5.7381 | 5.5403 | 5.3495 | 5.1654 | 4.9877 | 4.7538 | 4.5309 | 4.3186 | 4.1163 | 3.483 | 3.3204 | 3.1655 | 3.0178 | 2.8771 | 2.743 | 2.6152 | 2.4934 | 2.3772 | 2.2666 | 2.1611 | 2.0606 | 1.9666 | 1.9722 | 1.8916 | 2.3711 | 2.9512 | 3.4106 | 3.2855 | 3.089 | 0.7882 | 0.79318 | 0.79351 | 0.78998 | 0.78322 | 0.77381 | 0.76221 | 0.74885 | 0.73408 | 0.7182 | 0.70146 | 0.68409 | 0.66626 | 0.64815 | 0.62987 | 0.61155 | 0.59328 | 0.57513 | 0.55717 | 0.53945 | 0.52202 | 0.50491 | 0.48815 | 0.47177 | 0.45577 | 0.44017 | 0.42497 | 0.41019
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 6.2615 | 12.3047 | 18.1373 | 23.7667 | 29.1999 | 34.444 | 39.5054 | 44.3907 | 49.0451 | 53.4795 | 57.7044 | 61.7298 | 65.1245 | 68.3592 | 71.4416 | 74.3787 | 77.1774 | 79.8443 | 82.3856 | 84.8073 | 87.1149 | 89.314 | 91.4095 | 93.4064 | 95.3112 | 97.2235 | 99.0568 | 101.3714 | 104.2678 | 107.625 | 110.8554 | 113.8907 | 114.6789 | 115.4721 | 116.2656 | 117.0556 | 117.8388 | 118.6126 | 119.3749 | 120.1237 | 120.8578 | 121.576 | 122.2774 | 122.9615 | 123.6278 | 124.2759 | 124.9058 | 125.5174 | 126.1106 | 126.6858 | 127.2429 | 127.7824 | 128.3044 | 128.8093 | 129.2975 | 129.7693 | 130.225 | 130.6652 | 131.0902 | 131.5003
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.963 | 1.0595 | 1.1532 | 1.2441 | 1.3324 | 1.4181 | 1.5012 | 1.582 | 1.6604 | 1.7365 | 1.8103 | 1.882 | 1.9516 | 2.0192 | 2.0848 | 2.1484 | 2.2102 | 2.2702 | 2.3284 | 2.385 | 2.4399 | 2.4931 | 2.5483 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 6.3752 | 12.5303 | 18.4733 | 24.2113 | 29.7517 | 35.1012 | 40.2666 | 45.2543 | 50.0081 | 54.539 | 58.8576 | 62.9739 | 66.4569 | 69.7773 | 72.9428 | 75.9607 | 78.8378 | 81.5808 | 84.196 | 86.6893 | 89.0666 | 91.3331 | 93.4942 | 95.5548 | 97.5214 | 99.4937 | 101.3852 | 103.7564 | 106.7076 | 110.1182 | 113.4037 | 116.4926 | 117.2808 | 118.074 | 118.8675 | 119.6575 | 120.4407 | 121.2145 | 121.9768 | 122.7256 | 123.4597 | 124.1779 | 124.8794 | 125.5634 | 126.2297 | 126.8778 | 127.5077 | 128.1193 | 128.7126 | 129.2877 | 129.8448 | 130.3843 | 130.9063 | 131.4112 | 131.8994 | 132.3712 | 132.8269 | 133.2671 | 133.6921 | 134.1023

## CALC¦3
| Item | Unit | Index | Comments | Constant | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[6 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Costs and expenditure profile Tunnel
| Tunnel construction period | years |  |  | 8
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.059745
| Expenditure profile after Ofgem efficiency challenge | £m | 09/10 |  |  | 0.057598 | 3.0539 | 1.9348 | 19.9162 | 34.155 | 40.4284 | 9.339 | 2.4141 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Tunnel revenue profile to be used for modelling | £m | 09/10 |  |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 5.0555 | 5.0929 | 5.1172 | 5.1297 | 5.1319 | 5.1248 | 5.1094 | 5.0866 | 5.0572 | 5.022 | 4.9815 | 4.9364 | 4.8871 | 4.8342 | 4.7779 | 4.7187 | 4.6568 | 4.5926 | 4.5264 | 4.4583 | 4.3885 | 4.3172 | 4.2447 | 4.1709 | 4.0961 | 4.0204 | 3.9439 | 3.8666 | 3.7886 | 3.7101 | 3.631 | 3.5515 | 3.4715 | 3.3912 | 3.3106 | 3.2296 | 3.1484 | 3.067 | 2.9839 | 2.8297 | 2.7041 | 2.1531 | 1.279 | 0.28157 | -0.027348 | 0 | 0 | 0 | 0 | 0 | 0 | 0
2 | Costs and expenditure profile Mitigation
| Annual cost of inspections/pigging | £m | 09/10 |  | 0.29951
2.1 | Probablity adjusted cost of losing lease in any year
| Cost of replacing pipeline with a tunnel (after Ofgem efficiency challenge) | £m | 09/10 |  | 111.299
| Cost of loss of lease | £m | 09/10 |  |  | 1 2013/14: 0.97683; 2 2014/15: 0.96741; 3 2015/16: 0.95807; 4 2016/17: 0.94883; 5 2017/18: 0.93967; 6 2018/19: 0.9306; 7 2019/20: 0.92162; 8 2020/21: 0.91273; 9 2021/22: 0.90392; 10 2022/23: 0.8952; 11 2023/24: 0.88656; 12 2024/25: 0.878; 13 2025/26: 0.86953; 14 2026/27: 0.86114; 15 2027/28: 0.85283; 16 2028/29: 0.8446; 17 2029/30: 0.83645; 18 2030/31: 0.82838; 19 2031/32: 0.82039; 20 2032/33: 0.81247; 21 2033/34: 0.80463; 22 2034/35: 0.79686; 23 2035/36: 0.78917; 24 2036/37: 0.78156; 25 2037/38: 0.77402; 26 2038/39: 0.76655; 27 2039/40: 0.75915; 28 2040/41: 0.75182; 29 2041/42: 0.74457; 30 2042/43: 0.73738; 31 2043/44: 0.73027; 32 2044/45: 0.72322
| Probability that the lease is still in force and current pipeline is operational | % |  |  |  | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 100% | 98.53% | 97.08% | 95.65% | 94.24% | 92.86% | 91.49% | 90.15% | 88.82% | 87.51% | 86.23% | 84.96% | 83.71% | 82.48% | 81.26% | 80.07% | 78.89% | 77.73% | 76.59% | 75.46% | 74.35% | 73.26% | 72.18% | 71.12% | 70.07% | 69.04% | 68.02% | 67.02% | 66.04% | 65.07% | 64.11% | 63.17%
2.2 | Cost of mattressing
| Probability adjusted annual cost of mattressing | £m | 09/10 |  | 0.21218
2.3 | Freespan develops despite mattressing (less than 20m section)
| Probability of event | % |  |  | 0.58%
| Cost of emergency mattressing | £m | 09/10 | see footnote 4 | 0.012306
2.4 | Freespan develops despite mattressing (between 20m and 55m section)
| Probability of event |  |  |  | 0.117%
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0082848
| Constraint costs | £m | 09/10 |  | 0.22231
| Value of lost load (VOLL) | £m | 09/10 |  | 0.039195
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.28478
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 0.21359
2.5 | Freespan develops despite mattressing (greater than 55m section)
| Probability of event | % |  |  | 0.023%
| Cost of building a tunnel replacement | £m | 09/10 |  |  | 1 2013/14: 0.023282; 2 2014/15: 0.023277; 3 2015/16: 0.023271; 4 2016/17: 0.023266; 5 2017/18: 0.023261; 6 2018/19: 0.023255; 7 2019/20: 0.02325; 8 2020/21: 0.023245; 9 2021/22: 0.023239; 10 2022/23: 0.023234; 11 2023/24: 0.023229; 12 2024/25: 0.023223; 13 2025/26: 0.023218; 14 2026/27: 0.023213; 15 2027/28: 0.023207; 16 2028/29: 0.023202; 17 2029/30: 0.023197; 18 2030/31: 0.023191; 19 2031/32: 0.023186; 20 2032/33: 0.023181; 21 2033/34: 0.023175; 22 2034/35: 0.02317; 23 2035/36: 0.023165; 24 2036/37: 0.023159; 25 2037/38: 0.023154; 26 2038/39: 0.023149; 27 2039/40: 0.023143; 28 2040/41: 0.023138; 29 2041/42: 0.023133; 30 2042/43: 0.023127; 31 2043/44: 0.023122; 32 2044/45: 0.023117
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0016286
| Constraint costs | £m | 09/10 |  | 0.043702
| Value of lost load (VOLL) | £m | 09/10 |  | 0.007705
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.30811
| Wholesale gas and electricity price beyond 2024 | £m | 09/10 |  | 0.23108
2.6 | Third party interference
| Probability of event | % |  |  | 0.03125%
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 0.11536
| Cost of intervention | £m | 09/10 |  | 0.0031112
| Constraint costs | £m | 09/10 |  | 0.059378
| Value of lost load (VOLL) | £m | 09/10 |  | 0.010469
| Wholesale gas and electricity price impact for 16 months up to 2024 | £m | 09/10 |  | 0.41863
| Wholesale gas and electricity price impact for 16 months beyond 2024 | £m | 09/10 |  | 0.31397
| Disruption costs | £m | 09/10 |  | 0.0021628
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322
3 | Detailed Working: Constraint costs
3.1 | Constraint costs
| Total constraint costs following isolation/rupture | £m | 16/17 | See footnote 6 | 233.3589
4 | Detailed Workings: Wholesale Gas and Electricity Price Impacts
4.1 | Energy consumption
| Monthy domestic gas consumption | therm |  |  | 846311149.033
| Monthly domestic electricity consumption | therm |  |  | 240695461.8885
4.2 | To 2024
| First month average | £m | 16/17 |  | 91.8115
| Monthly average (excluding first month) | £m | 16/17 |  | 103.5608
4.3 | From 2024 to 2072
| First month average | £m | 16/17 |  | 68.8586
| Monthly average (excluding first month) | £m | 16/17 |  | 77.6706
4.4 | Damage intervention
4.4.1 | Localised mechanical/impact damage leading to repair clamp
| Probability | % |  |  | 0.7
| Expected duration | weeks |  |  | 33.6
| Expected cost | £m | 09/10 |  | 1.4876
4.4.2 | Localised failure leading to short replacement spool
| Probability | % |  |  | 0.175
| Expected duration | weeks |  |  | 12.075
| Expected cost | £m | 09/10 |  | 1.7954
4.4.3 | Extensive failure over pipeline span /rupture leading to long replacement spool
| Probability | % |  |  | 0.075
| Expected duration | weeks |  |  | 5.625
| Expected cost | £m | 09/10 |  | 1.1078
4.4.4 | Tunnel replacement
| Probability | % |  |  | 0.05
| Expected duration | weeks |  |  | 15.6
| Expected cost | £m | 09/10 |  | 5.5649
4.4.4 | Average cost of intervention | £m | 09/10 |  | 9.9557
| Item | Unit | Index | Notes | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 32 | 33 | 34 | 35 | 36 | 37 | 38 | 39 | 40 | 41 | 42 | 43 | 44 | 45 | 46 | 47 | 48 | 49 | 50 | 51 | 52 | 53 | 54 | 55 | 56 | 57 | 58 | 59 | 60 | 61 | 62 | 63 | 64 | 65
[5 empty] | 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | 2026/27 | 2027/28 | 2028/29 | 2029/30 | 2030/31 | 2031/32 | 2032/33 | 2033/34 | 2034/35 | 2035/36 | 2036/37 | 2037/38 | 2038/39 | 2039/40 | 2040/41 | 2041/42 | 2042/43 | 2043/44 | 2044/45 | 2045/46 | 2046/47 | 2047/48 | 2048/49 | 2049/50 | 2050/51 | 2051/52 | 2052/53 | 2053/54 | 2054/55 | 2055/56 | 2056/57 | 2057/58 | 2058/59 | 2059/60 | 2060/61 | 2061/62 | 2062/63 | 2063/64 | 2064/65 | 2065/66 | 2066/67 | 2067/68 | 2068/69 | 2069/70 | 2070/71 | 2071/72 | 2072/73 | 2073/74 | 2074/75 | 2075/76 | 2076/77 | 2077/78
1 | Option: Tunnel 2012
| Revenue impact of construction cost | £m | 09/10 |  | 0.0056228 | 0.30642 | 0.33761 | 2.2178 | 4.5614 | 6.6235 | 4.9886 | 4.7308 | 5.0555 | 5.0929 | 5.1172 | 5.1297 | 5.1319 | 5.1248 | 5.1094 | 5.0866 | 5.0572 | 5.022 | 4.9815 | 4.9364 | 4.8871 | 4.8342 | 4.7779 | 4.7187 | 4.6568 | 4.5926 | 4.5264 | 4.4583 | 4.3885 | 4.3172 | 4.2447 | 4.1709 | 4.0961 | 4.0204 | 3.9439 | 3.8666 | 3.7886 | 3.7101 | 3.631 | 3.5515 | 3.4715 | 3.3912 | 3.3106 | 3.2296 | 3.1484 | 3.067 | 2.9839 | 2.8297 | 2.7041 | 2.1531 | 1.279 | 0.28157 | -0.027348 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Operational costs | £m | 09/10 |  | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.29951 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Mattressing cost | £m | 09/10 |  | 0.21218 | 0.21218 | 0.21218 | 0.21218 | 0.21218 | 0.21218 | 0.21218 | 0.21218 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 0.012306 | 0.012306 | 0.012306 | 0.012306 | 0.012306 | 0.012306 | 0.012306 | 0.012306 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0082848 | 0.0082848 | 0.0082848 | 0.0082848 | 0.0082848 | 0.0082848 | 0.0082848 | 0.0082848 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.22231 | 0.22231 | 0.22231 | 0.22231 | 0.22231 | 0.22231 | 0.22231 | 0.22231 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.039195 | 0.039195 | 0.039195 | 0.039195 | 0.039195 | 0.039195 | 0.039195 | 0.039195 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.28478 | 0.28478 | 0.28478 | 0.28478 | 0.28478 | 0.28478 | 0.28478 | 0.28478 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Freespan (>55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 0.0016286 | 0.0016286 | 0.0016286 | 0.0016286 | 0.0016286 | 0.0016286 | 0.0016286 | 0.0016286 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.043702 | 0.043702 | 0.043702 | 0.043702 | 0.043702 | 0.043702 | 0.043702 | 0.043702 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.007705 | 0.007705 | 0.007705 | 0.007705 | 0.007705 | 0.007705 | 0.007705 | 0.007705 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.30811 | 0.30811 | 0.30811 | 0.30811 | 0.30811 | 0.30811 | 0.30811 | 0.30811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
Third party impact
| Probability adjusted cost associated with possible loss of life |  |  |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Cost of intervention |  |  |  | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0.0031112 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Constraint costs | £m | 09/10 |  | 0.059378 | 0.059378 | 0.059378 | 0.059378 | 0.059378 | 0.059378 | 0.059378 | 0.059378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| VOLL | £m | 09/10 |  | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0.010469 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 0.41863 | 0.41863 | 0.41863 | 0.41863 | 0.41863 | 0.41863 | 0.41863 | 0.41863 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10
| Estuary disruption costs | £m | 09/10 |  | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0.0021628 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Shipwreck clear up costs | £m | 09/10 |  | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0.061322 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total tunnel construction and operation cost | £m | 09/10 |  | 0.30513 | 0.60592 | 0.63712 | 2.5173 | 4.861 | 6.923 | 5.2881 | 5.0303 | 5.1153 | 5.1526 | 5.1769 | 5.1895 | 5.1916 | 5.1845 | 5.1691 | 5.1463 | 5.117 | 5.0817 | 5.0413 | 4.9961 | 4.9469 | 4.8939 | 4.8376 | 4.7784 | 4.7166 | 4.6524 | 4.5861 | 4.518 | 4.4482 | 4.377 | 4.3044 | 4.2307 | 4.1559 | 4.0802 | 4.0036 | 3.9263 | 3.8484 | 3.7698 | 3.6908 | 3.6112 | 3.5313 | 3.451 | 3.3703 | 3.2894 | 3.2081 | 3.1267 | 3.0437 | 2.8894 | 2.7638 | 2.2128 | 1.3388 | 0.34132 | 0.032397 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Total costs (excluding loss of life) | £m | 09/10 |  | 2.0004 | 2.3012 | 2.3324 | 4.2126 | 6.5562 | 8.6183 | 6.9834 | 6.7256 | 5.1153 | 5.1526 | 5.1769 | 5.1895 | 5.1916 | 5.1845 | 5.1691 | 5.1463 | 5.117 | 5.0817 | 5.0413 | 4.9961 | 4.9469 | 4.8939 | 4.8376 | 4.7784 | 4.7166 | 4.6524 | 4.5861 | 4.518 | 4.4482 | 4.377 | 4.3044 | 4.2307 | 4.1559 | 4.0802 | 4.0036 | 3.9263 | 3.8484 | 3.7698 | 3.6908 | 3.6112 | 3.5313 | 3.451 | 3.3703 | 3.2894 | 3.2081 | 3.1267 | 3.0437 | 2.8894 | 2.7638 | 2.2128 | 1.3388 | 0.34132 | 0.032397 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745 | 0.059745
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted total tunnel construction and operation cost | £m | 09/10 |  | 0.29481 | 0.56564 | 0.57464 | 2.1937 | 4.0928 | 5.6319 | 4.1564 | 3.8201 | 3.7532 | 3.6528 | 3.5459 | 3.4343 | 3.3196 | 3.2029 | 3.0854 | 2.9679 | 2.8512 | 2.7358 | 2.6222 | 2.5109 | 2.4021 | 2.296 | 2.1928 | 2.0927 | 1.9958 | 1.9021 | 1.8116 | 1.7243 | 1.6403 | 1.5594 | 1.7217 | 1.6429 | 1.5669 | 1.4935 | 1.4228 | 1.3547 | 1.2891 | 1.226 | 1.1654 | 1.107 | 1.051 | 0.99719 | 0.94552 | 0.89593 | 0.84836 | 0.80274 | 0.75866 | 0.69923 | 0.64936 | 0.50477 | 0.29649 | 0.073387 | 0.0067629 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 1.9328 | 2.1482 | 2.1037 | 3.671 | 5.5202 | 7.011 | 5.4889 | 5.1075 | 3.7532 | 3.6528 | 3.5459 | 3.4343 | 3.3196 | 3.2029 | 3.0854 | 2.9679 | 2.8512 | 2.7358 | 2.6222 | 2.5109 | 2.4021 | 2.296 | 2.1928 | 2.0927 | 1.9958 | 1.9021 | 1.8116 | 1.7243 | 1.6403 | 1.5594 | 1.7217 | 1.6429 | 1.5669 | 1.4935 | 1.4228 | 1.3547 | 1.2891 | 1.226 | 1.1654 | 1.107 | 1.051 | 0.99719 | 0.94552 | 0.89593 | 0.84836 | 0.80274 | 0.75866 | 0.69923 | 0.64936 | 0.50477 | 0.29649 | 0.073387 | 0.0067629 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 2.0464 | 2.2602 | 2.214 | 3.7797 | 5.6273 | 7.1165 | 5.5928 | 5.2099 | 3.7532 | 3.6528 | 3.5459 | 3.4343 | 3.3196 | 3.2029 | 3.0854 | 2.9679 | 2.8512 | 2.7358 | 2.6222 | 2.5109 | 2.4021 | 2.296 | 2.1928 | 2.0927 | 1.9958 | 1.9021 | 1.8116 | 1.7243 | 1.6403 | 1.5594 | 1.7217 | 1.6429 | 1.5669 | 1.4935 | 1.4228 | 1.3547 | 1.2891 | 1.226 | 1.1654 | 1.107 | 1.051 | 0.99719 | 0.94552 | 0.89593 | 0.84836 | 0.80274 | 0.75866 | 0.69923 | 0.64936 | 0.50477 | 0.29649 | 0.073387 | 0.0067629 | 0.012108 | 0.011756 | 0.011413 | 0.011081 | 0.010758 | 0.010445 | 0.010141
| Cumulative discounted tunnel construction and operation cost | £m | 09/10 |  | 0.29481 | 0.86045 | 1.4351 | 3.6288 | 7.7216 | 13.3534 | 17.5098 | 21.3299 | 25.0832 | 28.736 | 32.2819 | 35.7162 | 39.0357 | 42.2386 | 45.324 | 48.2919 | 51.1431 | 53.8789 | 56.5012 | 59.0121 | 61.4141 | 63.7101 | 65.9029 | 67.9957 | 69.9915 | 71.8935 | 73.7051 | 75.4294 | 77.0697 | 78.6291 | 80.3508 | 81.9938 | 83.5606 | 85.0542 | 86.477 | 87.8317 | 89.1208 | 90.3469 | 91.5122 | 92.6193 | 93.6703 | 94.6675 | 95.613 | 96.5089 | 97.3573 | 98.16 | 98.9187 | 99.6179 | 100.2673 | 100.7721 | 101.0685 | 101.1419 | 101.1487 | 101.1608 | 101.1726 | 101.184 | 101.1951 | 101.2058 | 101.2163 | 101.2264
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 1.9328 | 4.081 | 6.1846 | 9.8556 | 15.3758 | 22.3868 | 27.8757 | 32.9832 | 36.7364 | 40.3892 | 43.9351 | 47.3694 | 50.689 | 53.8919 | 56.9773 | 59.9452 | 62.7964 | 65.5322 | 68.1544 | 70.6653 | 73.0674 | 75.3633 | 77.5562 | 79.6489 | 81.6447 | 83.5468 | 85.3583 | 87.0827 | 88.7229 | 90.2824 | 92.0041 | 93.647 | 95.2139 | 96.7074 | 98.1302 | 99.4849 | 100.7741 | 102.0001 | 103.1655 | 104.2725 | 105.3235 | 106.3207 | 107.2662 | 108.1622 | 109.0105 | 109.8133 | 110.5719 | 111.2712 | 111.9205 | 112.4253 | 112.7218 | 112.7952 | 112.8019 | 112.814 | 112.8258 | 112.8372 | 112.8483 | 112.859 | 112.8695 | 112.8796
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359 | 0.86359
| Cumulative total discounted cost | £m | 09/10 |  | 2.0464 | 4.3066 | 6.5206 | 10.3003 | 15.9275 | 23.044 | 28.6368 | 33.8467 | 37.6 | 41.2528 | 44.7987 | 48.233 | 51.5526 | 54.7555 | 57.8408 | 60.8088 | 63.6599 | 66.3957 | 69.018 | 71.5289 | 73.9309 | 76.2269 | 78.4197 | 80.5125 | 82.5083 | 84.4104 | 86.2219 | 87.9462 | 89.5865 | 91.146 | 92.8677 | 94.5106 | 96.0775 | 97.571 | 98.9938 | 100.3485 | 101.6376 | 102.8637 | 104.0291 | 105.1361 | 106.1871 | 107.1843 | 108.1298 | 109.0257 | 109.8741 | 110.6768 | 111.4355 | 112.1347 | 112.7841 | 113.2889 | 113.5854 | 113.6587 | 113.6655 | 113.6776 | 113.6894 | 113.7008 | 113.7119 | 113.7226 | 113.7331 | 113.7432
2 | Option: Mitigate 2044
| Operational costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.29951; 9.9557 2 2014/15: 0.29951; 9.9557 3 2015/16: 0.29951; 9.9557 4 2016/17: 0.29951; 9.9557 5 2017/18: 0.29951; 9.9557 6 2018/19: 0.29951; 9.9557 7 2019/20: 0.29951; 9.9557 8 2020/21: 0.29951; 9.9557 9 2021/22: 0.29598; 9.9557 10 2022/23: 0.29251; 9.9557 11 2023/24: 0.28908; 9.9557 12 2024/25: 0.28571; 9.9557 13 2025/26: 0.28239; 9.9557 14 2026/27: 0.27911; 9.9557 15 2027/28: 0.27588; 9.9557 16 2028/29: 0.2727; 9.9557 17 2029/30: 0.26957; 9.9557 18 2030/31: 0.26648; 9.9557 19 2031/32: 0.26344; 9.9557 20 2032/33: 0.26045; 9.9557 21 2033/34: 0.25749; 9.9557 22 2034/35: 0.25458; 9.9557 23 2035/36: 0.25172; 9.9557 24 2036/37: 0.24889; 9.9557 25 2037/38: 0.24611; 9.9557 26 2038/39: 0.24337; 9.9557 27 2039/40: 0.24067; 9.9557 28 2040/41: 0.23801; 9.9557 29 2041/42: 0.23539; 9.9557 30 2042/43: 0.2328; 9.9557 31 2043/44: 0.23026; 9.9557 32 2044/45: 0.22775
| Loss of lease | £m | 09/10 |  | 9.9557 1 2013/14: 0.97683; 9.9557 2 2014/15: 0.96741; 9.9557 3 2015/16: 0.95807; 9.9557 4 2016/17: 0.94883; 9.9557 5 2017/18: 0.93967; 9.9557 6 2018/19: 0.9306; 9.9557 7 2019/20: 0.92162; 9.9557 8 2020/21: 0.91273; 9.9557 9 2021/22: 0.90392; 9.9557 10 2022/23: 0.8952; 9.9557 11 2023/24: 0.88656; 9.9557 12 2024/25: 0.878; 9.9557 13 2025/26: 0.86953; 9.9557 14 2026/27: 0.86114; 9.9557 15 2027/28: 0.85283; 9.9557 16 2028/29: 0.8446; 9.9557 17 2029/30: 0.83645; 9.9557 18 2030/31: 0.82838; 9.9557 19 2031/32: 0.82039; 9.9557 20 2032/33: 0.81247; 9.9557 21 2033/34: 0.80463; 9.9557 22 2034/35: 0.79686; 9.9557 23 2035/36: 0.78917; 9.9557 24 2036/37: 0.78156; 9.9557 25 2037/38: 0.77402; 9.9557 26 2038/39: 0.76655; 9.9557 27 2039/40: 0.75915; 9.9557 28 2040/41: 0.75182; 9.9557 29 2041/42: 0.74457; 9.9557 30 2042/43: 0.73738; 9.9557 31 2043/44: 0.73027; 9.9557 32 2044/45: 0.72322
| Mattressing cost | £m | 09/10 |  | 9.9557 1 2013/14: 0.21218; 9.9557 2 2014/15: 0.21218; 9.9557 3 2015/16: 0.21218; 9.9557 4 2016/17: 0.21218; 9.9557 5 2017/18: 0.21218; 9.9557 6 2018/19: 0.21218; 9.9557 7 2019/20: 0.21218; 9.9557 8 2020/21: 0.21218; 9.9557 9 2021/22: 0.20906; 9.9557 10 2022/23: 0.20598; 9.9557 11 2023/24: 0.20295; 9.9557 12 2024/25: 0.19997; 9.9557 13 2025/26: 0.19703; 9.9557 14 2026/27: 0.19413; 9.9557 15 2027/28: 0.19127; 9.9557 16 2028/29: 0.18846; 9.9557 17 2029/30: 0.18569; 9.9557 18 2030/31: 0.18295; 9.9557 19 2031/32: 0.18026; 9.9557 20 2032/33: 0.17761; 9.9557 21 2033/34: 0.175; 9.9557 22 2034/35: 0.17242; 9.9557 23 2035/36: 0.16989; 9.9557 24 2036/37: 0.16739; 9.9557 25 2037/38: 0.16493; 9.9557 26 2038/39: 0.1625; 9.9557 27 2039/40: 0.16011; 9.9557 28 2040/41: 0.15775; 9.9557 29 2041/42: 0.15543; 9.9557 30 2042/43: 0.15315; 9.9557 31 2043/44: 0.15089; 9.9557 32 2044/45: 0.14867
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 9.9557 1 2013/14: 0.012306; 9.9557 2 2014/15: 0.012306; 9.9557 3 2015/16: 0.012306; 9.9557 4 2016/17: 0.012306; 9.9557 5 2017/18: 0.012306; 9.9557 6 2018/19: 0.012306; 9.9557 7 2019/20: 0.012306; 9.9557 8 2020/21: 0.012306; 9.9557 9 2021/22: 0.012125; 9.9557 10 2022/23: 0.011947; 9.9557 11 2023/24: 0.011771; 9.9557 12 2024/25: 0.011598; 9.9557 13 2025/26: 0.011428; 9.9557 14 2026/27: 0.011259; 9.9557 15 2027/28: 0.011094; 9.9557 16 2028/29: 0.010931; 9.9557 17 2029/30: 0.01077; 9.9557 18 2030/31: 0.010611; 9.9557 19 2031/32: 0.010455; 9.9557 20 2032/33: 0.010301; 9.9557 21 2033/34: 0.01015; 9.9557 22 2034/35: 0.010001; 9.9557 23 2035/36: 0.0098535; 9.9557 24 2036/37: 0.0097085; 9.9557 25 2037/38: 0.0095657; 9.9557 26 2038/39: 0.009425; 9.9557 27 2039/40: 0.0092863; 9.9557 28 2040/41: 0.0091497; 9.9557 29 2041/42: 0.0090151; 9.9557 30 2042/43: 0.0088825; 9.9557 31 2043/44: 0.0087518; 9.9557 32 2044/45: 0.0086231
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0082848; 9.9557 2 2014/15: 0.0082848; 9.9557 3 2015/16: 0.0082848; 9.9557 4 2016/17: 0.0082848; 9.9557 5 2017/18: 0.0082848; 9.9557 6 2018/19: 0.0082848; 9.9557 7 2019/20: 0.0082848; 9.9557 8 2020/21: 0.0082848; 9.9557 9 2021/22: 0.0081629; 9.9557 10 2022/23: 0.0080428; 9.9557 11 2023/24: 0.0079245; 9.9557 12 2024/25: 0.0078079; 9.9557 13 2025/26: 0.0076931; 9.9557 14 2026/27: 0.0075799; 9.9557 15 2027/28: 0.0074684; 9.9557 16 2028/29: 0.0073585; 9.9557 17 2029/30: 0.0072503; 9.9557 18 2030/31: 0.0071436; 9.9557 19 2031/32: 0.0070385; 9.9557 20 2032/33: 0.006935; 9.9557 21 2033/34: 0.006833; 9.9557 22 2034/35: 0.0067325; 9.9557 23 2035/36: 0.0066334; 9.9557 24 2036/37: 0.0065358; 9.9557 25 2037/38: 0.0064397; 9.9557 26 2038/39: 0.006345; 9.9557 27 2039/40: 0.0062516; 9.9557 28 2040/41: 0.0061596; 9.9557 29 2041/42: 0.006069; 9.9557 30 2042/43: 0.0059798; 9.9557 31 2043/44: 0.0058918; 9.9557 32 2044/45: 0.0058051
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.22231; 9.9557 2 2014/15: 0.22231; 9.9557 3 2015/16: 0.22231; 9.9557 4 2016/17: 0.22231; 9.9557 5 2017/18: 0.22231; 9.9557 6 2018/19: 0.22231; 9.9557 7 2019/20: 0.22231; 9.9557 8 2020/21: 0.22231; 9.9557 9 2021/22: 0.21904; 9.9557 10 2022/23: 0.21582; 9.9557 11 2023/24: 0.21264; 9.9557 12 2024/25: 0.20952; 9.9557 13 2025/26: 0.20643; 9.9557 14 2026/27: 0.2034; 9.9557 15 2027/28: 0.2004; 9.9557 16 2028/29: 0.19746; 9.9557 17 2029/30: 0.19455; 9.9557 18 2030/31: 0.19169; 9.9557 19 2031/32: 0.18887; 9.9557 20 2032/33: 0.18609; 9.9557 21 2033/34: 0.18335; 9.9557 22 2034/35: 0.18066; 9.9557 23 2035/36: 0.178; 9.9557 24 2036/37: 0.17538; 9.9557 25 2037/38: 0.1728; 9.9557 26 2038/39: 0.17026; 9.9557 27 2039/40: 0.16775; 9.9557 28 2040/41: 0.16529; 9.9557 29 2041/42: 0.16286; 9.9557 30 2042/43: 0.16046; 9.9557 31 2043/44: 0.1581; 9.9557 32 2044/45: 0.15577
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.039195; 9.9557 2 2014/15: 0.039195; 9.9557 3 2015/16: 0.039195; 9.9557 4 2016/17: 0.039195; 9.9557 5 2017/18: 0.039195; 9.9557 6 2018/19: 0.039195; 9.9557 7 2019/20: 0.039195; 9.9557 8 2020/21: 0.039195; 9.9557 9 2021/22: 0.038618; 9.9557 10 2022/23: 0.03805; 9.9557 11 2023/24: 0.037491; 9.9557 12 2024/25: 0.036939; 9.9557 13 2025/26: 0.036396; 9.9557 14 2026/27: 0.03586; 9.9557 15 2027/28: 0.035333; 9.9557 16 2028/29: 0.034813; 9.9557 17 2029/30: 0.034301; 9.9557 18 2030/31: 0.033796; 9.9557 19 2031/32: 0.033299; 9.9557 20 2032/33: 0.032809; 9.9557 21 2033/34: 0.032327; 9.9557 22 2034/35: 0.031851; 9.9557 23 2035/36: 0.031382; 9.9557 24 2036/37: 0.030921; 9.9557 25 2037/38: 0.030466; 9.9557 26 2038/39: 0.030018; 9.9557 27 2039/40: 0.029576; 9.9557 28 2040/41: 0.029141; 9.9557 29 2041/42: 0.028712; 9.9557 30 2042/43: 0.02829; 9.9557 31 2043/44: 0.027874; 9.9557 32 2044/45: 0.027464
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.28478; 9.9557 2 2014/15: 0.28478; 9.9557 3 2015/16: 0.28478; 9.9557 4 2016/17: 0.28478; 9.9557 5 2017/18: 0.28478; 9.9557 6 2018/19: 0.28478; 9.9557 7 2019/20: 0.28478; 9.9557 8 2020/21: 0.28478; 9.9557 9 2021/22: 0.28059; 9.9557 10 2022/23: 0.27646; 9.9557 11 2023/24: 0.2724; 9.9557 12 2024/25: 0.26839
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.19833; 9.9557 14 2026/27: 0.19541; 9.9557 15 2027/28: 0.19254; 9.9557 16 2028/29: 0.18971; 9.9557 17 2029/30: 0.18692; 9.9557 18 2030/31: 0.18417; 9.9557 19 2031/32: 0.18146; 9.9557 20 2032/33: 0.17879; 9.9557 21 2033/34: 0.17616; 9.9557 22 2034/35: 0.17357; 9.9557 23 2035/36: 0.17101; 9.9557 24 2036/37: 0.1685; 9.9557 25 2037/38: 0.16602; 9.9557 26 2038/39: 0.16358; 9.9557 27 2039/40: 0.16117; 9.9557 28 2040/41: 0.1588; 9.9557 29 2041/42: 0.15646; 9.9557 30 2042/43: 0.15416; 9.9557 31 2043/44: 0.15189; 9.9557 32 2044/45: 0.14966
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 9.9557 1 2013/14: 0.023282; 9.9557 2 2014/15: 0.023277; 9.9557 3 2015/16: 0.023271; 9.9557 4 2016/17: 0.023266; 9.9557 5 2017/18: 0.023261; 9.9557 6 2018/19: 0.023255; 9.9557 7 2019/20: 0.02325; 9.9557 8 2020/21: 0.023245; 9.9557 9 2021/22: 0.023239; 9.9557 10 2022/23: 0.023234; 9.9557 11 2023/24: 0.023229; 9.9557 12 2024/25: 0.023223; 9.9557 13 2025/26: 0.023218; 9.9557 14 2026/27: 0.023213; 9.9557 15 2027/28: 0.023207; 9.9557 16 2028/29: 0.023202; 9.9557 17 2029/30: 0.023197; 9.9557 18 2030/31: 0.023191; 9.9557 19 2031/32: 0.023186; 9.9557 20 2032/33: 0.023181; 9.9557 21 2033/34: 0.023175; 9.9557 22 2034/35: 0.02317; 9.9557 23 2035/36: 0.023165; 9.9557 24 2036/37: 0.023159; 9.9557 25 2037/38: 0.023154; 9.9557 26 2038/39: 0.023149; 9.9557 27 2039/40: 0.023143; 9.9557 28 2040/41: 0.023138; 9.9557 29 2041/42: 0.023133; 9.9557 30 2042/43: 0.023127; 9.9557 31 2043/44: 0.023122; 9.9557 32 2044/45: 0.023117
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0016286; 9.9557 2 2014/15: 0.0016286; 9.9557 3 2015/16: 0.0016286; 9.9557 4 2016/17: 0.0016286; 9.9557 5 2017/18: 0.0016286; 9.9557 6 2018/19: 0.0016286; 9.9557 7 2019/20: 0.0016286; 9.9557 8 2020/21: 0.0016286; 9.9557 9 2021/22: 0.0016047; 9.9557 10 2022/23: 0.0015811; 9.9557 11 2023/24: 0.0015578; 9.9557 12 2024/25: 0.0015349; 9.9557 13 2025/26: 0.0015123; 9.9557 14 2026/27: 0.0014901; 9.9557 15 2027/28: 0.0014681; 9.9557 16 2028/29: 0.0014465; 9.9557 17 2029/30: 0.0014253; 9.9557 18 2030/31: 0.0014043; 9.9557 19 2031/32: 0.0013836; 9.9557 20 2032/33: 0.0013633; 9.9557 21 2033/34: 0.0013432; 9.9557 22 2034/35: 0.0013235; 9.9557 23 2035/36: 0.001304; 9.9557 24 2036/37: 0.0012848; 9.9557 25 2037/38: 0.0012659; 9.9557 26 2038/39: 0.0012473; 9.9557 27 2039/40: 0.0012289; 9.9557 28 2040/41: 0.0012109; 9.9557 29 2041/42: 0.0011931; 9.9557 30 2042/43: 0.0011755; 9.9557 31 2043/44: 0.0011582; 9.9557 32 2044/45: 0.0011412
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.043702; 9.9557 2 2014/15: 0.043702; 9.9557 3 2015/16: 0.043702; 9.9557 4 2016/17: 0.043702; 9.9557 5 2017/18: 0.043702; 9.9557 6 2018/19: 0.043702; 9.9557 7 2019/20: 0.043702; 9.9557 8 2020/21: 0.043702; 9.9557 9 2021/22: 0.043059; 9.9557 10 2022/23: 0.042426; 9.9557 11 2023/24: 0.041802; 9.9557 12 2024/25: 0.041187; 9.9557 13 2025/26: 0.040581; 9.9557 14 2026/27: 0.039984; 9.9557 15 2027/28: 0.039396; 9.9557 16 2028/29: 0.038816; 9.9557 17 2029/30: 0.038245; 9.9557 18 2030/31: 0.037683; 9.9557 19 2031/32: 0.037128; 9.9557 20 2032/33: 0.036582; 9.9557 21 2033/34: 0.036044; 9.9557 22 2034/35: 0.035514; 9.9557 23 2035/36: 0.034991; 9.9557 24 2036/37: 0.034477; 9.9557 25 2037/38: 0.033969; 9.9557 26 2038/39: 0.03347; 9.9557 27 2039/40: 0.032977; 9.9557 28 2040/41: 0.032492; 9.9557 29 2041/42: 0.032014; 9.9557 30 2042/43: 0.031543; 9.9557 31 2043/44: 0.031079; 9.9557 32 2044/45: 0.030622
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.007705; 9.9557 2 2014/15: 0.007705; 9.9557 3 2015/16: 0.007705; 9.9557 4 2016/17: 0.007705; 9.9557 5 2017/18: 0.007705; 9.9557 6 2018/19: 0.007705; 9.9557 7 2019/20: 0.007705; 9.9557 8 2020/21: 0.007705; 9.9557 9 2021/22: 0.0075917; 9.9557 10 2022/23: 0.00748; 9.9557 11 2023/24: 0.0073699; 9.9557 12 2024/25: 0.0072615; 9.9557 13 2025/26: 0.0071547; 9.9557 14 2026/27: 0.0070495; 9.9557 15 2027/28: 0.0069457; 9.9557 16 2028/29: 0.0068436; 9.9557 17 2029/30: 0.0067429; 9.9557 18 2030/31: 0.0066437; 9.9557 19 2031/32: 0.006546; 9.9557 20 2032/33: 0.0064497; 9.9557 21 2033/34: 0.0063548; 9.9557 22 2034/35: 0.0062613; 9.9557 23 2035/36: 0.0061692; 9.9557 24 2036/37: 0.0060785; 9.9557 25 2037/38: 0.005989; 9.9557 26 2038/39: 0.0059009; 9.9557 27 2039/40: 0.0058141; 9.9557 28 2040/41: 0.0057286; 9.9557 29 2041/42: 0.0056443; 9.9557 30 2042/43: 0.0055613; 9.9557 31 2043/44: 0.0054795; 9.9557 32 2044/45: 0.0053989
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.30811; 9.9557 2 2014/15: 0.30811; 9.9557 3 2015/16: 0.30811; 9.9557 4 2016/17: 0.30811; 9.9557 5 2017/18: 0.30811; 9.9557 6 2018/19: 0.30811; 9.9557 7 2019/20: 0.30811; 9.9557 8 2020/21: 0.30811; 9.9557 9 2021/22: 0.30358; 9.9557 10 2022/23: 0.29911; 9.9557 11 2023/24: 0.29471; 9.9557 12 2024/25: 0.29038
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.21458; 9.9557 14 2026/27: 0.21142; 9.9557 15 2027/28: 0.20831; 9.9557 16 2028/29: 0.20525; 9.9557 17 2029/30: 0.20223; 9.9557 18 2030/31: 0.19925; 9.9557 19 2031/32: 0.19632; 9.9557 20 2032/33: 0.19343; 9.9557 21 2033/34: 0.19059; 9.9557 22 2034/35: 0.18778; 9.9557 23 2035/36: 0.18502; 9.9557 24 2036/37: 0.1823; 9.9557 25 2037/38: 0.17962; 9.9557 26 2038/39: 0.17698; 9.9557 27 2039/40: 0.17437; 9.9557 28 2040/41: 0.17181; 9.9557 29 2041/42: 0.16928; 9.9557 30 2042/43: 0.16679; 9.9557 31 2043/44: 0.16434; 9.9557 32 2044/45: 0.16192
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 9.9557 1 2013/14: 0.0031112; 9.9557 2 2014/15: 0.0031112; 9.9557 3 2015/16: 0.0031112; 9.9557 4 2016/17: 0.0031112; 9.9557 5 2017/18: 0.0031112; 9.9557 6 2018/19: 0.0031112; 9.9557 7 2019/20: 0.0031112; 9.9557 8 2020/21: 0.0031112; 9.9557 9 2021/22: 0.0030654; 9.9557 10 2022/23: 0.0030203; 9.9557 11 2023/24: 0.0029759; 9.9557 12 2024/25: 0.0029321; 9.9557 13 2025/26: 0.002889; 9.9557 14 2026/27: 0.0028465; 9.9557 15 2027/28: 0.0028046; 9.9557 16 2028/29: 0.0027633; 9.9557 17 2029/30: 0.0027227; 9.9557 18 2030/31: 0.0026826; 9.9557 19 2031/32: 0.0026432; 9.9557 20 2032/33: 0.0026043; 9.9557 21 2033/34: 0.002566; 9.9557 22 2034/35: 0.0025282; 9.9557 23 2035/36: 0.002491; 9.9557 24 2036/37: 0.0024544; 9.9557 25 2037/38: 0.0024183; 9.9557 26 2038/39: 0.0023827; 9.9557 27 2039/40: 0.0023477; 9.9557 28 2040/41: 0.0023131; 9.9557 29 2041/42: 0.0022791; 9.9557 30 2042/43: 0.0022456; 9.9557 31 2043/44: 0.0022125; 9.9557 32 2044/45: 0.00218
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.059378; 9.9557 2 2014/15: 0.059378; 9.9557 3 2015/16: 0.059378; 9.9557 4 2016/17: 0.059378; 9.9557 5 2017/18: 0.059378; 9.9557 6 2018/19: 0.059378; 9.9557 7 2019/20: 0.059378; 9.9557 8 2020/21: 0.059378; 9.9557 9 2021/22: 0.058505; 9.9557 10 2022/23: 0.057644; 9.9557 11 2023/24: 0.056796; 9.9557 12 2024/25: 0.05596; 9.9557 13 2025/26: 0.055137; 9.9557 14 2026/27: 0.054326; 9.9557 15 2027/28: 0.053527; 9.9557 16 2028/29: 0.05274; 9.9557 17 2029/30: 0.051964; 9.9557 18 2030/31: 0.051199; 9.9557 19 2031/32: 0.050446; 9.9557 20 2032/33: 0.049704; 9.9557 21 2033/34: 0.048973; 9.9557 22 2034/35: 0.048252; 9.9557 23 2035/36: 0.047543; 9.9557 24 2036/37: 0.046843; 9.9557 25 2037/38: 0.046154; 9.9557 26 2038/39: 0.045475; 9.9557 27 2039/40: 0.044806; 9.9557 28 2040/41: 0.044147; 9.9557 29 2041/42: 0.043498; 9.9557 30 2042/43: 0.042858; 9.9557 31 2043/44: 0.042227; 9.9557 32 2044/45: 0.041606
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.010469; 9.9557 2 2014/15: 0.010469; 9.9557 3 2015/16: 0.010469; 9.9557 4 2016/17: 0.010469; 9.9557 5 2017/18: 0.010469; 9.9557 6 2018/19: 0.010469; 9.9557 7 2019/20: 0.010469; 9.9557 8 2020/21: 0.010469; 9.9557 9 2021/22: 0.010315; 9.9557 10 2022/23: 0.010163; 9.9557 11 2023/24: 0.010014; 9.9557 12 2024/25: 0.0098662; 9.9557 13 2025/26: 0.0097211; 9.9557 14 2026/27: 0.0095781; 9.9557 15 2027/28: 0.0094372; 9.9557 16 2028/29: 0.0092983; 9.9557 17 2029/30: 0.0091615; 9.9557 18 2030/31: 0.0090268; 9.9557 19 2031/32: 0.008894; 9.9557 20 2032/33: 0.0087631; 9.9557 21 2033/34: 0.0086342; 9.9557 22 2034/35: 0.0085072; 9.9557 23 2035/36: 0.0083821; 9.9557 24 2036/37: 0.0082588; 9.9557 25 2037/38: 0.0081373; 9.9557 26 2038/39: 0.0080176; 9.9557 27 2039/40: 0.0078996; 9.9557 28 2040/41: 0.0077834; 9.9557 29 2041/42: 0.0076689; 9.9557 30 2042/43: 0.0075561; 9.9557 31 2043/44: 0.0074449; 9.9557 32 2044/45: 0.0073354
|  | £m | 09/10
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.41863; 9.9557 2 2014/15: 0.41863; 9.9557 3 2015/16: 0.41863; 9.9557 4 2016/17: 0.41863; 9.9557 5 2017/18: 0.41863; 9.9557 6 2018/19: 0.41863; 9.9557 7 2019/20: 0.41863; 9.9557 8 2020/21: 0.41863; 9.9557 9 2021/22: 0.41247; 9.9557 10 2022/23: 0.4064; 9.9557 11 2023/24: 0.40042; 9.9557 12 2024/25: 0.39453
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.29155; 9.9557 14 2026/27: 0.28726; 9.9557 15 2027/28: 0.28303; 9.9557 16 2028/29: 0.27887; 9.9557 17 2029/30: 0.27477; 9.9557 18 2030/31: 0.27072; 9.9557 19 2031/32: 0.26674; 9.9557 20 2032/33: 0.26282; 9.9557 21 2033/34: 0.25895; 9.9557 22 2034/35: 0.25514; 9.9557 23 2035/36: 0.25139; 9.9557 24 2036/37: 0.24769; 9.9557 25 2037/38: 0.24405; 9.9557 26 2038/39: 0.24046; 9.9557 27 2039/40: 0.23692; 9.9557 28 2040/41: 0.23343; 9.9557 29 2041/42: 0.23; 9.9557 30 2042/43: 0.22662; 9.9557 31 2043/44: 0.22328; 9.9557 32 2044/45: 0.22
| Estuary disruption costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.0021628; 9.9557 2 2014/15: 0.0021628; 9.9557 3 2015/16: 0.0021628; 9.9557 4 2016/17: 0.0021628; 9.9557 5 2017/18: 0.0021628; 9.9557 6 2018/19: 0.0021628; 9.9557 7 2019/20: 0.0021628; 9.9557 8 2020/21: 0.0021628; 9.9557 9 2021/22: 0.002131; 9.9557 10 2022/23: 0.0020997; 9.9557 11 2023/24: 0.0020688; 9.9557 12 2024/25: 0.0020383; 9.9557 13 2025/26: 0.0020084; 9.9557 14 2026/27: 0.0019788; 9.9557 15 2027/28: 0.0019497; 9.9557 16 2028/29: 0.001921; 9.9557 17 2029/30: 0.0018928; 9.9557 18 2030/31: 0.0018649; 9.9557 19 2031/32: 0.0018375; 9.9557 20 2032/33: 0.0018104; 9.9557 21 2033/34: 0.0017838; 9.9557 22 2034/35: 0.0017576; 9.9557 23 2035/36: 0.0017317; 9.9557 24 2036/37: 0.0017062; 9.9557 25 2037/38: 0.0016811; 9.9557 26 2038/39: 0.0016564; 9.9557 27 2039/40: 0.001632; 9.9557 28 2040/41: 0.001608; 9.9557 29 2041/42: 0.0015844; 9.9557 30 2042/43: 0.0015611; 9.9557 31 2043/44: 0.0015381; 9.9557 32 2044/45: 0.0015155
| Shipwreck clear up costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.061322; 9.9557 2 2014/15: 0.061322; 9.9557 3 2015/16: 0.061322; 9.9557 4 2016/17: 0.061322; 9.9557 5 2017/18: 0.061322; 9.9557 6 2018/19: 0.061322; 9.9557 7 2019/20: 0.061322; 9.9557 8 2020/21: 0.061322; 9.9557 9 2021/22: 0.06042; 9.9557 10 2022/23: 0.059531; 9.9557 11 2023/24: 0.058656; 9.9557 12 2024/25: 0.057793; 9.9557 13 2025/26: 0.056943; 9.9557 14 2026/27: 0.056105; 9.9557 15 2027/28: 0.05528; 9.9557 16 2028/29: 0.054466; 9.9557 17 2029/30: 0.053665; 9.9557 18 2030/31: 0.052876; 9.9557 19 2031/32: 0.052098; 9.9557 20 2032/33: 0.051332; 9.9557 21 2033/34: 0.050576; 9.9557 22 2034/35: 0.049832; 9.9557 23 2035/36: 0.049099; 9.9557 24 2036/37: 0.048377; 9.9557 25 2037/38: 0.047665; 9.9557 26 2038/39: 0.046964; 9.9557 27 2039/40: 0.046273; 9.9557 28 2040/41: 0.045593; 9.9557 29 2041/42: 0.044922; 9.9557 30 2042/43: 0.044261; 9.9557 31 2043/44: 0.04361; 9.9557 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 2.9949; 9.9557 2 2014/15: 2.9855; 9.9557 3 2015/16: 2.9761; 9.9557 4 2016/17: 2.9669; 9.9557 5 2017/18: 2.9577; 9.9557 6 2018/19: 2.9486; 9.9557 7 2019/20: 2.9397; 9.9557 8 2020/21: 2.9308; 9.9557 9 2021/22: 2.8935; 9.9557 10 2022/23: 2.8567; 9.9557 11 2023/24: 2.8204; 9.9557 12 2024/25: 2.7846; 9.9557 13 2025/26: 2.5145; 9.9557 14 2026/27: 2.4831; 9.9557 15 2027/28: 2.4522; 9.9557 16 2028/29: 2.4216; 9.9557 17 2029/30: 2.3915; 9.9557 18 2030/31: 2.3618; 9.9557 19 2031/32: 2.3324; 9.9557 20 2032/33: 2.3035; 9.9557 21 2033/34: 2.2749; 9.9557 22 2034/35: 2.2468; 9.9557 23 2035/36: 2.2189; 9.9557 24 2036/37: 2.1915; 9.9557 25 2037/38: 2.1644; 9.9557 26 2038/39: 2.1377; 9.9557 27 2039/40: 2.1114; 9.9557 28 2040/41: 2.0854; 9.9557 29 2041/42: 2.0597; 9.9557 30 2042/43: 2.0344; 9.9557 31 2043/44: 2.0094; 9.9557 32 2044/45: 1.9848
| Cost of possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Discount factor for other costs |  |  |  | 9.9557 1 2013/14: 0.96618; 9.9557 2 2014/15: 0.93351; 9.9557 3 2015/16: 0.90194; 9.9557 4 2016/17: 0.87144; 9.9557 5 2017/18: 0.84197; 9.9557 6 2018/19: 0.8135; 9.9557 7 2019/20: 0.78599; 9.9557 8 2020/21: 0.75941; 9.9557 9 2021/22: 0.73373; 9.9557 10 2022/23: 0.70892; 9.9557 11 2023/24: 0.68495; 9.9557 12 2024/25: 0.66178; 9.9557 13 2025/26: 0.6394; 9.9557 14 2026/27: 0.61778; 9.9557 15 2027/28: 0.59689; 9.9557 16 2028/29: 0.57671; 9.9557 17 2029/30: 0.5572; 9.9557 18 2030/31: 0.53836; 9.9557 19 2031/32: 0.52016; 9.9557 20 2032/33: 0.50257; 9.9557 21 2033/34: 0.48557; 9.9557 22 2034/35: 0.46915; 9.9557 23 2035/36: 0.45329; 9.9557 24 2036/37: 0.43796; 9.9557 25 2037/38: 0.42315; 9.9557 26 2038/39: 0.40884; 9.9557 27 2039/40: 0.39501; 9.9557 28 2040/41: 0.38165; 9.9557 29 2041/42: 0.36875; 9.9557 30 2042/43: 0.35628; 9.9557 31 2043/44: 0.39999; 9.9557 32 2044/45: 0.38834
| Discount factor for loss of life costs |  |  |  | 9.9557 1 2013/14: 0.98522; 9.9557 2 2014/15: 0.97066; 9.9557 3 2015/16: 0.95632; 9.9557 4 2016/17: 0.94218; 9.9557 5 2017/18: 0.92826; 9.9557 6 2018/19: 0.91454; 9.9557 7 2019/20: 0.90103; 9.9557 8 2020/21: 0.88771; 9.9557 9 2021/22: 0.87459; 9.9557 10 2022/23: 0.86167; 9.9557 11 2023/24: 0.84893; 9.9557 12 2024/25: 0.83639; 9.9557 13 2025/26: 0.82403; 9.9557 14 2026/27: 0.81185; 9.9557 15 2027/28: 0.79985; 9.9557 16 2028/29: 0.78803; 9.9557 17 2029/30: 0.77639; 9.9557 18 2030/31: 0.76491; 9.9557 19 2031/32: 0.75361; 9.9557 20 2032/33: 0.74247; 9.9557 21 2033/34: 0.7315; 9.9557 22 2034/35: 0.72069; 9.9557 23 2035/36: 0.71004; 9.9557 24 2036/37: 0.69954; 9.9557 25 2037/38: 0.68921; 9.9557 26 2038/39: 0.67902; 9.9557 27 2039/40: 0.66899; 9.9557 28 2040/41: 0.6591; 9.9557 29 2041/42: 0.64936; 9.9557 30 2042/43: 0.63976; 9.9557 31 2043/44: 0.6721; 9.9557 32 2044/45: 0.66354
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 2.8936; 9.9557 2 2014/15: 2.787; 9.9557 3 2015/16: 2.6843; 9.9557 4 2016/17: 2.5855; 9.9557 5 2017/18: 2.4903; 9.9557 6 2018/19: 2.3987; 9.9557 7 2019/20: 2.3105; 9.9557 8 2020/21: 2.2257; 9.9557 9 2021/22: 2.123; 9.9557 10 2022/23: 2.0252; 9.9557 11 2023/24: 1.9318; 9.9557 12 2024/25: 1.8428; 9.9557 13 2025/26: 1.6078; 9.9557 14 2026/27: 1.534; 9.9557 15 2027/28: 1.4637; 9.9557 16 2028/29: 1.3966; 9.9557 17 2029/30: 1.3326; 9.9557 18 2030/31: 1.2715; 9.9557 19 2031/32: 1.2132; 9.9557 20 2032/33: 1.1577; 9.9557 21 2033/34: 1.1046; 9.9557 22 2034/35: 1.0541; 9.9557 23 2035/36: 1.0058; 9.9557 24 2036/37: 0.95979; 9.9557 25 2037/38: 0.91588; 9.9557 26 2038/39: 0.87399; 9.9557 27 2039/40: 0.83402; 9.9557 28 2040/41: 0.79589; 9.9557 29 2041/42: 0.75952; 9.9557 30 2042/43: 0.72481; 9.9557 31 2043/44: 0.80374; 9.9557 32 2044/45: 0.77076
| Discounted cost of loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11366; 9.9557 2 2014/15: 0.11198; 9.9557 3 2015/16: 0.11032; 9.9557 4 2016/17: 0.10869; 9.9557 5 2017/18: 0.10709; 9.9557 6 2018/19: 0.1055; 9.9557 7 2019/20: 0.10394; 9.9557 8 2020/21: 0.10241; 9.9557 9 2021/22: 0.09941; 9.9557 10 2022/23: 0.0965; 9.9557 11 2023/24: 0.093675; 9.9557 12 2024/25: 0.090933; 9.9557 13 2025/26: 0.088272; 9.9557 14 2026/27: 0.085688; 9.9557 15 2027/28: 0.083179; 9.9557 16 2028/29: 0.080745; 9.9557 17 2029/30: 0.078381; 9.9557 18 2030/31: 0.076087; 9.9557 19 2031/32: 0.07386; 9.9557 20 2032/33: 0.071698; 9.9557 21 2033/34: 0.069599; 9.9557 22 2034/35: 0.067562; 9.9557 23 2035/36: 0.065584; 9.9557 24 2036/37: 0.063664; 9.9557 25 2037/38: 0.061801; 9.9557 26 2038/39: 0.059992; 9.9557 27 2039/40: 0.058236; 9.9557 28 2040/41: 0.056531; 9.9557 29 2041/42: 0.054876; 9.9557 30 2042/43: 0.05327; 9.9557 31 2043/44: 0.05514; 9.9557 32 2044/45: 0.053637
| Total discounted cost | £m | 09/10 |  | 9.9557 1 2013/14: 3.0073; 9.9557 2 2014/15: 2.8989; 9.9557 3 2015/16: 2.7946; 9.9557 4 2016/17: 2.6942; 9.9557 5 2017/18: 2.5974; 9.9557 6 2018/19: 2.5042; 9.9557 7 2019/20: 2.4145; 9.9557 8 2020/21: 2.3281; 9.9557 9 2021/22: 2.2224; 9.9557 10 2022/23: 2.1217; 9.9557 11 2023/24: 2.0255; 9.9557 12 2024/25: 1.9338; 9.9557 13 2025/26: 1.6961; 9.9557 14 2026/27: 1.6197; 9.9557 15 2027/28: 1.5469; 9.9557 16 2028/29: 1.4773; 9.9557 17 2029/30: 1.4109; 9.9557 18 2030/31: 1.3476; 9.9557 19 2031/32: 1.2871; 9.9557 20 2032/33: 1.2294; 9.9557 21 2033/34: 1.1742; 9.9557 22 2034/35: 1.1216; 9.9557 23 2035/36: 1.0714; 9.9557 24 2036/37: 1.0235; 9.9557 25 2037/38: 0.97768; 9.9557 26 2038/39: 0.93398; 9.9557 27 2039/40: 0.89226; 9.9557 28 2040/41: 0.85242; 9.9557 29 2041/42: 0.81439; 9.9557 30 2042/43: 0.77808; 9.9557 31 2043/44: 0.85888; 9.9557 32 2044/45: 0.82439
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 9.9557 1 2013/14: 2.8936; 9.9557 2 2014/15: 5.6806; 9.9557 3 2015/16: 8.3649; 9.9557 4 2016/17: 10.9503; 9.9557 5 2017/18: 13.4407; 9.9557 6 2018/19: 15.8394; 9.9557 7 2019/20: 18.1499; 9.9557 8 2020/21: 20.3756; 9.9557 9 2021/22: 22.4986; 9.9557 10 2022/23: 24.5238; 9.9557 11 2023/24: 26.4556; 9.9557 12 2024/25: 28.2984; 9.9557 13 2025/26: 29.9062; 9.9557 14 2026/27: 31.4403; 9.9557 15 2027/28: 32.904; 9.9557 16 2028/29: 34.3005; 9.9557 17 2029/30: 35.6331; 9.9557 18 2030/31: 36.9046; 9.9557 19 2031/32: 38.1178; 9.9557 20 2032/33: 39.2755; 9.9557 21 2033/34: 40.3801; 9.9557 22 2034/35: 41.4342; 9.9557 23 2035/36: 42.44; 9.9557 24 2036/37: 43.3998; 9.9557 25 2037/38: 44.3156; 9.9557 26 2038/39: 45.1896; 9.9557 27 2039/40: 46.0236; 9.9557 28 2040/41: 46.8195; 9.9557 29 2041/42: 47.5791; 9.9557 30 2042/43: 48.3039; 9.9557 31 2043/44: 49.1076; 9.9557 32 2044/45: 49.8784
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11366; 9.9557 2 2014/15: 0.22563; 9.9557 3 2015/16: 0.33596; 9.9557 4 2016/17: 0.44465; 9.9557 5 2017/18: 0.55173; 9.9557 6 2018/19: 0.65724; 9.9557 7 2019/20: 0.76118; 9.9557 8 2020/21: 0.86359; 9.9557 9 2021/22: 0.963; 9.9557 10 2022/23: 1.0595; 9.9557 11 2023/24: 1.1532; 9.9557 12 2024/25: 1.2441; 9.9557 13 2025/26: 1.3324; 9.9557 14 2026/27: 1.4181; 9.9557 15 2027/28: 1.5012; 9.9557 16 2028/29: 1.582; 9.9557 17 2029/30: 1.6604; 9.9557 18 2030/31: 1.7365; 9.9557 19 2031/32: 1.8103; 9.9557 20 2032/33: 1.882; 9.9557 21 2033/34: 1.9516; 9.9557 22 2034/35: 2.0192; 9.9557 23 2035/36: 2.0848; 9.9557 24 2036/37: 2.1484; 9.9557 25 2037/38: 2.2102; 9.9557 26 2038/39: 2.2702; 9.9557 27 2039/40: 2.3284; 9.9557 28 2040/41: 2.385; 9.9557 29 2041/42: 2.4399; 9.9557 30 2042/43: 2.4931; 9.9557 31 2043/44: 2.5483; 9.9557 32 2044/45: 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 9.9557 1 2013/14: 3.0073; 9.9557 2 2014/15: 5.9062; 9.9557 3 2015/16: 8.7008; 9.9557 4 2016/17: 11.395; 9.9557 5 2017/18: 13.9924; 9.9557 6 2018/19: 16.4966; 9.9557 7 2019/20: 18.9111; 9.9557 8 2020/21: 21.2392; 9.9557 9 2021/22: 23.4616; 9.9557 10 2022/23: 25.5833; 9.9557 11 2023/24: 27.6088; 9.9557 12 2024/25: 29.5425; 9.9557 13 2025/26: 31.2386; 9.9557 14 2026/27: 32.8583; 9.9557 15 2027/28: 34.4052; 9.9557 16 2028/29: 35.8825; 9.9557 17 2029/30: 37.2935; 9.9557 18 2030/31: 38.641; 9.9557 19 2031/32: 39.9281; 9.9557 20 2032/33: 41.1575; 9.9557 21 2033/34: 42.3317; 9.9557 22 2034/35: 43.4533; 9.9557 23 2035/36: 44.5247; 9.9557 24 2036/37: 45.5482; 9.9557 25 2037/38: 46.5259; 9.9557 26 2038/39: 47.4598; 9.9557 27 2039/40: 48.3521; 9.9557 28 2040/41: 49.2045; 9.9557 29 2041/42: 50.0189; 9.9557 30 2042/43: 50.797; 9.9557 31 2043/44: 51.6559; 9.9557 32 2044/45: 52.4803
3 | Option: Mitigate with tunnel replacement in 2044
| Revenue impact of tunnel commissioned in 2045/46 | £m | 09/10 | See footnote 5 | 9.9557 25 2037/38: 0.0044358; 9.9557 26 2038/39: 0.24173; 9.9557 27 2039/40: 0.26634; 9.9557 28 2040/41: 1.7496; 9.9557 29 2041/42: 3.5985; 9.9557 30 2042/43: 5.2253; 9.9557 31 2043/44: 3.9355; 9.9557 32 2044/45: 3.7321; 9.9557 33 2045/46: 3.9883; 9.9557 34 2046/47: 4.0178; 9.9557 35 2047/48: 4.0369; 9.9557 36 2048/49: 4.0468; 9.9557 37 2049/50: 4.0485; 9.9557 38 2050/51: 4.0429; 9.9557 39 2051/52: 4.0308; 9.9557 40 2052/53: 4.0128; 9.9557 41 2053/54: 3.9896; 9.9557 42 2054/55: 3.9618; 9.9557 43 2055/56: 3.9299; 9.9557 44 2056/57: 3.8943; 9.9557 45 2057/58: 3.8554; 9.9557 46 2058/59: 3.8137; 9.9557 47 2059/60: 3.7693; 9.9557 48 2060/61: 3.7225; 9.9557 49 2061/62: 3.6738; 9.9557 50 2062/63: 3.6231; 9.9557 51 2063/64: 3.5709; 9.9557 52 2064/65: 3.5171; 9.9557 53 2065/66: 3.4621; 9.9557 54 2066/67: 3.4059; 9.9557 55 2067/68: 3.3486; 9.9557 56 2068/69: 3.2904; 9.9557 57 2069/70: 3.2314; 9.9557 58 2070/71: 3.1717; 9.9557 59 2071/72: 3.1113; 9.9557 60 2072/73: 3.0503
| Operational costs untill 2044/45 | £m | 09/10 |  | 9.9557 1 2013/14: 0.29951; 9.9557 2 2014/15: 0.29951; 9.9557 3 2015/16: 0.29951; 9.9557 4 2016/17: 0.29951; 9.9557 5 2017/18: 0.29951; 9.9557 6 2018/19: 0.29951; 9.9557 7 2019/20: 0.29951; 9.9557 8 2020/21: 0.29951; 9.9557 9 2021/22: 0.29598; 9.9557 10 2022/23: 0.29251; 9.9557 11 2023/24: 0.28908; 9.9557 12 2024/25: 0.28571; 9.9557 13 2025/26: 0.28239; 9.9557 14 2026/27: 0.27911; 9.9557 15 2027/28: 0.27588; 9.9557 16 2028/29: 0.2727; 9.9557 17 2029/30: 0.26957; 9.9557 18 2030/31: 0.26648; 9.9557 19 2031/32: 0.26344; 9.9557 20 2032/33: 0.26045; 9.9557 21 2033/34: 0.25749; 9.9557 22 2034/35: 0.25458; 9.9557 23 2035/36: 0.25172; 9.9557 24 2036/37: 0.24889; 9.9557 25 2037/38: 0.24611; 9.9557 26 2038/39: 0.24337; 9.9557 27 2039/40: 0.24067; 9.9557 28 2040/41: 0.23801; 9.9557 29 2041/42: 0.23539; 9.9557 30 2042/43: 0.2328; 9.9557 31 2043/44: 0.23026; 9.9557 32 2044/45: 0.22775
| Operational costs for tunnel commissioned in 2045/46 |  |  |  | 9.9557 33 2045/46: 0.059745; 9.9557 34 2046/47: 0.059745; 9.9557 35 2047/48: 0.059745; 9.9557 36 2048/49: 0.059745; 9.9557 37 2049/50: 0.059745; 9.9557 38 2050/51: 0.059745; 9.9557 39 2051/52: 0.059745; 9.9557 40 2052/53: 0.059745; 9.9557 41 2053/54: 0.059745; 9.9557 42 2054/55: 0.059745; 9.9557 43 2055/56: 0.059745; 9.9557 44 2056/57: 0.059745; 9.9557 45 2057/58: 0.059745; 9.9557 46 2058/59: 0.059745; 9.9557 47 2059/60: 0.059745; 9.9557 48 2060/61: 0.059745; 9.9557 49 2061/62: 0.059745; 9.9557 50 2062/63: 0.059745; 9.9557 51 2063/64: 0.059745; 9.9557 52 2064/65: 0.059745; 9.9557 53 2065/66: 0.059745; 9.9557 54 2066/67: 0.059745; 9.9557 55 2067/68: 0.059745; 9.9557 56 2068/69: 0.059745; 9.9557 57 2069/70: 0.059745; 9.9557 58 2070/71: 0.059745; 9.9557 59 2071/72: 0.059745; 9.9557 60 2072/73: 0.059745
| Loss of lease | £m | 09/10 |  | 9.9557 1 2013/14: 0.97683; 9.9557 2 2014/15: 0.96741; 9.9557 3 2015/16: 0.95807; 9.9557 4 2016/17: 0.94883; 9.9557 5 2017/18: 0.93967; 9.9557 6 2018/19: 0.9306; 9.9557 7 2019/20: 0.92162; 9.9557 8 2020/21: 0.91273; 9.9557 9 2021/22: 0.90392; 9.9557 10 2022/23: 0.8952; 9.9557 11 2023/24: 0.88656; 9.9557 12 2024/25: 0.878; 9.9557 13 2025/26: 0.86953; 9.9557 14 2026/27: 0.86114; 9.9557 15 2027/28: 0.85283; 9.9557 16 2028/29: 0.8446; 9.9557 17 2029/30: 0.83645; 9.9557 18 2030/31: 0.82838; 9.9557 19 2031/32: 0.82039; 9.9557 20 2032/33: 0.81247; 9.9557 21 2033/34: 0.80463; 9.9557 22 2034/35: 0.79686; 9.9557 23 2035/36: 0.78917; 9.9557 24 2036/37: 0.78156; 9.9557 25 2037/38: 0.77402; 9.9557 26 2038/39: 0.76655; 9.9557 27 2039/40: 0.75915; 9.9557 28 2040/41: 0.75182; 9.9557 29 2041/42: 0.74457; 9.9557 30 2042/43: 0.73738; 9.9557 31 2043/44: 0.73027; 9.9557 32 2044/45: 0.72322
| Mattressing cost | £m | 09/10 |  | 9.9557 1 2013/14: 0.21218; 9.9557 2 2014/15: 0.21218; 9.9557 3 2015/16: 0.21218; 9.9557 4 2016/17: 0.21218; 9.9557 5 2017/18: 0.21218; 9.9557 6 2018/19: 0.21218; 9.9557 7 2019/20: 0.21218; 9.9557 8 2020/21: 0.21218; 9.9557 9 2021/22: 0.20906; 9.9557 10 2022/23: 0.20598; 9.9557 11 2023/24: 0.20295; 9.9557 12 2024/25: 0.19997; 9.9557 13 2025/26: 0.19703; 9.9557 14 2026/27: 0.19413; 9.9557 15 2027/28: 0.19127; 9.9557 16 2028/29: 0.18846; 9.9557 17 2029/30: 0.18569; 9.9557 18 2030/31: 0.18295; 9.9557 19 2031/32: 0.18026; 9.9557 20 2032/33: 0.17761; 9.9557 21 2033/34: 0.175; 9.9557 22 2034/35: 0.17242; 9.9557 23 2035/36: 0.16989; 9.9557 24 2036/37: 0.16739; 9.9557 25 2037/38: 0.16493; 9.9557 26 2038/39: 0.1625; 9.9557 27 2039/40: 0.16011; 9.9557 28 2040/41: 0.15775; 9.9557 29 2041/42: 0.15543; 9.9557 30 2042/43: 0.15315; 9.9557 31 2043/44: 0.15089; 9.9557 32 2044/45: 0.14867
Freespan (<20m)
| Emergency mattressing following freespan | £m | 09/10 |  | 9.9557 1 2013/14: 0.012306; 9.9557 2 2014/15: 0.012306; 9.9557 3 2015/16: 0.012306; 9.9557 4 2016/17: 0.012306; 9.9557 5 2017/18: 0.012306; 9.9557 6 2018/19: 0.012306; 9.9557 7 2019/20: 0.012306; 9.9557 8 2020/21: 0.012306; 9.9557 9 2021/22: 0.012125; 9.9557 10 2022/23: 0.011947; 9.9557 11 2023/24: 0.011771; 9.9557 12 2024/25: 0.011598; 9.9557 13 2025/26: 0.011428; 9.9557 14 2026/27: 0.011259; 9.9557 15 2027/28: 0.011094; 9.9557 16 2028/29: 0.010931; 9.9557 17 2029/30: 0.01077; 9.9557 18 2030/31: 0.010611; 9.9557 19 2031/32: 0.010455; 9.9557 20 2032/33: 0.010301; 9.9557 21 2033/34: 0.01015; 9.9557 22 2034/35: 0.010001; 9.9557 23 2035/36: 0.0098535; 9.9557 24 2036/37: 0.0097085; 9.9557 25 2037/38: 0.0095657; 9.9557 26 2038/39: 0.009425; 9.9557 27 2039/40: 0.0092863; 9.9557 28 2040/41: 0.0091497; 9.9557 29 2041/42: 0.0090151; 9.9557 30 2042/43: 0.0088825; 9.9557 31 2043/44: 0.0087518; 9.9557 32 2044/45: 0.0086231
Freespan (20-55m)
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0082848; 9.9557 2 2014/15: 0.0082848; 9.9557 3 2015/16: 0.0082848; 9.9557 4 2016/17: 0.0082848; 9.9557 5 2017/18: 0.0082848; 9.9557 6 2018/19: 0.0082848; 9.9557 7 2019/20: 0.0082848; 9.9557 8 2020/21: 0.0082848; 9.9557 9 2021/22: 0.0081629; 9.9557 10 2022/23: 0.0080428; 9.9557 11 2023/24: 0.0079245; 9.9557 12 2024/25: 0.0078079; 9.9557 13 2025/26: 0.0076931; 9.9557 14 2026/27: 0.0075799; 9.9557 15 2027/28: 0.0074684; 9.9557 16 2028/29: 0.0073585; 9.9557 17 2029/30: 0.0072503; 9.9557 18 2030/31: 0.0071436; 9.9557 19 2031/32: 0.0070385; 9.9557 20 2032/33: 0.006935; 9.9557 21 2033/34: 0.006833; 9.9557 22 2034/35: 0.0067325; 9.9557 23 2035/36: 0.0066334; 9.9557 24 2036/37: 0.0065358; 9.9557 25 2037/38: 0.0064397; 9.9557 26 2038/39: 0.006345; 9.9557 27 2039/40: 0.0062516; 9.9557 28 2040/41: 0.0061596; 9.9557 29 2041/42: 0.006069; 9.9557 30 2042/43: 0.0059798; 9.9557 31 2043/44: 0.0058918; 9.9557 32 2044/45: 0.0058051
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.22231; 9.9557 2 2014/15: 0.22231; 9.9557 3 2015/16: 0.22231; 9.9557 4 2016/17: 0.22231; 9.9557 5 2017/18: 0.22231; 9.9557 6 2018/19: 0.22231; 9.9557 7 2019/20: 0.22231; 9.9557 8 2020/21: 0.22231; 9.9557 9 2021/22: 0.21904; 9.9557 10 2022/23: 0.21582; 9.9557 11 2023/24: 0.21264; 9.9557 12 2024/25: 0.20952; 9.9557 13 2025/26: 0.20643; 9.9557 14 2026/27: 0.2034; 9.9557 15 2027/28: 0.2004; 9.9557 16 2028/29: 0.19746; 9.9557 17 2029/30: 0.19455; 9.9557 18 2030/31: 0.19169; 9.9557 19 2031/32: 0.18887; 9.9557 20 2032/33: 0.18609; 9.9557 21 2033/34: 0.18335; 9.9557 22 2034/35: 0.18066; 9.9557 23 2035/36: 0.178; 9.9557 24 2036/37: 0.17538; 9.9557 25 2037/38: 0.1728; 9.9557 26 2038/39: 0.17026; 9.9557 27 2039/40: 0.16775; 9.9557 28 2040/41: 0.16529; 9.9557 29 2041/42: 0.16286; 9.9557 30 2042/43: 0.16046; 9.9557 31 2043/44: 0.1581; 9.9557 32 2044/45: 0.15577
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.039195; 9.9557 2 2014/15: 0.039195; 9.9557 3 2015/16: 0.039195; 9.9557 4 2016/17: 0.039195; 9.9557 5 2017/18: 0.039195; 9.9557 6 2018/19: 0.039195; 9.9557 7 2019/20: 0.039195; 9.9557 8 2020/21: 0.039195; 9.9557 9 2021/22: 0.038618; 9.9557 10 2022/23: 0.03805; 9.9557 11 2023/24: 0.037491; 9.9557 12 2024/25: 0.036939; 9.9557 13 2025/26: 0.036396; 9.9557 14 2026/27: 0.03586; 9.9557 15 2027/28: 0.035333; 9.9557 16 2028/29: 0.034813; 9.9557 17 2029/30: 0.034301; 9.9557 18 2030/31: 0.033796; 9.9557 19 2031/32: 0.033299; 9.9557 20 2032/33: 0.032809; 9.9557 21 2033/34: 0.032327; 9.9557 22 2034/35: 0.031851; 9.9557 23 2035/36: 0.031382; 9.9557 24 2036/37: 0.030921; 9.9557 25 2037/38: 0.030466; 9.9557 26 2038/39: 0.030018; 9.9557 27 2039/40: 0.029576; 9.9557 28 2040/41: 0.029141; 9.9557 29 2041/42: 0.028712; 9.9557 30 2042/43: 0.02829; 9.9557 31 2043/44: 0.027874; 9.9557 32 2044/45: 0.027464
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.28478; 9.9557 2 2014/15: 0.28478; 9.9557 3 2015/16: 0.28478; 9.9557 4 2016/17: 0.28478; 9.9557 5 2017/18: 0.28478; 9.9557 6 2018/19: 0.28478; 9.9557 7 2019/20: 0.28478; 9.9557 8 2020/21: 0.28478; 9.9557 9 2021/22: 0.28059; 9.9557 10 2022/23: 0.27646; 9.9557 11 2023/24: 0.2724; 9.9557 12 2024/25: 0.26839
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.19833; 9.9557 14 2026/27: 0.19541; 9.9557 15 2027/28: 0.19254; 9.9557 16 2028/29: 0.18971; 9.9557 17 2029/30: 0.18692; 9.9557 18 2030/31: 0.18417; 9.9557 19 2031/32: 0.18146; 9.9557 20 2032/33: 0.17879; 9.9557 21 2033/34: 0.17616; 9.9557 22 2034/35: 0.17357; 9.9557 23 2035/36: 0.17101; 9.9557 24 2036/37: 0.1685; 9.9557 25 2037/38: 0.16602; 9.9557 26 2038/39: 0.16358; 9.9557 27 2039/40: 0.16117; 9.9557 28 2040/41: 0.1588; 9.9557 29 2041/42: 0.15646; 9.9557 30 2042/43: 0.15416; 9.9557 31 2043/44: 0.15189; 9.9557 32 2044/45: 0.14966
Freespan (>55m)
| Cost of building a replacement tunnel | £m | 09/10 |  | 9.9557 1 2013/14: 0.023282; 9.9557 2 2014/15: 0.023277; 9.9557 3 2015/16: 0.023271; 9.9557 4 2016/17: 0.023266; 9.9557 5 2017/18: 0.023261; 9.9557 6 2018/19: 0.023255; 9.9557 7 2019/20: 0.02325; 9.9557 8 2020/21: 0.023245; 9.9557 9 2021/22: 0.023239; 9.9557 10 2022/23: 0.023234; 9.9557 11 2023/24: 0.023229; 9.9557 12 2024/25: 0.023223; 9.9557 13 2025/26: 0.023218; 9.9557 14 2026/27: 0.023213; 9.9557 15 2027/28: 0.023207; 9.9557 16 2028/29: 0.023202; 9.9557 17 2029/30: 0.023197; 9.9557 18 2030/31: 0.023191; 9.9557 19 2031/32: 0.023186; 9.9557 20 2032/33: 0.023181; 9.9557 21 2033/34: 0.023175; 9.9557 22 2034/35: 0.02317; 9.9557 23 2035/36: 0.023165; 9.9557 24 2036/37: 0.023159; 9.9557 25 2037/38: 0.023154; 9.9557 26 2038/39: 0.023149; 9.9557 27 2039/40: 0.023143; 9.9557 28 2040/41: 0.023138; 9.9557 29 2041/42: 0.023133; 9.9557 30 2042/43: 0.023127; 9.9557 31 2043/44: 0.023122; 9.9557 32 2044/45: 0.023117
| Cost of emergency mattressing - major | £m | 09/10 |  | 9.9557 1 2013/14: 0.0016286; 9.9557 2 2014/15: 0.0016286; 9.9557 3 2015/16: 0.0016286; 9.9557 4 2016/17: 0.0016286; 9.9557 5 2017/18: 0.0016286; 9.9557 6 2018/19: 0.0016286; 9.9557 7 2019/20: 0.0016286; 9.9557 8 2020/21: 0.0016286; 9.9557 9 2021/22: 0.0016047; 9.9557 10 2022/23: 0.0015811; 9.9557 11 2023/24: 0.0015578; 9.9557 12 2024/25: 0.0015349; 9.9557 13 2025/26: 0.0015123; 9.9557 14 2026/27: 0.0014901; 9.9557 15 2027/28: 0.0014681; 9.9557 16 2028/29: 0.0014465; 9.9557 17 2029/30: 0.0014253; 9.9557 18 2030/31: 0.0014043; 9.9557 19 2031/32: 0.0013836; 9.9557 20 2032/33: 0.0013633; 9.9557 21 2033/34: 0.0013432; 9.9557 22 2034/35: 0.0013235; 9.9557 23 2035/36: 0.001304; 9.9557 24 2036/37: 0.0012848; 9.9557 25 2037/38: 0.0012659; 9.9557 26 2038/39: 0.0012473; 9.9557 27 2039/40: 0.0012289; 9.9557 28 2040/41: 0.0012109; 9.9557 29 2041/42: 0.0011931; 9.9557 30 2042/43: 0.0011755; 9.9557 31 2043/44: 0.0011582; 9.9557 32 2044/45: 0.0011412
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.043702; 9.9557 2 2014/15: 0.043702; 9.9557 3 2015/16: 0.043702; 9.9557 4 2016/17: 0.043702; 9.9557 5 2017/18: 0.043702; 9.9557 6 2018/19: 0.043702; 9.9557 7 2019/20: 0.043702; 9.9557 8 2020/21: 0.043702; 9.9557 9 2021/22: 0.043059; 9.9557 10 2022/23: 0.042426; 9.9557 11 2023/24: 0.041802; 9.9557 12 2024/25: 0.041187; 9.9557 13 2025/26: 0.040581; 9.9557 14 2026/27: 0.039984; 9.9557 15 2027/28: 0.039396; 9.9557 16 2028/29: 0.038816; 9.9557 17 2029/30: 0.038245; 9.9557 18 2030/31: 0.037683; 9.9557 19 2031/32: 0.037128; 9.9557 20 2032/33: 0.036582; 9.9557 21 2033/34: 0.036044; 9.9557 22 2034/35: 0.035514; 9.9557 23 2035/36: 0.034991; 9.9557 24 2036/37: 0.034477; 9.9557 25 2037/38: 0.033969; 9.9557 26 2038/39: 0.03347; 9.9557 27 2039/40: 0.032977; 9.9557 28 2040/41: 0.032492; 9.9557 29 2041/42: 0.032014; 9.9557 30 2042/43: 0.031543; 9.9557 31 2043/44: 0.031079; 9.9557 32 2044/45: 0.030622
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.007705; 9.9557 2 2014/15: 0.007705; 9.9557 3 2015/16: 0.007705; 9.9557 4 2016/17: 0.007705; 9.9557 5 2017/18: 0.007705; 9.9557 6 2018/19: 0.007705; 9.9557 7 2019/20: 0.007705; 9.9557 8 2020/21: 0.007705; 9.9557 9 2021/22: 0.0075917; 9.9557 10 2022/23: 0.00748; 9.9557 11 2023/24: 0.0073699; 9.9557 12 2024/25: 0.0072615; 9.9557 13 2025/26: 0.0071547; 9.9557 14 2026/27: 0.0070495; 9.9557 15 2027/28: 0.0069457; 9.9557 16 2028/29: 0.0068436; 9.9557 17 2029/30: 0.0067429; 9.9557 18 2030/31: 0.0066437; 9.9557 19 2031/32: 0.006546; 9.9557 20 2032/33: 0.0064497; 9.9557 21 2033/34: 0.0063548; 9.9557 22 2034/35: 0.0062613; 9.9557 23 2035/36: 0.0061692; 9.9557 24 2036/37: 0.0060785; 9.9557 25 2037/38: 0.005989; 9.9557 26 2038/39: 0.0059009; 9.9557 27 2039/40: 0.0058141; 9.9557 28 2040/41: 0.0057286; 9.9557 29 2041/42: 0.0056443; 9.9557 30 2042/43: 0.0055613; 9.9557 31 2043/44: 0.0054795; 9.9557 32 2044/45: 0.0053989
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.30811; 9.9557 2 2014/15: 0.30811; 9.9557 3 2015/16: 0.30811; 9.9557 4 2016/17: 0.30811; 9.9557 5 2017/18: 0.30811; 9.9557 6 2018/19: 0.30811; 9.9557 7 2019/20: 0.30811; 9.9557 8 2020/21: 0.30811; 9.9557 9 2021/22: 0.30358; 9.9557 10 2022/23: 0.29911; 9.9557 11 2023/24: 0.29471; 9.9557 12 2024/25: 0.29038
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.21458; 9.9557 14 2026/27: 0.21142; 9.9557 15 2027/28: 0.20831; 9.9557 16 2028/29: 0.20525; 9.9557 17 2029/30: 0.20223; 9.9557 18 2030/31: 0.19925; 9.9557 19 2031/32: 0.19632; 9.9557 20 2032/33: 0.19343; 9.9557 21 2033/34: 0.19059; 9.9557 22 2034/35: 0.18778; 9.9557 23 2035/36: 0.18502; 9.9557 24 2036/37: 0.1823; 9.9557 25 2037/38: 0.17962; 9.9557 26 2038/39: 0.17698; 9.9557 27 2039/40: 0.17437; 9.9557 28 2040/41: 0.17181; 9.9557 29 2041/42: 0.16928; 9.9557 30 2042/43: 0.16679; 9.9557 31 2043/44: 0.16434; 9.9557 32 2044/45: 0.16192
Third party impact
| Probability adjusted cost associated with possible loss of life | £m | 09/10 |  | 9.9557 1 2013/14: 0.11536; 9.9557 2 2014/15: 0.11536; 9.9557 3 2015/16: 0.11536; 9.9557 4 2016/17: 0.11536; 9.9557 5 2017/18: 0.11536; 9.9557 6 2018/19: 0.11536; 9.9557 7 2019/20: 0.11536; 9.9557 8 2020/21: 0.11536; 9.9557 9 2021/22: 0.11366; 9.9557 10 2022/23: 0.11199; 9.9557 11 2023/24: 0.11034; 9.9557 12 2024/25: 0.10872; 9.9557 13 2025/26: 0.10712; 9.9557 14 2026/27: 0.10555; 9.9557 15 2027/28: 0.10399; 9.9557 16 2028/29: 0.10246; 9.9557 17 2029/30: 0.10096; 9.9557 18 2030/31: 0.099471; 9.9557 19 2031/32: 0.098008; 9.9557 20 2032/33: 0.096566; 9.9557 21 2033/34: 0.095146; 9.9557 22 2034/35: 0.093746; 9.9557 23 2035/36: 0.092367; 9.9557 24 2036/37: 0.091008; 9.9557 25 2037/38: 0.089669; 9.9557 26 2038/39: 0.08835; 9.9557 27 2039/40: 0.087051; 9.9557 28 2040/41: 0.08577; 9.9557 29 2041/42: 0.084508; 9.9557 30 2042/43: 0.083265; 9.9557 31 2043/44: 0.08204; 9.9557 32 2044/45: 0.080833
| Cost of intervention | £m | 09/10 |  | 9.9557 1 2013/14: 0.0031112; 9.9557 2 2014/15: 0.0031112; 9.9557 3 2015/16: 0.0031112; 9.9557 4 2016/17: 0.0031112; 9.9557 5 2017/18: 0.0031112; 9.9557 6 2018/19: 0.0031112; 9.9557 7 2019/20: 0.0031112; 9.9557 8 2020/21: 0.0031112; 9.9557 9 2021/22: 0.0030654; 9.9557 10 2022/23: 0.0030203; 9.9557 11 2023/24: 0.0029759; 9.9557 12 2024/25: 0.0029321; 9.9557 13 2025/26: 0.002889; 9.9557 14 2026/27: 0.0028465; 9.9557 15 2027/28: 0.0028046; 9.9557 16 2028/29: 0.0027633; 9.9557 17 2029/30: 0.0027227; 9.9557 18 2030/31: 0.0026826; 9.9557 19 2031/32: 0.0026432; 9.9557 20 2032/33: 0.0026043; 9.9557 21 2033/34: 0.002566; 9.9557 22 2034/35: 0.0025282; 9.9557 23 2035/36: 0.002491; 9.9557 24 2036/37: 0.0024544; 9.9557 25 2037/38: 0.0024183; 9.9557 26 2038/39: 0.0023827; 9.9557 27 2039/40: 0.0023477; 9.9557 28 2040/41: 0.0023131; 9.9557 29 2041/42: 0.0022791; 9.9557 30 2042/43: 0.0022456; 9.9557 31 2043/44: 0.0022125; 9.9557 32 2044/45: 0.00218
| Constraint costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.059378; 9.9557 2 2014/15: 0.059378; 9.9557 3 2015/16: 0.059378; 9.9557 4 2016/17: 0.059378; 9.9557 5 2017/18: 0.059378; 9.9557 6 2018/19: 0.059378; 9.9557 7 2019/20: 0.059378; 9.9557 8 2020/21: 0.059378; 9.9557 9 2021/22: 0.058505; 9.9557 10 2022/23: 0.057644; 9.9557 11 2023/24: 0.056796; 9.9557 12 2024/25: 0.05596; 9.9557 13 2025/26: 0.055137; 9.9557 14 2026/27: 0.054326; 9.9557 15 2027/28: 0.053527; 9.9557 16 2028/29: 0.05274; 9.9557 17 2029/30: 0.051964; 9.9557 18 2030/31: 0.051199; 9.9557 19 2031/32: 0.050446; 9.9557 20 2032/33: 0.049704; 9.9557 21 2033/34: 0.048973; 9.9557 22 2034/35: 0.048252; 9.9557 23 2035/36: 0.047543; 9.9557 24 2036/37: 0.046843; 9.9557 25 2037/38: 0.046154; 9.9557 26 2038/39: 0.045475; 9.9557 27 2039/40: 0.044806; 9.9557 28 2040/41: 0.044147; 9.9557 29 2041/42: 0.043498; 9.9557 30 2042/43: 0.042858; 9.9557 31 2043/44: 0.042227; 9.9557 32 2044/45: 0.041606
| VOLL | £m | 09/10 |  | 9.9557 1 2013/14: 0.010469; 9.9557 2 2014/15: 0.010469; 9.9557 3 2015/16: 0.010469; 9.9557 4 2016/17: 0.010469; 9.9557 5 2017/18: 0.010469; 9.9557 6 2018/19: 0.010469; 9.9557 7 2019/20: 0.010469; 9.9557 8 2020/21: 0.010469; 9.9557 9 2021/22: 0.010315; 9.9557 10 2022/23: 0.010163; 9.9557 11 2023/24: 0.010014; 9.9557 12 2024/25: 0.0098662; 9.9557 13 2025/26: 0.0097211; 9.9557 14 2026/27: 0.0095781; 9.9557 15 2027/28: 0.0094372; 9.9557 16 2028/29: 0.0092983; 9.9557 17 2029/30: 0.0091615; 9.9557 18 2030/31: 0.0090268; 9.9557 19 2031/32: 0.008894; 9.9557 20 2032/33: 0.0087631; 9.9557 21 2033/34: 0.0086342; 9.9557 22 2034/35: 0.0085072; 9.9557 23 2035/36: 0.0083821; 9.9557 24 2036/37: 0.0082588; 9.9557 25 2037/38: 0.0081373; 9.9557 26 2038/39: 0.0080176; 9.9557 27 2039/40: 0.0078996; 9.9557 28 2040/41: 0.0077834; 9.9557 29 2041/42: 0.0076689; 9.9557 30 2042/43: 0.0075561; 9.9557 31 2043/44: 0.0074449; 9.9557 32 2044/45: 0.0073354
| Wholesale gas and electricity price impact up to 2024 | £m | 09/10 |  | 9.9557 1 2013/14: 0.41863; 9.9557 2 2014/15: 0.41863; 9.9557 3 2015/16: 0.41863; 9.9557 4 2016/17: 0.41863; 9.9557 5 2017/18: 0.41863; 9.9557 6 2018/19: 0.41863; 9.9557 7 2019/20: 0.41863; 9.9557 8 2020/21: 0.41863; 9.9557 9 2021/22: 0.41247; 9.9557 10 2022/23: 0.4064; 9.9557 11 2023/24: 0.40042; 9.9557 12 2024/25: 0.39453
| Wholesale gas and electricity price impact beyond 2024 | £m | 09/10 |  | 9.9557 13 2025/26: 0.29155; 9.9557 14 2026/27: 0.28726; 9.9557 15 2027/28: 0.28303; 9.9557 16 2028/29: 0.27887; 9.9557 17 2029/30: 0.27477; 9.9557 18 2030/31: 0.27072; 9.9557 19 2031/32: 0.26674; 9.9557 20 2032/33: 0.26282; 9.9557 21 2033/34: 0.25895; 9.9557 22 2034/35: 0.25514; 9.9557 23 2035/36: 0.25139; 9.9557 24 2036/37: 0.24769; 9.9557 25 2037/38: 0.24405; 9.9557 26 2038/39: 0.24046; 9.9557 27 2039/40: 0.23692; 9.9557 28 2040/41: 0.23343; 9.9557 29 2041/42: 0.23; 9.9557 30 2042/43: 0.22662; 9.9557 31 2043/44: 0.22328; 9.9557 32 2044/45: 0.22
| Estuary disruption costs | £m | 09/10 |  | 9.9557 1 2013/14: 0.0021628; 9.9557 2 2014/15: 0.0021628; 9.9557 3 2015/16: 0.0021628; 9.9557 4 2016/17: 0.0021628; 9.9557 5 2017/18: 0.0021628; 9.9557 6 2018/19: 0.0021628; 9.9557 7 2019/20: 0.0021628; 9.9557 8 2020/21: 0.0021628; 9.9557 9 2021/22: 0.002131; 9.9557 10 2022/23: 0.0020997; 9.9557 11 2023/24: 0.0020688; 9.9557 12 2024/25: 0.0020383; 9.9557 13 2025/26: 0.0020084; 9.9557 14 2026/27: 0.0019788; 9.9557 15 2027/28: 0.0019497; 9.9557 16 2028/29: 0.001921; 9.9557 17 2029/30: 0.0018928; 9.9557 18 2030/31: 0.0018649; 9.9557 19 2031/32: 0.0018375; 9.9557 20 2032/33: 0.0018104; 9.9557 21 2033/34: 0.0017838; 9.9557 22 2034/35: 0.0017576; 9.9557 23 2035/36: 0.0017317; 9.9557 24 2036/37: 0.0017062; 9.9557 25 2037/38: 0.0016811; 9.9557 26 2038/39: 0.0016564; 9.9557 27 2039/40: 0.001632; 9.9557 28 2040/41: 0.001608; 9.9557 29 2041/42: 0.0015844; 9.9557 30 2042/43: 0.0015611; 9.9557 31 2043/44: 0.0015381; 9.9557 32 2044/45: 0.0015155
| Shipwreck clear up costs (£m) (09/10 prices) | £m | 09/10 |  | 9.9557 1 2013/14: 0.061322; 9.9557 2 2014/15: 0.061322; 9.9557 3 2015/16: 0.061322; 9.9557 4 2016/17: 0.061322; 9.9557 5 2017/18: 0.061322; 9.9557 6 2018/19: 0.061322; 9.9557 7 2019/20: 0.061322; 9.9557 8 2020/21: 0.061322; 9.9557 9 2021/22: 0.06042; 9.9557 10 2022/23: 0.059531; 9.9557 11 2023/24: 0.058656; 9.9557 12 2024/25: 0.057793; 9.9557 13 2025/26: 0.056943; 9.9557 14 2026/27: 0.056105; 9.9557 15 2027/28: 0.05528; 9.9557 16 2028/29: 0.054466; 9.9557 17 2029/30: 0.053665; 9.9557 18 2030/31: 0.052876; 9.9557 19 2031/32: 0.052098; 9.9557 20 2032/33: 0.051332; 9.9557 21 2033/34: 0.050576; 9.9557 22 2034/35: 0.049832; 9.9557 23 2035/36: 0.049099; 9.9557 24 2036/37: 0.048377; 9.9557 25 2037/38: 0.047665; 9.9557 26 2038/39: 0.046964; 9.9557 27 2039/40: 0.046273; 9.9557 28 2040/41: 0.045593; 9.9557 29 2041/42: 0.044922; 9.9557 30 2042/43: 0.044261; 9.9557 31 2043/44: 0.04361; 9.9557 32 2044/45: 0.042968
| Total costs (excluding loss of life) | £m | 09/10 |  | 2.9949 | 2.9855 | 2.9761 | 2.9669 | 2.9577 | 2.9486 | 2.9397 | 2.9308 | 2.8935 | 2.8567 | 2.8204 | 2.7846 | 2.5145 | 2.4831 | 2.4522 | 2.4216 | 2.3915 | 2.3618 | 2.3324 | 2.3035 | 2.2749 | 2.2468 | 2.2189 | 2.1915 | 2.1689 | 2.3795 | 2.3777 | 3.835 | 5.6582 | 7.2597 | 5.9449 | 5.7169 | 4.048 | 4.0775 | 4.0967 | 4.1066 | 4.1083 | 4.1027 | 4.0905 | 4.0725 | 4.0494 | 4.0216 | 3.9897 | 3.9541 | 3.9152 | 3.8734 | 3.829 | 3.7823 | 3.7335 | 3.6829 | 3.6306 | 3.5769 | 3.5218 | 3.4656 | 3.4083 | 3.3502 | 3.2912 | 3.2314 | 3.171 | 3.1101
| Cost of possible loss of life | £m | 09/10 |  | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11536 | 0.11366 | 0.11199 | 0.11034 | 0.10872 | 0.10712 | 0.10555 | 0.10399 | 0.10246 | 0.10096 | 0.099471 | 0.098008 | 0.096566 | 0.095146 | 0.093746 | 0.092367 | 0.091008 | 0.089669 | 0.08835 | 0.087051 | 0.08577 | 0.084508 | 0.083265 | 0.08204 | 0.080833 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Discount factor for other costs |  |  |  | 0.96618 | 0.93351 | 0.90194 | 0.87144 | 0.84197 | 0.8135 | 0.78599 | 0.75941 | 0.73373 | 0.70892 | 0.68495 | 0.66178 | 0.6394 | 0.61778 | 0.59689 | 0.57671 | 0.5572 | 0.53836 | 0.52016 | 0.50257 | 0.48557 | 0.46915 | 0.45329 | 0.43796 | 0.42315 | 0.40884 | 0.39501 | 0.38165 | 0.36875 | 0.35628 | 0.39999 | 0.38834 | 0.37703 | 0.36604 | 0.35538 | 0.34503 | 0.33498 | 0.32523 | 0.31575 | 0.30656 | 0.29763 | 0.28896 | 0.28054 | 0.27237 | 0.26444 | 0.25674 | 0.24926 | 0.242 | 0.23495 | 0.22811 | 0.22146 | 0.21501 | 0.20875 | 0.20267 | 0.19677 | 0.19104 | 0.18547 | 0.18007 | 0.17483 | 0.16973
| Discount factor for loss of life costs |  |  |  | 0.98522 | 0.97066 | 0.95632 | 0.94218 | 0.92826 | 0.91454 | 0.90103 | 0.88771 | 0.87459 | 0.86167 | 0.84893 | 0.83639 | 0.82403 | 0.81185 | 0.79985 | 0.78803 | 0.77639 | 0.76491 | 0.75361 | 0.74247 | 0.7315 | 0.72069 | 0.71004 | 0.69954 | 0.68921 | 0.67902 | 0.66899 | 0.6591 | 0.64936 | 0.63976 | 0.6721 | 0.66354 | 0.65509 | 0.64675 | 0.63851 | 0.63038 | 0.62235 | 0.61443 | 0.6066 | 0.59888 | 0.59125 | 0.58372 | 0.57629 | 0.56895 | 0.5617 | 0.55455 | 0.54748 | 0.54051 | 0.53363 | 0.52683 | 0.52012 | 0.5135 | 0.50696 | 0.5005 | 0.49413 | 0.48783 | 0.48162 | 0.47549 | 0.46943 | 0.46345
| Discounted costs (excluding loss of life) | £m | 09/10 |  | 2.8936 | 2.787 | 2.6843 | 2.5855 | 2.4903 | 2.3987 | 2.3105 | 2.2257 | 2.123 | 2.0252 | 1.9318 | 1.8428 | 1.6078 | 1.534 | 1.4637 | 1.3966 | 1.3326 | 1.2715 | 1.2132 | 1.1577 | 1.1046 | 1.0541 | 1.0058 | 0.95979 | 0.91775 | 0.97281 | 0.93923 | 1.4636 | 2.0865 | 2.5865 | 2.3779 | 2.2201 | 1.5262 | 1.4926 | 1.4559 | 1.4169 | 1.3762 | 1.3343 | 1.2916 | 1.2485 | 1.2052 | 1.1621 | 1.1193 | 1.077 | 1.0353 | 0.99444 | 0.95441 | 0.91531 | 0.87719 | 0.84009 | 0.80404 | 0.76907 | 0.73518 | 0.70237 | 0.67065 | 0.64 | 0.61042 | 0.58188 | 0.55438 | 0.52788
| Discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.11198 | 0.11032 | 0.10869 | 0.10709 | 0.1055 | 0.10394 | 0.10241 | 0.09941 | 0.0965 | 0.093675 | 0.090933 | 0.088272 | 0.085688 | 0.083179 | 0.080745 | 0.078381 | 0.076087 | 0.07386 | 0.071698 | 0.069599 | 0.067562 | 0.065584 | 0.063664 | 0.061801 | 0.059992 | 0.058236 | 0.056531 | 0.054876 | 0.05327 | 0.05514 | 0.053637 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Total discounted cost | £m | 09/10 |  | 3.0073 | 2.8989 | 2.7946 | 2.6942 | 2.5974 | 2.5042 | 2.4145 | 2.3281 | 2.2224 | 2.1217 | 2.0255 | 1.9338 | 1.6961 | 1.6197 | 1.5469 | 1.4773 | 1.4109 | 1.3476 | 1.2871 | 1.2294 | 1.1742 | 1.1216 | 1.0714 | 1.0235 | 0.97956 | 1.0328 | 0.99746 | 1.5202 | 2.1413 | 2.6397 | 2.433 | 2.2737 | 1.5262 | 1.4926 | 1.4559 | 1.4169 | 1.3762 | 1.3343 | 1.2916 | 1.2485 | 1.2052 | 1.1621 | 1.1193 | 1.077 | 1.0353 | 0.99444 | 0.95441 | 0.91531 | 0.87719 | 0.84009 | 0.80404 | 0.76907 | 0.73518 | 0.70237 | 0.67065 | 0.64 | 0.61042 | 0.58188 | 0.55438 | 0.52788
| Cumulative discounted costs (excluding loss of life) | £m | 09/10 |  | 2.8936 | 5.6806 | 8.3649 | 10.9503 | 13.4407 | 15.8394 | 18.1499 | 20.3756 | 22.4986 | 24.5238 | 26.4556 | 28.2984 | 29.9062 | 31.4403 | 32.904 | 34.3005 | 35.6331 | 36.9046 | 38.1178 | 39.2755 | 40.3801 | 41.4342 | 42.44 | 43.3998 | 44.3175 | 45.2903 | 46.2296 | 47.6932 | 49.7797 | 52.3661 | 54.744 | 56.9641 | 58.4903 | 59.9829 | 61.4387 | 62.8556 | 64.2318 | 65.5661 | 66.8577 | 68.1062 | 69.3114 | 70.4735 | 71.5927 | 72.6697 | 73.705 | 74.6995 | 75.6539 | 76.5692 | 77.4464 | 78.2865 | 79.0905 | 79.8596 | 80.5948 | 81.2971 | 81.9678 | 82.6078 | 83.2182 | 83.8001 | 84.3545 | 84.8824
| Cumulative discounted cost of loss of life | £m | 09/10 |  | 0.11366 | 0.22563 | 0.33596 | 0.44465 | 0.55173 | 0.65724 | 0.76118 | 0.86359 | 0.963 | 1.0595 | 1.1532 | 1.2441 | 1.3324 | 1.4181 | 1.5012 | 1.582 | 1.6604 | 1.7365 | 1.8103 | 1.882 | 1.9516 | 2.0192 | 2.0848 | 2.1484 | 2.2102 | 2.2702 | 2.3284 | 2.385 | 2.4399 | 2.4931 | 2.5483 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019 | 2.6019
| Cumulative total discounted cost | £m | 09/10 |  | 3.0073 | 5.9062 | 8.7008 | 11.395 | 13.9924 | 16.4966 | 18.9111 | 21.2392 | 23.4616 | 25.5833 | 27.6088 | 29.5425 | 31.2386 | 32.8583 | 34.4052 | 35.8825 | 37.2935 | 38.641 | 39.9281 | 41.1575 | 42.3317 | 43.4533 | 44.5247 | 45.5482 | 46.5277 | 47.5605 | 48.558 | 50.0782 | 52.2195 | 54.8592 | 57.2923 | 59.566 | 61.0922 | 62.5848 | 64.0406 | 65.4575 | 66.8338 | 68.168 | 69.4596 | 70.7081 | 71.9133 | 73.0754 | 74.1946 | 75.2716 | 76.3069 | 77.3014 | 78.2558 | 79.1711 | 80.0483 | 80.8884 | 81.6924 | 82.4615 | 83.1967 | 83.899 | 84.5697 | 85.2097 | 85.8201 | 86.402 | 86.9564 | 87.4843

## OUTPUT¦ Summary results
RESULTS
|  |  |  | Scenario 1 |  | Scenario 2 |  | Scenario 3
|  |  |  | Tunnel costs, £m | 139.887 | Tunnel costs, £m | 111.299 | Tunnel costs, £m | 111.299
|  |  |  | Probabilities | NGGT | Probabilities | High | Probabilities | Low
|  |  |  | WACC | 4.375% | WACC | 1.27% | WACC | 3.615%
1 | Cumulative Net Present Costs (NPC)
|  |  |  | NPC horizon |  | NPC horizon |  | NPC horizon
|  |  |  | 2044 | 2072 | 2044 | 2072 | 2044 | 2072
| Option 1: Tunnel in 2012 | £m | 09/10 | 365.7402 | 386.3287 | 96.7318 | 112.753 | 94.5106 | 113.7432
| Option 2: Mitigation upto 2044 | £m | 09/10 | 653.5649 |  | 109.4069 |  | 52.4803
| Option 3: Mitigation upto 2044 then tunnel | £m | 09/10 | 663.1513 | 699.7635 | 116.4926 | 134.1023 | 59.566 | 87.4843
2 | NPC of option relative to Option 1
|  |  |  | NPC horizon |  | NPC horizon |  | NPC horizon
|  |  |  | 2044 | 2072 | 2044 | 2072 | 2044 | 2072
| Option 1: Tunnel in 2012 (base case) | £m | 09/10
| Option 2: Mitigation upto 2044 | £m | 09/10 | 287.8248 |  | 12.6752 |  | -42.0303
| Option 3: Mitigation upto 2044 then tunnel | £m | 09/10 |  | 313.4348 |  | 21.3493 |  | -26.2589

## FOOTNOTES
Footnote. | Notes
1 | These probabilities are absolute probabilities based on a decision tree and are calculated by multiplying the different relevant probabilities on the relevant branch of a decision tree.
2 | Probability calculated on the basis that there is a 20% chance that the lease would be lost by 2044, this is equivalent to NGGT's calculations set out in response to SQ54.
3 | Based on NG forecast that a reduction in Easington area capability could result in 78-103 days of constraints per year, which could result in buyback costs …[…]. See slide 21 of NG presentation to Ofgem on 7Feb2018.
4 | Assumed that remediation could be minor or major (weighted using probability of each) - NGGT assumed Major which is not reasonable or in line with probabilities presented to Ofgem.
5 | The revenue profile to NGGT for a tunnel commissioned in 2045/46 commences in 2037/38 (assuming an eight-year construction phase).
6 | The constraint cost estimates are divided by 2 to reflect the assumption that failure of the pipeline during the winter peak period of 78-103 days would occur at the mid-point of the period.
7
8
9
10
11
12