## Slide 1: NGN recommend that Ofgem amend the methodology used to calculate the pressure / MEG impact figure (row 17, table 2.17)
NGN’s main concerns about Ofgem’s current approach
NGN’s suggested solution
The methodology detailed in slides 2 to 5 calculates the impact of pressure and MEG using that year’s low pressure leakage amount only.
Our recommended methodology better reflects the shrinkage modelling assumptions. This is because pressure and MEG levels only influence the calculation of LP leakage in the shrinkage model.
Medium pressure mains are included in the pressure / MEG impact calculation. However, only pressure / MEG influences the low pressure leakage calculation in the shrinkage model
Problem 1

## Slide 2: Step 1: Establish network low pressure leakage
Step 1 Description
Steps to carry out in the shrinkage model
Value to be copied into another excel spreadsheet
Step 1: Open up the shrinkage model used to calculate FY 2020/21’s forecast. Go to the tab named “Emissions Reporting Summary” and copy the figure in cell B8 to another excel spreadsheet. This figure is total network LP leakage.
Problem 1

## Slide 3: Step 2: Calculating REPEX impact
Step 2 Description
REPEX impact calculation
In LP North and North East tabs set all system pressure network nodes to 30 mbarg and all MEG saturation network nodes to 25%. This cancels out the reference pressures and MEG % leaving only pipe length and rates in the calculation,
Steps to carry out in the shrinkage model
Value to be copied into another excel spreadsheet
After setting the correction factors to their respective reference rates. Go to the tab named “Emissions Reporting Summary” and copy Cell B8 to another excel spreadsheet.
Problem 1

## Slide 4: Step 3: Calculating Pressure impact
Step 3 Description
Steps to carry out in the shrinkage model
Value to be copied into another excel spreadsheet
After setting the pressure correction factor to 30 mbarg. Go to the tab named “Emissions Reporting Summary” and copy Cell B8 to another excel spreadsheet.
Calculate system pressure impact
  Step 3(a): In LP North and North East tabs set all system pressure network nodes to 30 mbarg
  Step 3(a): This removes the pressure correction factor from the leakage calculation
  Step 3(b): Calculate the difference between LP Pressure leakage and total LP leakage in the GD2 forecast
Problem 1

## Slide 5: Step 4: Calculating MEG impact
Step 4 Description
Steps to carry out in the shrinkage model
Value to be copied into another excel spreadsheet
After setting the MEG correction factor to 25%. Go to the tab named “Emissions Reporting Summary” and copy Cell B8 to another excel spreadsheet.
Calculate the MEG impact
  Step 4(a): In LP North and North East tabs set all MEG saturation network nodes to 25%
  Step 4(a): This removes the MEG correction factor from the leakage calculation
  Step 4(b): Calculate the difference between LP MEG leakage and total LP leakage in the GD2 forecast
Problem 1

## Slide 6: NGN recommend that Ofgem amend the methodology used to calculate leakage @ benchmark pressure / MEG (row 16, table 2.17)
NGN’s main concerns about Ofgem’s current approach
NGN’s suggested solution
NGN have accounted for this operational requirement of increased system pressure YoY in their GD2 shrinkage forecast (see graph 1).
The leakage benchmark target (row 16, table 2.17) that NGN are being instructed to achieve should be based on the pressure / MEG figures we submitted in our plan.
To calculate the benchmark target Ofgem could split the pressure / MEG impact from the low pressure leakage figure that we’ve submitted in our GD2 forecast.
The graph on slide 7 outlines the pressure / MEG impact figures using the steps outlined in slides 2-5. NGN would be in support of being held to these impact measures, subject to them being revised to account for COVID-19.
The proposed Ofgem methodology would lead GDN’s who are forecasting increases in their system pressure to be in a penalty situation for most years of GD2.
In many instances increases in system pressure are the best outcome for our customers. The main driver for our pressure increases is to reduce the overall cost and disruption of reinforcement. This improves the customer experience.
Penalizing networks on account of this is unjustified and unfair.
Problem 2
Chart: Formula Year
| GD1 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | average | GD2
Barg | 31.5304 | 31.7577 | 31.8831 | 32.1077 | 32.3165 | 32.5358
Graph 1: Avg. system pressure figures submitted in GD2 plan

## Slide 7: NGN are forecasting a continuation of the excellent work they’ve carried out in GD1
Chart: Formula Year
| 2013/14 | 2014/15 | 2015/16 | 2016/17 | 2017/18 | 2018/19 | 2019/20 | 2020/21 | 2021/22 | 2022/23 | 2023/24 | 2024/25 | 2025/26 | RIIO GD1 | RIIO GD2
REPEX impact on LP network (GWh) | 291.0227 | 274.6828 | 260.8187 | 245.7598 | 236.0524 | 222.6747 | 207.3079 | 193.9301 | 181.0612 | 167.8452 | 155.0741 | 142.7058 | 130.3593
Pressure impact on LP network (GWh) | 19.8747 | 9.6782 | 11.4882 | 7.2433 | 6.925 | 10.8046 | 3.3849 | 10.6006 | 7.0223 | 7.1924 | 7.8193 | 8.1816 | 8.39
MEG impact on LP network (GWh) | 1.1747 | 2.2405 | 1.6846 | 1.4964 | 0.73505 | 0.82434 | 1.2886 | 0.74149 | 0.67605 | 0.62322 | 0.58448 | 0.54761 | 0.52225
Shrinkage - RRP submission (GWh) | 425.4221 | 399.1233 | 384.9966 | 364.1682 | 352.0707 | 340.5264
Shrinkage Forecast (GWh) | 340.5264 | 319.1354 | 312.2354 | 295.0001 | 281.1773 | 267.9299 | 254.7831 | 241.5325
The REPEX, pressure and MEG impact has been derived using the LP leakage figure calculated in that year only.
Pressure & MEG only influence LP leakage in the shrinkage model