## SC DEMAND
Based on Actual Recorded Daily Demand from April 2013 - March 2020
| Minimum Design Pressure (mbar) |  |  |  | 21 |  | Average LDZ Pressures | 2017/18 | 2018/19 | 2019/20 | Average
| SC 3-Year Average Pressure (mbar) |  |  |  | 26.42 |  |  | 26.54 | 26.42 | 26.31 | 26.4233
Average Annual Demand (mscm)
|  | SNT | Cold | Warm
| 2020 | 127718 | 173660 | 91439
| % Difference |  | -35.97% | 28.41%
|  |  | 1.3957 | 0.7159
| Available Pressure Differential (mbar) |  |  |  | 5.42
| Cold Deadband Pressure (mbar) |  |  |  | 7.5647 | 2.1447 | mbar
| Warm Deadband Pressure (mbar) |  |  |  | 3.8802 | -1.5398 | mbar
Average Annual Peak Demand % (AVE, HIGH, LOW Years)
| AVERAGE | 40.51%
| HIGH | 43.47%
| LOW | 37.53%
HIGH
| % Demand Diff | Square
| 1.073 | 1.1514
| Average Pressure Differential (mbar) |  |  |  | 5.42
| HIGH Deadband Pressure Diff (mbar) |  |  |  | 6.2406
| HIGH Deadband Threshold (mbar) |  |  |  | 0.82056
LOW
| % Demand Diff | Square
| 0.92641 | 0.85823
| Average Pressure Differential (mbar) |  |  |  | 5.42
| LOW Deadband Pressure Diff (mbar) |  |  |  | 4.6516 | Absolute Value
| LOW Deadband Threshold (mbar) |  |  |  | -0.76841 | 0.76841
| Average (+/-) |  |  |  | 0.79448 | mbar
Note on F27: Difference between 3-Year Average Pressure and Design Temperature
Note on F29: Average Pressure Differential * Square of % Demand Diff.
Note on F30: Cold Deadband Pressure Differential - Average Pressure Differential

## SE DEMAND
Based on Actual Recorded Daily Demand from April 2013 - March 2020
| Minimum Design Pressure (mbar) |  |  |  | 21 |  | Average LDZ Pressures | 2017/18 | 2018/19 | 2019/20 | Average
| SE 3-Year Average Pressure (mbar) |  |  |  | 26.39 |  |  | 26.41 | 26.55 | 26.2 | 26.3867
Average Annual Demand (mscm)
|  | SNT | Cold | Warm
| 2020 | 139958 | 209229 | 87667
| % Difference |  | -49.49% | 37.36%
|  |  | 1.4949 | 0.6264
| Available Pressure Differential (mbar) |  |  |  | 5.39
| Cold Deadband Pressure (mbar) |  |  |  | 8.0575 | 2.6675 | mbar
| Warm Deadband Pressure (mbar) |  |  |  | 3.3763 | -2.0137 | mbar
Average Annual Peak Demand % (AVE, HIGH, LOW Years)
| AVERAGE | 31.87%
| HIGH | 34.38%
| LOW | 30.18%
HIGH
| % Demand Diff | Square
| 1.0787 | 1.1636
| Average Pressure Differential (mbar) |  |  |  | 5.39
| HIGH Deadband Pressure Diff (mbar) |  |  |  | 6.2719
| HIGH Deadband Threshold (mbar) |  |  |  | 0.88188
LOW
| % Demand Diff | Square
| 0.94693 | 0.89668
| Average Pressure Differential (mbar) |  |  |  | 5.39
| LOW Deadband Pressure Diff (mbar) |  |  |  | 4.8331 | Absolute Value
| LOW Deadband Threshold (mbar) |  |  |  | -0.55692 | 0.55692
| Average (+/-) |  |  |  | 0.7194 | mbar

## SO DEMAND
Based on Actual Recorded Daily Demand from April 2013 - March 2020
| Minimum Design Pressure (mbar) |  |  |  | 21 |  | Average LDZ Pressures | 2017/18 | 2018/19 | 2019/20 | Average
| SO 3-Year Average Pressure (mbar) |  |  |  | 26.89 |  |  | 27.01 | 26.93 | 26.72 | 26.8867
Average Annual Demand (mscm)
|  | SNT | Cold | Warm
| 2020 | 105281 | 151319 | 72249
| % Difference |  | -43.73% | 31.38%
|  |  | 1.4373 | 0.6862
| Available Pressure Differential (mbar) |  |  |  | 5.89
| Cold Deadband Pressure (mbar) |  |  |  | 8.4657 | 2.5757 | mbar
| Warm Deadband Pressure (mbar) |  |  |  | 4.0417 | -1.8483 | mbar
Average Annual Peak Demand % (AVE, HIGH, LOW Years)
| AVERAGE | 30.83%
| HIGH | 33.3%
| LOW | 28.85%
HIGH
| % Demand Diff | Square
| 1.08 | 1.1664
| Average Pressure Differential (mbar) |  |  |  | 5.89
| HIGH Deadband Pressure Diff (mbar) |  |  |  | 6.8703
| HIGH Deadband Threshold (mbar) |  |  |  | 0.98031
LOW
| % Demand Diff | Square
| 0.93569 | 0.87552
| Average Pressure Differential (mbar) |  |  |  | 5.89
| LOW Deadband Pressure Diff (mbar) |  |  |  | 5.1568 | Absolute Value
| LOW Deadband Threshold (mbar) |  |  |  | -0.73321 | 0.73321
| Average (+/-) |  |  |  | 0.85676 | mbar

## Historical 7Y Average
SCOTLAND | [6 empty] | SOUTH-EAST | [6 empty] | SOUTH
| SC 2012/13 | [6 empty] | SE 2012/13 | [6 empty] | SO 2012/13
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 48.45% | 55.65% | [5 empty] | 34.35% | 44.35% | [5 empty] | 34.09% | 44.09%
| SC 2013/14 | [6 empty] | SE 2013/14 | [6 empty] | SO 2013/14
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 43.47% | 51.09% | HIGH DEMAND |  |  |  |  | 31.94% | 41.94% | [5 empty] | 31.17% | 41.17%
| SC 2014/15 | [6 empty] | SE 2014/15 | [6 empty] | SO 2014/15
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 41.92% | 49.55% | [5 empty] | 30.18% | 40.18% | LOW DEMAND |  |  |  |  | 29.85% | 39.85%
| SC 2015/16 | [6 empty] | SE 2015/16 | [6 empty] | SO 2015/16
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 42.03% | 49.77% | [5 empty] | 31.28% | 41.28% | [5 empty] | 28.85% | 38.85% | LOW DEMAND
| SC 2016/17 | [6 empty] | SE 2016/17 | [6 empty] | SO 2016/17
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 39.07% | 46.99% | [5 empty] | 33.42% | 43.42% | [5 empty] | 31.55% | 41.55%
| SC 2017/18 | [6 empty] | SE 2017/18 | [6 empty] | SO 2017/18
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 40.53% | 48.24% | [5 empty] | 34.38% | 44.38% | HIGH DEMAND |  |  |  |  | 33.3% | 43.3% | HIGH DEMAND
| SC 2018/19 | [6 empty] | SE 2018/19 | [6 empty] | SO 2018/19
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 37.53% | 45.48% | LOW DEMAND |  |  |  |  | 30.63% | 40.63% | [5 empty] | 31.06% | 41.06%
| SC 2019/20 | [6 empty] | SE 2019/20 | [6 empty] | SO 2019/20
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 39.03% | 46.92% | [5 empty] | 31.27% | 41.27% | [5 empty] | 30.05% | 40.05%
| SC 7-Year Averages | [6 empty] | SE 7-Year Averages | [6 empty] | SO 7-Year Averages
| % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour | [5 empty] | % of 1:20 Firm Daily Demand | Actual Firm Peak Hour
| 40.51% | 48.29% | [5 empty] | 31.87% | 41.87% | [5 empty] | 30.83% | 40.83%
| Minimum Design Pressure |  |  | 21 | mbar |  |  | Minimum Design Pressure |  |  | 21 | mbar |  |  | Minimum Design Pressure |  |  | 21 | mbar
| 3-Year Average Pressure (LDZ) |  |  | 26.42 | mbar |  |  | 3-Year Average Pressure (LDZ) |  |  | 26.3867 | mbar |  |  | 3-Year Average Pressure (LDZ) |  |  | 26.89 | mbar
| Average Profile | 40.51% | [5 empty] | Average Profile | 31.87% | [5 empty] | Average Profile | 30.83%
| HIGH Profile | 43.47% | 2.959% | From AVE |  |  |  | HIGH Profile | 34.38% | 2.509% | From AVE |  |  |  | HIGH Profile | 33.3% | 2.467% | From AVE
| LOW Profile | 37.53% | 2.981% | From AVE |  |  |  | LOW Profile | 30.18% | 1.691% | From AVE |  |  |  | LOW Profile | 28.85% | 1.983% | From AVE
| HIGH | [6 empty] | HIGH | [6 empty] | HIGH
| % Demand Diff | Square | [5 empty] | % Demand Diff | Square | [5 empty] | % Demand Diff | Square
| 1.073 | 1.1514 | [5 empty] | 1.0787 | 1.1636 | [5 empty] | 1.08 | 1.1664
| LOW | [6 empty] | LOW | [6 empty] | LOW
| % Demand Diff | Square | [5 empty] | % Demand Diff | Square | [5 empty] | % Demand Diff | Square
| 0.92641 | 0.85823 | [5 empty] | 0.94693 | 0.89668 | [5 empty] | 0.93569 | 0.87552
| Average Pressure Differential |  |  | 5.42 | mbar |  |  | Average Pressure Differential |  |  | 5.3867 | mbar |  |  | Average Pressure Differential |  |  | 5.89 | mbar
[6 empty] | Diff | [6 empty] | Diff | [6 empty] | Diff
| HIGH Deadband Pressure Differential |  |  | 6.2406 | mbar | 0.82056 |  | HIGH Deadband Pressure Differential |  |  | 6.268 | mbar | 0.88133 |  | HIGH Deadband Pressure Differential |  |  | 6.8703 | mbar | 0.98031
| LOW Deadband Pressure Differential |  |  | 4.6516 | mbar | 0.76841 |  | LOW Deadband Pressure Differential |  |  | 4.8301 | mbar | 0.55657 |  | LOW Deadband Pressure Differential |  |  | 5.1568 | mbar | 0.73321
| Deadband Pressure Threshold (+/-) |  |  | 0.79448 | mbar |  |  | Deadband Pressure Threshold (+/-) |  |  | 0.71895 | mbar |  |  | Deadband Pressure Threshold (+/-) |  |  | 0.85676 | mbar
| SGN Average Pressure Differential (+/-) |  |  | 0.79007 | mbar